## JULY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L.GUANZON
[13 empty] | 10pm - 6am | ORLANDO L. OCAMPO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26238 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 82467325 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 28984330 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6329702 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 99 | 82471459 | 4134 | 99.216 | 4.134 | 5.2 | 5.2 | 2B | 0 | 0 | 1065 | 0 | 1110 | N/A | N/A | N/A | N/A | 28985042 | 712 | 172.2303 | 0% | 0% | 100% | 0% | 100% | 35% | 6330535 | 833 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 95 | 82475406 | 3947 | 94.728 | 3.947 | 6.3 | 6.3 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 28985698 | 656 | 166.2022 | 0% | 0% | 100% | 0% | 100% | 35% | 6331554 | 1019 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 82479279 | 3873 | 92.952 | 3.873 | 7.4 | 7.4 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 28986330 | 632 | 163.181 | 0% | 0% | 100% | 0% | 100% | 35% | 6332668 | 1114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 98 | 82483171 | 3892 | 93.408 | 3.892 | 8.7 | 8.7 | 2B | 0 | 0 | 965 | 0 | 1110 | N/A | N/A | N/A | N/A | 28986942 | 612 | 157.2456 | 0% | 0% | 100% | 0% | 100% | 35% | 6333870 | 1202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 108 | 82487375 | 4204 | 100.896 | 4.204 | 9.5 | 9.5 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 28987594 | 652 | 155.0904 | 0% | 0% | 100% | 0% | 100% | 35% | 6334751 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 124 | 82492083 | 4708 | 112.992 | 4.708 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1110 | N/A | N/A | N/A | N/A | 28988348 | 754 | 160.1529 | 0% | 0% | 100% | 0% | 100% | 0% | 6334751 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 152 | 82498307 | 6224 | 149.376 | 6.224 | 9 | 9 | 3B+1S | 0 | 1040 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28989724 | 1376 | 221.0797 | 0% | 0% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 82504521 | 6214 | 149.136 | 6.214 | 8.4 | 8.4 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28991044 | 1320 | 212.4236 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 151 | 82510780 | 6259 | 150.216 | 6.259 | 7.6 | 7.6 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28992496 | 1452 | 231.9859 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 82517083 | 6303 | 151.272 | 6.303 | 6.9 | 6.9 | 3B+1S | 0 | 1092 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28993902 | 1406 | 223.0684 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 82523121 | 6038 | 144.912 | 6.038 | 6.3 | 6.3 | 3B+1S | 0 | 1091 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28995252 | 1350 | 223.584 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 82529232 | 6111 | 146.664 | 6.111 | 5.6 | 5.6 | 3B+1S | 0 | 1101 | 1163 | 1185 | 1197 | N/A | N/A | N/A | N/A | 28996638 | 1386 | 226.8041 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 139 | 82535201 | 5969 | 143.256 | 5.969 | 5.2 | 5.2 | 3B+1S | 0 | 1029 | 1168 | 1185 | 1198 | N/A | N/A | N/A | N/A | 28997962 | 1324 | 221.8127 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 82541086 | 5885 | 141.24 | 5.885 | 5 | 5 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 28999302 | 1340 | 227.6975 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 132 | 82546714 | 5628 | 135.072 | 5.628 | 4.9 | 4.9 | 3B+1S | 0 | 916 | 1199 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29000580 | 1278 | 227.0789 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 136 | 82552376 | 5662 | 135.888 | 5.662 | 4.8 | 4.8 | 3B+1S | 0 | 819 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29001886 | 1306 | 230.6605 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 82558179 | 5803 | 139.272 | 5.803 | 4.7 | 4.7 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29003206 | 1320 | 227.4686 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 138 | 82563836 | 5657 | 135.768 | 5.657 | 4.6 | 4.6 | 3B+1S | 0 | 1029 | 1145 | 1185 | 1150 | N/A | N/A | N/A | N/A | 29004442 | 1236 | 218.4904 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 139 | 82569508 | 5672 | 136.128 | 5.672 | 4.3 | 4.3 | 3B+1S | 0 | 1029 | 1156 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29005688 | 1246 | 219.6756 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 130 | 82575057 | 5549 | 133.176 | 5.549 | 3.9 | 3.9 | 3B+1S | 0 | 1004 | 1136 | 1185 | 1140 | N/A | N/A | N/A | N/A | 29006910 | 1222 | 220.2199 | 0% | 100% | 100% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 131 | 82580662 | 5605 | 134.52 | 5.605 | 3 | 3 | 2B+1S | 0 | 1100 | 0 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29008026 | 1116 | 199.1079 | 0% | 100% | 0% | 100% | 100% | 0% | 6334751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 125 | 82586112 | 5450 | 130.8 | 5.45 | 2.5 | 2.5 | 2B+1S | 0 | 1045 | 0 | 1185 | 1200 | N/A | N/A | N/A | N/A | 29009106 | 1080 | 198.1651 | 0% | 100% | 0% | 100% | 100% | 0% | 6334751 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 109 | 82590618 | 4506 | 108.144 | 4.506 | 2.9 | 2.9 | 2B | 0 | 0 | 0 | 1185 | 1012 | N/A | N/A | N/A | N/A | 29009870 | 764 | 169.5517 | 0% | 0% | 0% | 100% | 100% | 25% | 6335524 | 773 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 101 | 82594807 | 4189 | 100.536 | 4.189 | 3.9 | 3.9 | 2B | 0 | 0 | 0 | 1185 | 940 | N/A | N/A | N/A | N/A | 29010568 | 698 | 166.6269 | 0% | 0% | 0% | 100% | 100% | 25% | 6336358 | 834 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.625 | 127482 | 127482 | 127.482 | 127.482 | [12 empty] | 26238 | 26238 | 205.8173 | [6 empty] | 6656 | 6656 | 0.96833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:37 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:45 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP1 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:31 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm
WATER NETWORK | [12 empty] | 2pm - 10pm
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26406 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 82594807 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29010568 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6336358 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 96 | 82599019 | 4212 | 101.088 | 4.212 | 4.8 | 4.8 | 2B | 0 | 0 | 1055 | 0 | 1076 | N/A | N/A | N/A | N/A | 29011282 | 714 | 169.5157 | 0% | 0% | 100% | 0% | 100% | 35% | 6337246 | 888 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | FRANCIS M. CARREON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 94 | 82602708 | 3689 | 88.536 | 3.689 | 6.1 | 6.1 | 2B | 0 | 0 | 1055 | 0 | 1049 | N/A | N/A | N/A | N/A | 29011886 | 604 | 163.73 | 0% | 0% | 100% | 0% | 100% | 35% | 6338165 | 919 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 92 | 82606497 | 3789 | 90.936 | 3.789 | 7.3 | 7.3 | 2B | 0 | 0 | 1035 | 0 | 1026 | N/A | N/A | N/A | N/A | 29012482 | 596 | 157.2974 | 0% | 0% | 100% | 0% | 100% | 35% | 6339354 | 1189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | ROBERTO M. QUINIO
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 92 | 82610327 | 3830 | 91.92 | 3.83 | 8.4 | 8.4 | 2B | 0 | 0 | 1035 | 0 | 1017 | N/A | N/A | N/A | N/A | 29013074 | 592 | 154.5692 | 0% | 0% | 100% | 0% | 100% | 35% | 6340480 | 1126 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ARTURO M. TRINIDAD
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 136 | 106 | 82614557 | 4230 | 101.52 | 4.23 | 9.3 | 9.3 | 2B | 0 | 0 | 1035 | 0 | 1122 | N/A | N/A | N/A | N/A | 29013722 | 648 | 153.1915 | 0% | 0% | 100% | 0% | 100% | 35% | 6341353 | 873 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 127 | 124 | 82619402 | 4845 | 116.28 | 4.845 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29014562 | 840 | 173.3746 | 0% | 0% | 100% | 0% | 100% | 0% | 6341496 | 143 | 0.85 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 146 | 82625639 | 6237 | 149.688 | 6.237 | 8.9 | 8.9 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29015942 | 1380 | 221.2602 | 0% | 0% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 154 | 82631957 | 6318 | 151.632 | 6.318 | 8.2 | 8.2 | 3B+1S | 0 | 1118 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29017350 | 1408 | 222.8553 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 150 | 82638281 | 6324 | 151.776 | 6.324 | 7.2 | 7.2 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29018778 | 1428 | 225.8065 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 82644439 | 6158 | 147.792 | 6.158 | 6.6 | 6.6 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29020158 | 1380 | 224.0987 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 82650676 | 6237 | 149.688 | 6.237 | 5.8 | 5.8 | 3B+1S | 0 | 1147 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 29021578 | 1420 | 227.6736 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 82656751 | 6075 | 145.8 | 6.075 | 5.1 | 5.1 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29022964 | 1386 | 228.1481 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 82662604 | 5853 | 140.472 | 5.853 | 4.8 | 4.8 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29024290 | 1326 | 226.5505 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 134 | 82668460 | 5856 | 140.544 | 5.856 | 4.6 | 4.6 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29025630 | 1340 | 228.8251 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 135 | 82674069 | 5609 | 134.616 | 5.609 | 4.5 | 4.5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29026922 | 1292 | 230.3441 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 140 | 82679733 | 5664 | 135.936 | 5.664 | 4.4 | 4.4 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29028238 | 1316 | 232.3446 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 82685444 | 5711 | 137.064 | 5.711 | 4.3 | 4.3 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29029546 | 1308 | 229.0317 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 82691126 | 5682 | 136.368 | 5.682 | 4.2 | 4.2 | 3B+1S | 0 | 980 | 1175 | 1185 | 1174 | N/A | N/A | N/A | N/A | 29030842 | 1296 | 228.0887 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 135 | 82696808 | 5682 | 136.368 | 5.682 | 4 | 4 | 3B+1S | 0 | 999 | 1175 | 1185 | 1174 | N/A | N/A | N/A | N/A | 29032095 | 1253 | 220.5209 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 133 | 82702426 | 5618 | 134.832 | 5.618 | 3.9 | 3.9 | 3B+1S | 0 | 978 | 1189 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29033381 | 1286 | 228.9071 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 82707881 | 5455 | 130.92 | 5.455 | 3.2 | 3.2 | 2B+1S | 0 | 1112 | 1186 | 0 | 1190 | N/A | N/A | N/A | N/A | 29034486 | 1105 | 202.5665 | 0% | 100% | 100% | 100% | 100% | 0% | 6341496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 125 | 82713340 | 5459 | 131.016 | 5.459 | 2.5 | 2.5 | 2B+1S | 0 | 1060 | 1194 | 0 | 1190 | N/A | N/A | N/A | N/A | 29035582 | 1096 | 200.7694 | 0% | 100% | 100% | 0% | 100% | 0% | 6341496 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 104 | 82717901 | 4561 | 109.464 | 4.561 | 3 | 3 | 2B | 0 | 0 | 1053 | 0 | 1110 | N/A | N/A | N/A | N/A | 29036326 | 744 | 163.1221 | 0% | 0% | 100% | 0% | 100% | 25% | 6342087 | 591 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 94 | 82722074 | 4173 | 100.152 | 4.173 | 3.9 | 3.9 | 2B | 0 | 0 | 1060 | 0 | 1110 | N/A | N/A | N/A | N/A | 29036974 | 648 | 155.284 | 0% | 0% | 100% | 0% | 100% | 25% | 6342933 | 846 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.5417 | 127267 | 127267 | 127.267 | 127.267 | [12 empty] | 26406 | 26406 | 207.4851 | [6 empty] | 6575 | 6575 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
BP1 STARTED @ 12:01 AM / BP2 STOPPED @ 12:01AM
XCV1 CLOSED @ 4:57 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ORLANDO L. OCAMPO
WATER NETWORK | [12 empty] | 2pm - 10pm
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26796 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 82722074 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29036974 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6342933 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 94 | 82726060 | 3986 | 95.664 | 3.986 | 5.1 | 5.1 | 2B | 0 | 0 | 1032 | 0 | 1110 | N/A | N/A | N/A | N/A | 29037650 | 676 | 169.5936 | 0% | 0% | 100% | 0% | 100% | 35% | 6343894 | 961 |  | Additional 3 psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | FRANCIS M. CARREON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 82729839 | 3779 | 90.696 | 3.779 | 6.2 | 6.2 | 2B | 0 | 0 | 983 | 0 | 1110 | N/A | N/A | N/A | N/A | 29038282 | 632 | 167.24 | 0% | 0% | 100% | 0% | 100% | 35% | 6344997 | 1103 | 0.88 | Additional 3 psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 87 | 82733589 | 3750 | 90 | 3.75 | 7.4 | 7.4 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 29038890 | 608 | 162.1333 | 0% | 0% | 100% | 0% | 100% | 35% | 6346169 | 1172 |  | Additional 3 psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | ROBERTO M. QUINIO
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 91 | 82737274 | 3685 | 88.44 | 3.685 | 8.7 | 8.7 | 2B | 0 | 0 | 940 | 0 | 1110 | N/A | N/A | N/A | N/A | 29039478 | 588 | 159.5658 | 0% | 0% | 100% | 0% | 100% | 35% | 6347291 | 1122 |  | Additional 3 psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ARTURO M. TRINIDAD
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 104 | 82741349 | 4075 | 97.8 | 4.075 | 9.5 | 9.5 | 2B | 0 | 0 | 1042 | 0 | 1110 | N/A | N/A | N/A | N/A | 29040122 | 644 | 158.0368 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 911 |  | Additional 3 psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 129 | 82746342 | 4993 | 119.832 | 4.993 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29040958 | 836 | 167.4344 | 0% | 0% | 100% | 0% | 100% | 0% | 6348202 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 82752256 | 5914 | 141.936 | 5.914 | 9 | 9 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29042274 | 1316 | 222.5228 | 0% | 0% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 82758496 | 6240 | 149.76 | 6.24 | 8.5 | 8.5 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29043650 | 1376 | 220.5128 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 82764712 | 6216 | 149.184 | 6.216 | 7.8 | 7.8 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29045042 | 1392 | 223.9382 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 82770974 | 6262 | 150.288 | 6.262 | 7.1 | 7.1 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29046428 | 1386 | 221.335 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 145 | 82777068 | 6094 | 146.256 | 6.094 | 6.5 | 6.5 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29047812 | 1384 | 227.1086 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 82783099 | 6031 | 144.744 | 6.031 | 5.8 | 5.8 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29049178 | 1366 | 226.4964 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 138 | 82788987 | 5888 | 141.312 | 5.888 | 5.6 | 5.6 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29050512 | 1334 | 226.5625 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 82794726 | 5739 | 137.736 | 5.739 | 5.3 | 5.3 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29051850 | 1338 | 233.1417 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 82800486 | 5760 | 138.24 | 5.76 | 5.2 | 5.2 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29053104 | 1254 | 217.7083 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 82806229 | 5743 | 137.832 | 5.743 | 5 | 5 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29054394 | 1290 | 224.6213 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 82812076 | 5847 | 140.328 | 5.847 | 4.7 | 4.7 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29055726 | 1332 | 227.8091 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 82817712 | 5636 | 135.264 | 5.636 | 4.6 | 4.6 | 3B+1S | 0 | 986 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 29057014 | 1288 | 228.5309 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 139 | 82823269 | 5557 | 133.368 | 5.557 | 4.5 | 4.5 | 3B+1S | 0 | 1000 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29058278 | 1264 | 227.4609 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 82828869 | 5600 | 134.4 | 5.6 | 4.5 | 4.5 | 3B | 0 | 0 | 1150 | 1185 | 1139 | N/A | N/A | N/A | N/A | 29059550 | 1272 | 227.1429 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 128 | 82834419 | 5550 | 133.2 | 5.55 | 4.5 | 4.5 | 3B | 0 | 0 | 1114 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29060622 | 1072 | 193.1532 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 122 | 82839556 | 5137 | 123.288 | 5.137 | 4.5 | 4.5 | 3B | 0 | 0 | 1064 | 1185 | 1067 | N/A | N/A | N/A | N/A | 29061670 | 1048 | 204.0101 | 0% | 100% | 100% | 0% | 100% | 0% | 6348202 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 100 | 109 | 82844068 | 4512 | 108.288 | 4.512 | 4.5 | 4.5 | 3B | 0 | 0 | 1096 | 1185 | 1099 | N/A | N/A | N/A | N/A | 29062714 | 1044 | 231.383 | 0% | 0% | 100% | 0% | 100% | 25% | 6348202 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 92 | 100 | 82848296 | 4228 | 101.472 | 4.228 | 4.5 | 4.5 | 3B | 0 | 0 | 1025 | 1185 | 1028 | N/A | N/A | N/A | N/A | 29063770 | 1056 | 249.7635 | 0% | 0% | 100% | 0% | 100% | 25% | 6348202 | 2700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.1667 | 126222 | 126222 | 126.222 | 126.222 | [12 empty] | 26796 | 26796 | 212.2926 | [6 empty] | 5269 | 8469 | 0.95333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:55 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am ( july 4 ) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED (25%) @ 10:01 PM FOR REFILLING
BP2 - STARTED @ 10:28 PM FOR REFILLING
NORMAL OPERATION

## JULY 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ORLANDO L. OCAMPO
WATER NETWORK | [12 empty] | 2pm - 10pm | GUANZON, DENNIS L.
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25856 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 82848296 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29063770 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6348202 |  | mg /l |  | Automatic - i2O | AI | MALLARI, REIVIN M.
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 99 | 82852482 | 4186 | 100.464 | 4.186 | 9.5 | 9.5 | 2B | 0 | 0 | 1046 | 0 | 1048 | N/A | N/A | N/A | N/A | 29064700 | 930 | 222.1691 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GUANZON, DENNIS L.
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 91 | 82856548 | 4066 | 97.584 | 4.066 | 9.5 | 9.5 | 2B | 0 | 0 | 990 | 0 | 990 | N/A | N/A | N/A | N/A | 29065607 | 907 | 223.0694 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | OCAMPO, ORLANDO L.
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 93 | 82860703 | 4155 | 99.72 | 4.155 | 9.5 | 9.5 | 2B | 0 | 0 | 984 | 0 | 998 | N/A | N/A | N/A | N/A | 29066522 | 915 | 220.2166 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 88 | 82864279 | 3576 | 85.824 | 3.576 | 9.5 | 9.5 | 2B | 0 | 0 | 974 | 0 | 968 | N/A | N/A | N/A | N/A | 29067018 | 496 | 138.7025 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 125 | 108 | 82868317 | 4038 | 96.912 | 4.038 | 9.5 | 9.5 | 2B | 0 | 0 | 1004 | 0 | 1009 | N/A | N/A | N/A | N/A | 29067538 | 520 | 128.7766 | 0% | 0% | 100% | 0% | 100% | 35% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 140 | 124 | 82873291 | 4974 | 119.376 | 4.974 | 9.5 | 9.5 | 2B | 0 | 0 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 29068326 | 788 | 158.4238 | 0% | 0% | 100% | 0% | 100% | 0% | 6348202 | 0 | 1.3 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 150 | 82879356 | 6065 | 145.56 | 6.065 | 9.1 | 9.1 | 3B+1S | 0 | 1028 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29069646 | 1320 | 217.6422 | 0% | 0% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 82885810 | 6454 | 154.896 | 6.454 | 8.7 | 8.7 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29071074 | 1428 | 221.2581 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 144 | 82891662 | 5852 | 140.448 | 5.852 | 8.2 | 8.2 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29072356 | 1282 | 219.0704 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 82897652 | 5990 | 143.76 | 5.99 | 7.6 | 7.6 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29073690 | 1334 | 222.7045 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 82903820 | 6168 | 148.032 | 6.168 | 7 | 7 | 3B+1S | 0 | 1090 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29075066 | 1376 | 223.0869 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 82909924 | 6104 | 146.496 | 6.104 | 6.4 | 6.4 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29076432 | 1366 | 223.7877 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 144 | 82915911 | 5987 | 143.688 | 5.987 | 6.2 | 6.2 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29077768 | 1336 | 223.1502 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 136 | 82921705 | 5794 | 139.056 | 5.794 | 6 | 6 | 3B+1S | 0 | 993 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29079088 | 1320 | 227.8219 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 0.98 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 137 | 82927384 | 5679 | 136.296 | 5.679 | 5.9 | 5.9 | 3B+1S | 0 | 991 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 29080342 | 1254 | 220.8135 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 82933009 | 5625 | 135 | 5.625 | 5.8 | 5.8 | 3B+1S | 0 | 991 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29081472 | 1130 | 200.8889 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 82938629 | 5620 | 134.88 | 5.62 | 5.7 | 5.7 | 3B+1S | 0 | 990 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29082627 | 1155 | 205.516 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 138 | 82944229 | 5600 | 134.4 | 5.6 | 5.5 | 5.5 | 3B+1S | 0 | 1017 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 29083777 | 1150 | 205.3571 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 138 | 82949842 | 5613 | 134.712 | 5.613 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 29084932 | 1155 | 205.7723 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 133 | 82955371 | 5529 | 132.696 | 5.529 | 5 | 5 | 3B+1S | 0 | 981 | 1114 | 1185 | 1119 | N/A | N/A | N/A | N/A | 29086068 | 1136 | 205.4621 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 126 | 82960833 | 5462 | 131.088 | 5.462 | 4.8 | 4.8 | 3B+1S | 0 | 972 | 1094 | 1185 | 1099 | N/A | N/A | N/A | N/A | 29087164 | 1096 | 200.6591 | 0% | 100% | 100% | 100% | 100% | 0% | 6348202 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 127 | 124 | 82965915 | 5082 | 121.968 | 5.082 | 4.6 | 4.6 | 3B+1S | 0 | 989 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29088234 | 1070 | 210.547 | 0% | 100% | 100% | 0% | 100% | 0% | 6348202 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 103 | 82970514 | 4599 | 110.376 | 4.599 | 5 | 5 | 2B | 0 | 0 | 1070 | 0 | 1100 | N/A | N/A | N/A | N/A | 29088978 | 744 | 161.7743 | 0% | 0% | 100% | 0% | 100% | 25% | 6348643 | 441 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 97 | 82974727 | 4213 | 101.112 | 4.213 | 5.6 | 5.6 | 2B | 0 | 0 | 960 | 0 | 1100 | N/A | N/A | N/A | N/A | 29089626 | 648 | 153.8096 | 0% | 0% | 100% | 0% | 100% | 25% | 6349262 | 619 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.2083 | 126431 | 126431 | 126.431 | 126.431 | [12 empty] | 25856 | 25856 | 204.5068 | [6 empty] | 1060 | 1060 | 1.005 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV4 OPENING INCREASED TO 25 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV4 CLOSED @ 12:45 AM,WATER ELEVATION 9.5M
BP2 - STOPPED @ 12:45 AM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
| BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE |  |  |  |  | BP2 STOPPED @ 9:01 PM
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:50 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ORLANDO L. OCAMPO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26652 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 82974727 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29089626 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6349262 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 96 | 82978723 | 3996 | 95.904 | 3.996 | 6.4 | 6.4 | 2B | 0 | 0 | 1030 | 0 | 1100 | N/A | N/A | N/A | N/A | 29090298 | 672 | 168.1682 | 0% | 0% | 100% | 0% | 100% | 35% | 6350080 | 818 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 92 | 82982599 | 3876 | 93.024 | 3.876 | 7.5 | 7.5 | 2B | 0 | 0 | 995 | 0 | 1100 | N/A | N/A | N/A | N/A | 29090928 | 630 | 162.5387 | 0% | 0% | 100% | 0% | 100% | 35% | 6351082 | 1002 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 88 | 82986362 | 3763 | 90.312 | 3.763 | 8.6 | 8.6 | 2B | 0 | 0 | 961 | 0 | 1100 | N/A | N/A | N/A | N/A | 29091560 | 632 | 167.9511 | 0% | 0% | 100% | 0% | 100% | 35% | 6352114 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 90 | 82990150 | 3788 | 90.912 | 3.788 | 9.5 | 9.5 | 2B | 0 | 0 | 923 | 0 | 1100 | N/A | N/A | N/A | N/A | 29092126 | 566 | 149.4192 | 0% | 0% | 100% | 0% | 100% | 35% | 6353031 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 93 | 82994034 | 3884 | 93.216 | 3.884 | 9.5 | 9.5 | 2B | 0 | 0 | 872 | 0 | 988 | N/A | N/A | N/A | N/A | 29092614 | 488 | 125.6437 | 0% | 0% | 100% | 0% | 100% | 35% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 82998473 | 4439 | 106.536 | 4.439 | 9.5 | 9.5 | 2B | 0 | 0 | 1114 | 0 | 1089 | N/A | N/A | N/A | N/A | 29093226 | 612 | 137.8689 | 0% | 0% | 100% | 0% | 100% | 0% | 6353031 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 150 | 145 | 83004409 | 5936 | 142.464 | 5.936 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29094442 | 1216 | 204.8518 | 0% | 0% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 148 | 83010524 | 6115 | 146.76 | 6.115 | 9.1 | 9.1 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29095778 | 1336 | 218.4791 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 153 | 83016838 | 6314 | 151.536 | 6.314 | 8.4 | 8.4 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29097178 | 1400 | 221.7295 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 83023223 | 6385 | 153.24 | 6.385 | 7.6 | 7.6 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29098610 | 1432 | 224.2756 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 151 | 83029652 | 6429 | 154.296 | 6.429 | 6.6 | 6.6 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29100060 | 1450 | 225.5405 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 149 | 83035947 | 6295 | 151.08 | 6.295 | 5.6 | 5.6 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29101516 | 1456 | 231.2947 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 148 | 83042157 | 6210 | 149.04 | 6.21 | 4.9 | 4.9 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29102912 | 1396 | 224.7987 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 146 | 83048281 | 6124 | 146.976 | 6.124 | 4.1 | 4.1 | 3B+1S | 0 | 1152 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29104284 | 1372 | 224.0366 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 145 | 83054339 | 6058 | 145.392 | 6.058 | 3.3 | 3.3 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29105648 | 1364 | 225.1568 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 83060336 | 5997 | 143.928 | 5.997 | 3 | 3 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29107030 | 1382 | 230.4486 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 83066226 | 5890 | 141.36 | 5.89 | 2.6 | 2.6 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29108378 | 1348 | 228.8625 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 136 | 83072008 | 5782 | 138.768 | 5.782 | 2.5 | 2.5 | 3B+1S | 0 | 1101 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29109754 | 1376 | 237.9799 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 135 | 83077696 | 5688 | 136.512 | 5.688 | 2.5 | 2.5 | 3B+1S | 0 | 1070 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29111158 | 1404 | 246.8354 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 135 | 83083250 | 5554 | 133.296 | 5.554 | 2.7 | 2.7 | 3B+1S | 0 | 1020 | 1154 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29112514 | 1356 | 244.1484 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 137 | 134 | 83088625 | 5375 | 129 | 5.375 | 3 | 3 | 3B+1S | 0 | 1020 | 1111 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29113780 | 1266 | 235.5349 | 0% | 100% | 100% | 100% | 100% | 0% | 6353031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 123 | 83093958 | 5333 | 127.992 | 5.333 | 2.5 | 2.5 | 2B+1S | 0 | 1062 | 1194 | 0 | 1199 | N/A | N/A | N/A | N/A | 29114816 | 1036 | 194.2621 | 0% | 100% | 100% | 0% | 100% | 0% | 6353031 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 106 | 83098585 | 4627 | 111.048 | 4.627 | 3.1 | 3.1 | 2B | 0 | 0 | 1082 | 0 | 1110 | N/A | N/A | N/A | N/A | 29115596 | 780 | 168.5758 | 0% | 0% | 100% | 0% | 100% | 25% | 6353610 | 579 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 103 | 83102929 | 4344 | 104.256 | 4.344 | 3.8 | 3.8 | 2B | 0 | 0 | 1003 | 0 | 1110 | N/A | N/A | N/A | N/A | 29116278 | 682 | 156.9982 | 0% | 0% | 100% | 0% | 100% | 25% | 6354334 | 724 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.875 | 128202 | 128202 | 128.202 | 128.202 | [12 empty] | 26652 | 26652 | 207.8907 | [6 empty] | 5072 | 5072 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:14 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (July 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED ( 13% ) @ 5:01 PM FOR REFILLING
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV4 - CLOSED @ 9:01 PM, WATER ELEVATION ( 3.0M)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ORLANDO L. OCAMPO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25450 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83102929 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29116278 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6354334 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 98 | 83107084 | 4155 | 99.72 | 4.155 | 4.9 | 4.9 | 2B | 0 | 0 | 1073 | 0 | 1110 | N/A | N/A | N/A | N/A | 29116986 | 708 | 170.3971 | 0% | 0% | 100% | 0% | 100% | 35% | 6355277 | 943 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 92 | 83111007 | 3923 | 94.152 | 3.923 | 6.2 | 6.2 | 2B | 0 | 0 | 1028 | 0 | 1110 | N/A | N/A | N/A | N/A | 29117650 | 664 | 169.2582 | 0% | 0% | 100% | 0% | 100% | 35% | 6356532 | 1255 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 89 | 83114840 | 3833 | 91.992 | 3.833 | 7.6 | 7.6 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 29118286 | 636 | 165.9275 | 0% | 0% | 100% | 0% | 100% | 35% | 6357847 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 93 | 83118652 | 3812 | 91.488 | 3.812 | 8.7 | 8.7 | 2B | 0 | 0 | 993 | 0 | 1110 | N/A | N/A | N/A | N/A | 29118906 | 620 | 162.6443 | 0% | 0% | 100% | 0% | 100% | 35% | 6358950 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 96 | 83122552 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1050 | N/A | N/A | N/A | N/A | 29119498 | 592 | 151.7949 | 0% | 0% | 100% | 0% | 100% | 35% | 6359706 | 756 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 114 | 109 | 83126907 | 4355 | 104.52 | 4.355 | 9.5 | 9.5 | 3B | 0 | 0 | 1087 | 0 | 1027 | N/A | N/A | N/A | N/A | 29120072 | 574 | 131.8025 | 0% | 0% | 100% | 0% | 100% | 0% | 6359706 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 83132477 | 5570 | 133.68 | 5.57 | 9.5 | 9.5 | 3B | 0 | 0 | 1132 | 1185 | 1129 | N/A | N/A | N/A | N/A | 29121156 | 1084 | 194.614 | 0% | 0% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 147 | 83138526 | 6049 | 145.176 | 6.049 | 9.4 | 9.4 | 3B+1S | 0 | 974 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29122434 | 1278 | 211.2746 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 83144660 | 6134 | 147.216 | 6.134 | 9 | 9 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29123794 | 1360 | 221.715 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 83150931 | 6271 | 150.504 | 6.271 | 8.3 | 8.3 | 3B+1S | 0 | 1092 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29125140 | 1346 | 214.6388 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 | 0.86 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 150 | 83157207 | 6276 | 150.624 | 6.276 | 7.5 | 7.5 | 3B+1S | 0 | 1113 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29126510 | 1370 | 218.2919 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 151 | 83163369 | 6162 | 147.888 | 6.162 | 6.7 | 6.7 | 3B+1S | 0 | 1116 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29127946 | 1436 | 233.0412 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 143 | 83169415 | 6046 | 145.104 | 6.046 | 6.1 | 6.1 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29129370 | 1424 | 235.5276 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 142 | 83175504 | 6089 | 146.136 | 6.089 | 5.5 | 5.5 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29130762 | 1392 | 228.609 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 83181398 | 5894 | 141.456 | 5.894 | 5.1 | 5.1 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29132106 | 1344 | 228.0285 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 83187103 | 5705 | 136.92 | 5.705 | 4.8 | 4.8 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29133438 | 1332 | 233.4794 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 83192854 | 5751 | 138.024 | 5.751 | 4.6 | 4.6 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29134746 | 1308 | 227.4387 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 134 | 83198586 | 5732 | 137.568 | 5.732 | 4.4 | 4.4 | 3B+1S | 0 | 1025 | 1135 | 1185 | 1140 | N/A | N/A | N/A | N/A | 29136030 | 1284 | 224.0056 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 135 | 83204304 | 5718 | 137.232 | 5.718 | 4 | 4 | 3B+1S | 0 | 1028 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 29137258 | 1228 | 214.7604 | 0% | 100% | 100% | 100% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 131 | 83209530 | 5226 | 125.424 | 5.226 | 3.3 | 3.3 | 2B+1S | 0 | 1062 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29138294 | 1036 | 198.2396 | 0% | 100% | 100% | 0% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 128 | 83214742 | 5212 | 125.088 | 5.212 | 2.8 | 2.8 | 2B+1S | 0 | 1034 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29139298 | 1004 | 192.6324 | 0% | 100% | 100% | 0% | 100% | 0% | 6359706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 126 | 83220089 | 5347 | 128.328 | 5.347 | 2.4 | 2.4 | 2B+1S | 0 | 1011 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29140332 | 1034 | 193.3795 | 0% | 100% | 100% | 0% | 100% | 0% | 6359706 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 105 | 83224570 | 4481 | 107.544 | 4.481 | 3 | 3 | 2B | 0 | 0 | 1057 | 0 | 1110 | N/A | N/A | N/A | N/A | 29141078 | 746 | 166.4807 | 0% | 0% | 100% | 0% | 100% | 25% | 6360369 | 663 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 98 | 83228706 | 4136 | 99.264 | 4.136 | 3.9 | 3.9 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 29141728 | 650 | 157.1567 | 0% | 0% | 100% | 0% | 100% | 25% | 6361210 | 841 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5833 | 125777 | 125777 | 125.777 | 125.777 | [12 empty] | 25450 | 25450 | 202.3422 | [6 empty] | 6876 | 6876 | 0.965 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 7) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ORLANDO L. OCAMPO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24662 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83228706 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29141728 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6361210 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 95 | 83232717 | 4011 | 96.264 | 4.011 | 5.2 | 5.2 | 2B | 0 | 0 | 1052 | 0 | 1110 | N/A | N/A | N/A | N/A | 29142406 | 678 | 169.0352 | 0% | 0% | 100% | 0% | 100% | 35% | 6362242 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 91 | 83236608 | 3891 | 93.384 | 3.891 | 6.3 | 6.3 | 2B | 0 | 0 | 999 | 0 | 1110 | N/A | N/A | N/A | N/A | 29143050 | 644 | 165.5102 | 0% | 0% | 100% | 0% | 100% | 35% | 6363351 | 1109 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 83240354 | 3746 | 89.904 | 3.746 | 7.6 | 7.6 | 2B | 0 | 0 | 957 | 0 | 1110 | N/A | N/A | N/A | N/A | 29143662 | 612 | 163.3743 | 0% | 0% | 100% | 0% | 100% | 35% | 6364530 | 1179 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 93 | 83244078 | 3724 | 89.376 | 3.724 | 8.7 | 8.7 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 29144254 | 592 | 158.9689 | 0% | 0% | 100% | 0% | 100% | 35% | 6365712 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 83248142 | 4064 | 97.536 | 4.064 | 9.5 | 9.5 | 2B | 0 | 0 | 952 | 0 | 1110 | N/A | N/A | N/A | N/A | 29144874 | 620 | 152.5591 | 0% | 0% | 100% | 0% | 100% | 35% | 6366481 | 769 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 114 | 83252846 | 4704 | 112.896 | 4.704 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29145630 | 756 | 160.7143 | 0% | 0% | 100% | 0% | 100% | 0% | 6366481 | 0 | 1.01 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 83258864 | 6018 | 144.432 | 6.018 | 9.1 | 9.1 | 3B+1S | 0 | 1031 | 1150 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29146948 | 1318 | 219.0096 | 0% | 0% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 83262095 | 3231 | 77.544 | 3.231 | 8.6 | 8.6 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29147664 | 716 | 221.6032 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 83268361 | 6266 | 150.384 | 6.266 | 8 | 8 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29148801 | 1137 | 181.4555 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 83274703 | 6342 | 152.208 | 6.342 | 7.4 | 7.4 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29150144 | 1343 | 211.7629 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 83281071 | 6368 | 152.832 | 6.368 | 6.9 | 6.9 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29151614 | 1470 | 230.8417 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 83287127 | 6056 | 145.344 | 6.056 | 6.4 | 6.4 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29153020 | 1406 | 232.1664 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 83293016 | 5889 | 141.336 | 5.889 | 6 | 6 | 3B+1S | 0 | 1021 | 1145 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29154326 | 1306 | 221.7694 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 136 | 83298741 | 5725 | 137.4 | 5.725 | 5.7 | 5.7 | 3B+1S | 0 | 1050 | 1104 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29155610 | 1284 | 224.2795 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 138 | 83304482 | 5741 | 137.784 | 5.741 | 5.2 | 5.2 | 3B+1S | 0 | 1050 | 1076 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29156860 | 1250 | 217.7321 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 136 | 83310138 | 5656 | 135.744 | 5.656 | 4.8 | 4.8 | 3B+1S | 0 | 1039 | 1089 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29158114 | 1254 | 221.7115 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 83315807 | 5669 | 136.056 | 5.669 | 4.6 | 4.6 | 3B+1S | 0 | 1041 | 1113 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29159364 | 1250 | 220.4974 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 133 | 83321493 | 5686 | 136.464 | 5.686 | 4.3 | 4.3 | 3B+1S | 0 | 999 | 1073 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29160618 | 1254 | 220.5417 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 131 | 83326982 | 5489 | 131.736 | 5.489 | 4.1 | 4.1 | 3B+1S | 0 | 999 | 1116 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29161828 | 1210 | 220.4409 | 0% | 100% | 100% | 100% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 133 | 83332532 | 5550 | 133.2 | 5.55 | 3.4 | 3.4 | 2B+1S | 0 | 1081 | 1193 | 0 | 1198 | N/A | N/A | N/A | N/A | 29162926 | 1098 | 197.8378 | 0% | 100% | 100% | 0% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 126 | 83338054 | 5522 | 132.528 | 5.522 | 2.7 | 2.7 | 2B+1S | 0 | 1081 | 1153 | 0 | 1199 | N/A | N/A | N/A | N/A | 29163990 | 1064 | 192.6838 | 0% | 100% | 100% | 0% | 100% | 0% | 6366481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 12.6 | 111 | 124 | 83343127 | 5073 | 121.752 | 5.073 | 2.1 | 2.1 | 2B | 0 | 1079 | 1119 | 0 | 1199 | N/A | N/A | N/A | N/A | 29164950 | 960 | 189.2371 | 0% | 100% | 100% | 0% | 100% | 0% | 6366481 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 103 | 83347596 | 4469 | 107.256 | 4.469 | 2.5 | 2.5 | 2B | 0 | 0 | 984 | 0 | 1199 | N/A | N/A | N/A | N/A | 29165722 | 772 | 172.7456 | 0% | 0% | 100% | 0% | 100% | 25% | 6367060 | 579 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 99 | 83351707 | 4111 | 98.664 | 4.111 | 3.3 | 3.3 | 2B | 0 | 0 | 903 | 0 | 1182 | N/A | N/A | N/A | N/A | 29166390 | 668 | 162.4909 | 0% | 0% | 100% | 0% | 100% | 25% | 6367823 | 763 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7917 | 123001 | 123001 | 123.001 | 123.001 | [12 empty] | 24662 | 24662 | 200.5024 | [6 empty] | 6613 | 6613 | 0.95167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:45 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
POWER FLUCTUATION @ 7:35 AM,
BP3 RE-STARTED @ 7:40 AM & SP2,BP1 & BP2 RE-STARTED @ 8:08 AM, RESUME NORMAL OPERATION @ 8:10 AM
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 8) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:05 PM TO 4:15 PM FOR 10 MINUTES RUN, NORMAL CONDITION
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:16 PM TO 4:26 PM FOR 10 MINUTES RUN, NORMAL CONDITION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | ORLANDO L. OCAMPO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25604 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83351707 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29166390 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6367823 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 95 | 83355655 | 3948 | 94.752 | 3.948 | 4.4 | 4.4 | 2B | 0 | 0 | 977 | 0 | 1182 | N/A | N/A | N/A | N/A | 29167082 | 692 | 175.2786 | 0% | 0% | 100% | 0% | 100% | 35% | 6368762 | 939 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 91 | 83359493 | 3838 | 92.112 | 3.838 | 5.5 | 5.5 | 2B | 0 | 0 | 937 | 0 | 1182 | N/A | N/A | N/A | N/A | 29167750 | 668 | 174.049 | 0% | 0% | 100% | 0% | 100% | 35% | 6369773 | 1011 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 93 | 83363465 | 3972 | 95.328 | 3.972 | 6.6 | 6.6 | 2B | 0 | 0 | 903 | 0 | 1180 | N/A | N/A | N/A | N/A | 29168426 | 676 | 170.1913 | 0% | 0% | 100% | 0% | 100% | 35% | 6370919 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 92 | 83367086 | 3621 | 86.904 | 3.621 | 7.7 | 7.7 | 2B | 0 | 0 | 943 | 0 | 1109 | N/A | N/A | N/A | N/A | 29168998 | 572 | 157.9674 | 0% | 0% | 100% | 0% | 100% | 35% | 6371975 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 126 | 112 | 83372443 | 5357 | 128.568 | 5.357 | 9 | 9 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 29169810 | 812 | 151.5774 | 0% | 0% | 100% | 0% | 100% | 35% | 6372998 | 1023 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 119 | 83375945 | 3502 | 84.048 | 3.502 | 9.1 | 9.1 | 2B | 0 | 0 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 29170384 | 574 | 163.9063 | 0% | 0% | 100% | 0% | 100% | 0% | 6372998 | 0 | 0.86 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 145 | 83381984 | 6039 | 144.936 | 6.039 | 8.5 | 8.5 | 3B+1S | 0 | 1092 | 1135 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29171714 | 1330 | 220.2351 | 0% | 0% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 83388079 | 6095 | 146.28 | 6.095 | 7.7 | 7.7 | 3B+1S | 0 | 1093 | 1169 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29173050 | 1336 | 219.1961 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 149 | 83394165 | 6086 | 146.064 | 6.086 | 7 | 7 | 3B+1S | 0 | 1081 | 1185 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29174410 | 1360 | 223.4637 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 83400343 | 6178 | 148.272 | 6.178 | 6.4 | 6.4 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29175746 | 1336 | 216.2512 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 83406381 | 6038 | 144.912 | 6.038 | 6 | 6 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29177138 | 1392 | 230.5399 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 83412380 | 5999 | 143.976 | 5.999 | 5.5 | 5.5 | 3B+1S | 0 | 1079 | 1180 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29178494 | 1356 | 226.0377 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 139 | 83418254 | 5874 | 140.976 | 5.874 | 5.3 | 5.3 | 3B+1S | 0 | 995 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29179824 | 1330 | 226.4215 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 83424023 | 5769 | 138.456 | 5.769 | 5.2 | 5.2 | 3B+1S | 0 | 1002 | 1190 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29181138 | 1314 | 227.7691 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 83429623 | 5600 | 134.4 | 5.6 | 5 | 5 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29182442 | 1304 | 232.8571 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 83435283 | 5660 | 135.84 | 5.66 | 4.9 | 4.9 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29183754 | 1312 | 231.8021 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 83440897 | 5614 | 134.736 | 5.614 | 4.8 | 4.8 | 3B+1S | 0 | 1024 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29184998 | 1244 | 221.5889 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 130 | 83446473 | 5576 | 133.824 | 5.576 | 4.6 | 4.6 | 3B+1S | 0 | 1007 | 1115 | 1185 | 1110 | N/A | N/A | N/A | N/A | 29186170 | 1172 | 210.1865 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 138 | 83452113 | 5640 | 135.36 | 5.64 | 4.2 | 4.2 | 3B+1S | 0 | 1034 | 1114 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29187366 | 1196 | 212.0567 | 0% | 100% | 100% | 100% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 132 | 83457660 | 5547 | 133.128 | 5.547 | 3.4 | 3.4 | 2B+1S | 0 | 1097 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29188454 | 1088 | 196.1421 | 0% | 100% | 100% | 0% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 130 | 83463102 | 5442 | 130.608 | 5.442 | 2.7 | 2.7 | 2B+1S | 0 | 1053 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29189530 | 1076 | 197.7214 | 0% | 100% | 100% | 0% | 100% | 0% | 6372998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 125 | 83468318 | 5216 | 125.184 | 5.216 | 2.3 | 2.3 | 2B+1S | 0 | 1010 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29190558 | 1028 | 197.0859 | 0% | 100% | 100% | 0% | 100% | 0% | 6372998 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 97 | 83472954 | 4636 | 111.264 | 4.636 | 3.1 | 3.1 | 2B | 0 | 0 | 1061 | 0 | 1100 | N/A | N/A | N/A | N/A | 29191366 | 808 | 174.2882 | 0% | 0% | 100% | 0% | 100% | 25% | 6373946 | 948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 95 | 83477004 | 4050 | 97.2 | 4.05 | 3.9 | 3.9 | 2B | 0 | 0 | 1014 | 0 | 1059 | N/A | N/A | N/A | N/A | 29191994 | 628 | 155.0617 | 0% | 0% | 100% | 0% | 100% | 25% | 6374849 | 903 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.4167 | 125297 | 125297 | 125.297 | 125.297 | [12 empty] | 25604 | 25604 | 204.3465 | [6 empty] | 7026 | 7026 | 0.90667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 5:40 AM,WATER ELEVATION 9.1M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (July 9) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:21 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 PM, NORMAL OPERATION
NORMAL OPERATION

## JULY 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25290 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83477004 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29191994 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6374849 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 93 | 83480964 | 3960 | 95.04 | 3.96 | 5.2 | 5.2 | 2B | 0 | 0 | 1060 | 0 | 1078 | N/A | N/A | N/A | N/A | 29192676 | 682 | 172.2222 | 0% | 0% | 100% | 0% | 100% | 40% | 6375910 | 1061 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 83484864 | 3900 | 93.6 | 3.9 | 6.4 | 6.4 | 2B | 0 | 0 | 1013 | 0 | 1078 | N/A | N/A | N/A | N/A | 29193306 | 630 | 161.5385 | 0% | 0% | 100% | 0% | 100% | 40% | 6377015 | 1105 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 90 | 83488716 | 3852 | 92.448 | 3.852 | 7.6 | 7.6 | 2B | 0 | 0 | 1010 | 0 | 1078 | N/A | N/A | N/A | N/A | 29193908 | 602 | 156.2825 | 0% | 0% | 100% | 0% | 100% | 40% | 6378098 | 1083 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 92 | 83492584 | 3868 | 92.832 | 3.868 | 8.8 | 8.8 | 2B | 0 | 0 | 1000 | 0 | 1078 | N/A | N/A | N/A | N/A | 29194468 | 560 | 144.7777 | 0% | 0% | 100% | 0% | 100% | 40% | 6379196 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 103 | 83496484 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1009 | N/A | N/A | N/A | N/A | 29195054 | 586 | 150.2564 | 0% | 0% | 100% | 0% | 100% | 40% | 6380124 | 928 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 123 | 83501284 | 4800 | 115.2 | 4.8 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1150 | N/A | N/A | N/A | N/A | 29195822 | 768 | 160 | 0% | 0% | 100% | 0% | 100% | 0% | 6380124 | 0 | 0.88 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 151 | 83507435 | 6151 | 147.624 | 6.151 | 9 | 9 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29197178 | 1356 | 220.452 | 0% | 0% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 83513611 | 6176 | 148.224 | 6.176 | 8.4 | 8.4 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29198542 | 1364 | 220.8549 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 83519760 | 6149 | 147.576 | 6.149 | 7.8 | 7.8 | 3B+1S | 0 | 1071 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29199910 | 1368 | 222.4752 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 83525992 | 6232 | 149.568 | 6.232 | 7.2 | 7.2 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29201298 | 1388 | 222.7214 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 83532003 | 6011 | 144.264 | 6.011 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29202644 | 1346 | 223.9228 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 83538050 | 6047 | 145.128 | 6.047 | 6.3 | 6.3 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29204016 | 1372 | 226.8894 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 141 | 83543859 | 5809 | 139.416 | 5.809 | 6.1 | 6.1 | 3B+1S | 0 | 988 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29205326 | 1310 | 225.5121 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 83549701 | 5842 | 140.208 | 5.842 | 6 | 6 | 3B+1S | 0 | 1005 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29206662 | 1336 | 228.6888 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 132 | 83555239 | 5538 | 132.912 | 5.538 | 5.9 | 5.9 | 3B+1S | 0 | 975 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29207946 | 1284 | 231.8527 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 132 | 83560873 | 5634 | 135.216 | 5.634 | 5.8 | 5.8 | 3B+1S | 0 | 970 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29209256 | 1310 | 232.5169 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 83566408 | 5535 | 132.84 | 5.535 | 5.7 | 5.7 | 3B+1S | 0 | 996 | 1170 | 1185 | 1174 | N/A | N/A | N/A | N/A | 29210478 | 1222 | 220.7769 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 134 | 83571945 | 5537 | 132.888 | 5.537 | 5.6 | 5.6 | 3B+1S | 0 | 978 | 1113 | 1185 | 1119 | N/A | N/A | N/A | N/A | 29211654 | 1176 | 212.3894 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 129 | 83577565 | 5620 | 134.88 | 5.62 | 5.5 | 5.5 | 3B+1S | 0 | 1001 | 1113 | 1185 | 1119 | N/A | N/A | N/A | N/A | 29212838 | 1184 | 210.6762 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 135 | 83583027 | 5462 | 131.088 | 5.462 | 5 | 5 | 2B+1S | 0 | 1065 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29213894 | 1056 | 193.3358 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 129 | 83588387 | 5360 | 128.64 | 5.36 | 4.4 | 4.4 | 2B+1S | 0 | 1017 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29214934 | 1040 | 194.0299 | 0% | 100% | 100% | 100% | 100% | 0% | 6380124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 122 | 83593620 | 5233 | 125.592 | 5.233 | 3.6 | 3.6 | 2B+1S | 0 | 1109 | 1125 | 0 | 1129 | N/A | N/A | N/A | N/A | 29215928 | 994 | 189.9484 | 0% | 100% | 100% | 0% | 100% | 0% | 6380124 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 101 | 83598018 | 4398 | 105.552 | 4.398 | 4.2 | 4.2 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 29216632 | 704 | 160.0728 | 0% | 0% | 100% | 0% | 100% | 25% | 6380662 | 538 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 93 | 83602214 | 4196 | 100.704 | 4.196 | 5 | 5 | 2B | 0 | 0 | 947 | 0 | 1110 | N/A | N/A | N/A | N/A | 29217284 | 652 | 155.3861 | 0% | 0% | 100% | 0% | 100% | 25% | 6381354 | 692 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125 | 125210 | 125210 | 125.21 | 125.21 | [12 empty] | 25290 | 25290 | 201.9807 | [6 empty] | 6505 | 6505 | 0.945 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:37 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am (JULY 10) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:18 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JUNE 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28014 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83602214 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29217284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6381354 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 93 | 83606163 | 3949 | 94.776 | 3.949 | 5.9 | 5.9 | 2B | 0 | 0 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 29217940 | 656 | 166.118 | 0% | 0% | 100% | 0% | 100% | 35% | 6382205 | 851 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 89 | 83609991 | 3828 | 91.872 | 3.828 | 6.8 | 6.8 | 2B | 0 | 0 | 995 | 0 | 1110 | N/A | N/A | N/A | N/A | 29218576 | 636 | 166.1442 | 0% | 0% | 100% | 0% | 100% | 35% | 6383148 | 943 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 87 | 83613745 | 3754 | 90.096 | 3.754 | 7.9 | 7.9 | 2B | 0 | 0 | 965 | 0 | 1110 | N/A | N/A | N/A | N/A | 29219186 | 610 | 162.4933 | 0% | 0% | 100% | 0% | 100% | 35% | 6384154 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 95 | 83617569 | 3824 | 91.776 | 3.824 | 8.9 | 8.9 | 2B | 0 | 0 | 970 | 0 | 1110 | N/A | N/A | N/A | N/A | 29219798 | 612 | 160.0418 | 0% | 0% | 100% | 0% | 100% | 35% | 6385094 | 940 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 108 | 83621640 | 4071 | 97.704 | 4.071 | 9.5 | 9.5 | 2B | 0 | 0 | 952 | 0 | 1110 | N/A | N/A | N/A | N/A | 29220424 | 626 | 153.7706 | 0% | 0% | 100% | 0% | 100% | 35% | 6385774 | 680 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 124 | 83626691 | 5051 | 121.224 | 5.051 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 29221242 | 818 | 161.9481 | 0% | 0% | 100% | 0% | 100% | 0% | 6385774 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 150 | 83632426 | 5735 | 137.64 | 5.735 | 9 | 9 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29222522 | 1280 | 223.1909 | 0% | 0% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 83638533 | 6107 | 146.568 | 6.107 | 8.5 | 8.5 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29223874 | 1352 | 221.3853 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 83644449 | 5916 | 141.984 | 5.916 | 7.9 | 7.9 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29225272 | 1398 | 236.3083 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.7 | 135 | 150 | 83650976 | 6527 | 156.648 | 6.527 | 6.9 | 6.9 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29226691 | 1419 | 217.4046 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
58:00 | 11:00 | 8 | 5.6338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.7 | 128 | 145 | 83657260 | 6284 | 150.816 | 6.284 | 5.9 | 5.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29228126 | 1435 | 228.3577 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
59:00 | 12:00 | 9 | 6.338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.3 | 129 | 152 | 83663481 | 6221 | 149.304 | 6.221 | 5.1 | 5.1 | 3B+1S | 0 | 1187 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29229572 | 1446 | 232.4385 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | UNITS
60:00 | 13:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 19 | A ONG | 17.5 | 135 | 145 | 83669508 | 6027 | 144.648 | 6.027 | 4.5 | 4.5 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29231022 | 1450 | 240.584 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 17.3 | 130 | 147 | 83675460 | 5952 | 142.848 | 5.952 | 3.7 | 3.7 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29232440 | 1418 | 238.2392 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 | 0.91 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 16.9 | 130 | 145 | 83681589 | 6129 | 147.096 | 6.129 | 3 | 3 | 3B+1S | 0 | 1180 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29233894 | 1454 | 237.2328 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 133 | 145 | 83687776 | 6187 | 148.488 | 6.187 | 2.3 | 2.3 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29235370 | 1476 | 238.5647 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 135 | 145 | 83693649 | 5873 | 140.952 | 5.873 | 1.9 | 1.9 | 3B+1S | 0 | 1183 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29236794 | 1424 | 242.4655 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 145 | 145 | 83699391 | 5742 | 137.808 | 5.742 | 1.8 | 1.8 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29238242 | 1448 | 252.1769 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.6 | 141 | 145 | 83705525 | 6134 | 147.216 | 6.134 | 1.7 | 1.7 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29239758 | 1516 | 247.147 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 143 | 139 | 83711402 | 5877 | 141.048 | 5.877 | 1.6 | 1.6 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29241090 | 1332 | 226.6462 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 140 | 136 | 83717275 | 5873 | 140.952 | 5.873 | 1.5 | 1.5 | 3B+1S | 0 | 930 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29242414 | 1324 | 225.4384 | 0% | 100% | 100% | 100% | 100% | 0% | 6385774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 134 | 136 | 83723008 | 5733 | 137.592 | 5.733 | 1.5 | 1.5 | 3B | 0 | 0 | 1120 | 1185 | 1160 | N/A | N/A | N/A | N/A | 29243634 | 1220 | 212.8031 | 0% | 100% | 100% | 0% | 100% | 0% | 6385774 | 0 | 0.98 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 133 | 113 | 83727809 | 4801 | 115.224 | 4.801 | 2.1 | 2.1 | 2B | 0 | 0 | 1155 | 0 | 1150 | N/A | N/A | N/A | N/A | 29244506 | 872 | 181.6288 | 0% | 0% | 100% | 0% | 100% | 25% | 6386457 | 683 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 133 | 111 | 83732399 | 4590 | 110.16 | 4.59 | 3.1 | 3.1 | 2B | 0 | 0 | 1085 | 0 | 1130 | N/A | N/A | N/A | N/A | 29245298 | 792 | 172.549 | 0% | 0% | 100% | 0% | 100% | 25% | 6387364 | 907 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 130.6667 | 130185 | 130185 | 130.185 | 130.185 | [12 empty] | 28014 | 28014 | 215.1861 | [6 empty] | 6010 | 6010 | 0.95167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 9:01 pm to 12 pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 86 psi @ 9:01 Am as per request of Engr Edmundo Llagas Jr (SPM- South)
Additional 5 psi to target discharge pressure @ 12:01 pm to 5 pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
XCV4 - OPENED ( 12% ) @ 12:01PM FOR DRAW AND FILL OPERATION XCV4 CLOSED @ 3:14 PM (10%)
XCV4 - OPENED ( 15% ) @ 5:01PM FOR DRAW AND FILL OPERATION XCV4 CLOSED @ 7:08 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:47 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JULY 10) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29076 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83732399 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29245298 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6387364 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 131 | 106 | 83736850 | 4451 | 106.824 | 4.451 | 4.1 | 4.1 | 2B | 0 | 0 | 1140 | 0 | 1130 | N/A | N/A | N/A | N/A | 29246106 | 808 | 181.5322 | 0% | 0% | 100% | 0% | 100% | 35% | 6388297 | 933 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 134 | 98 | 83741146 | 4296 | 103.104 | 4.296 | 5.5 | 5.5 | 2B | 0 | 0 | 1130 | 0 | 1110 | N/A | N/A | N/A | N/A | 29246874 | 768 | 178.7709 | 0% | 0% | 100% | 0% | 100% | 35% | 6389444 | 1147 | 0.95 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 140 | 98 | 83745322 | 4176 | 100.224 | 4.176 | 7.1 | 7.1 | 2B | 0 | 0 | 1195 | 0 | 1195 | N/A | N/A | N/A | N/A | 29247682 | 808 | 193.4866 | 0% | 0% | 100% | 0% | 100% | 35% | 6390532 | 1088 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 126 | 100 | 83749448 | 4126 | 99.024 | 4.126 | 8.7 | 8.7 | 2B | 0 | 0 | 1056 | 0 | 1110 | N/A | N/A | N/A | N/A | 29248618 | 936 | 226.8541 | 0% | 0% | 100% | 0% | 100% | 35% | 6390901 | 369 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A.ONG | 13.1 | 110 | 108 | 83753866 | 4418 | 106.032 | 4.418 | 9.5 | 9.5 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 29249374 | 756 | 171.1182 | 0% | 0% | 100% | 0% | 100% | 35% | 6391555 | 654 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 50.7158 | 19 | A ONG | 13.1 | 126 | 145 | 83758814 | 4948 | 118.752 | 4.948 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1196 | N/A | N/A | N/A | N/A | 29250206 | 832 | 168.1487 | 0% | 0% | 100% | 0% | 100% | 0% | 6391555 | 0 | 0.93 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 16.7 | 133 | 149 | 83764785 | 5971 | 143.304 | 5.971 | 8.9 | 8.9 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29251540 | 1334 | 223.4132 | 0% | 0% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.3 | 130 | 148 | 83771108 | 6323 | 151.752 | 6.323 | 8 | 8 | 3B+1S | 0 | 1155 | 1195 | 1185 | 1196 | N/A | N/A | N/A | N/A | 29252972 | 1432 | 226.4748 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 18.4 | 129 | 155 | 83777424 | 6316 | 151.584 | 6.316 | 7.1 | 7.1 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29254398 | 1426 | 225.7758 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.7 | 133 | 154 | 83783777 | 6353 | 152.472 | 6.353 | 6.1 | 6.1 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29255850 | 1452 | 228.5534 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
58:00 | 11:00 | 8 | 5.6338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.7 | 133 | 155 | 83790256 | 6479 | 155.496 | 6.479 | 5.1 | 5.1 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29257314 | 1464 | 225.9608 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
59:00 | 12:00 | 9 | 6.338 | 86 | 60.5634 | Automatic - Pressure Setting | 59.1549 | 60.5634 | 61.9834 | 19 | A ONG | 17.3 | 133 | 153 | 83796474 | 6218 | 149.232 | 6.218 | 4.2 | 4.2 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29258750 | 1436 | 230.9424 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | UNITS
60:00 | 13:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 19 | A ONG | 17.5 | 136 | 144 | 83802610 | 6136 | 147.264 | 6.136 | 3.5 | 3.5 | 3B+1S | 0 | 1177 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29260198 | 1448 | 235.9844 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 17.3 | 130 | 144 | 83808513 | 5903 | 141.672 | 5.903 | 2.8 | 2.8 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29261614 | 1416 | 239.878 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 | 0.88 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 16.9 | 130 | 151 | 83814582 | 6069 | 145.656 | 6.069 | 2.6 | 2.6 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29263114 | 1500 | 247.1577 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 137 | 147 | 83820490 | 5908 | 141.792 | 5.908 | 2.3 | 2.3 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29264588 | 1474 | 249.4922 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 137 | 149 | 83826444 | 5954 | 142.896 | 5.954 | 2.1 | 2.1 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29266070 | 1482 | 248.9083 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 139 | 144 | 83832457 | 6013 | 144.312 | 6.013 | 1.9 | 1.9 | 3B+1S | 0 | 1026 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29267420 | 1350 | 224.5136 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.6 | 141 | 144 | 83838510 | 6053 | 145.272 | 6.053 | 1..7 | 1..8 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29268798 | 1378 | 227.6557 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 141 | 137 | 83844359 | 5849 | 140.376 | 5.849 | 1.5 | 1.5 | 3B+1S | 0 | 1023 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29270120 | 1322 | 226.0215 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 140 | 139 | 83850170 | 5811 | 139.464 | 5.811 | 1.4 | 1.4 | 3B+1S | 0 | 800 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29271434 | 1314 | 226.1229 | 0% | 100% | 100% | 100% | 100% | 0% | 6391555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 136 | 137 | 83855938 | 5768 | 138.432 | 5.768 | 1.4 | 1.4 | 3B | 0 | 0 | 1136 | 1185 | 1148 | N/A | N/A | N/A | N/A | 29272670 | 1236 | 214.2857 | 0% | 100% | 100% | 0% | 100% | 0% | 6391555 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 137 | 118 | 83860750 | 4812 | 115.488 | 4.812 | 2.2 | 2.2 | 2B | 0 | 0 | 1175 | 0 | 1160 | N/A | N/A | N/A | N/A | 29273554 | 884 | 183.7074 | 0% | 0% | 100% | 0% | 100% | 25% | 6392245 | 690 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 141 | 112 | 83865404 | 4654 | 111.696 | 4.654 | 3.3 | 3.3 | 2B | 0 | 0 | 1110 | 0 | 1140 | N/A | N/A | N/A | N/A | 29274374 | 820 | 176.1925 | 0% | 0% | 100% | 0% | 100% | 25% | 6393338 | 1093 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 134.7917 | 133005 | 133005 | 133.005 | 133.005 | [12 empty] | 29076 | 29076 | 218.6083 | [6 empty] | 5974 | 5974 | 0.91167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 5 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:55 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 85 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 85 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:11 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 9:01 pm to 12 pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 86 psi @ 9:01 Am as per request of Engr Edmundo Llagas Jr (SPM- South)
Additional 5 psi to target discharge pressure @ 12:01 pm to 5 pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
XCV4 - OPENED ( 11% ) @ 12:01PM FOR DRAW AND FILL OPERATION XCV4 - CLOSED @ 5:19 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:31 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:01PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JUNE 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | O. OCAMPO / A. CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83865404 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29274374 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6393338 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 6 | 4.2254 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 133 | 108 | 83869892 | 4488 | 107.712 | 4.488 | 4.5 | 4.5 | 2B | 0 | 0 | 1148 | 0 | 1150 | N/A | N/A | N/A | N/A | 29275194 | 820 | 182.7094 | 0% | 0% | 100% | 0% | 100% | 35% | 6394328 | 990 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 135 | 102 | 83874305 | 4413 | 105.912 | 4.413 | 5.8 | 5.8 | 2B | 0 | 0 | 1108 | 0 | 1150 | N/A | N/A | N/A | N/A | 29275978 | 784 | 177.6569 | 0% | 0% | 100% | 0% | 100% | 35% | 6395496 | 1168 | 0.96 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 136 | 104 | 83878550 | 4245 | 101.88 | 4.245 | 7.2 | 7.2 | 2B | 0 | 0 | 1095 | 0 | 1120 | N/A | N/A | N/A | N/A | 29276716 | 738 | 173.8516 | 0% | 0% | 100% | 0% | 100% | 35% | 6396822 | 1326 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 131 | 101 | 83882740 | 4190 | 100.56 | 4.19 | 8.4 | 8.4 | 2B | 0 | 0 | 1080 | 0 | 1110 | N/A | N/A | N/A | N/A | 29277434 | 718 | 171.3604 | 0% | 0% | 100% | 0% | 100% | 35% | 6398103 | 1281 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A.ONG | 13.1 | 102 | 103 | 83887036 | 4296 | 103.104 | 4.296 | 9.5 | 9.5 | 2B | 0 | 0 | 940 | 0 | 1080 | N/A | N/A | N/A | N/A | 29278308 | 874 | 203.4451 | 0% | 0% | 100% | 0% | 100% | 35% | 6398242 | 139 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 14 | 9.8592 | 70 | 49.2958 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 50.7158 | 19 | A ONG | 13.1 | 121 | 122 | 83891718 | 4682 | 112.368 | 4.682 | 9.5 | 9.5 | 2B | 0 | 0 | 1145 | 0 | 1160 | N/A | N/A | N/A | N/A | 29279018 | 710 | 151.6446 | 0% | 0% | 100% | 0% | 100% | 0% | 6398242 | 0 | 0.91 | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 16.7 | 136 | 145 | 83897665 | 5947 | 142.728 | 5.947 | 9.1 | 9.1 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29280324 | 1306 | 219.6065 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.3 | 130 | 153 | 83903954 | 6289 | 150.936 | 6.289 | 8.4 | 8.4 | 3B+1S | 0 | 1177 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29281738 | 1414 | 224.837 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 18.4 | 130 | 153 | 83910302 | 6348 | 152.352 | 6.348 | 7.4 | 7.4 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29283148 | 1410 | 222.1172 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.7 | 131 | 153 | 83916698 | 6396 | 153.504 | 6.396 | 6.2 | 6.2 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29284556 | 1408 | 220.1376 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 | 0.88 | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
58:00 | 11:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.7 | 130 | 147 | 83923068 | 6370 | 152.88 | 6.37 | 5.2 | 5.2 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29285974 | 1418 | 222.606 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
59:00 | 12:00 | 5 | 3.5211 | 82 | 57.7465 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 17.3 | 129 | 149 | 83929382 | 6314 | 151.536 | 6.314 | 4.2 | 4.2 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29287534 | 1560 | 247.07 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | UNITS
60:00 | 13:00 | 6 | 4.2254 | 82 | 57.7465 | Automatic - Pressure Setting | 56.338 | 57.7465 | 61.9718 | 19 | A ONG | 17.5 | 129 | 148 | 83935666 | 6284 | 150.816 | 6.284 | 3.1 | 3.1 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29289082 | 1548 | 246.3399 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 80 | 56.338 | Power Interruption | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 17.3 | 129 | 144 | 83940990 | 5324 | 127.776 | 5.324 | 2.5 | 2.5 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29289082 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 | 0.93 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 80 | 56.338 | Power Interruption | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.9 | 127 | 137 | 83946197 | 5207 | 124.968 | 5.207 | 2 | 2 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29289082 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 82 | 57.7465 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.7 | 129 | 134 | 83950797 | 4600 | 110.4 | 4.6 | 1.6 | 1.6 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29290318 | 1236 | 268.6957 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 136 | 135 | 83956409 | 5612 | 134.688 | 5.612 | 1.3 | 1.3 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29291468 | 1150 | 204.918 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 139 | 132 | 83962144 | 5735 | 137.64 | 5.735 | 1.3 | 1.3 | 3B | 0 | 0 | 1161 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29292686 | 1218 | 212.3801 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.6 | 141 | 135 | 83967436 | 5292 | 127.008 | 5.292 | 1.4 | 1.4 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29293910 | 1224 | 231.2925 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 132 | 83973041 | 5605 | 134.52 | 5.605 | 1.5 | 1.5 | 3B | 0 | 0 | 1077 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29295108 | 1198 | 213.7377 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 130 | 127 | 83978315 | 5274 | 126.576 | 5.274 | 1.5 | 1.5 | 3B | 0 | 0 | 1105 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29296274 | 1166 | 221.0846 | 0% | 100% | 100% | 100% | 100% | 0% | 6398242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 129 | 128 | 83983989 | 5674 | 136.176 | 5.674 | 1.5 | 1.5 | 3B | 0 | 0 | 1040 | 1185 | 1127 | N/A | N/A | N/A | N/A | 29297434 | 1160 | 204.4413 | 0% | 100% | 100% | 0% | 100% | 0% | 6398242 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 139 | 116 | 83988328 | 4339 | 104.136 | 4.339 | 2.6 | 2.6 | 2B | 0 | 0 | 1150 | 0 | 1160 | N/A | N/A | N/A | N/A | 29298292 | 858 | 197.7414 | 0% | 0% | 100% | 0% | 100% | 25% | 6399187 | 945 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 143 | 105 | 83992819 | 4491 | 107.784 | 4.491 | 3.8 | 3.8 | 2B | 0 | 0 | 1100 | 0 | 1110 | N/A | N/A | N/A | N/A | 29299022 | 730 | 162.5473 | 0% | 0% | 100% | 0% | 100% | 25% | 6400429 | 1242 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.7083 | 127415 | 127415 | 127.415 | 127.415 | [12 empty] | 24648 | 24648 | 193.4466 | [6 empty] | 7091 | 7091 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 5 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 45 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 85 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 85 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 85 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
POWERINTERRUPTION @ 1:20 PM
GENSET (G2) - STARTED @ 1:25 PM
STARTED ALL MOTORS @ 1:27 PM , NORMAL OPERATION @ 1:28 PM
MERALCO POWER RE-STORED @ 3:15 PM
GENSET (G2) STOPPED @ 3:20 PM
RE-STARTED SP2,BP1,BP2,BP3 @ 3:26 PM WITH MERALCO POWER
SP2 - STOPPED @ 4:31 PM DUE TO LOW WATER LEVEL
XCV4 - OPENED @6:OO PM (10%) / CLOSED @ 8:00 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JULY 12) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | O. OCAMPO / A. CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27042 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 83992819 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29299022 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6400429 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 129 | 101 | 83997188 | 4369 | 104.856 | 4.369 | 5 | 5 | 2B | 0 | 0 | 1135 | 0 | 1130 | N/A | N/A | N/A | N/A | 29299824 | 802 | 183.566 | 0% | 0% | 100% | 0% | 100% | 35% | 6401362 | 933 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 131 | 103 | 84001480 | 4292 | 103.008 | 4.292 | 6.1 | 6.1 | 2B | 0 | 0 | 1115 | 0 | 1120 | N/A | N/A | N/A | N/A | 29300590 | 766 | 178.4716 | 0% | 0% | 100% | 0% | 100% | 35% | 6402466 | 1104 | 0.98 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 131 | 102 | 84005760 | 4280 | 102.72 | 4.28 | 7.3 | 7.3 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 29301334 | 744 | 173.8318 | 0% | 0% | 100% | 0% | 100% | 35% | 6403625 | 1159 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 126 | 104 | 84010022 | 4262 | 102.288 | 4.262 | 8.4 | 8.4 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 29302062 | 728 | 170.8118 | 0% | 0% | 100% | 0% | 100% | 35% | 6404674 | 1049 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A.ONG | 13.1 | 134 | 103 | 84014276 | 4254 | 102.096 | 4.254 | 9.5 | 9.5 | 2B | 0 | 0 | 1185 | 0 | 1190 | N/A | N/A | N/A | N/A | 29302926 | 864 | 203.103 | 0% | 0% | 100% | 0% | 100% | 35% | 6404958 | 284 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 22 | 15.493 | 70 | 49.2958 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 50.7158 | 19 | A ONG | 13.1 | 115 | 112 | 84018810 | 4534 | 108.816 | 4.534 | 9.5 | 9.5 | 2B | 0 | 0 | 1185 | 0 | 1199 | N/A | N/A | N/A | N/A | 29303622 | 696 | 153.5068 | 0% | 0% | 100% | 0% | 100% | 0% | 6404958 | 0 | 0.94 | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 15 | 10.5634 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 16.7 | 146 | 146 | 84024438 | 5628 | 135.072 | 5.628 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29304770 | 1148 | 203.9801 | 0% | 0% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.3 | 139 | 150 | 84030507 | 6069 | 145.656 | 6.069 | 9.3 | 9.3 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29306091 | 1321 | 217.6635 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 18.4 | 131 | 147 | 84036760 | 6253 | 150.072 | 6.253 | 8.6 | 8.6 | 3B+1S | 0 | 1164 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29307394 | 1303 | 208.38 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.7 | 129 | 150 | 84043049 | 6289 | 150.936 | 6.289 | 7.6 | 7.6 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29308846 | 1452 | 230.8793 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 | 0.88 | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
58:00 | 11:00 | 6 | 4.2254 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.7 | 127 | 148 | 84049240 | 6191 | 148.584 | 6.191 | 6.6 | 6.6 | 3B+1S | 0 | 1190 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29310342 | 1496 | 241.6411 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
59:00 | 12:00 | 7 | 4.9296 | 85 | 59.8592 | Automatic - Pressure Setting | 58.4507 | 59.8592 | 61.2792 | 19 | A ONG | 17.3 | 126 | 147 | 84055381 | 6141 | 147.384 | 6.141 | 5.6 | 5.6 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29311818 | 1476 | 240.3517 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 2psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 141 | 84061340 | 5959 | 143.016 | 5.959 | 5.1 | 5.1 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29313178 | 1360 | 228.2262 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 142 | 84067181 | 5841 | 140.184 | 5.841 | 4.2 | 4.2 | 3B+1S | 0 | 1118 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29314676 | 1498 | 256.4629 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 138 | 84072898 | 5717 | 137.208 | 5.717 | 3.4 | 3.4 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29315934 | 1258 | 220.0455 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 84078390 | 5492 | 131.808 | 5.492 | 3 | 3 | 3B+1S | 0 | 1052 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29317270 | 1336 | 243.2629 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 132 | 84084065 | 5675 | 136.2 | 5.675 | 2.8 | 2.8 | 3B+1S | 0 | 1138 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29318626 | 1356 | 238.9427 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 144 | 131 | 84089500 | 5435 | 130.44 | 5.435 | 3.1 | 3.1 | 3B+1S | 0 | 992 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29319966 | 1340 | 246.5501 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 141 | 135 | 84094976 | 5476 | 131.424 | 5.476 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1170 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29321270 | 1304 | 238.13 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 84100381 | 5405 | 129.72 | 5.405 | 3 | 3 | 2B+1S | 0 | 1171 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29322414 | 1144 | 211.6559 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 84105597 | 5216 | 125.184 | 5.216 | 2.5 | 2.5 | 2B+1S | 0 | 1167 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 29323548 | 1134 | 217.408 | 0% | 100% | 100% | 100% | 100% | 0% | 6404958 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 84110862 | 5265 | 126.36 | 5.265 | 2.1 | 2.1 | 2B+1S | 0 | 1010 | 1195 | 0 | 1180 | N/A | N/A | N/A | N/A | 29324638 | 1090 | 207.0275 | 0% | 100% | 100% | 0% | 100% | 0% | 6404958 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 100 | 84115032 | 4170 | 100.08 | 4.17 | 3 | 3 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 29325376 | 738 | 176.9784 | 0% | 0% | 100% | 0% | 100% | 25% | 6405775 | 817 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 104 | 84119250 | 4218 | 101.232 | 4.218 | 4.3 | 4.3 | 2B | 0 | 0 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 29326064 | 688 | 163.1105 | 0% | 0% | 100% | 0% | 100% | 25% | 6406990 | 1215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.7917 | 126431 | 126431 | 126.431 | 126.431 | [12 empty] | 27042 | 27042 | 213.8874 | [6 empty] | 6561 | 6561 | 0.92667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:15 AM
XCV4 OPENED @ 4:15AM FOR REFILLING
XCV4 CLOSED @ 4:55AM, WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
Additional 2 psi to target discharge pressure from 6:01 am to 12 pm as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 85 psi @ 6:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 14) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV4 -OPENED @ 4:30 PM (13%)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JUNE 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | O. OCAMPO / A. CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26018 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84119250 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29326064 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6406990 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 103 | 84123412 | 4162 | 99.888 | 4.162 | 5.7 | 5.7 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 29326778 | 714 | 171.5521 | 0% | 0% | 100% | 0% | 100% | 35% | 6408111 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 100 | 84127590 | 4178 | 100.272 | 4.178 | 6.7 | 6.7 | 2B | 0 | 0 | 1050 | 0 | 1110 | N/A | N/A | N/A | N/A | 29327480 | 702 | 168.023 | 0% | 0% | 100% | 0% | 100% | 35% | 6409233 | 1122 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 97 | 84131650 | 4060 | 97.44 | 4.06 | 7.9 | 7.9 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 29328146 | 666 | 164.0394 | 0% | 0% | 100% | 0% | 100% | 35% | 6410408 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 101 | 84135758 | 4108 | 98.592 | 4.108 | 9 | 9 | 2B | 0 | 0 | 1015 | 0 | 1110 | N/A | N/A | N/A | N/A | 29328804 | 658 | 160.1753 | 0% | 0% | 100% | 0% | 100% | 35% | 6411529 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 106 | 84140077 | 4319 | 103.656 | 4.319 | 9.5 | 9.5 | 2B | 0 | 0 | 985 | 0 | 1110 | N/A | N/A | N/A | N/A | 29329462 | 658 | 152.3501 | 0% | 0% | 100% | 0% | 100% | 35% | 6412036 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 125 | 84144861 | 4784 | 114.816 | 4.784 | 9.5 | 9.5 | 2B | 0 | 0 | 1175 | 0 | 1170 | N/A | N/A | N/A | N/A | 29330222 | 760 | 158.8629 | 0% | 0% | 100% | 0% | 100% | 0% | 6412036 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 84150814 | 5953 | 142.872 | 5.953 | 9.1 | 9.1 | 3B+1S | 0 | 996 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29331542 | 1320 | 221.7369 | 0% | 0% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 84156950 | 6136 | 147.264 | 6.136 | 8.7 | 8.7 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29332844 | 1302 | 212.1904 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 84163077 | 6127 | 147.048 | 6.127 | 8.2 | 8.2 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29334242 | 1398 | 228.1704 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 152 | 84169215 | 6138 | 147.312 | 6.138 | 7.5 | 7.5 | 3B+1S | 0 | 1183 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29335636 | 1394 | 227.1098 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 146 | 84175337 | 6122 | 146.928 | 6.122 | 6.6 | 6.6 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29337048 | 1412 | 230.6436 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 84181420 | 6083 | 145.992 | 6.083 | 5.9 | 5.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29338426 | 1378 | 226.533 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 140 | 84187224 | 5804 | 139.296 | 5.804 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29339746 | 1320 | 227.4294 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 84193029 | 5805 | 139.32 | 5.805 | 5.4 | 5.4 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29341062 | 1316 | 226.7011 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 84198760 | 5731 | 137.544 | 5.731 | 5.1 | 5.1 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29342422 | 1360 | 237.3059 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 84204260 | 5500 | 132 | 5.5 | 5 | 5 | 3B+1S | 0 | 995 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29343718 | 1296 | 235.6364 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 84209807 | 5547 | 133.128 | 5.547 | 5 | 5 | 3B+1S | 0 | 100 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29344982 | 1264 | 227.8709 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 137 | 84215000 | 5193 | 124.632 | 5.193 | 5 | 5 | 3B | 0 | 0 | 1077 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29346086 | 1104 | 212.5939 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 84220618 | 5618 | 134.832 | 5.618 | 5 | 5 | 3B | 0 | 0 | 1109 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29347282 | 1196 | 212.8871 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 128 | 84225918 | 5300 | 127.2 | 5.3 | 5 | 5 | 3B | 0 | 0 | 1076 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29348426 | 1144 | 215.8491 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 128 | 84231281 | 5363 | 128.712 | 5.363 | 5 | 5 | 3B | 0 | 0 | 1042 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29349572 | 1146 | 213.6864 | 0% | 100% | 100% | 100% | 100% | 0% | 6412036 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 121 | 84236560 | 5279 | 126.696 | 5.279 | 5 | 5 | 3B | 0 | 0 | 990 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29350718 | 1146 | 217.0866 | 0% | 100% | 100% | 0% | 100% | 0% | 6412036 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 103 | 84240758 | 4198 | 100.752 | 4.198 | 5.6 | 5.6 | 2B | 0 | 0 | 1025 | 0 | 1110 | N/A | N/A | N/A | N/A | 29351478 | 760 | 181.0386 | 0% | 0% | 100% | 0% | 100% | 25% | 6412515 | 479 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 100 | 84244930 | 4172 | 100.128 | 4.172 | 6.1 | 6.1 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 29352082 | 604 | 144.7747 | 0% | 0% | 100% | 0% | 100% | 25% | 6413150 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.7917 | 125680 | 125680 | 125.68 | 125.68 | [12 empty] | 26018 | 26018 | 207.0178 | [6 empty] | 6160 | 6160 | 0.955 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:55 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 15
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
| WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[14 empty] | 10pm - 6am | O. OCAMPO / A. CABREROS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2014-07-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24936 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84244930 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29352082 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6413150 |  | mg /l |  | Automatic - i2O | AI
| 48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 100 | 84249122 | 4192 | 100.608 | 4.192 | 6.8 | 6.8 | 2B | 0 | 0 | 1050 | 0 | 1110 | N/A | N/A | N/A | N/A | 29352774 | 692 | 165.0763 | 0% | 0% | 100% | 0% | 100% | 35% | 6413777 | 627 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
| 49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 99 | 84253174 | 4052 | 97.248 | 4.052 | 7.6 | 7.6 | 2B | 0 | 0 | 1015 | 0 | 1110 | N/A | N/A | N/A | N/A | 29353438 | 664 | 163.8697 | 0% | 0% | 100% | 0% | 100% | 35% | 6414628 | 851 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
| 50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 96 | 84257112 | 3938 | 94.512 | 3.938 | 8.7 | 8.7 | 2B | 0 | 0 | 970 | 0 | 1110 | N/A | N/A | N/A | N/A | 29354068 | 630 | 159.9797 | 0% | 0% | 100% | 0% | 100% | 35% | 6415604 | 976 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
| 51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 95 | 84261094 | 3982 | 95.568 | 3.982 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1010 | N/A | N/A | N/A | N/A | 29354634 | 566 | 142.1396 | 0% | 0% | 100% | 0% | 100% | 35% | 6416407 | 803 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
| 52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 102 | 84265089 | 3995 | 95.88 | 3.995 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1010 | N/A | N/A | N/A | N/A | 29355182 | 548 | 137.1715 | 0% | 0% | 100% | 0% | 100% | 35% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
| 53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 121 | 84269710 | 4621 | 110.904 | 4.621 | 9.5 | 9.5 | 2B | 0 | 0 | 1445 | 0 | 1110 | N/A | N/A | N/A | N/A | 29355870 | 688 | 148.8855 | 0% | 0% | 100% | 0% | 100% | 0% | 6416407 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
| 54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 144 | 84275432 | 5722 | 137.328 | 5.722 | 9.4 | 9.4 | 3B+1S | 0 | 986 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29357154 | 1284 | 224.3971 | 0% | 0% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Normal operation schedule | Power Interruption | PI
| 55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 84281602 | 6170 | 148.08 | 6.17 | 9 | 9 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29358522 | 1368 | 221.718 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 84287754 | 6152 | 147.648 | 6.152 | 8.3 | 8.3 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29359894 | 1372 | 223.0169 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 84293824 | 6070 | 145.68 | 6.07 | 7.8 | 7.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29361258 | 1364 | 224.7117 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 | 0.86 | Normal operation schedule
| 58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 84299913 | 6089 | 146.136 | 6.089 | 7.4 | 7.4 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29362614 | 1356 | 222.6967 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 84305881 | 5968 | 143.232 | 5.968 | 6.9 | 6.9 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29363970 | 1356 | 227.2118 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 84311761 | 5880 | 141.12 | 5.88 | 6.6 | 6.6 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29365310 | 1340 | 227.8912 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 84317510 | 5749 | 137.976 | 5.749 | 6.3 | 6.3 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29366630 | 1320 | 229.6051 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 138 | 84323240 | 5730 | 137.52 | 5.73 | 6.1 | 6.1 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29367932 | 1302 | 227.2251 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 84328705 | 5465 | 131.16 | 5.465 | 5.9 | 5.9 | 3B+1S | 0 | 992 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29369246 | 1314 | 240.4392 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 120 | 130 | 84334045 | 5340 | 128.16 | 5.34 | 5.7 | 5.7 | 3B+1S | 0 | 1055 | 1114 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29370432 | 1186 | 222.0974 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 121 | 128 | 84339413 | 5368 | 128.832 | 5.368 | 5.4 | 5.4 | 3B+1S | 0 | 1019 | 1073 | 1185 | 1078 | N/A | N/A | N/A | N/A | 29371556 | 1124 | 209.389 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 128 | 84344721 | 5308 | 127.392 | 5.308 | 4.9 | 4.9 | 3B+1S | 0 | 1031 | 1074 | 1185 | 1079 | N/A | N/A | N/A | N/A | 29372674 | 1118 | 210.6255 | 0% | 100% | 100% | 100% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 108 | 124 | 84350169 | 5448 | 130.752 | 5.448 | 4 | 4 | 2B+1S | 0 | 1133 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 29373730 | 1056 | 193.8326 | 0% | 100% | 100% | 0% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 126 | 84355314 | 5145 | 123.48 | 5.145 | 3.3 | 3.3 | 2B+1S | 0 | 1015 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29374734 | 1004 | 195.1409 | 0% | 100% | 100% | 0% | 100% | 0% | 6416407 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 118 | 84360193 | 4879 | 117.096 | 4.879 | 3.1 | 3.1 | 2B | 0 | 0 | 1170 | 0 | 1199 | N/A | N/A | N/A | N/A | 29375682 | 948 | 194.3021 | 0% | 0% | 100% | 0% | 100% | 0% | 6416407 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 102 | 84364666 | 4473 | 107.352 | 4.473 | 4.1 | 4.1 | 2B | 0 | 0 | 989 | 0 | 1140 | N/A | N/A | N/A | N/A | 29376418 | 736 | 164.5428 | 0% | 0% | 100% | 0% | 100% | 35% | 6417433 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 90 | 84368485 | 3819 | 91.656 | 3.819 | 5.6 | 5.6 | 2B | 0 | 0 | 1000 | 0 | 1009 | N/A | N/A | N/A | N/A | 29377018 | 600 | 157.1092 | 0% | 0% | 100% | 0% | 100% | 35% | 6418681 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL |  |  |  | 123.9583 | 123555 | 123555 | 123.555 | 123.555 | [12 empty] | 24936 | 24936 | 201.8211 | [6 empty] | 5531 | 5531 | 0.91667 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
|  | XCV1 OPENING INCREASED TO 30 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:50 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 16) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:23 PM, NORMAL OPERATION
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:16 PM TO 4:26 PM FOR 10 MINUTES RUN, NORMAL CONDITION |  | GENSET # 2 EXERCISED WITHOUT LOAD @ 4:00 PM TO 4:10 PM FOR 10 MINUTES RUN, NORMAL CONDITION
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:11 PM TO 4:21 PM FOR 10 MINUTES RUN, NORMAL CONDITION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:45 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:45 PM, NORMAL OPERATION
NORMAL OPERATION

## JULY 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | O. OCAMPO / A. CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ORLANDO L. OCAMPO
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 4824 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84368485 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29377018 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6418681 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 89 | 84372386 | 3901 | 93.624 | 3.901 | 6.4 | 6.4 | 2B | 0 | 0 | 1064 | 0 | 1008 | N/A | N/A | N/A | N/A | 29377648 | 630 | 161.4971 | 0% | 0% | 100% | 0% | 100% | 35% | 6419603 | 922 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 87 | 84373919 | 1533 | 36.792 | 1.533 | 7.4 | 7.4 | 2B | 0 | 0 | 1011 | 0 | 1018 | N/A | N/A | N/A | N/A | 29378194 | 546 | 356.1644 | 0% | 0% | 100% | 0% | 100% | 35% | 6420532 | 929 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 88 | 84379503 | 5584 | 134.016 | 5.584 | 8.5 | 8.5 | 2B | 0 | 0 | 948 | 0 | 1059 | N/A | N/A | N/A | N/A | 29378736 | 542 | 97.063 | 0% | 0% | 100% | 0% | 100% | 35% | 6421667 | 1135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 87 | 84382568 | 3065 | 73.56 | 3.065 | 9.5 | 9.5 | 2B | 0 | 0 | 837 | 0 | 1019 | N/A | N/A | N/A | N/A | 29379152 | 416 | 135.7259 | 0% | 0% | 100% | 0% | 100% | 35% | 6422375 | 708 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 109 | 84385754 | 3186 | 76.464 | 3.186 | 9.5 | 9.5 | 2B | 0 | 0 | 925 | 0 | 1009 | N/A | N/A | N/A | N/A | 29379664 | 512 | 160.7031 | 0% | 0% | 100% | 0% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 32 | 22.5352 | 68 | 47.8873 | Power Interruption | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 98 | 106 | 84388941 | 3187 | 76.488 | 3.187 | 9.5 | 9.5 | 2B | 0 | 0 | 876 | 0 | 1009 | N/A | N/A | N/A | N/A | 29379664 | 827 | 259.4917 | 0% | 0% | 100% | 0% | 100% | 0% | 6422375 | 0 | 0.96 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 21 | 14.7887 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 112 | 137 | 84391303 | 2362 | 56.688 | 2.362 | 9.5 | 9.5 | 3B | 0 | 0 | 1058 | 1185 | 1058 | N/A | N/A | N/A | N/A | 29379664 | 994 | 420.8298 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 18 | 12.6761 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 112 | 132 | 84399833 | 8530 | 204.72 | 8.53 | 9.5 | 9.5 | 3B | 0 | 0 | 1085 | 1185 | 1058 | N/A | N/A | N/A | N/A | 29379664 | 953 | 111.7233 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 21 | 14.7887 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 123 | 136 | 84404650 | 4817 | 115.608 | 4.817 | 9.5 | 9.5 | 3B | 0 | 0 | 1050 | 1185 | 1079 | N/A | N/A | N/A | N/A | 29379664 | 927 | 192.4434 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 20 | 14.0845 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 133 | 84410414 | 5764 | 138.336 | 5.764 | 9.5 | 9.5 | 3B | 0 | 0 | 1051 | 1185 | 1078 | N/A | N/A | N/A | N/A | 29379664 | 905 | 157.009 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 20 | 14.0845 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 139 | 84416122 | 5708 | 136.992 | 5.708 | 9.5 | 9.5 | 3B | 0 | 0 | 1092 | 1185 | 1078 | N/A | N/A | N/A | N/A | 29379664 | 920 | 161.1773 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Normal operation schedule
59:00 | 12:00 | 18 | 12.6761 | 83 | 58.4507 | Power Interruption | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 137 | 84422292 | 6170 | 148.08 | 6.17 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1177 | N/A | N/A | N/A | N/A | 29379664 | 950 | 153.9708 | 0% | 0% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 18 | 12.6761 | 81 | 57.0423 | Power Interruption | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 121 | 137 | 84427751 | 5459 | 131.016 | 5.459 | 8.9 | 8.9 | 2B+1S | 0 | 1074 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29379664 | 910 | 166.6972 | 0% | 100% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 84433704 | 5953 | 142.872 | 5.953 | 7.9 | 7.9 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29379664 | 1100 | 184.7808 | 0% | 100% | 100% | 100% | 100% | 0% | 6422375 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 132 | 84439582 | 5878 | 141.072 | 5.878 | 7.6 | 7.6 | 3B+1S | 0 | 1014 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29379664 | 1080 | 183.736 | 0% | 100% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 84444914 | 5332 | 127.968 | 5.332 | 7.2 | 7.2 | 3B+1S | 0 | 1017 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29379664 | 1070 | 200.6752 | 0% | 100% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 134 | 84450624 | 5710 | 137.04 | 5.71 | 6.8 | 6.8 | 3B+1S | 0 | 1037 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29379664 | 1050 | 183.8879 | 0% | 100% | 100% | 100% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 112 | 132 | 84455992 | 5368 | 128.832 | 5.368 | 6 | 6 | 2B+1S | 0 | 1099 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29379664 | 890 | 165.7973 | 0% | 100% | 100% | 0% | 100% | 0% | 6422375 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 128 | 84461406 | 5414 | 129.936 | 5.414 | 5.4 | 5.4 | 2B+1S | 0 | 1048 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29379664 | 880 | 162.5416 | 0% | 100% | 100% | 0% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 121 | 84466647 | 5241 | 125.784 | 5.241 | 4.9 | 4.9 | 2B+1S | 0 | 1039 | 1177 | 0 | 1180 | N/A | N/A | N/A | N/A | 29379664 | 830 | 158.3667 | 0% | 100% | 100% | 0% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 32 | 22.5352 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 119 | 84471252 | 4605 | 110.52 | 4.605 | 4.5 | 4.5 | 2B+1S | 0 | 1020 | 905 | 0 | 1199 | N/A | N/A | N/A | N/A | 29379784 | 120 | 26.0586 | 0% | 100% | 100% | 0% | 100% | 0% | 6422375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 118 | 84476050 | 4798 | 115.152 | 4.798 | 4 | 4 | 2B+1S | 0 | 1020 | 1090 | 0 | 1160 | N/A | N/A | N/A | N/A | 29380662 | 878 | 182.9929 | 0% | 100% | 100% | 0% | 100% | 0% | 6422375 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 95 | 84480112 | 4062 | 97.488 | 4.062 | 4.8 | 4.8 | 2B | 0 | 0 | 905 | 0 | 1110 | N/A | N/A | N/A | N/A | 29381272 | 610 | 150.1723 | 0% | 0% | 100% | 0% | 100% | 25% | 6423118 | 743 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 84484175 | 4063 | 97.512 | 4.063 | 5.8 | 5.8 | 2B | 0 | 0 | 870 | 0 | 1110 | N/A | N/A | N/A | N/A | 29381842 | 570 | 140.2904 | 0% | 0% | 100% | 0% | 100% | 25% | 6424027 | 909 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.2917 | 115690 | 115690 | 115.69 | 115.69 | [12 empty] | 4824 | 19110 | 165.1828 | [6 empty] | 5346 | 5346 | 0.99833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION 9.5M
POWER FLUCTUATION @ 2:20 AM / POWER RESTORED @ 2:21 AM
NORMAL OPERATION @ 2:28 AM, 2B
POWER FLUCTUATION @ 3:11 AM / POWER RESTORED @ 3:12 AM
POWER FLUCTUATION @ 3:17 AM / POWER RESTORED @ 3:18 AM
NORMAL OPERATION @ 3:26 AM, 2B
POWER FLUCTUATION @ 4:23 AM / POWER RESTORED @ 4:24 AM
NORMAL OPERATION @ 4:28 AM, 2B
POWER FLUCTUATION @ 4:30 AM / POWER RESTORED @ 4:31 AM
NORMAL OPERATION @ 5:00 AM, 2B
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
POWER INTERRUPTION @ 5:10 AM
GENSET2 - STARTED @ 5:15 AM
NORMAL OPERATION @ 5:17 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 PM, NO OPERATION DUE TO POWER INTERRUPTION
BP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am ( july 17) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20 PM, NO OPERATION DUE TO POWER INTERRUPTION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:55 PM, NORMAL OPERATION, MERALCO POWER
MERALCO POWER RESTORED @ 8:31 PM, RESUMED NORMAL OPN @ 8:42 PM
GENSET2 STOPPED @ 8:36 PM, NORMAL CONDITION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 18212 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84484175 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29381842 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6424027 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 97 | 84488274 | 4099 | 98.376 | 4.099 | 6.7 | 6.7 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 29382490 | 648 | 158.0873 | 0% | 0% | 100% | 0% | 100% | 30% | 6424942 | 915 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 95 | 84492250 | 3976 | 95.424 | 3.976 | 7.6 | 7.6 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 29383104 | 614 | 154.4266 | 0% | 0% | 100% | 0% | 100% | 30% | 6425877 | 935 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 97 | 84496260 | 4010 | 96.24 | 4.01 | 8.5 | 8.5 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 29383706 | 602 | 150.1247 | 0% | 0% | 100% | 0% | 100% | 30% | 6426776 | 899 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 98 | 84500824 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 2B | 0 | 0 | 855 | 0 | 1010 | N/A | N/A | N/A | N/A | 29384266 | 560 | 122.6994 | 0% | 0% | 100% | 0% | 100% | 30% | 6427686 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 96 | 84504334 | 3510 | 84.24 | 3.51 | 9.5 | 9.5 | 2B | 0 | 0 | 910 | 0 | 1010 | N/A | N/A | N/A | N/A | 29384774 | 508 | 144.7293 | 0% | 0% | 100% | 0% | 100% | 0% | 6427686 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 115 | 84508742 | 4408 | 105.792 | 4.408 | 9.5 | 9.5 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 29385390 | 616 | 139.7459 | 0% | 0% | 100% | 0% | 100% | 0% | 6427686 | 0 | 0.89 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 84514472 | 5730 | 137.52 | 5.73 | 9.4 | 9.4 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29386646 | 1256 | 219.1972 | 0% | 0% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 84521366 | 6894 | 165.456 | 6.894 | 8.9 | 8.9 | 3B+1S | 0 | 1055 | 1198 | 1185 | 1200 | N/A | N/A | N/A | N/A | 29388190 | 1544 | 223.9629 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 144 | 84526466 | 5100 | 122.4 | 5.1 | 8.4 | 8.4 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29389330 | 1140 | 223.5294 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 84532755 | 6289 | 150.936 | 6.289 | 7.6 | 7.6 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29390754 | 1424 | 226.4271 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 47 | 84538870 | 6115 | 146.76 | 6.115 | 7 | 7 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29391734 | 980 | 160.2617 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 84544324 | 5454 | 130.896 | 5.454 | 6.2 | 6.2 | 3B+1S | 0 | 1146 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 990 | 181.5182 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Power Interruption | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 142 | 84549779 | 5455 | 130.92 | 5.455 | 5.7 | 5.7 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Power Interruption | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 132 | 84556020 | 6241 | 149.784 | 6.241 | 5 | 5 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 | 0.92 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Power Interruption | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 84561406 | 5386 | 129.264 | 5.386 | 4.6 | 4.6 | 3B+1S | 0 | 1092 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Power Interruption | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 84567108 | 5702 | 136.848 | 5.702 | 3.8 | 3.8 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Power Interruption | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 137 | 84572889 | 5781 | 138.744 | 5.781 | 3.5 | 3.5 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Power Interruption | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 140 | 84578139 | 5250 | 126 | 5.25 | 2.9 | 2.9 | 3B+1S | 0 | 1004 | 1181 | 1185 | 1176 | N/A | N/A | N/A | N/A | 29392724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 84583303 | 5164 | 123.936 | 5.164 | 2.8 | 2.8 | 3B+1S | 0 | 1002 | 1181 | 1185 | 1175 | N/A | N/A | N/A | N/A | 29394990 | 2266 | 438.8071 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 130 | 84588602 | 5299 | 127.176 | 5.299 | 2.7 | 2.7 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29396194 | 1204 | 227.2127 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 125 | 130 | 84593999 | 5397 | 129.528 | 5.397 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1130 | 1185 | 1133 | N/A | N/A | N/A | N/A | 29397372 | 1178 | 218.2694 | 0% | 100% | 100% | 100% | 100% | 0% | 6427686 | 0 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 123 | 126 | 84599468 | 5469 | 131.256 | 5.469 | 2.6 | 2.6 | 3B+1S | 0 | 1010 | 1085 | 1185 | 1130 | N/A | N/A | N/A | N/A | 29398542 | 1170 | 213.9331 | 0% | 100% | 100% | 0% | 100% | 0% | 6427686 | 0 | 1.03 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 127 | 108 | 84604015 | 4547 | 109.128 | 4.547 | 3.4 | 3.4 | 2B | 0 | 0 | 1105 | 0 | 1130 | N/A | N/A | N/A | N/A | 29399340 | 798 | 175.5003 | 0% | 0% | 100% | 0% | 100% | 30% | 6428361 | 675 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 127 | 99 | 84608377 | 4362 | 104.688 | 4.362 | 4.6 | 4.6 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 29400054 | 714 | 163.6864 | 0% | 0% | 100% | 0% | 100% | 30% | 6429392 | 1031 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.7917 | 124202 | 124202 | 124.202 | 124.202 | [12 empty] | 18212 | 18212 | 146.6321 | [6 empty] | 5365 | 5365 | 0.97 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 30 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:50 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
POWER INTERRUPTION @ 11:56AM
GENSET2 - STARTED @12:01PM
NORMAL OPERATION @12:08PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 PM, NORMAL OPERATION
GENSET2 - STOPPED @ 5:40 PM, NORMAL CONDITION
MERALCO POWER RESTORED @ 5:40 PM, RESUMED NORMAL OPERATION @ 5:45 PM
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JULY 18) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:30 PM DUE TO EXCESS CAPACITY
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 19894 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84608377 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29400054 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6429392 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 127 | 96 | 84612562 | 4185 | 100.44 | 4.185 | 5.8 | 5.8 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 29400794 | 740 | 176.822 | 0% | 0% | 100% | 0% | 100% | 40% | 6430421 | 1029 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 126 | 99 | 84616670 | 4108 | 98.592 | 4.108 | 6.9 | 6.9 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 29401490 | 696 | 169.4255 | 0% | 0% | 100% | 0% | 100% | 40% | 6431556 | 1135 | 0.94 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 126 | 97 | 84620668 | 3998 | 95.952 | 3.998 | 8.1 | 8.1 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 29402152 | 662 | 165.5828 | 0% | 0% | 100% | 0% | 100% | 40% | 6432802 | 1246 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 124 | 95 | 84624678 | 4010 | 96.24 | 4.01 | 9.3 | 9.3 | 2B | 0 | 0 | 1000 | 0 | 1110 | N/A | N/A | N/A | N/A | 29402794 | 642 | 160.0998 | 0% | 0% | 100% | 0% | 100% | 40% | 6434066 | 1264 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A.ONG | 13.1 | 101 | 103 | 84628798 | 4120 | 98.88 | 4.12 | 9.5 | 9.5 | 2B | 0 | 0 | 955 | 0 | 1040 | N/A | N/A | N/A | N/A | 29403350 | 556 | 134.9515 | 0% | 0% | 100% | 0% | 100% | 40% | 6434196 | 130 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 119 | 84633330 | 4532 | 108.768 | 4.532 | 9.5 | 9.5 | 2B | 0 | 0 | 1147 | 0 | 1109 | N/A | N/A | N/A | N/A | 29404046 | 696 | 153.5746 | 0% | 0% | 100% | 0% | 100% | 0% | 6434196 | 0 | 0.91 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 143 | 84639265 | 5935 | 142.44 | 5.935 | 9.3 | 9.3 | 3B+1S | 0 | 993 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29405338 | 1292 | 217.6917 | 0% | 0% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 84645409 | 6144 | 147.456 | 6.144 | 8.8 | 8.8 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29406593 | 1255 | 204.2643 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 142 | 84651729 | 6320 | 151.68 | 6.32 | 8.2 | 8.2 | 3B+1S | 0 | 1063 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29407852 | 1259 | 199.2089 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 84657686 | 5957 | 142.968 | 5.957 | 7.6 | 7.6 | 3B+1S | 0 | 1053 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29409016 | 1164 | 195.4004 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 | 0.87 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 84663829 | 6143 | 147.432 | 6.143 | 7.1 | 7.1 | 3B+1S | 0 | 1025 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29410249 | 1233 | 200.7163 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 84669862 | 6033 | 144.792 | 6.033 | 6.6 | 6.6 | 3B+1S | 0 | 1073 | 1196 | 1185 | 1200 | N/A | N/A | N/A | N/A | 29411416 | 1167 | 193.4361 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 142 | 84675688 | 5826 | 139.824 | 5.826 | 6.2 | 6.2 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29413450 | 2034 | 349.1246 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 122 | 139 | 84681474 | 5786 | 138.864 | 5.786 | 5.5 | 5.5 | 3B+1S | 0 | 1109 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29414764 | 1314 | 227.0999 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 134 | 84686347 | 4873 | 116.952 | 4.873 | 4.9 | 4.9 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29414764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 84692123 | 5776 | 138.624 | 5.776 | 4.4 | 4.4 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29414764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 84697764 | 5641 | 135.384 | 5.641 | 4 | 4 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29414764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 84703431 | 5667 | 136.008 | 5.667 | 3.8 | 3.8 | 3B+1S | 0 | 1003 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 29414764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 137 | 84708694 | 5263 | 126.312 | 5.263 | 3.7 | 3.7 | 3B+1S | 0 | 1055 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29415366 | 602 | 114.3834 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 129 | 84713816 | 5122 | 122.928 | 5.122 | 3.1 | 3.1 | 2B+1S | 0 | 1074 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29416394 | 1028 | 200.7029 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 84719094 | 5278 | 126.672 | 5.278 | 2.4 | 2.4 | 2B+1S | 0 | 1068 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29417442 | 1048 | 198.5601 | 0% | 100% | 100% | 100% | 100% | 0% | 6434196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 130 | 84724266 | 5172 | 124.128 | 5.172 | 2 | 2 | 2B+1S | 0 | 1027 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29418464 | 1022 | 197.6025 | 0% | 100% | 100% | 0% | 100% | 0% | 6434196 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 108 | 84728859 | 4593 | 110.232 | 4.593 | 2.7 | 2.7 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 29419254 | 790 | 172.0009 | 0% | 0% | 100% | 0% | 100% | 25% | 6434896 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 84733080 | 4221 | 101.304 | 4.221 | 3.8 | 3.8 | 2B | 0 | 0 | 1005 | 0 | 1110 | N/A | N/A | N/A | N/A | 29419948 | 694 | 164.416 | 0% | 0% | 100% | 0% | 100% | 25% | 6435941 | 1045 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.6667 | 124703 | 124703 | 124.703 | 124.703 | [12 empty] | 19894 | 19894 | 159.531 | [6 empty] | 6549 | 6549 | 0.90167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 5 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 12:01 pm to 5 am ( JULY 19) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:25 PM, NORMAL OPERATION
POWER INTERUPTION 2:00 PM
GENSET2 - STARTED @ 2:15 PM RESUME NORMAL OPERATION 2:20 PM
GENSET2 - STOPPED @ 6:38 PM, NORMAL CONDITION
MERALCO POWER RESTORED @ 6:38 PM, RESUMED NORMAL OPERATION @ 6:42 PM
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 19) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | O. OCAMPO / A. CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25906 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84733080 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29419948 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6435941 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 98 | 84737192 | 4112 | 98.688 | 4.112 | 5 | 5 | 2B | 0 | 0 | 1075 | 0 | 1110 | N/A | N/A | N/A | N/A | 29420658 | 710 | 172.6654 | 0% | 0% | 100% | 0% | 100% | 35% | 6436897 | 956 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 100 | 84741328 | 4136 | 99.264 | 4.136 | 6.1 | 6.1 | 2B | 0 | 0 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 29421344 | 686 | 165.8607 | 0% | 0% | 100% | 0% | 100% | 35% | 6438026 | 1129 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 84745330 | 4002 | 96.048 | 4.002 | 7.6 | 7.6 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 29422006 | 662 | 165.4173 | 0% | 0% | 100% | 0% | 100% | 35% | 6439324 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 132 | 96 | 84749376 | 4046 | 97.104 | 4.046 | 8.8 | 8.8 | 2B | 0 | 0 | 1005 | 0 | 1110 | N/A | N/A | N/A | N/A | 29422648 | 642 | 158.6752 | 0% | 0% | 100% | 0% | 100% | 35% | 6440601 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 99 | 84753360 | 3984 | 95.616 | 3.984 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 1010 | N/A | N/A | N/A | N/A | 29423238 | 590 | 148.0924 | 0% | 0% | 100% | 0% | 100% | 35% | 6441344 | 743 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 110 | 116 | 84757746 | 4386 | 105.264 | 4.386 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1110 | N/A | N/A | N/A | N/A | 29423830 | 592 | 134.9749 | 0% | 0% | 100% | 0% | 100% | 0% | 6441344 | 0 | 0.89 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 139 | 84763672 | 5926 | 142.224 | 5.926 | 9.5 | 9.5 | 3B | 0 | 0 | 1105 | 1185 | 1196 | N/A | N/A | N/A | N/A | 29425044 | 1214 | 204.8599 | 0% | 0% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 84769281 | 5609 | 134.616 | 5.609 | 9.3 | 9.3 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29426276 | 1232 | 219.647 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 147 | 84775464 | 6183 | 148.392 | 6.183 | 8.8 | 8.8 | 3B+1S | 0 | 1117 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29427652 | 1376 | 222.5457 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 149 | 84781574 | 6110 | 146.64 | 6.11 | 7.9 | 7.9 | 3B+1S | 0 | 1131 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29429042 | 1390 | 227.4959 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 147 | 84787755 | 6181 | 148.344 | 6.181 | 7.2 | 7.2 | 3B+1S | 0 | 1128 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29430434 | 1392 | 225.2063 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 148 | 84793906 | 6151 | 147.624 | 6.151 | 6.3 | 6.3 | 3B+1S | 0 | 1107 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29431842 | 1408 | 228.9059 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 143 | 84799875 | 5969 | 143.256 | 5.969 | 5.8 | 5.8 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29433190 | 1348 | 225.8335 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 124 | 139 | 84805798 | 5923 | 142.152 | 5.923 | 5.2 | 5.2 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29434570 | 1380 | 232.99 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 140 | 84811649 | 5851 | 140.424 | 5.851 | 4.4 | 4.4 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29435932 | 1362 | 232.7807 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 84817662 | 6013 | 144.312 | 6.013 | 3.7 | 3.7 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29437328 | 1396 | 232.1636 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 84823295 | 5633 | 135.192 | 5.633 | 3.3 | 3.3 | 3B+1S | 0 | 1187 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29438722 | 1394 | 247.4703 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 141 | 132 | 84828818 | 5523 | 132.552 | 5.523 | 3.4 | 3.4 | 3B+1S | 0 | 1087 | 1196 | 1185 | 1196 | N/A | N/A | N/A | N/A | 29440062 | 1340 | 242.6218 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 144 | 129 | 84834173 | 5355 | 128.52 | 5.355 | 3.9 | 3.9 | 3B+1S | 0 | 991 | 1197 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29441378 | 1316 | 245.7516 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 129 | 84839550 | 5377 | 129.048 | 5.377 | 3.5 | 3.5 | 2B+1S | 0 | 1038 | 1197 | 0 | 1197 | N/A | N/A | N/A | N/A | 29442440 | 1062 | 197.5079 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 84844651 | 5101 | 122.424 | 5.101 | 3 | 3 | 2B+1S | 0 | 1024 | 1197 | 0 | 1196 | N/A | N/A | N/A | N/A | 29443446 | 1006 | 197.2162 | 0% | 100% | 100% | 100% | 100% | 0% | 6441344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 119 | 84849753 | 5102 | 122.448 | 5.102 | 2.8 | 2.8 | 2B+1S | 0 | 986 | 1196 | 0 | 1196 | N/A | N/A | N/A | N/A | 29444452 | 1006 | 197.1776 | 0% | 100% | 100% | 0% | 100% | 0% | 6441344 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 99 | 84854072 | 4319 | 103.656 | 4.319 | 3.7 | 3.7 | 2B | 0 | 0 | 1075 | 0 | 1110 | N/A | N/A | N/A | N/A | 29445186 | 734 | 169.9467 | 0% | 0% | 100% | 0% | 100% | 25% | 6442079 | 735 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 101 | 84858213 | 4141 | 99.384 | 4.141 | 4.7 | 4.7 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 29445854 | 668 | 161.3137 | 0% | 0% | 100% | 0% | 100% | 25% | 6443019 | 940 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.3333 | 125133 | 125133 | 125.133 | 125.133 | [12 empty] | 25906 | 25906 | 207.0277 | [6 empty] | 7078 | 7078 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:55 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 20) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
XCV4 OPENED @ 4:05 PM (13%) / CLOSED @ 7:00 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 20) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25186 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84858213 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29445854 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6443019 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 98 | 84862344 | 4131 | 99.144 | 4.131 | 5.6 | 5.6 | 2B | 0 | 0 | 1080 | 0 | 1110 | N/A | N/A | N/A | N/A | 29446562 | 708 | 171.3871 | 0% | 0% | 100% | 0% | 100% | 35% | 6443854 | 835 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 97 | 84866332 | 3988 | 95.712 | 3.988 | 6.6 | 6.6 | 2B | 0 | 0 | 1048 | 0 | 1110 | N/A | N/A | N/A | N/A | 29447244 | 682 | 171.013 | 0% | 0% | 100% | 0% | 100% | 35% | 6444791 | 937 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 93 | 84870295 | 3963 | 95.112 | 3.963 | 7.7 | 7.7 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 29447906 | 662 | 167.0452 | 0% | 0% | 100% | 0% | 100% | 35% | 6445937 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 91 | 84874212 | 3917 | 94.008 | 3.917 | 8.8 | 8.8 | 2B | 0 | 0 | 1005 | 0 | 1110 | N/A | N/A | N/A | N/A | 29448542 | 636 | 162.3692 | 0% | 0% | 100% | 0% | 100% | 35% | 6447008 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 92 | 84878190 | 3978 | 95.472 | 3.978 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1010 | N/A | N/A | N/A | N/A | 29449118 | 576 | 144.7964 | 0% | 0% | 100% | 0% | 100% | 35% | 6447646 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 107 | 108 | 84882426 | 4236 | 101.664 | 4.236 | 9.5 | 9.5 | 2B | 0 | 0 | 1015 | 0 | 1030 | N/A | N/A | N/A | N/A | 29449658 | 540 | 127.4788 | 0% | 0% | 100% | 0% | 100% | 0% | 6447646 | 0 | 0.94 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 136 | 84887761 | 5335 | 128.04 | 5.335 | 9.5 | 9.5 | 3B | 0 | 0 | 1073 | 1185 | 1138 | N/A | N/A | N/A | N/A | 29450710 | 1052 | 197.1884 | 0% | 0% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 139 | 84893486 | 5725 | 137.4 | 5.725 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29451900 | 1190 | 207.8603 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 84899460 | 5974 | 143.376 | 5.974 | 9.3 | 9.3 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29453202 | 1302 | 217.9444 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 84905628 | 6168 | 148.032 | 6.168 | 8.7 | 8.7 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 29454556 | 1354 | 219.5201 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 | 0.86 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 147 | 84911826 | 6198 | 148.752 | 6.198 | 7.9 | 7.9 | 3B+1S | 0 | 1165 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 29455940 | 1384 | 223.2978 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 150 | 84917966 | 6140 | 147.36 | 6.14 | 6.9 | 6.9 | 3B+1S | 0 | 1159 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29457344 | 1404 | 228.6645 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 84923947 | 5981 | 143.544 | 5.981 | 6.2 | 6.2 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29458758 | 1414 | 236.4153 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 144 | 84929812 | 5865 | 140.76 | 5.865 | 5.5 | 5.5 | 3B+1S | 0 | 1119 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29460118 | 1360 | 231.8841 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 126 | 141 | 84935818 | 6006 | 144.144 | 6.006 | 4.7 | 4.7 | 3B+1S | 0 | 1087 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29461518 | 1400 | 233.1002 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 136 | 84941787 | 5969 | 143.256 | 5.969 | 4 | 4 | 3B+1S | 0 | 1078 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29462906 | 1388 | 232.5348 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 84947482 | 5695 | 136.68 | 5.695 | 3.5 | 3.5 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29464222 | 1316 | 231.0799 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 16 | 11.2676 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 84953099 | 5617 | 134.808 | 5.617 | 3.5 | 3.5 | 3B | 0 | 0 | 1125 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29465426 | 1204 | 214.3493 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 23 | 16.1972 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 130 | 84958654 | 5555 | 133.32 | 5.555 | 2.9 | 2.9 | 2B+1S | 0 | 1101 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29466518 | 1092 | 196.5797 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 117 | 84963978 | 5324 | 127.776 | 5.324 | 2.4 | 2.4 | 2B+1S | 0 | 1049 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 29467566 | 1048 | 196.8445 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 124 | 84969153 | 5175 | 124.2 | 5.175 | 1.9 | 1.9 | 2B+1S | 0 | 1032 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29468572 | 1006 | 194.3961 | 0% | 100% | 100% | 100% | 100% | 0% | 6447646 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 118 | 84974255 | 5102 | 122.448 | 5.102 | 1.7 | 1.7 | 2B+1S | 0 | 995 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29469592 | 1020 | 199.9216 | 0% | 100% | 100% | 0% | 100% | 0% | 6447646 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 134 | 101 | 84978579 | 4324 | 103.776 | 4.324 | 2.8 | 2.8 | 2B | 0 | 0 | 1115 | 0 | 1110 | N/A | N/A | N/A | N/A | 29470334 | 742 | 171.6004 | 0% | 0% | 100% | 0% | 100% | 30% | 6448688 | 1042 |  | Additional 5psi to normal target discharge pressure as request OF Engr. E.Llagas Jr. & Engr. M Buligan
71:00 | 24:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 129 | 103 | 84982782 | 4203 | 100.872 | 4.203 | 4.3 | 4.3 | 2B | 0 | 0 | 1085 | 0 | 1110 | N/A | N/A | N/A | N/A | 29471040 | 706 | 167.9753 | 0% | 0% | 100% | 0% | 100% | 30% | 6450024 | 1336 |  | Additional 5psi to normal target discharge pressure as request OF Engr. E.Llagas Jr. & Engr. M Buligan | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.25 | 124569 | 124569 | 124.569 | 124.569 | [12 empty] | 25186 | 25186 | 202.1851 | [6 empty] | 7005 | 7005 | 0.93667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 21) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 5:01 PM
SP2 - OPENED @ 6:01 PM
BP2 - STOPPED @6:01 PM
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:30 pm to 5am (JULY 21) as per request of Engr. Michael R. Buligan (WN Officer)
Target Discharge Pressure set to 68 psi @ 10:30 pm as per request of Engr. Michael R. Buligan (WN Officer)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ORLANDO L. OCAMPO
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25430 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 84982782 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29471040 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6450024 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 127 | 101 | 84986992 | 4210 | 101.04 | 4.21 | 5.4 | 5.4 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 29471784 | 744 | 176.7221 | 0% | 0% | 100% | 0% | 100% | 40% | 6451084 | 1060 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 127 | 99 | 84991046 | 4054 | 97.296 | 4.054 | 6.6 | 6.6 | 2B | 0 | 0 | 1068 | 0 | 1110 | N/A | N/A | N/A | N/A | 29472482 | 698 | 172.1756 | 0% | 0% | 100% | 0% | 100% | 40% | 6452202 | 1118 | 0.95 | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 126 | 99 | 84995122 | 4076 | 97.824 | 4.076 | 7.7 | 7.7 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 29473158 | 676 | 165.8489 | 0% | 0% | 100% | 0% | 100% | 40% | 6453418 | 1216 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 119 | 101 | 84999168 | 4046 | 97.104 | 4.046 | 8.9 | 8.9 | 2B | 0 | 0 | 1000 | 0 | 1110 | N/A | N/A | N/A | N/A | 29473810 | 652 | 161.1468 | 0% | 0% | 100% | 0% | 100% | 40% | 6454619 | 1201 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A.ONG | 13.1 | 107 | 108 | 85003277 | 4109 | 98.616 | 4.109 | 9.5 | 9.5 | 2B | 0 | 0 | 1030 | 0 | 1048 | N/A | N/A | N/A | N/A | 29474408 | 598 | 145.5342 | 0% | 0% | 100% | 0% | 100% | 40% | 6455088 | 469 |  | Additional 5psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 125 | 85008088 | 4811 | 115.464 | 4.811 | 9.5 | 9.5 | 2B | 0 | 0 | 1170 | 0 | 1160 | N/A | N/A | N/A | N/A | 29475170 | 762 | 158.387 | 0% | 0% | 100% | 0% | 100% | 0% | 6455088 | 0 | 0.87 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 146 | 85013962 | 5874 | 140.976 | 5.874 | 9.3 | 9.3 | 3B+1S | 0 | 978 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29476474 | 1304 | 221.9952 | 0% | 0% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 85019957 | 5995 | 143.88 | 5.995 | 9 | 9 | 3B+1S | 0 | 1011 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29477798 | 1324 | 220.8507 | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 144 | 85026043 | 6086 | 146.064 | 6.086 | 8.6 | 8.6 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29479134 | 1336 | 219.5202 | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 142 | 85032125 | 6082 | 145.968 | 6.082 | 8.1 | 8.1 | 3B+1S | 0 | 1033 | 1196 | 1185 | 1196 | N/A | N/A | N/A | N/A | 29480490 | 1356 | 222.953 | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 0 | 85032125 | 0 | 0 | 0 | 7.5 | 7.5 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29481870 | 1380 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Normal operation schedule
59:00 | 12:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 0 | 85032125 | 0 | 0 | 0 | 6.9 | 6.9 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29483202 | 1332 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 0 | 85032125 | 0 | 0 | 0 | 6.7 | 6.7 | 3B+1S | 0 | 998 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29484512 | 1310 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 0 | 85032125 | 0 | 0 | 0 | 6.6 | 6.6 | 3B+1S | 0 | 999 | 1187 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29485802 | 1290 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 0 | 85032125 | 0 | 0 | 0 | 6.4 | 6.4 | 3B+1S | 0 | 998 | 1166 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29487078 | 1276 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 0 | 85032125 | 0 | 0 | 0 | 6.1 | 6.1 | 3B+1S | 0 | 999 | 1134 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29488357 | 1279 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 0 | 85032125 | 0 | 0 | 0 | 6 | 6 | 3B+1S | 0 | 999 | 1150 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29489642 | 1285 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 14 | 9.8592 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 0 | 85032125 | 0 | 0 | 0 | 5.7 | 5.7 | 3B+1S | 0 | 1021 | 1086 | 1185 | 1110 | N/A | N/A | N/A | N/A | 29490834 | 1192 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 0 | 85032125 | 0 | 0 | 0 | 5.2 | 5.2 | 3B+1S | 0 | 1021 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29491922 | 1088 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 0 | 85032125 | 0 | 0 | 0 | 4.5 | 4.5 | 2B+1S | 0 | 1061 | 1191 | 0 | 1198 | N/A | N/A | N/A | N/A | 29493008 | 1086 | #DIV/0! | 0% | 100% | 100% | 0% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 0 | 85032125 | 0 | 0 | 0 | 3.7 | 3.7 | 2B+1S | 0 | 1081 | 1180 | 0 | 1198 | N/A | N/A | N/A | N/A | 29494086 | 1078 | #DIV/0! | 0% | 100% | 100% | 0% | 100% | 0% | 6455088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 0 | 85032125 | 0 | 0 | 0 | 3.1 | 3.1 | 2B+1S | 0 | 1040 | 1132 | 0 | 1190 | N/A | N/A | N/A | N/A | 29495170 | 1084 | #DIV/0! | 0% | 100% | 100% | 0% | 100% | 0% | 6455088 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 0 | 85032125 | 0 | 0 | 0 | 3.6 | 3.6 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 29495812 | 642 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 25% | 6455571 | 483 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 0 | 85032125 | 0 | 0 | 0 | 4.6 | 4.6 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 29496470 | 658 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 25% | 6456372 | 801 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 50.5 | 49343 | 49343 | 49.343 | 49.343 | [12 empty] | 25430 | 25430 | 515.372 | [6 empty] | 6348 | 6348 | 0.91833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 5 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South) & Engr. M. Buligan.
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
NOTE : DISCHARGE FLOW METER INSTRUMENTATION DEFECTIVE AS OF 11 AM, FOR TELEM MAINTENANCE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 22) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South) & Engr. M. Buligan.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24682 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 0 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29496470 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6456372 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 0 | 0 | 0 | 0 | 0 | 5.5 | 5.5 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 29497166 | 696 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 35% | 6457193 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 29497818 | 652 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 35% | 6458210 | 1017 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 0 | 0 | 0 | 0 | 0 | 7.6 | 7.6 | 2B | 0 | 0 | 975 | 0 | 1110 | N/A | N/A | N/A | N/A | 29498434 | 616 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 35% | 6459251 | 1041 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 0 | 0 | 0 | 0 | 0 | 8.7 | 8.7 | 2B | 0 | 0 | 959 | 0 | 1110 | N/A | N/A | N/A | N/A | 29499054 | 620 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 35% | 6460280 | 1029 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 0 | 0 | 0 | 0 | 0 | 9.5 | 9.5 | 2B | 0 | 0 | 986 | 0 | 1048 | N/A | N/A | N/A | N/A | 29499650 | 596 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 35% | 6461152 | 872 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 0 | 0 | 0 | 0 | 0 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1110 | N/A | N/A | N/A | N/A | 29500380 | 730 | #DIV/0! | 0% | 0% | 100% | 0% | 100% | 0% | 6461152 | 0 | 0.91 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 0 | 0 | 0 | 0 | 0 | 9.4 | 9.4 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29501626 | 1246 | #DIV/0! | 0% | 0% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29502976 | 1350 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 0 | 0 | 0 | 0 | 0 | 8.7 | 8.7 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29504294 | 1318 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 0 | 0 | 0 | 0 | 0 | 8.3 | 8.3 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29505654 | 1360 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 0 | 0 | 0 | 0 | 0 | 8.1 | 8.1 | 3B+1S | 0 | 994 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29506966 | 1312 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Normal operation schedule
59:00 | 12:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 0 | 0 | 0 | 0 | 0 | 7.9 | 7.9 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29508284 | 1318 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 142 | 4685 | 4685 | 112.44 | 4.685 | 7.7 | 7.7 | 3B+1S | 0 | 1031 | 1035 | 1185 | 1039 | N/A | N/A | N/A | N/A | 29509546 | 1262 | 269.3703 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 123 | 126 | 10166 | 5481 | 131.544 | 5.481 | 7.3 | 7.3 | 3B+1S | 0 | 1014 | 1035 | 1185 | 1038 | N/A | N/A | N/A | N/A | 29510758 | 1212 | 221.1275 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 124 | 122 | 15455 | 5289 | 126.936 | 5.289 | 7 | 7 | 3B+1S | 0 | 1034 | 1115 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29511982 | 1224 | 231.4237 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 134 | 20916 | 5461 | 131.064 | 5.461 | 6.4 | 6.4 | 3B+1S | 0 | 1073 | 1115 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29513124 | 1142 | 209.1192 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 139 | 26495 | 5579 | 133.896 | 5.579 | 5.9 | 5.9 | 3B+1S | 0 | 1064 | 1115 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29514322 | 1198 | 214.7338 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 131 | 31883 | 5388 | 129.312 | 5.388 | 5.6 | 5.6 | 3B+1S | 0 | 1023 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29515480 | 1158 | 214.922 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 128 | 37449 | 5566 | 133.584 | 5.566 | 5.2 | 5.2 | 3B+1S | 0 | 1043 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29516646 | 1166 | 209.4862 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 42887 | 5438 | 130.512 | 5.438 | 4.3 | 4.3 | 2B+1S | 0 | 1079 | 1176 | 0 | 1182 | N/A | N/A | N/A | N/A | 29517710 | 1064 | 195.6602 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 48133 | 5246 | 125.904 | 5.246 | 3.5 | 3.5 | 2B+1S | 0 | 1074 | 1176 | 0 | 1182 | N/A | N/A | N/A | N/A | 29518738 | 1028 | 195.9588 | 0% | 100% | 100% | 100% | 100% | 0% | 6461152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 122 | 53400 | 5267 | 126.408 | 5.267 | 3.1 | 3.1 | 2B+1S | 0 | 993 | 1155 | 0 | 1160 | N/A | N/A | N/A | N/A | 29519750 | 1012 | 192.1397 | 0% | 100% | 100% | 0% | 100% | 0% | 6461152 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 105 | 57568 | 4168 | 100.032 | 4.168 | 4 | 4 | 2B | 0 | 0 | 1084 | 0 | 1110 | N/A | N/A | N/A | N/A | 29520506 | 756 | 181.382 | 0% | 0% | 100% | 0% | 100% | 25% | 6462013 | 861 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 97 | 61741 | 4173 | 100.152 | 4.173 | 5.3 | 5.3 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 29521152 | 646 | 154.8047 | 0% | 0% | 100% | 0% | 100% | 25% | 6462214 | 201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 62.625 | 61741 | 61741 | 61.741 | 61.741 | [12 empty] | 24682 | 24682 | 399.7668 | [6 empty] | 5842 | 5842 | 0.93833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:45 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 23) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:45 PM, NORMAL OPERATION
Additional 5 psi to target discharge pressure @ 10:01 pm to 5am (JUNE 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm
WATER NETWORK | [12 empty] | 2pm - 10pm
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24466 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61741 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29521152 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6462214 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 | 78 | 65731 | 3990 | 95.76 | 3.99 | 6 | 6 | 2B | 0 | 0 | 1037 | 0 | 1110 | N/A | N/A | N/A | N/A | 29521824 | 672 | 168.4211 | 0% | 0% | 100% | 0% | 100% | 35% | 6463940 | 1726 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 90 | 69621 | 3890 | 93.36 | 3.89 | 7 | 7 | 2B | 0 | 0 | 994 | 0 | 1110 | N/A | N/A | N/A | N/A | 29522474 | 650 | 167.0951 | 0% | 0% | 100% | 0% | 100% | 35% | 6464819 | 879 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 91 | 73421 | 3800 | 91.2 | 3.8 | 7.9 | 7.9 | 2B | 0 | 0 | 1041 | 0 | 1110 | N/A | N/A | N/A | N/A | 29523074 | 600 | 157.8947 | 0% | 0% | 100% | 0% | 100% | 35% | 6465749 | 930 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 137 | 96 | 77200 | 3779 | 90.696 | 3.779 | 8.9 | 8.9 | 2B | 0 | 0 | 1026 | 0 | 1028 | N/A | N/A | N/A | N/A | 29523650 | 576 | 152.4213 | 0% | 0% | 100% | 0% | 100% | 35% | 6466656 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 105 | 81316 | 4116 | 98.784 | 4.116 | 9.6 | 9.6 | 2B | 0 | 0 | 996 | 0 | 1028 | N/A | N/A | N/A | N/A | 29524232 | 582 | 141.3994 | 0% | 0% | 100% | 0% | 100% | 35% | 6467286 | 630 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 115 | 85699 | 4383 | 105.192 | 4.383 | 9.6 | 9.6 | 2B | 0 | 0 | 1196 | 0 | 1028 | N/A | N/A | N/A | N/A | 29524874 | 642 | 146.475 | 0% | 0% | 100% | 0% | 100% | 0% | 6467286 | 0 | 0.88 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 140 | 91617 | 5918 | 142.032 | 5.918 | 9.3 | 9.3 | 3B+1S | 0 | 1031 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 29526138 | 1264 | 213.5857 | 0% | 0% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 143 | 97459 | 5842 | 140.208 | 5.842 | 8.8 | 8.8 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29527414 | 1276 | 218.4183 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 144 | 103542 | 6083 | 145.992 | 6.083 | 8.4 | 8.4 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29528750 | 1336 | 219.6285 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 139 | 109604 | 6062 | 145.488 | 6.062 | 8 | 8 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29530104 | 1354 | 223.3586 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 141 | 115634 | 6030 | 144.72 | 6.03 | 7.7 | 7.7 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29531444 | 1340 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 136 | 121429 | 5795 | 139.08 | 5.795 | 7.6 | 7.6 | 3B+1S | 0 | 889 | 1157 | 1185 | 1160 | N/A | N/A | N/A | N/A | 29532726 | 1282 | 221.2252 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 140 | 127104 | 5675 | 136.2 | 5.675 | 7.6 | 7.6 | 3B | 0 | 0 | 1192 | 1185 | 1189 | N/A | N/A | N/A | N/A | 29533948 | 1222 | 215.3304 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 131 | 132910 | 5806 | 139.344 | 5.806 | 7.5 | 7.5 | 3B+1S | 0 | 1004 | 1192 | 1185 | 1189 | N/A | N/A | N/A | N/A | 29535274 | 1326 | 228.3844 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 | 0.96 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 131 | 138343 | 5433 | 130.392 | 5.433 | 7.4 | 7.4 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 29536518 | 1244 | 228.9711 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 131 | 143921 | 5578 | 133.872 | 5.578 | 7.2 | 7.2 | 3B+1S | 0 | 999 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 29537770 | 1252 | 224.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 134 | 149594 | 5673 | 136.152 | 5.673 | 6.6 | 6.6 | 3B+1S | 0 | 1078 | 1115 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29539002 | 1232 | 217.169 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 113 | 129 | 154927 | 5333 | 127.992 | 5.333 | 5.9 | 5.9 | 3B+1S | 0 | 1094 | 1053 | 1185 | 1057 | N/A | N/A | N/A | N/A | 29540106 | 1104 | 207.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 15 | 10.5634 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 116 | 129 | 160352 | 5425 | 130.2 | 5.425 | 5.1 | 5.1 | 3B+1S | 0 | 1094 | 1053 | 1185 | 1057 | N/A | N/A | N/A | N/A | 29541262 | 1156 | 213.0876 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 131 | 165698 | 5346 | 128.304 | 5.346 | 4 | 4 | 2B+1S | 0 | 1134 | 1155 | 0 | 1160 | N/A | N/A | N/A | N/A | 29542322 | 1060 | 198.2791 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 170845 | 5147 | 123.528 | 5.147 | 3.2 | 3.2 | 2B+1S | 0 | 1046 | 1176 | 0 | 1181 | N/A | N/A | N/A | N/A | 29543302 | 980 | 190.4022 | 0% | 100% | 100% | 100% | 100% | 0% | 6467286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 118 | 176040 | 5195 | 124.68 | 5.195 | 3 | 3 | 2B+1S | 0 | 635 | 1198 | 0 | 1181 | N/A | N/A | N/A | N/A | 29544312 | 1010 | 194.4177 | 0% | 100% | 100% | 0% | 100% | 0% | 6467286 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 100 | 180265 | 4225 | 101.4 | 4.225 | 3.8 | 3.8 | 2B | 0 | 0 | 960 | 0 | 1110 | N/A | N/A | N/A | N/A | 29545004 | 692 | 163.787 | 0% | 0% | 100% | 0% | 100% | 25% | 6468061 | 775 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 99 | 184326 | 4061 | 97.464 | 4.061 | 4.9 | 4.9 | 2B | 0 | 0 | 856 | 0 | 1110 | N/A | N/A | N/A | N/A | 29545618 | 614 | 151.1943 | 0% | 0% | 100% | 0% | 100% | 25% | 6469089 | 1028 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.4583 | 122585 | 122585 | 122.585 | 122.585 | [12 empty] | 24466 | 24466 | 199.584 | [6 empty] | 6875 | 6875 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 10:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION 9.6M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:15 AM TO MAINTAIN 83 PSI TARGET PRESSURE
SP2 - STOPPED @ 11:45 AM
SP2- OPENED @ 1:20 PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 24) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:33 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 23) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24912 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 184326 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29545618 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6469089 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 98 | 188348 | 4022 | 96.528 | 4.022 | 5.9 | 5.9 | 2B | 0 | 0 | 1012 | 0 | 1110 | N/A | N/A | N/A | N/A | 29546292 | 674 | 167.5783 | 0% | 0% | 100% | 0% | 100% | 35% | 6470044 | 955 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 97 | 192313 | 3965 | 95.16 | 3.965 | 7.1 | 7.1 | 2B | 0 | 0 | 969 | 0 | 1110 | N/A | N/A | N/A | N/A | 29546930 | 638 | 160.9079 | 0% | 0% | 100% | 0% | 100% | 35% | 6471086 | 1042 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 97 | 196086 | 3773 | 90.552 | 3.773 | 8.9 | 8.9 | 2B | 0 | 0 | 940 | 0 | 1110 | N/A | N/A | N/A | N/A | 29547526 | 596 | 157.9645 | 0% | 0% | 100% | 0% | 100% | 35% | 6472168 | 1082 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 93 | 199964 | 3878 | 93.072 | 3.878 | 9.2 | 9.2 | 2B | 0 | 0 | 835 | 0 | 1050 | N/A | N/A | N/A | N/A | 29548098 | 572 | 147.4987 | 0% | 0% | 100% | 0% | 100% | 35% | 6473189 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 104 | 203792 | 3828 | 91.872 | 3.828 | 9.5 | 9.5 | 2B | 0 | 0 | 940 | 0 | 1010 | N/A | N/A | N/A | N/A | 29548586 | 488 | 127.4817 | 0% | 0% | 100% | 0% | 100% | 35% | 6473502 | 313 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 118 | 208460 | 4668 | 112.032 | 4.668 | 9.5 | 9.5 | 2B | 0 | 0 | 1177 | 0 | 1109 | N/A | N/A | N/A | N/A | 29549282 | 696 | 149.1003 | 0% | 0% | 100% | 0% | 100% | 0% | 6473502 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 136 | 214333 | 5873 | 140.952 | 5.873 | 9.3 | 9.3 | 3B+1S | 0 | 967 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29550598 | 1316 | 224.0763 | 0% | 0% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 134 | 220298 | 5965 | 143.16 | 5.965 | 8.9 | 8.9 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29551908 | 1310 | 219.6144 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 226404 | 6106 | 146.544 | 6.106 | 8.5 | 8.5 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29553290 | 1382 | 226.3348 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 232829 | 6425 | 154.2 | 6.425 | 7.9 | 7.9 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29554622 | 1332 | 207.3152 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 238585 | 5756 | 138.144 | 5.756 | 7.4 | 7.4 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29556004 | 1382 | 240.0973 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 142 | 244653 | 6068 | 145.632 | 6.068 | 7.1 | 7.1 | 3B+1S | 0 | 996 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29557374 | 1370 | 225.7746 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 136 | 250343 | 5690 | 136.56 | 5.69 | 7.1 | 7.1 | 3B | 0 | 0 | 1188 | 1185 | 1195 | N/A | N/A | N/A | N/A | 29558618 | 1244 | 218.6292 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 134 | 256123 | 5780 | 138.72 | 5.78 | 6.9 | 6.9 | 3B+1S | 0 | 992 | 1160 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29559934 | 1316 | 227.6817 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 | 0.85 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 130 | 261538 | 5415 | 129.96 | 5.415 | 6.6 | 6.6 | 3B+1S | 0 | 968 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 29561188 | 1254 | 231.5789 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 267088 | 5550 | 133.2 | 5.55 | 6.5 | 6.5 | 3B+1S | 0 | 1029 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 29562446 | 1258 | 226.6667 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 135 | 272809 | 5721 | 137.304 | 5.721 | 6.1 | 6.1 | 3B+1S | 0 | 1058 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 29563682 | 1236 | 216.0461 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 17 | 11.9718 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 118 | 131 | 278276 | 5467 | 131.208 | 5.467 | 5.5 | 5.5 | 3B+1S | 0 | 1066 | 1060 | 1185 | 1067 | N/A | N/A | N/A | N/A | 29564822 | 1140 | 208.5239 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 17 | 11.9718 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 116 | 135 | 283744 | 5468 | 131.232 | 5.468 | 4.8 | 4.8 | 3B+1S | 0 | 1126 | 1064 | 1185 | 1067 | N/A | N/A | N/A | N/A | 29565962 | 1140 | 208.4857 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 133 | 289282 | 5538 | 132.912 | 5.538 | 3.9 | 3.9 | 2B+1S | 0 | 1064 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29567058 | 1096 | 197.9054 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 134 | 294609 | 5327 | 127.848 | 5.327 | 3.3 | 3.3 | 2B+1S | 0 | 1040 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29568102 | 1044 | 195.9827 | 0% | 100% | 100% | 100% | 100% | 0% | 6473502 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 122 | 299756 | 5147 | 123.528 | 5.147 | 2.9 | 2.9 | 2B+1S | 0 | 988 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29569128 | 1026 | 199.3394 | 0% | 100% | 100% | 0% | 100% | 0% | 6473502 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 97 | 304312 | 4556 | 109.344 | 4.556 | 3.7 | 3.7 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 29569888 | 760 | 166.813 | 0% | 0% | 100% | 0% | 100% | 25% | 6474176 | 674 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 98 | 308352 | 4040 | 96.96 | 4.04 | 4.8 | 4.8 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 29570530 | 642 | 158.9109 | 0% | 0% | 100% | 0% | 100% | 25% | 6475126 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.375 | 124026 | 124026 | 124.026 | 124.026 | [12 empty] | 24912 | 24912 | 200.8611 | [6 empty] | 6037 | 6037 | 0.91 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:15 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 12:05 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 25) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION
PERRY'S FUEL ARRIVED @ 9:55 PM FOR DELIVERY OF 8,000 LITERS OF DEISEL FUEL.

## JULY 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25656 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 308352 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29570530 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6475126 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 102 | 312416 | 4064 | 97.536 | 4.064 | 5.6 | 5.6 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 29571222 | 692 | 170.2756 | 0% | 0% | 100% | 0% | 100% | 35% | 6475944 | 818 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 94 | 316471 | 4055 | 97.32 | 4.055 | 6.5 | 6.5 | 2B | 0 | 0 | 1012 | 0 | 1110 | N/A | N/A | N/A | N/A | 29571890 | 668 | 164.7349 | 0% | 0% | 100% | 0% | 100% | 35% | 6476964 | 1020 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 92 | 320260 | 3789 | 90.936 | 3.789 | 7.7 | 7.7 | 2B | 0 | 0 | 972 | 0 | 1110 | N/A | N/A | N/A | N/A | 29572514 | 624 | 164.6873 | 0% | 0% | 100% | 0% | 100% | 35% | 6478041 | 1077 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 91 | 324128 | 3868 | 92.832 | 3.868 | 8.9 | 8.9 | 2B | 0 | 0 | 960 | 0 | 1110 | N/A | N/A | N/A | N/A | 29573130 | 616 | 159.2554 | 0% | 0% | 100% | 0% | 100% | 35% | 6479142 | 1101 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 108 | 328080 | 3952 | 94.848 | 3.952 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 29573728 | 598 | 151.3158 | 0% | 0% | 100% | 0% | 100% | 35% | 6479722 | 580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 124 | 332846 | 4766 | 114.384 | 4.766 | 9.5 | 9.5 | 2B | 0 | 0 | 1178 | 0 | 1196 | N/A | N/A | N/A | N/A | 29574506 | 778 | 163.2396 | 0% | 0% | 100% | 0% | 100% | 0% | 6479722 | 0 | 0.81 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 142 | 338741 | 5895 | 141.48 | 5.895 | 9.1 | 9.1 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29575810 | 1304 | 221.2044 | 0% | 0% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 161 | 344743 | 6002 | 144.048 | 6.002 | 8.6 | 8.6 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29577158 | 1348 | 224.5918 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 152 | 351118 | 6375 | 153 | 6.375 | 7.9 | 7.9 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29578544 | 1386 | 217.4118 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 147 | 357093 | 5975 | 143.4 | 5.975 | 7.1 | 7.1 | 3B+1S | 0 | 1115 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29579933 | 1389 | 232.4686 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 363396 | 6303 | 151.272 | 6.303 | 6.4 | 6.4 | 3B+1S | 0 | 1076 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29581362 | 1429 | 226.7174 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 137 | 369064 | 5668 | 136.032 | 5.668 | 5.9 | 5.9 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29582654 | 1292 | 227.9464 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 375059 | 5995 | 143.88 | 5.995 | 5.7 | 5.7 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29584022 | 1368 | 228.1902 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 380834 | 5775 | 138.6 | 5.775 | 5.3 | 5.3 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29585350 | 1328 | 229.9567 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 | 0.96 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 386529 | 5695 | 136.68 | 5.695 | 4.9 | 4.9 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29586674 | 1324 | 232.4846 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 129 | 392154 | 5625 | 135 | 5.625 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29587994 | 1320 | 234.6667 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 131 | 397667 | 5513 | 132.312 | 5.513 | 4.7 | 4.7 | 3B+1S | 0 | 915 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29589246 | 1252 | 227.0996 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 133 | 403142 | 5475 | 131.4 | 5.475 | 4.6 | 4.6 | 3B+1S | 0 | 1000 | 1005 | 1185 | 1108 | N/A | N/A | N/A | N/A | 29590440 | 1194 | 218.0822 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 131 | 408521 | 5379 | 129.096 | 5.379 | 4.4 | 4.4 | 3B+1S | 0 | 1011 | 1114 | 1185 | 1118 | N/A | N/A | N/A | N/A | 29591598 | 1158 | 215.2817 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 129 | 413981 | 5460 | 131.04 | 5.46 | 3.6 | 3.6 | 2B+1S | 0 | 1088 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29592682 | 1084 | 198.5348 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 127 | 419345 | 5364 | 128.736 | 5.364 | 2.9 | 2.9 | 2B+1S | 0 | 1053 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29593750 | 1068 | 199.1051 | 0% | 100% | 100% | 100% | 100% | 0% | 6479722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 115 | 424480 | 5135 | 123.24 | 5.135 | 2.6 | 2.6 | 2B+1S | 0 | 1040 | 1163 | 0 | 1150 | N/A | N/A | N/A | N/A | 29594754 | 1004 | 195.5209 | 0% | 100% | 100% | 0% | 100% | 0% | 6479722 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 101 | 428965 | 4485 | 107.64 | 4.485 | 3.2 | 3.2 | 2B | 0 | 0 | 1075 | 0 | 1110 | N/A | N/A | N/A | N/A | 29595516 | 762 | 169.8997 | 0% | 0% | 100% | 0% | 100% | 25% | 6480365 | 643 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 99 | 433176 | 4211 | 101.064 | 4.211 | 4.1 | 4.1 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 29596186 | 670 | 159.1071 | 0% | 0% | 100% | 0% | 100% | 25% | 6481232 | 867 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.25 | 124824 | 124824 | 124.824 | 124.824 | [12 empty] | 25656 | 25656 | 205.5374 | [6 empty] | 6106 | 6106 | 0.94167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:18 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:00 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 26) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26480 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 433176 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29596186 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6481232 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 101 | 437240 | 4064 | 97.536 | 4.064 | 5.2 | 5.2 | 2B | 0 | 0 | 1058 | 0 | 1110 | N/A | N/A | N/A | N/A | 29596890 | 704 | 173.2283 | 0% | 0% | 100% | 0% | 100% | 35% | 6482113 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 98 | 441187 | 3947 | 94.728 | 3.947 | 6.3 | 6.3 | 2B | 0 | 0 | 1017 | 0 | 1110 | N/A | N/A | N/A | N/A | 29597550 | 660 | 167.2156 | 0% | 0% | 100% | 0% | 100% | 35% | 6483135 | 1022 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 97 | 445084 | 3897 | 93.528 | 3.897 | 7.3 | 7.3 | 2B | 0 | 0 | 985 | 0 | 1110 | N/A | N/A | N/A | N/A | 29598182 | 632 | 162.176 | 0% | 0% | 100% | 0% | 100% | 35% | 6484254 | 1119 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 95 | 449030 | 3946 | 94.704 | 3.946 | 8.5 | 8.5 | 2B | 0 | 0 | 968 | 0 | 1110 | N/A | N/A | N/A | N/A | 29598806 | 624 | 158.1348 | 0% | 0% | 100% | 0% | 100% | 35% | 6485390 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 96 | 452949 | 3919 | 94.056 | 3.919 | 9.5 | 9.5 | 2B | 0 | 0 | 885 | 0 | 1010 | N/A | N/A | N/A | N/A | 29599372 | 566 | 144.4246 | 0% | 0% | 100% | 0% | 100% | 35% | 6486269 | 879 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 116 | 457314 | 4365 | 104.76 | 4.365 | 9.5 | 9.5 | 2B | 0 | 0 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 29599982 | 610 | 139.748 | 0% | 0% | 100% | 0% | 100% | 0% | 6486269 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 140 | 463011 | 5697 | 136.728 | 5.697 | 9.5 | 9.5 | 3B | 0 | 0 | 1170 | 1185 | 1190 | N/A | N/A | N/A | N/A | 29601186 | 1204 | 211.3393 | 0% | 0% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 151 | 469043 | 6032 | 144.768 | 6.032 | 9.2 | 9.2 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29602492 | 1306 | 216.5119 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 144 | 475255 | 6212 | 149.088 | 6.212 | 8.6 | 8.6 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29603872 | 1380 | 222.1507 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 153 | 481571 | 6316 | 151.584 | 6.316 | 7.6 | 7.6 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29605312 | 1440 | 227.9924 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 487852 | 6281 | 150.744 | 6.281 | 6.9 | 6.9 | 3B+1S | 0 | 1137 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29606718 | 1406 | 223.8497 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 147 | 494044 | 6192 | 148.608 | 6.192 | 5.9 | 5.9 | 3B+1S | 0 | 1175 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29608142 | 1424 | 229.9742 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 144 | 500084 | 6040 | 144.96 | 6.04 | 5.2 | 5.2 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29609534 | 1392 | 230.4636 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 141 | 505974 | 5890 | 141.36 | 5.89 | 4.5 | 4.5 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29610894 | 1360 | 230.8998 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 138 | 511679 | 5705 | 136.92 | 5.705 | 3.6 | 3.6 | 3B+1S | 0 | 1115 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29612258 | 1364 | 239.0885 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 517570 | 5891 | 141.384 | 5.891 | 2.9 | 2.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29613658 | 1400 | 237.6507 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 523641 | 6071 | 145.704 | 6.071 | 2.5 | 2.5 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29615166 | 1508 | 248.394 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 143 | 133 | 529159 | 5518 | 132.432 | 5.518 | 2.6 | 2.6 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29616504 | 1338 | 242.4792 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 143 | 135 | 534805 | 5646 | 135.504 | 5.646 | 2.9 | 2.9 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29617874 | 1370 | 242.6497 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 130 | 540043 | 5238 | 125.712 | 5.238 | 2.5 | 2.5 | 2B+1S | 0 | 1163 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29619014 | 1140 | 217.6403 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 545503 | 5460 | 131.04 | 5.46 | 2.1 | 2.1 | 2B+1S | 0 | 1189 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29620206 | 1192 | 218.315 | 0% | 100% | 100% | 100% | 100% | 0% | 6486269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 119 | 550238 | 4735 | 113.64 | 4.735 | 1.9 | 1.9 | 2B+1S | 0 | 1050 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29621222 | 1016 | 214.5723 | 0% | 100% | 100% | 0% | 100% | 0% | 6486269 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 105 | 554887 | 4649 | 111.576 | 4.649 | 3 | 3 | 2B | 0 | 0 | 1048 | 0 | 1110 | N/A | N/A | N/A | N/A | 29621998 | 776 | 166.9176 | 0% | 0% | 100% | 0% | 100% | 30% | 6487238 | 969 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 100 | 559184 | 4297 | 103.128 | 4.297 | 4.1 | 4.1 | 2B | 0 | 0 | 996 | 0 | 1110 | N/A | N/A | N/A | N/A | 29622666 | 668 | 155.4573 | 0% | 0% | 100% | 0% | 100% | 30% | 6488341 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.4583 | 126008 | 126008 | 126.008 | 126.008 | [12 empty] | 26480 | 26480 | 210.1454 | [6 empty] | 7109 | 7109 | 0.92167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 27) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
XCV4 - OPENED @ 3:45 PM (10%)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 27) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25060 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 559184 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29622666 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6488341 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 102 | 563264 | 4080 | 97.92 | 4.08 | 5.3 | 5.3 | 2B | 0 | 0 | 1088 | 0 | 1110 | N/A | N/A | N/A | N/A | 29623394 | 728 | 178.4314 | 0% | 0% | 100% | 0% | 100% | 40% | 6489354 | 1013 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 99 | 567287 | 4023 | 96.552 | 4.023 | 6.5 | 6.5 | 2B | 0 | 0 | 1056 | 0 | 1110 | N/A | N/A | N/A | N/A | 29624080 | 686 | 170.5195 | 0% | 0% | 100% | 0% | 100% | 40% | 6490518 | 1164 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 97 | 571288 | 4001 | 96.024 | 4.001 | 7.7 | 7.7 | 2B | 0 | 0 | 1022 | 0 | 1110 | N/A | N/A | N/A | N/A | 29624734 | 654 | 163.4591 | 0% | 0% | 100% | 0% | 100% | 40% | 6491715 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 95 | 575204 | 3916 | 93.984 | 3.916 | 8.9 | 8.9 | 2B | 0 | 0 | 972 | 0 | 1110 | N/A | N/A | N/A | N/A | 29625378 | 644 | 164.4535 | 0% | 0% | 100% | 0% | 100% | 40% | 6492876 | 1161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 95 | 578933 | 3729 | 89.496 | 3.729 | 9.5 | 9.5 | 2B | 0 | 0 | 862 | 0 | 1028 | N/A | N/A | N/A | N/A | 29625914 | 536 | 143.7383 | 0% | 0% | 100% | 0% | 100% | 40% | 6493451 | 575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 112 | 583226 | 4293 | 103.032 | 4.293 | 9.5 | 9.5 | 2B | 0 | 0 | 1018 | 0 | 1028 | N/A | N/A | N/A | N/A | 29626450 | 536 | 124.8544 | 0% | 0% | 100% | 0% | 100% | 0% | 6493451 | 0 | 0.97 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 588650 | 5424 | 130.176 | 5.424 | 9.5 | 9.5 | 3B | 0 | 0 | 1040 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29627562 | 1112 | 205.0147 | 0% | 0% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 148 | 594502 | 5852 | 140.448 | 5.852 | 9.5 | 9.5 | 3B | 0 | 0 | 1192 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29628762 | 1200 | 205.0581 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 151 | 600547 | 6045 | 145.08 | 6.045 | 9.4 | 9.4 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29630060 | 1298 | 214.7229 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 606703 | 6156 | 147.744 | 6.156 | 8.8 | 8.8 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29631430 | 1370 | 222.5471 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 612916 | 6213 | 149.112 | 6.213 | 8.1 | 8.1 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29632812 | 1382 | 222.4368 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 619061 | 6145 | 147.48 | 6.145 | 7.4 | 7.4 | 3B+1S | 0 | 1119 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29634210 | 1398 | 227.502 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 116 | 625077 | 6016 | 144.384 | 6.016 | 6.9 | 6.9 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29635566 | 1356 | 225.3989 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 140 | 631057 | 5980 | 143.52 | 5.98 | 6.3 | 6.3 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29636958 | 1392 | 232.7759 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 130 | 637150 | 6093 | 146.232 | 6.093 | 5.8 | 5.8 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29638354 | 1396 | 229.1154 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 642275 | 5125 | 123 | 5.125 | 5.7 | 5.7 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29639558 | 1204 | 234.9268 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 135 | 647839 | 5564 | 133.536 | 5.564 | 5.5 | 5.5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29640834 | 1276 | 229.3314 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 653536 | 5697 | 136.728 | 5.697 | 5.2 | 5.2 | 3B+1S | 0 | 1011 | 1072 | 1185 | 1170 | N/A | N/A | N/A | N/A | 29642062 | 1228 | 215.552 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 136 | 658976 | 5440 | 130.56 | 5.44 | 5 | 5 | 3B+1S | 0 | 997 | 1075 | 1185 | 1149 | N/A | N/A | N/A | N/A | 29643232 | 1170 | 215.0735 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 129 | 664358 | 5382 | 129.168 | 5.382 | 4.5 | 4.5 | 2B+1S | 0 | 1024 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 29644304 | 1072 | 199.1825 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 669582 | 5224 | 125.376 | 5.224 | 3.6 | 3.6 | 2B+1S | 0 | 1104 | 1177 | 0 | 1199 | N/A | N/A | N/A | N/A | 29645320 | 1016 | 194.487 | 0% | 100% | 100% | 100% | 100% | 0% | 6493451 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 119 | 674599 | 5017 | 120.408 | 5.017 | 3.3 | 3.3 | 2B+1S | 0 | 998 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29646306 | 986 | 196.5318 | 0% | 100% | 100% | 0% | 100% | 0% | 6493451 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 101 | 679231 | 4632 | 111.168 | 4.632 | 4.1 | 4.1 | 2B | 0 | 0 | 1046 | 0 | 1110 | N/A | N/A | N/A | N/A | 29647082 | 776 | 167.5302 | 0% | 0% | 100% | 0% | 100% | 25% | 6494164 | 713 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 99 | 683329 | 4098 | 98.352 | 4.098 | 4.9 | 4.9 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 29647726 | 644 | 157.1498 | 0% | 0% | 100% | 0% | 100% | 25% | 6494951 | 787 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.375 | 124145 | 124145 | 124.145 | 124.145 | [12 empty] | 25060 | 25060 | 201.8607 | [6 empty] | 6610 | 6610 | 0.94667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:40 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 28) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24690 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 683329 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29647726 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6494951 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 97 | 687452 | 4123 | 98.952 | 4.123 | 5.9 | 5.9 | 2B | 0 | 0 | 1032 | 0 | 1110 | N/A | N/A | N/A | N/A | 29648406 | 680 | 164.9285 | 0% | 0% | 100% | 0% | 100% | 35% | 6495712 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 95 | 691402 | 3950 | 94.8 | 3.95 | 6.8 | 6.8 | 2B | 0 | 0 | 1002 | 0 | 1110 | N/A | N/A | N/A | N/A | 29649050 | 644 | 163.038 | 0% | 0% | 100% | 0% | 100% | 35% | 6496697 | 985 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 94 | 695272 | 3870 | 92.88 | 3.87 | 7.8 | 7.8 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 29649674 | 624 | 161.2403 | 0% | 0% | 100% | 0% | 100% | 35% | 6497725 | 1028 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 97 | 699184 | 3912 | 93.888 | 3.912 | 8.9 | 8.9 | 2B | 0 | 0 | 955 | 0 | 1110 | N/A | N/A | N/A | N/A | 29650286 | 612 | 156.4417 | 0% | 0% | 100% | 0% | 100% | 35% | 6498763 | 1038 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 105 | 703198 | 4014 | 96.336 | 4.014 | 9.5 | 9.5 | 2B | 0 | 0 | 1004 | 0 | 1010 | N/A | N/A | N/A | N/A | 29650858 | 572 | 142.5012 | 0% | 0% | 100% | 0% | 100% | 35% | 6499363 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 120 | 707803 | 4605 | 110.52 | 4.605 | 9.5 | 9.5 | 2B | 0 | 0 | 1140 | 0 | 1110 | N/A | N/A | N/A | N/A | 29651574 | 716 | 155.4832 | 0% | 0% | 100% | 0% | 100% | 0% | 6499363 | 0 | 1.02 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 141 | 713634 | 5831 | 139.944 | 5.831 | 9.3 | 9.3 | 3B+1S | 0 | 969 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29652890 | 1316 | 225.6903 | 0% | 0% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 719748 | 6114 | 146.736 | 6.114 | 9.1 | 9.1 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29654246 | 1356 | 221.7861 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 725944 | 6196 | 148.704 | 6.196 | 8.6 | 8.6 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29655598 | 1352 | 218.2053 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 732135 | 6191 | 148.584 | 6.191 | 7.9 | 7.9 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29656940 | 1342 | 216.7663 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 142 | 738111 | 5976 | 143.424 | 5.976 | 7.6 | 7.6 | 3B+1S | 0 | 1007 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29658316 | 1376 | 230.2544 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 139 | 743915 | 5804 | 139.296 | 5.804 | 7.3 | 7.3 | 3B+1S | 0 | 960 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29659636 | 1320 | 227.4294 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 122 | 145 | 749753 | 5838 | 140.112 | 5.838 | 7.1 | 7.1 | 3B+1S | 0 | 1065 | 1105 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29660888 | 1252 | 214.457 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 136 | 755492 | 5739 | 137.736 | 5.739 | 6.7 | 6.7 | 3B+1S | 0 | 982 | 1155 | 1185 | 1178 | N/A | N/A | N/A | N/A | 29662178 | 1290 | 224.7778 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 122 | 136 | 760885 | 5393 | 129.432 | 5.393 | 6.6 | 6.6 | 3B+1S | 0 | 1128 | 1124 | 1185 | 1128 | N/A | N/A | N/A | N/A | 29663366 | 1188 | 220.2856 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 137 | 766465 | 5580 | 133.92 | 5.58 | 6.2 | 6.2 | 3B+1S | 0 | 1043 | 1170 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29664622 | 1256 | 225.0896 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 136 | 772064 | 5599 | 134.376 | 5.599 | 6 | 6 | 3B+1S | 0 | 1024 | 1130 | 1185 | 1139 | N/A | N/A | N/A | N/A | 29665830 | 1208 | 215.7528 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 134 | 777597 | 5533 | 132.792 | 5.533 | 5.5 | 5.5 | 3B+1S | 0 | 1033 | 1082 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29666976 | 1146 | 207.1209 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 128 | 782779 | 5182 | 124.368 | 5.182 | 5.1 | 5.1 | 3B+1S | 0 | 1027 | 1063 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29668058 | 1082 | 208.7997 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 131 | 788378 | 5599 | 134.376 | 5.599 | 4.6 | 4.6 | 2B+1S | 0 | 1026 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29669158 | 1100 | 196.4637 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 136 | 793650 | 5272 | 126.528 | 5.272 | 3.9 | 3.9 | 2B+1S | 0 | 1026 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29670190 | 1032 | 195.7511 | 0% | 100% | 100% | 100% | 100% | 0% | 6499363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 118 | 798708 | 5058 | 121.392 | 5.058 | 3.7 | 3.7 | 2B+1S | 0 | 1010 | 1115 | 0 | 1129 | N/A | N/A | N/A | N/A | 29671144 | 954 | 188.6121 | 0% | 100% | 100% | 0% | 100% | 0% | 6499363 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 99 | 803025 | 4317 | 103.608 | 4.317 | 4.6 | 4.6 | 2B | 0 | 0 | 987 | 0 | 1110 | N/A | N/A | N/A | N/A | 29671826 | 682 | 157.9801 | 0% | 0% | 100% | 0% | 100% | 25% | 6500084 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 92 | 806987 | 3962 | 95.088 | 3.962 | 5.5 | 5.5 | 2B | 0 | 0 | 887 | 0 | 1110 | N/A | N/A | N/A | N/A | 29672416 | 590 | 148.9147 | 0% | 0% | 100% | 0% | 100% | 25% | 6500979 | 895 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.8333 | 123658 | 123658 | 123.658 | 123.658 | [12 empty] | 24690 | 24690 | 199.6636 | [6 empty] | 6028 | 6028 | 0.97667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 29) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3psi to target discharge pressure @ 10:01 pm to 5am (JULY 29) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24362 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 806987 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29672416 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6500979 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 | 91 | 810732 | 3745 | 89.88 | 3.745 | 6.4 | 6.4 | 2B | 0 | 0 | 973 | 0 | 1110 | N/A | N/A | N/A | N/A | 29673032 | 616 | 164.486 | 0% | 0% | 100% | 0% | 100% | 30% | 6501791 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 89 | 814414 | 3682 | 88.368 | 3.682 | 7.3 | 7.3 | 2B | 0 | 0 | 926 | 0 | 1110 | N/A | N/A | N/A | N/A | 29673626 | 594 | 161.3254 | 0% | 0% | 100% | 0% | 100% | 30% | 6502688 | 897 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 86 | 817974 | 3560 | 85.44 | 3.56 | 8.2 | 8.2 | 2B | 0 | 0 | 954 | 0 | 1010 | N/A | N/A | N/A | N/A | 29674178 | 552 | 155.0562 | 0% | 0% | 100% | 0% | 100% | 30% | 6503652 | 964 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 89 | 821608 | 3634 | 87.216 | 3.634 | 9.2 | 9.2 | 2B | 0 | 0 | 931 | 0 | 1010 | N/A | N/A | N/A | N/A | 29674682 | 504 | 138.6901 | 0% | 0% | 100% | 0% | 100% | 30% | 6504557 | 905 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 96 | 825406 | 3798 | 91.152 | 3.798 | 9.5 | 9.5 | 2B | 0 | 0 | 886 | 0 | 987 | N/A | N/A | N/A | N/A | 29675152 | 470 | 123.7493 | 0% | 0% | 100% | 0% | 100% | 30% | 6504857 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 29 | 20.4225 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 112 | 829672 | 4266 | 102.384 | 4.266 | 9.5 | 9.5 | 2B | 0 | 0 | 989 | 0 | 987 | N/A | N/A | N/A | N/A | 29675836 | 684 | 160.3376 | 0% | 0% | 100% | 0% | 100% | 0% | 6504857 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 138 | 835204 | 5532 | 132.768 | 5.532 | 9.5 | 9.5 | 3B | 0 | 0 | 1061 | 1185 | 1080 | N/A | N/A | N/A | N/A | 29676962 | 1126 | 203.543 | 0% | 0% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 142 | 841191 | 5987 | 143.688 | 5.987 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29678186 | 1224 | 204.443 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 151 | 847158 | 5967 | 143.208 | 5.967 | 9.1 | 9.1 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29679488 | 1302 | 218.2001 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 149 | 853340 | 6182 | 148.368 | 6.182 | 8.9 | 8.9 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29680816 | 1328 | 214.8172 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 859577 | 6237 | 149.688 | 6.237 | 7.8 | 7.8 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29682076 | 1260 | 202.0202 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 865670 | 6093 | 146.232 | 6.093 | 7.3 | 7.3 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29683450 | 1374 | 225.5047 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 871414 | 5744 | 137.856 | 5.744 | 6.9 | 6.9 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29684758 | 1308 | 227.7159 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 132 | 877194 | 5780 | 138.72 | 5.78 | 6.6 | 6.6 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29686088 | 1330 | 230.1038 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 133 | 882997 | 5803 | 139.272 | 5.803 | 6.3 | 6.3 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29687422 | 1334 | 229.8811 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 888675 | 5678 | 136.272 | 5.678 | 6 | 6 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29688706 | 1284 | 226.136 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 894357 | 5682 | 136.368 | 5.682 | 5.8 | 5.8 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29690022 | 1316 | 231.6086 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 16 | 11.2676 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 899969 | 5612 | 134.688 | 5.612 | 5.6 | 5.6 | 3B+1S | 0 | 997 | 1104 | 1185 | 1108 | N/A | N/A | N/A | N/A | 29691222 | 1200 | 213.8275 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 130 | 905531 | 5562 | 133.488 | 5.562 | 5.3 | 5.3 | 3B+1S | 0 | 1032 | 1104 | 1185 | 1108 | N/A | N/A | N/A | N/A | 29692384 | 1162 | 208.9177 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 129 | 910942 | 5411 | 129.864 | 5.411 | 4.6 | 4.6 | 2B+1S | 0 | 1055 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29693446 | 1062 | 196.2669 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 128 | 916300 | 5358 | 128.592 | 5.358 | 3.9 | 3.9 | 2B+1S | 0 | 1013 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 29694498 | 1052 | 196.3419 | 0% | 100% | 100% | 100% | 100% | 0% | 6504857 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 117 | 921385 | 5085 | 122.04 | 5.085 | 3.4 | 3.4 | 2B+1S | 0 | 1004 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 29695442 | 944 | 185.6441 | 0% | 100% | 100% | 0% | 100% | 0% | 6504857 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 100 | 925758 | 4373 | 104.952 | 4.373 | 3.9 | 3.9 | 2B | 0 | 0 | 1024 | 0 | 1088 | N/A | N/A | N/A | N/A | 29696140 | 698 | 159.6158 | 0% | 0% | 100% | 0% | 100% | 25% | 6505447 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 105 | 929971 | 4213 | 101.112 | 4.213 | 4.8 | 4.8 | 2B | 0 | 0 | 987 | 0 | 1089 | N/A | N/A | N/A | N/A | 29696778 | 638 | 151.436 | 0% | 0% | 100% | 0% | 100% | 25% | 6506139 | 692 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.75 | 122984 | 122984 | 122.984 | 122.984 | [12 empty] | 24362 | 24362 | 198.0908 | [6 empty] | 5160 | 5160 | 0.95167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 30 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:30 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 pm to 5am (July 30) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24754 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 929971 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29696778 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6506139 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 99 | 934147 | 4176 | 100.224 | 4.176 | 5.6 | 5.6 | 2B | 0 | 0 | 1078 | 0 | 1089 | N/A | N/A | N/A | N/A | 29697470 | 692 | 165.7088 | 0% | 0% | 100% | 0% | 100% | 30% | 6506951 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 97 | 938313 | 4166 | 99.984 | 4.166 | 6.5 | 6.5 | 2B | 0 | 0 | 1030 | 0 | 1083 | N/A | N/A | N/A | N/A | 29698130 | 660 | 158.4253 | 0% | 0% | 100% | 0% | 100% | 30% | 6507840 | 889 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 93 | 942280 | 3967 | 95.208 | 3.967 | 8.3 | 8.3 | 2B | 0 | 0 | 1002 | 0 | 1088 | N/A | N/A | N/A | N/A | 29698754 | 624 | 157.2977 | 0% | 0% | 100% | 0% | 100% | 30% | 6508895 | 1055 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 97 | 946248 | 3968 | 95.232 | 3.968 | 8.9 | 8.9 | 2B | 0 | 0 | 991 | 0 | 1089 | N/A | N/A | N/A | N/A | 29699388 | 634 | 159.7782 | 0% | 0% | 100% | 0% | 100% | 30% | 6510047 | 1152 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 108 | 951257 | 5009 | 120.216 | 5.009 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 0 | 1089 | N/A | N/A | N/A | N/A | 29700094 | 706 | 140.9463 | 0% | 0% | 100% | 0% | 100% | 30% | 6510660 | 613 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 135 | 955651 | 4394 | 105.456 | 4.394 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1145 | N/A | N/A | N/A | N/A | 29700816 | 722 | 164.315 | 0% | 0% | 100% | 0% | 100% | 0% | 6510660 | 0 | 0.98 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 143 | 961637 | 5986 | 143.664 | 5.986 | 8.9 | 8.9 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29702076 | 1260 | 210.4911 | 0% | 0% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 967682 | 6045 | 145.08 | 6.045 | 8.4 | 8.4 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29703444 | 1368 | 226.3027 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 973781 | 6099 | 146.376 | 6.099 | 7.8 | 7.8 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29704792 | 1348 | 221.0198 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 979835 | 6054 | 145.296 | 6.054 | 7.3 | 7.3 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29706153 | 1361 | 224.81 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 | 0.85 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 140 | 985748 | 5913 | 141.912 | 5.913 | 6.9 | 6.9 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29707495 | 1342 | 226.9576 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 142 | 991680 | 5932 | 142.368 | 5.932 | 6.6 | 6.6 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29708814 | 1319 | 222.3533 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 125 | 140 | 997238 | 5558 | 133.392 | 5.558 | 6.2 | 6.2 | 3B+1S | 0 | 1067 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29710040 | 1226 | 220.5829 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 133 | 1002893 | 5655 | 135.72 | 5.655 | 5.6 | 5.6 | 3B+1S | 0 | 1045 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29711320 | 1280 | 226.3484 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 | 0.91 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 130 | 1008437 | 5544 | 133.056 | 5.544 | 5.2 | 5.2 | 3B+1S | 0 | 1035 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29712530 | 1210 | 218.254 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 1013982 | 5545 | 133.08 | 5.545 | 4.9 | 4.9 | 3B+1S | 0 | 1018 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 29713792 | 1262 | 227.5924 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 1019457 | 5475 | 131.4 | 5.475 | 4.7 | 4.7 | 3B+1S | 0 | 1023 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 29714994 | 1202 | 219.5434 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 129 | 1024955 | 5498 | 131.952 | 5.498 | 4.6 | 4.6 | 3B+1S | 0 | 997 | 1095 | 1185 | 1099 | N/A | N/A | N/A | N/A | 29716138 | 1144 | 208.0757 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 129 | 1030165 | 5210 | 125.04 | 5.21 | 4.5 | 4.5 | 3B+1S | 0 | 1001 | 1083 | 1185 | 1087 | N/A | N/A | N/A | N/A | 29717225 | 1087 | 208.6372 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 120 | 1035448 | 5283 | 126.792 | 5.283 | 4.1 | 4.1 | 2B+1S | 0 | 1004 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 29718273 | 1048 | 198.3721 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 121 | 1040531 | 5083 | 121.992 | 5.083 | 3.7 | 3.7 | 2B+1S | 0 | 981 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 29719274 | 1001 | 196.9309 | 0% | 100% | 100% | 100% | 100% | 0% | 6510660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 114 | 1045411 | 4880 | 117.12 | 4.88 | 3.4 | 3.4 | 2B+1S | 0 | 981 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 29720198 | 924 | 189.3443 | 0% | 100% | 100% | 0% | 100% | 0% | 6510660 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 101 | 1049667 | 4256 | 102.144 | 4.256 | 4.1 | 4.1 | 2B | 0 | 0 | 1001 | 0 | 1110 | N/A | N/A | N/A | N/A | 29720896 | 698 | 164.0038 | 0% | 0% | 100% | 0% | 100% | 25% | 6511287 | 627 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 96 | 1053864 | 4197 | 100.728 | 4.197 | 5 | 5 | 2B | 0 | 0 | 1007 | 0 | 1110 | N/A | N/A | N/A | N/A | 29721532 | 636 | 151.5368 | 0% | 0% | 100% | 0% | 100% | 25% | 6512021 | 734 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.4583 | 123893 | 123893 | 123.893 | 123.893 | [12 empty] | 24754 | 24754 | 199.8014 | [6 empty] | 5882 | 5882 | 0.9 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:28 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 12:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (JULY 31) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 68 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JULY 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-07-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24238 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1053864 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 29721532 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6512021 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 101 | 1057988 | 4124 | 98.976 | 4.124 | 5.7 | 5.7 | 2B | 0 | 0 | 1061 | 0 | 1110 | N/A | N/A | N/A | N/A | 29722226 | 694 | 168.2832 | 0% | 0% | 100% | 0% | 100% | 35% | 6512769 | 748 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 99 | 1061918 | 3930 | 94.32 | 3.93 | 6.6 | 6.6 | 2B | 0 | 0 | 995 | 0 | 1110 | N/A | N/A | N/A | N/A | 29722872 | 646 | 164.3766 | 0% | 0% | 100% | 0% | 100% | 35% | 6513662 | 893 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 96 | 1065836 | 3918 | 94.032 | 3.918 | 7.6 | 7.6 | 2B | 0 | 0 | 960 | 0 | 1110 | N/A | N/A | N/A | N/A | 29723494 | 622 | 158.7545 | 0% | 0% | 100% | 0% | 100% | 35% | 6514615 | 953 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 95 | 1069729 | 3893 | 93.432 | 3.893 | 8.6 | 8.6 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 29724098 | 604 | 155.1503 | 0% | 0% | 100% | 0% | 100% | 35% | 6515600 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 112 | 1073940 | 4211 | 101.064 | 4.211 | 9.5 | 9.5 | 2B | 0 | 0 | 1022 | 0 | 1049 | N/A | N/A | N/A | N/A | 29724714 | 616 | 146.2835 | 0% | 0% | 100% | 0% | 100% | 35% | 6516454 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / A. CABREROS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 118 | 1079008 | 5068 | 121.632 | 5.068 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1109 | N/A | N/A | N/A | N/A | 29725448 | 734 | 144.8303 | 0% | 0% | 100% | 0% | 100% | 0% | 6516454 | 0 | 1.02 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 144 | 1084438 | 5430 | 130.32 | 5.43 | 9.3 | 9.3 | 3B+1S | 0 | 987 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29726706 | 1258 | 231.6759 | 0% | 0% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 1090557 | 6119 | 146.856 | 6.119 | 9 | 9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29728058 | 1352 | 220.9511 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 1096729 | 6172 | 148.128 | 6.172 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 29729426 | 1368 | 221.6461 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 1102631 | 5902 | 141.648 | 5.902 | 8.2 | 8.2 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29730750 | 1324 | 224.3307 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 142 | 1108695 | 6064 | 145.536 | 6.064 | 7.9 | 7.9 | 3B+1S | 0 | 995 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 29732094 | 1344 | 221.6359 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 138 | 1114508 | 5813 | 139.512 | 5.813 | 7.8 | 7.8 | 3B+1S | 0 | 986 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 29733366 | 1272 | 218.8199 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 123 | 139 | 1120356 | 5848 | 140.352 | 5.848 | 7.6 | 7.6 | 3B+1S | 0 | 1023 | 1063 | 1185 | 1181 | N/A | N/A | N/A | N/A | 29734662 | 1296 | 221.6142 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 122 | 130 | 1125759 | 5403 | 129.672 | 5.403 | 6.7 | 6.7 | 3B+1S | 0 | 1023 | 1163 | 1185 | 1181 | N/A | N/A | N/A | N/A | 29735822 | 1160 | 214.6955 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 | 0.98 | Normal operation schedule | m of H2O | 14.7
62:00 | 15:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 122 | 130 | 1131288 | 5529 | 132.696 | 5.529 | 6.3 | 6.3 | 3B+1S | 0 | 1066 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29737034 | 1212 | 219.2078 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Normal operation schedule | psi | 10.36
63:00 | 16:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 130 | 1136840 | 5552 | 133.248 | 5.552 | 5.8 | 5.8 | 3B+1S | 0 | 1039 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29738224 | 1190 | 214.3372 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 17 | 11.9718 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 129 | 1142134 | 5294 | 127.056 | 5.294 | 5.4 | 5.4 | 3B+1S | 0 | 1030 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 29739366 | 1142 | 215.7159 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 15 | 10.5634 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 128 | 1147316 | 5182 | 124.368 | 5.182 | 5.2 | 5.2 | 3B+1S | 0 | 1006 | 1064 | 1185 | 1068 | N/A | N/A | N/A | N/A | 29740450 | 1084 | 209.1856 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 14 | 9.8592 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 1152622 | 5306 | 127.344 | 5.306 | 4.9 | 4.9 | 3B+1S | 0 | 1011 | 1064 | 1185 | 1068 | N/A | N/A | N/A | N/A | 29741554 | 1104 | 208.0663 | 0% | 100% | 100% | 100% | 100% | 0% | 6516454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 124 | 1157784 | 5162 | 123.888 | 5.162 | 4.7 | 4.7 | 2B+1S | 0 | 1000 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 29742570 | 1016 | 196.8229 | 0% | 100% | 100% | 0% | 100% | 0% | 6516454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 19 | 13.3803 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 119 | 1162882 | 5098 | 122.352 | 5.098 | 3.9 | 3.9 | 2B+1S | 0 | 1035 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 29743580 | 1010 | 198.1169 | 0% | 100% | 100% | 0% | 100% | 0% | 6516454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 | 105 | 1167869 | 4987 | 119.688 | 4.987 | 3.6 | 3.6 | 2B+1S | 0 | 1000 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 29744466 | 886 | 177.6619 | 0% | 100% | 100% | 0% | 100% | 0% | 6516454 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 100 | 1172202 | 4333 | 103.992 | 4.333 | 4.4 | 4.4 | 2B | 0 | 0 | 966 | 0 | 1110 | N/A | N/A | N/A | N/A | 29745178 | 712 | 164.3203 | 0% | 0% | 100% | 0% | 100% | 25% | 6517109 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 95 | 1176142 | 3940 | 94.56 | 3.94 | 5.3 | 5.3 | 2B | 0 | 0 | 885 | 0 | 1110 | N/A | N/A | N/A | N/A | 29745770 | 592 | 150.2538 | 0% | 0% | 100% | 0% | 100% | 25% | 6518002 | 893 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.7917 | 122278 | 122278 | 122.278 | 122.278 | [12 empty] | 24238 | 24238 | 198.2204 | [6 empty] | 5981 | 5981 | 0.96333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
| XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING | [42 empty] | Convert Flowrate (Enter Unit and Value)
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MAINTAIN 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 3:01 pm to10pm as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 3:01 pm as per request of Engr Edmundo Llagas Jr (SPM- South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:45 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (AUGUST 1) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION