## SEPT 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25410 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5001966 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30532014 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6715896 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 94 | 5005750 | 3784 | 90.816 | 3.784 | 6.1 | 6.1 | 2B | 0 | 0 | 981 | 0 | 1110 | N/A | N/A | N/A | N/A | 30532644 | 630 | 166.4905 | 0% | 0% | 100% | 0% | 100% | 35% | 6716886 | 990 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 5009531 | 3781 | 90.744 | 3.781 | 7.2 | 7.2 | 2B | 0 | 0 | 938 | 0 | 1110 | N/A | N/A | N/A | N/A | 30533244 | 600 | 158.6882 | 0% | 0% | 100% | 0% | 100% | 35% | 6717964 | 1078 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 96 | 5013521 | 3990 | 95.76 | 3.99 | 8.4 | 8.4 | 2B | 0 | 0 | 906 | 0 | 1110 | N/A | N/A | N/A | N/A | 30533863 | 619 | 155.1378 | 0% | 0% | 100% | 0% | 100% | 35% | 6719075 | 1111 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 90 | 5017512 | 3991 | 95.784 | 3.991 | 9.5 | 9.5 | 2B | 0 | 0 | 845 | 0 | 1110 | N/A | N/A | N/A | N/A | 30534482 | 619 | 155.099 | 0% | 0% | 100% | 0% | 100% | 35% | 6720186 | 1111 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 99 | 5021013 | 3501 | 84.024 | 3.501 | 9.5 | 9.5 | 2B | 0 | 0 | 918 | 0 | 1110 | N/A | N/A | N/A | N/A | 30534988 | 506 | 144.5301 | 0% | 0% | 100% | 0% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 120 | 5025596 | 4583 | 109.992 | 4.583 | 9.5 | 9.5 | 2B | 0 | 0 | 1194 | 0 | 1194 | N/A | N/A | N/A | N/A | 30535698 | 710 | 154.9204 | 0% | 0% | 100% | 0% | 100% | 0% | 6720186 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 144 | 5031596 | 6000 | 144 | 6 | 9 | 9 | 3B+1S | 0 | 1046 | 1134 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30537012 | 1314 | 219 | 0% | 0% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 5037655 | 6059 | 145.416 | 6.059 | 8.4 | 8.4 | 3B+1S | 0 | 1058 | 1165 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30538342 | 1330 | 219.5082 | 0% | 0% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 5043764 | 6109 | 146.616 | 6.109 | 7.7 | 7.7 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30539732 | 1390 | 227.5331 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 5050042 | 6278 | 150.672 | 6.278 | 7.1 | 7.1 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30541122 | 1390 | 221.4081 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 5056039 | 5997 | 143.928 | 5.997 | 6.6 | 6.6 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30542462 | 1340 | 223.4451 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 5062059 | 6020 | 144.48 | 6.02 | 6.2 | 6.2 | 3B+1S | 0 | 1065 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30543826 | 1364 | 226.5781 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 5067780 | 5721 | 137.304 | 5.721 | 6.1 | 6.1 | 3B+1S | 0 | 1001 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30545130 | 1304 | 227.9322 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 145 | 5073674 | 5894 | 141.456 | 5.894 | 5.9 | 5.9 | 3B+1S | 0 | 989 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30546434 | 1304 | 221.2419 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 143 | 5079310 | 5636 | 135.264 | 5.636 | 5.8 | 5.8 | 3B+1S | 0 | 805 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30547702 | 1268 | 224.9823 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 5084940 | 5630 | 135.12 | 5.63 | 5.7 | 5.7 | 3B+1S | 0 | 990 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30548974 | 1272 | 225.9325 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 147 | 5090650 | 5710 | 137.04 | 5.71 | 5.5 | 5.5 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30550280 | 1306 | 228.7215 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 142 | 5096295 | 5645 | 135.48 | 5.645 | 5.4 | 5.4 | 3B+1S | 0 | 987 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30551548 | 1268 | 224.6236 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 5101882 | 5587 | 134.088 | 5.587 | 5.3 | 5.3 | 3B+1S | 0 | 995 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30552794 | 1246 | 223.0177 | 0% | 100% | 100% | 100% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 5107398 | 5516 | 132.384 | 5.516 | 4.6 | 4.6 | 2B+1S | 0 | 1099 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30553904 | 1110 | 201.2328 | 0% | 100% | 100% | 0% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 5112705 | 5307 | 127.368 | 5.307 | 3.7 | 3.7 | 2B+1S | 0 | 1059 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30554974 | 1070 | 201.6205 | 0% | 100% | 100% | 0% | 100% | 0% | 6720186 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 128 | 5117962 | 5257 | 126.168 | 5.257 | 3.2 | 3.2 | 2B+1S | 0 | 1024 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30556018 | 1044 | 198.5924 | 0% | 100% | 100% | 0% | 100% | 0% | 6720186 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 98 | 5122281 | 4319 | 103.656 | 4.319 | 3.6 | 3.6 | 2B | 0 | 0 | 1110 | 0 | 1087 | N/A | N/A | N/A | N/A | 30556770 | 752 | 174.1144 | 0% | 0% | 100% | 0% | 100% | 25% | 6720637 | 451 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 93 | 5126253 | 3972 | 95.328 | 3.972 | 4.4 | 4.4 | 2B | 0 | 0 | 1110 | 0 | 979 | N/A | N/A | N/A | N/A | 30557424 | 654 | 164.6526 | 0% | 0% | 100% | 0% | 100% | 25% | 6721238 | 601 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.5833 | 124287 | 124287 | 124.287 | 124.287 | [12 empty] | 25410 | 25410 | 204.4462 | [6 empty] | 5342 | 5342 | 0.97 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:01AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 1) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 1) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25172 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5126253 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30557424 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6721238 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 105 | 87 | 5129978 | 3725 | 89.4 | 3.725 | 5.6 | 5.6 | 2B | 0 | 0 | 1029 | 0 | 1028 | N/A | N/A | N/A | N/A | 30557959 | 535 | 143.6242 | 0% | 0% | 100% | 0% | 100% | 35% | 6722224 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 89 | 5133686 | 3708 | 88.992 | 3.708 | 6.9 | 6.9 | 2B | 0 | 0 | 978 | 0 | 1028 | N/A | N/A | N/A | N/A | 30558486 | 527 | 142.1251 | 0% | 0% | 100% | 0% | 100% | 35% | 6723271 | 1047 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 85 | 5137380 | 3694 | 88.656 | 3.694 | 7.9 | 7.9 | 2B | 0 | 0 | 962 | 0 | 1029 | N/A | N/A | N/A | N/A | 30558988 | 502 | 135.896 | 0% | 0% | 100% | 0% | 100% | 35% | 6724713 | 1442 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 107 | 90 | 5141092 | 3712 | 89.088 | 3.712 | 9.3 | 9.3 | 2B | 0 | 0 | 979 | 0 | 1008 | N/A | N/A | N/A | N/A | 30559504 | 516 | 139.0086 | 0% | 0% | 100% | 0% | 100% | 35% | 6726177 | 1464 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 99 | 5144838 | 3746 | 89.904 | 3.746 | 9.5 | 9.5 | 2B | 0 | 0 | 969 | 0 | 1009 | N/A | N/A | N/A | N/A | 30560196 | 692 | 184.7304 | 0% | 0% | 100% | 0% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 118 | 5149491 | 4653 | 111.672 | 4.653 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1129 | N/A | N/A | N/A | N/A | 30560946 | 750 | 161.1863 | 0% | 0% | 100% | 0% | 100% | 0% | 6726177 | 0 | 1.09 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 147 | 5155388 | 5897 | 141.528 | 5.897 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30562260 | 1314 | 222.8252 | 0% | 0% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 5161609 | 6221 | 149.304 | 6.221 | 8.6 | 8.6 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30563646 | 1386 | 222.7938 | 0% | 0% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 142 | 5167686 | 6077 | 145.848 | 6.077 | 8.1 | 8.1 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30565006 | 1360 | 223.7946 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 140 | 5173698 | 6012 | 144.288 | 6.012 | 7.6 | 7.6 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30566358 | 1352 | 224.8836 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 138 | 145 | 5179802 | 6104 | 146.496 | 6.104 | 7.3 | 7.3 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30567722 | 1364 | 223.46 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 5185794 | 5992 | 143.808 | 5.992 | 7.1 | 7.1 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30569062 | 1340 | 223.6315 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 137 | 5191589 | 5795 | 139.08 | 5.795 | 6.9 | 6.9 | 3B+1S | 0 | 994 | 1164 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30570382 | 1320 | 227.7826 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 148 | 5197254 | 5665 | 135.96 | 5.665 | 6.8 | 6.8 | 3B+1S | 0 | 980 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30571658 | 1276 | 225.2427 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 146 | 5202790 | 5536 | 132.864 | 5.536 | 6.7 | 6.7 | 3B+1S | 0 | 976 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30572910 | 1252 | 226.1561 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 5208326 | 5536 | 132.864 | 5.536 | 6.6 | 6.6 | 3B+1S | 0 | 985 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30574170 | 1260 | 227.6012 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 5213947 | 5621 | 134.904 | 5.621 | 6.3 | 6.3 | 3B+1S | 0 | 985 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30575456 | 1286 | 228.7849 | 0% | 100% | 100% | 100% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 5219533 | 5586 | 134.064 | 5.586 | 6.2 | 6.2 | 3B+1S | 0 | 985 | 1105 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30576704 | 1248 | 223.4157 | 0% | 100% | 100% | 0% | 100% | 0% | 6726177 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 5225196 | 5663 | 135.912 | 5.663 | 6 | 6 | 3B+1S | 0 | 988 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30577956 | 1252 | 221.0842 | 0% | 100% | 100% | 0% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 131 | 5230730 | 5534 | 132.816 | 5.534 | 5.2 | 5.2 | 2B+1S | 0 | 1140 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30579080 | 1124 | 203.1081 | 0% | 100% | 100% | 0% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 5236140 | 5410 | 129.84 | 5.41 | 4.2 | 4.2 | 2B+1S | 0 | 1068 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30580170 | 1090 | 201.4787 | 0% | 100% | 100% | 0% | 100% | 0% | 6726177 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 120 | 5241126 | 4986 | 119.664 | 4.986 | 3.7 | 3.7 | 2B+1S | 0 | 1000 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30581166 | 996 | 199.7593 | 0% | 100% | 100% | 0% | 100% | 0% | 6726177 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 105 | 5245498 | 4372 | 104.928 | 4.372 | 4.1 | 4.1 | 2B | 0 | 0 | 1049 | 0 | 1109 | N/A | N/A | N/A | N/A | 30581926 | 760 | 173.8335 | 0% | 0% | 100% | 0% | 100% | 25% | 6726587 | 410 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 95 | 5249570 | 4072 | 97.728 | 4.072 | 4.8 | 4.8 | 2B | 0 | 0 | 1041 | 0 | 1048 | N/A | N/A | N/A | N/A | 30582596 | 670 | 164.5383 | 0% | 0% | 100% | 0% | 100% | 25% | 6727135 | 548 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.9583 | 123317 | 123317 | 123.317 | 123.317 | [12 empty] | 25172 | 25172 | 204.1243 | [6 empty] | 5897 | 5897 | 0.94 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:15 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 2) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24978 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5249570 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30582596 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6727135 |  | mg /l |  | Automatic - i2O | AI | REIVIN M. MALLARI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 101 | 99 | 5253508 | 3938 | 94.512 | 3.938 | 5.6 | 5.6 | 2B | 0 | 0 | 1051 | 0 | 1059 | N/A | N/A | N/A | N/A | 30583234 | 638 | 162.0112 | 0% | 0% | 100% | 0% | 100% | 35% | 6728101 | 966 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS L. GUANZON
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 88 | 5257362 | 3854 | 92.496 | 3.854 | 6.3 | 6.3 | 2B | 0 | 0 | 1051 | 0 | 1059 | N/A | N/A | N/A | N/A | 30583824 | 590 | 153.0877 | 0% | 0% | 100% | 0% | 100% | 35% | 6729121 | 1020 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ALEXANDER CABREROS
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 86 | 5261078 | 3716 | 89.184 | 3.716 | 8.1 | 8.1 | 2B | 0 | 0 | 980 | 0 | 1059 | N/A | N/A | N/A | N/A | 30584388 | 564 | 151.7761 | 0% | 0% | 100% | 0% | 100% | 35% | 6730379 | 1258 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY O. REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 84 | 5264688 | 3610 | 86.64 | 3.61 | 9.1 | 9.1 | 2B | 0 | 0 | 945 | 0 | 1059 | N/A | N/A | N/A | N/A | 30584936 | 548 | 151.8006 | 0% | 0% | 100% | 0% | 100% | 35% | 6731462 | 1083 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 106 | 5268605 | 3917 | 94.008 | 3.917 | 9.5 | 9.5 | 2B | 0 | 0 | 996 | 0 | 988 | N/A | N/A | N/A | N/A | 30585458 | 522 | 133.2653 | 0% | 0% | 100% | 0% | 100% | 35% | 6731651 | 189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 119 | 5272300 | 3695 | 88.68 | 3.695 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30586164 | 706 | 191.069 | 0% | 0% | 100% | 0% | 100% | 0% | 6731651 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 141 | 5279253 | 6953 | 166.872 | 6.953 | 8.9 | 8.9 | 3B+1S | 0 | 1061 | 1135 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30587470 | 1306 | 187.8326 | 0% | 0% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 5285405 | 6152 | 147.648 | 6.152 | 8.1 | 8.1 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30588828 | 1358 | 220.7412 | 0% | 0% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 153 | 5291565 | 6160 | 147.84 | 6.16 | 7.4 | 7.4 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 30590214 | 1386 | 225 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 5297775 | 6210 | 149.04 | 6.21 | 6.8 | 6.8 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30591614 | 1400 | 225.4428 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 | 0.85 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 141 | 148 | 5303827 | 6052 | 145.248 | 6.052 | 6.3 | 6.3 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30592974 | 1360 | 224.7191 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 5309835 | 6008 | 144.192 | 6.008 | 5.9 | 5.9 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30594324 | 1350 | 224.7004 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 5315661 | 5826 | 139.824 | 5.826 | 5.8 | 5.8 | 3B+1S | 0 | 997 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30595654 | 1330 | 228.287 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 5321366 | 5705 | 136.92 | 5.705 | 5.7 | 5.7 | 3B+1S | 0 | 998 | 1105 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30596922 | 1268 | 222.2612 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 143 | 5326859 | 5493 | 131.832 | 5.493 | 5.6 | 5.6 | 3B+1S | 0 | 980 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30598174 | 1252 | 227.9265 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 133 | 5332350 | 5491 | 131.784 | 5.491 | 5.6 | 5.6 | 3B+1S | 0 | 1004 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30599418 | 1244 | 226.5525 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 5337857 | 5507 | 132.168 | 5.507 | 5.5 | 5.5 | 3B+1S | 0 | 1008 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30600664 | 1246 | 226.2575 | 0% | 100% | 100% | 100% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 143 | 5343305 | 5448 | 130.752 | 5.448 | 5.4 | 5.4 | 3B+1S | 0 | 975 | 1104 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30601890 | 1226 | 225.0367 | 0% | 100% | 100% | 0% | 100% | 0% | 6731651 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 5348770 | 5465 | 131.16 | 5.465 | 5.3 | 5.3 | 3B+1S | 0 | 990 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30603126 | 1236 | 226.1665 | 0% | 100% | 100% | 0% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 130 | 5354197 | 5427 | 130.248 | 5.427 | 4.6 | 4.6 | 2B+1S | 0 | 1070 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30604206 | 1080 | 199.005 | 0% | 100% | 100% | 0% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 128 | 5359449 | 5252 | 126.048 | 5.252 | 3.9 | 3.9 | 2B+1S | 0 | 995 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30605248 | 1042 | 198.4006 | 0% | 100% | 100% | 0% | 100% | 0% | 6731651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 126 | 5364616 | 5167 | 124.008 | 5.167 | 3.7 | 3.7 | 2B+1S | 0 | 836 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30606286 | 1038 | 200.8903 | 0% | 100% | 100% | 0% | 100% | 0% | 6731651 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 101 | 5368654 | 4038 | 96.912 | 4.038 | 4.3 | 4.3 | 2B | 0 | 0 | 1085 | 0 | 1088 | N/A | N/A | N/A | N/A | 30606950 | 664 | 164.4378 | 0% | 0% | 100% | 0% | 100% | 25% | 6732107 | 456 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 92 | 5372552 | 3898 | 93.552 | 3.898 | 4.9 | 4.9 | 2B | 0 | 0 | 1029 | 0 | 1029 | N/A | N/A | N/A | N/A | 30607574 | 624 | 160.0821 | 0% | 0% | 100% | 0% | 100% | 25% | 6732673 | 566 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.75 | 122982 | 122982 | 122.982 | 122.982 | [12 empty] | 24978 | 24978 | 203.1029 | [6 empty] | 5538 | 5538 | 0.94833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:15 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 3) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 3) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24964 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5372552 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30607574 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6732673 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 89 | 5376627 | 4075 | 97.8 | 4.075 | 6.2 | 6.2 | 2B | 0 | 0 | 1055 | 0 | 1037 | N/A | N/A | N/A | N/A | 30608254 | 680 | 166.8712 | 0% | 0% | 100% | 0% | 100% | 35% | 6733785 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 88 | 5380499 | 3872 | 92.928 | 3.872 | 7.5 | 7.5 | 2B | 0 | 0 | 1009 | 0 | 1038 | N/A | N/A | N/A | N/A | 30608806 | 552 | 142.562 | 0% | 0% | 100% | 0% | 100% | 35% | 6734964 | 1179 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 101 | 87 | 5384179 | 3680 | 88.32 | 3.68 | 8.9 | 8.9 | 2B | 0 | 0 | 1009 | 0 | 1038 | N/A | N/A | N/A | N/A | 30609352 | 546 | 148.3696 | 0% | 0% | 100% | 0% | 100% | 35% | 6736288 | 1324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 88 | 5387747 | 3568 | 85.632 | 3.568 | 9.5 | 9.5 | 2B | 0 | 0 | 941 | 0 | 957 | N/A | N/A | N/A | N/A | 30609862 | 510 | 142.9372 | 0% | 0% | 100% | 0% | 100% | 35% | 6737067 | 779 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 97 | 5391339 | 3592 | 86.208 | 3.592 | 9.5 | 9.5 | 2B | 0 | 0 | 999 | 0 | 1009 | N/A | N/A | N/A | N/A | 30610334 | 472 | 131.4031 | 0% | 0% | 100% | 0% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 119 | 5396046 | 4707 | 112.968 | 4.707 | 9.5 | 9.5 | 2B | 0 | 0 | 1154 | 0 | 1170 | N/A | N/A | N/A | N/A | 30611088 | 754 | 160.187 | 0% | 0% | 100% | 0% | 100% | 0% | 6737067 | 0 | 0.88 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 141 | 5402470 | 6424 | 154.176 | 6.424 | 9.1 | 9.1 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30612423 | 1335 | 207.8144 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 5408569 | 6099 | 146.376 | 6.099 | 8.3 | 8.3 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30613791 | 1368 | 224.2991 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 140 | 5414652 | 6083 | 145.992 | 6.083 | 7.5 | 7.5 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30615180 | 1389 | 228.3413 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 138 | 5420424 | 5772 | 138.528 | 5.772 | 7.3 | 7.3 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30616544 | 1364 | 236.3132 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 139 | 146 | 5426455 | 6031 | 144.744 | 6.031 | 6.9 | 6.9 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30617898 | 1354 | 224.5067 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 5432430 | 5975 | 143.4 | 5.975 | 6.6 | 6.6 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30619244 | 1346 | 225.272 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 130 | 5438144 | 5714 | 137.136 | 5.714 | 6.5 | 6.5 | 3B+1S | 0 | 999 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30620534 | 1290 | 225.7613 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 5443840 | 5696 | 136.704 | 5.696 | 6.4 | 6.4 | 3B+1S | 0 | 1012 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30621808 | 1274 | 223.6657 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 5449500 | 5660 | 135.84 | 5.66 | 6.3 | 6.3 | 3B+1S | 0 | 972 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30623054 | 1246 | 220.1413 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 5455066 | 5566 | 133.584 | 5.566 | 6.2 | 6.2 | 3B+1S | 0 | 990 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30624310 | 1256 | 225.6558 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 5460634 | 5568 | 133.632 | 5.568 | 6.1 | 6.1 | 3B+1S | 0 | 1010 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30625566 | 1256 | 225.5747 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 139 | 5466186 | 5552 | 133.248 | 5.552 | 6 | 6 | 3B+1S | 0 | 970 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30626820 | 1254 | 225.8646 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 5471656 | 5470 | 131.28 | 5.47 | 5.9 | 5.9 | 3B+1S | 0 | 970 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30628058 | 1238 | 226.3254 | 0% | 100% | 100% | 100% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 128 | 5477118 | 5462 | 131.088 | 5.462 | 5.2 | 5.2 | 2B+1S | 0 | 1105 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30629162 | 1104 | 202.1238 | 0% | 100% | 100% | 0% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 5482399 | 5281 | 126.744 | 5.281 | 4.4 | 4.4 | 2B+1S | 0 | 1049 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30630228 | 1066 | 201.8557 | 0% | 100% | 100% | 0% | 100% | 0% | 6737067 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 123 | 5487398 | 4999 | 119.976 | 4.999 | 4.2 | 4.2 | 2B+1S | 0 | 970 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 30631206 | 978 | 195.6391 | 0% | 100% | 100% | 0% | 100% | 0% | 6737067 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 98 | 5491669 | 4271 | 102.504 | 4.271 | 4.7 | 4.7 | 2B | 0 | 0 | 1090 | 0 | 1110 | N/A | N/A | N/A | N/A | 30631946 | 740 | 173.2615 | 0% | 0% | 100% | 0% | 100% | 0% | 6737470 | 403 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 99 | 5495694 | 4025 | 96.6 | 4.025 | 5.4 | 5.4 | 2B | 0 | 0 | 925 | 0 | 1110 | N/A | N/A | N/A | N/A | 30632538 | 592 | 147.0807 | 0% | 0% | 100% | 0% | 100% | 0% | 6738340 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5833 | 123142 | 123142 | 123.142 | 123.142 | [12 empty] | 24964 | 24964 | 202.7253 | [6 empty] | 5667 | 5667 | 0.965 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:01 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @10:05 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 4) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25680 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5495694 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30632538 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6738340 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 89 | 5499552 | 3858 | 92.592 | 3.858 | 6.7 | 6.7 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 30633132 | 594 | 153.9658 | 0% | 0% | 100% | 0% | 100% | 35% | 6739364 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 90 | 5503284 | 3732 | 89.568 | 3.732 | 7.6 | 7.6 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 30633730 | 598 | 160.2358 | 0% | 0% | 100% | 0% | 100% | 35% | 6740401 | 1037 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 85 | 5507009 | 3725 | 89.4 | 3.725 | 8.7 | 8.7 | 2B | 0 | 0 | 940 | 0 | 1060 | N/A | N/A | N/A | N/A | 30634298 | 568 | 152.4832 | 0% | 0% | 100% | 0% | 100% | 35% | 6741397 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 90 | 5510656 | 3647 | 87.528 | 3.647 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1009 | N/A | N/A | N/A | N/A | 30634830 | 532 | 145.8733 | 0% | 0% | 100% | 0% | 100% | 35% | 6742203 | 806 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 107 | 5514622 | 3966 | 95.184 | 3.966 | 9.5 | 9.5 | 2B | 0 | 0 | 990 | 0 | 1009 | N/A | N/A | N/A | N/A | 30635366 | 536 | 135.1488 | 0% | 0% | 100% | 0% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 122 | 5519248 | 4626 | 111.024 | 4.626 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1150 | N/A | N/A | N/A | N/A | 30636022 | 656 | 141.8072 | 0% | 0% | 100% | 0% | 100% | 0% | 6742203 | 0 | 1.1 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 153 | 5525275 | 6027 | 144.648 | 6.027 | 8.8 | 8.8 | 3B+1S | 0 | 1079 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30637370 | 1348 | 223.6602 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 157 | 5531524 | 6249 | 149.976 | 6.249 | 7.9 | 7.9 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30638705 | 1335 | 213.6342 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 154 | 5537800 | 6276 | 150.624 | 6.276 | 7 | 7 | 3B+1S | 0 | 1150 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30640142 | 1437 | 228.9675 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 5544000 | 6200 | 148.8 | 6.2 | 6 | 6 | 3B+1S | 0 | 1155 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30641624 | 1482 | 239.0323 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 136 | 145 | 5550313 | 6313 | 151.512 | 6.313 | 5.3 | 5.3 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30643046 | 1422 | 225.2495 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 5556456 | 6143 | 147.432 | 6.143 | 4.6 | 4.6 | 3B+1S | 0 | 1103 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30644436 | 1390 | 226.2738 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 137 | 5562191 | 5735 | 137.64 | 5.735 | 4.3 | 4.3 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30645734 | 1298 | 226.3296 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 140 | 145 | 5567863 | 5672 | 136.128 | 5.672 | 4.2 | 4.2 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30647044 | 1310 | 230.9591 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 143 | 5573582 | 5719 | 137.256 | 5.719 | 4.2 | 4.2 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30648362 | 1318 | 230.4599 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 5579299 | 5717 | 137.208 | 5.717 | 4.1 | 4.1 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30649670 | 1308 | 228.7913 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 142 | 5584930 | 5631 | 135.144 | 5.631 | 4.1 | 4.1 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30650978 | 1308 | 232.2856 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 139 | 5590397 | 5467 | 131.208 | 5.467 | 3.9 | 3.9 | 3B+1S | 0 | 999 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30652214 | 1236 | 226.0838 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 141 | 5595914 | 5517 | 132.408 | 5.517 | 3.8 | 3.8 | 3B+1S | 0 | 999 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30653502 | 1288 | 233.4602 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 132 | 5601423 | 5509 | 132.216 | 5.509 | 3.6 | 3.6 | 3B+1S | 0 | 999 | 1005 | 1185 | 1100 | N/A | N/A | N/A | N/A | 30654640 | 1138 | 206.5711 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 132 | 5606732 | 5309 | 127.416 | 5.309 | 3.4 | 3.4 | 3B+1S | 0 | 999 | 1010 | 1185 | 1100 | N/A | N/A | N/A | N/A | 30655778 | 1138 | 214.353 | 0% | 100% | 100% | 100% | 100% | 0% | 6742203 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 125 | 5611740 | 5008 | 120.192 | 5.008 | 3.2 | 3.2 | 2B | 0 | 982 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30656778 | 1000 | 199.6805 | 0% | 0% | 100% | 0% | 100% | 0% | 6742203 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 100 | 5616083 | 4343 | 104.232 | 4.343 | 3.7 | 3.7 | 2B | 0 | 0 | 1095 | 0 | 1087 | N/A | N/A | N/A | N/A | 30657504 | 726 | 167.1656 | 0% | 0% | 100% | 0% | 100% | 25% | 6742703 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 93 | 5620322 | 4239 | 101.736 | 4.239 | 4.5 | 4.5 | 2B | 0 | 0 | 0 | 1185 | 960 | N/A | N/A | N/A | N/A | 30658218 | 714 | 168.436 | 0% | 0% | 0% | 100% | 100% | 25% | 6743319 | 616 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.2083 | 124628 | 124628 | 124.628 | 124.628 | [12 empty] | 25680 | 25680 | 206.0532 | [6 empty] | 4979 | 4979 | 0.95 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:40 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 5) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
BP2 - RESTARTED @ 11:01 PM
BP1 - STOPPED @ 11:01 PM
NORMAL OPERATION

## SEPT 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26340 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5620322 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30658218 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6743319 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 92 | 5624312 | 3990 | 95.76 | 3.99 | 5 | 5 | 2B | 0 | 0 | 971 | 1185 | 0 | N/A | N/A | N/A | N/A | 30658910 | 692 | 173.4336 | 0% | 0% | 100% | 100% | 0% | 35% | 6744567 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 5627951 | 3639 | 87.336 | 3.639 | 6 | 6 | 2B | 0 | 0 | 1019 | 0 | 1049 | N/A | N/A | N/A | N/A | 30659515 | 605 | 166.2545 | 0% | 0% | 100% | 0% | 100% | 35% | 6745862 | 1295 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 5631549 | 3598 | 86.352 | 3.598 | 7.3 | 7.3 | 2B | 0 | 0 | 1018 | 0 | 1008 | N/A | N/A | N/A | N/A | 30660138 | 623 | 173.1518 | 0% | 0% | 100% | 0% | 100% | 35% | 6747203 | 1341 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 92 | 5636184 | 4635 | 111.24 | 4.635 | 8.5 | 8.5 | 2B | 0 | 0 | 10117 | 0 | 1009 | N/A | N/A | N/A | N/A | 30660770 | 632 | 136.3538 | 0% | 0% | 100% | 0% | 100% | 35% | 6748028 | 825 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 128 | 99 | 5639590 | 3406 | 81.744 | 3.406 | 6.3 | 6.3 | 2B | 0 | 0 | 1049 | 0 | 1008 | N/A | N/A | N/A | N/A | 30661278 | 508 | 149.1486 | 0% | 0% | 100% | 0% | 100% | 35% | 6748141 | 113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 124 | 5644156 | 4566 | 109.584 | 4.566 | 9.5 | 9.5 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 30661894 | 616 | 134.9102 | 0% | 0% | 100% | 0% | 100% | 0% | 6748141 | 0 | 0.98 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 146 | 5649900 | 5744 | 137.856 | 5.744 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30663130 | 1236 | 215.1811 | 0% | 0% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 5655993 | 6093 | 146.232 | 6.093 | 8.9 | 8.9 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30664458 | 1328 | 217.955 | 0% | 0% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 149 | 5662059 | 6066 | 145.584 | 6.066 | 8.2 | 8.2 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30665830 | 1372 | 226.1787 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 151 | 5668574 | 6515 | 156.36 | 6.515 | 7.2 | 7.2 | 3B+1S | 0 | 1160 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30667308 | 1478 | 226.8611 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 129 | 148 | 5674786 | 6212 | 149.088 | 6.212 | 6.2 | 6.2 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30668740 | 1432 | 230.5216 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 153 | 5681029 | 6243 | 149.832 | 6.243 | 5.2 | 5.2 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30670190 | 1450 | 232.2601 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 147 | 5687122 | 6093 | 146.232 | 6.093 | 4.4 | 4.4 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30671600 | 1410 | 231.4131 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 5692937 | 5815 | 139.56 | 5.815 | 3.9 | 3.9 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30672970 | 1370 | 235.5976 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 136 | 5698568 | 5631 | 135.144 | 5.631 | 3.4 | 3.4 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30674312 | 1342 | 238.3236 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 5704117 | 5549 | 133.176 | 5.549 | 3.2 | 3.2 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30675649 | 1337 | 240.9443 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 5710014 | 5897 | 141.528 | 5.897 | 2.7 | 2.7 | 3B+1S | 0 | 1162 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30677002 | 1353 | 229.4387 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 5715667 | 5653 | 135.672 | 5.653 | 2.6 | 2.6 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30678330 | 1328 | 234.9195 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 137 | 5721312 | 5645 | 135.48 | 5.645 | 2.4 | 2.4 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30679626 | 1296 | 229.5837 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 129 | 5726802 | 5490 | 131.76 | 5.49 | 2.2 | 2.2 | 3B+1S | 0 | 1010 | 1140 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30680854 | 1228 | 223.6794 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 | 131 | 5732219 | 5417 | 130.008 | 5.417 | 2.1 | 2.1 | 3B+1S | 0 | 1010 | 1110 | 1185 | 1118 | N/A | N/A | N/A | N/A | 30682048 | 1194 | 220.4172 | 0% | 100% | 100% | 100% | 100% | 0% | 6748141 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 125 | 5737359 | 5140 | 123.36 | 5.14 | 1.7 | 1.7 | 2B+1S | 0 | 1016 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30683086 | 1038 | 201.9455 | 0% | 100% | 100% | 0% | 100% | 0% | 6748141 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 105 | 5741727 | 4368 | 104.832 | 4.368 | 2.6 | 2.6 | 2B | 0 | 0 | 1060 | 0 | 1140 | N/A | N/A | N/A | N/A | 30683850 | 764 | 174.9084 | 0% | 0% | 100% | 0% | 100% | 35% | 6749173 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 99 | 5745934 | 4207 | 100.968 | 4.207 | 3.8 | 3.8 | 2B | 0 | 0 | 1106 | 0 | 1100 | N/A | N/A | N/A | N/A | 30684558 | 708 | 168.2909 | 0% | 0% | 100% | 0% | 100% | 35% | 6750280 | 1107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.9167 | 125612 | 125612 | 125.612 | 125.612 | [12 empty] | 26340 | 26340 | 209.6933 | [6 empty] | 6961 | 6961 | 0.97 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
BP1 - RESTARTED @ 12:01 AM
BP3 - STOPPED @ 12:01 AM
RESTARTED @ 1:30 AM
BP2 - STOPPED @ 1:30 AM
XCV1 CLOSED @ 5:05 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 12:01 pm to 5Pm (SEPT 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 OPENED @ 4:00 PM - DUE TO LOW LEVEL OF RESEVOIR / CLOSED @ 5:20 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26050 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5745934 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30684558 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6750280 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 111 | 97 | 5750125 | 4191 | 100.584 | 4.191 | 4.7 | 4.7 | 2B | 0 | 0 | 1038 | 0 | 1045 | N/A | N/A | N/A | N/A | 30685285 | 727 | 173.467 | 0% | 0% | 100% | 0% | 100% | 35% | 6751091 | 811 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 92 | 5754264 | 4139 | 99.336 | 4.139 | 5.6 | 5.6 | 2B | 0 | 0 | 1036 | 0 | 1100 | N/A | N/A | N/A | N/A | 30686012 | 727 | 175.6463 | 0% | 0% | 100% | 0% | 100% | 35% | 6751927 | 836 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 91 | 5758064 | 3800 | 91.2 | 3.8 | 6.5 | 6.5 | 2B | 0 | 0 | 1035 | 0 | 1059 | N/A | N/A | N/A | N/A | 30686633 | 621 | 163.4211 | 0% | 0% | 100% | 0% | 100% | 35% | 6752792 | 865 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 89 | 5761875 | 3811 | 91.464 | 3.811 | 7.6 | 7.6 | 2B | 0 | 0 | 1040 | 0 | 1045 | N/A | N/A | N/A | N/A | 30687254 | 621 | 162.9494 | 0% | 0% | 100% | 0% | 100% | 35% | 6753620 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 139 | 93 | 5765398 | 3523 | 84.552 | 3.523 | 8.5 | 8.5 | 2B | 0 | 0 | 1066 | 0 | 1109 | N/A | N/A | N/A | N/A | 30687886 | 632 | 179.3926 | 0% | 0% | 100% | 0% | 100% | 0% | 6754285 | 665 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 129 | 112 | 5769950 | 4552 | 109.248 | 4.552 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1030 | N/A | N/A | N/A | N/A | 30688636 | 750 | 164.7627 | 0% | 0% | 100% | 0% | 100% | 0% | 6754285 | 0 | 0.87 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 5775180 | 5230 | 125.52 | 5.23 | 9.5 | 9.5 | 3B | 0 | 0 | 1079 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30689652 | 1016 | 194.2639 | 0% | 0% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 5781300 | 6120 | 146.88 | 6.12 | 8.9 | 8.9 | 3B+1S | 0 | 1148 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30690956 | 1304 | 213.0719 | 0% | 0% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 5787589 | 6289 | 150.936 | 6.289 | 8.3 | 8.3 | 3B+1S | 0 | 1134 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30692352 | 1396 | 221.9749 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 5793787 | 6198 | 148.752 | 6.198 | 7.4 | 7.4 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30693748 | 1396 | 225.2339 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 127 | 151 | 5800032 | 6245 | 149.88 | 6.245 | 6.6 | 6.6 | 3B+1S | 0 | 1171 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30695174 | 1426 | 228.3427 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 149 | 5806109 | 6077 | 145.848 | 6.077 | 5.7 | 5.7 | 3B+1S | 0 | 1117 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30696596 | 1422 | 233.997 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 5812005 | 5896 | 141.504 | 5.896 | 5.3 | 5.3 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30697936 | 1340 | 227.2727 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 5817787 | 5782 | 138.768 | 5.782 | 4.9 | 4.9 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30699260 | 1324 | 228.9865 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 139 | 5823541 | 5754 | 138.096 | 5.754 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30700578 | 1318 | 229.058 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 5829277 | 5736 | 137.664 | 5.736 | 4.6 | 4.6 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30701890 | 1312 | 228.7308 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 5835012 | 5735 | 137.64 | 5.735 | 4.3 | 4.3 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30703230 | 1340 | 233.653 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 141 | 5840716 | 5704 | 136.896 | 5.704 | 4.1 | 4.1 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30704539 | 1309 | 229.4881 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 137 | 5846398 | 5682 | 136.368 | 5.682 | 3.9 | 3.9 | 3B+1S | 0 | 999 | 1179 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30705840 | 1301 | 228.9687 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 135 | 5852101 | 5703 | 136.872 | 5.703 | 3.6 | 3.6 | 3B+1S | 0 | 999 | 1119 | 1185 | 1128 | N/A | N/A | N/A | N/A | 30707084 | 1244 | 218.1308 | 0% | 100% | 100% | 100% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 128 | 5857448 | 5347 | 128.328 | 5.347 | 3.1 | 3.1 | 2B+1S | 0 | 1041 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30708132 | 1048 | 195.9978 | 0% | 100% | 100% | 0% | 100% | 0% | 6754285 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 124 | 5862624 | 5176 | 124.224 | 5.176 | 2.6 | 2.6 | 2B+1S | 0 | 1009 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30709152 | 1020 | 197.0634 | 0% | 100% | 100% | 0% | 100% | 0% | 6754285 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 109 | 5866982 | 4358 | 104.592 | 4.358 | 2.9 | 2.9 | 2B | 0 | 0 | 1097 | 0 | 1109 | N/A | N/A | N/A | N/A | 30709922 | 770 | 176.6866 | 0% | 0% | 100% | 0% | 100% | 25% | 6755175 | 890 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 95 | 5871089 | 4107 | 98.568 | 4.107 | 3.5 | 3.5 | 2B | 0 | 0 | 1022 | 0 | 1109 | N/A | N/A | N/A | N/A | 30710608 | 686 | 167.0319 | 0% | 0% | 100% | 0% | 100% | 25% | 6755767 | 592 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.8333 | 125155 | 125155 | 125.155 | 125.155 | [12 empty] | 26050 | 26050 | 208.1419 | [6 empty] | 5487 | 5487 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 5:28AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:16 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
MAGALLANES- ONLINE BOOSTER RESUMED NORMAL OPERATION @ 7:35 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:40 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 7) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED GENSET EXERCISES TO G1 AND G2 FOR 10 MINUTES EACH, NORMAL CONDITION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25330 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5871089 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30710608 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6755767 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 109 | 94 | 5875001 | 3912 | 93.888 | 3.912 | 4.3 | 4.3 | 2B | 0 | 0 | 1020 | 0 | 1038 | N/A | N/A | N/A | N/A | 30711182 | 574 | 146.728 | 0% | 0% | 100% | 0% | 100% | 25% | 6756416 | 649 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 106 | 90 | 5878759 | 3758 | 90.192 | 3.758 | 5.1 | 5.1 | 2B | 0 | 0 | 1028 | 0 | 1039 | N/A | N/A | N/A | N/A | 30711751 | 569 | 151.4103 | 0% | 0% | 100% | 0% | 100% | 25% | 6757108 | 692 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 107 | 88 | 5882381 | 3622 | 86.928 | 3.622 | 5.9 | 5.9 | 2B | 0 | 0 | 1018 | 0 | 1039 | N/A | N/A | N/A | N/A | 30712304 | 553 | 152.6781 | 0% | 0% | 100% | 0% | 100% | 25% | 6757929 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 89 | 5886096 | 3715 | 89.16 | 3.715 | 6.7 | 6.7 | 2B | 0 | 0 | 1008 | 0 | 1039 | N/A | N/A | N/A | N/A | 30712872 | 568 | 152.8937 | 0% | 0% | 100% | 0% | 100% | 25% | 6758647 | 718 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 131 | 101 | 5890203 | 4107 | 98.568 | 4.107 | 7.7 | 7.7 | 2B | 0 | 0 | 1141 | 0 | 1152 | N/A | N/A | N/A | N/A | 30713518 | 646 | 157.2924 | 0% | 0% | 100% | 0% | 100% | 35% | 6759400 | 753 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 121 | 5895495 | 5292 | 127.008 | 5.292 | 9 | 9 | 2B | 0 | 0 | 1153 | 0 | 1150 | N/A | N/A | N/A | N/A | 30714604 | 1086 | 205.2154 | 0% | 0% | 100% | 0% | 100% | 35% | 6759400 | 0 | 0.98 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 145 | 145 | 5900787 | 5292 | 127.008 | 5.292 | 8.3 | 8.3 | 3B | 0 | 970 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30715690 | 1086 | 205.2154 | 0% | 0% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.3 | 142 | 149 | 5906766 | 5979 | 143.496 | 5.979 | 8.1 | 8.1 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30717010 | 1320 | 220.7727 | 0% | 0% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 18.4 | 141 | 143 | 5912939 | 6173 | 148.152 | 6.173 | 7.8 | 7.8 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30718374 | 1364 | 220.9623 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 5919218 | 6279 | 150.696 | 6.279 | 7.1 | 7.1 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30719786 | 1412 | 224.8766 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 131 | 144 | 5925183 | 5965 | 143.16 | 5.965 | 6.3 | 6.3 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30721152 | 1366 | 229.0025 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 5931154 | 5971 | 143.304 | 5.971 | 5.8 | 5.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30722522 | 1370 | 229.4423 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 135 | 5936941 | 5787 | 138.888 | 5.787 | 5.5 | 5.5 | 3B+1S | 0 | 1007 | 1135 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30723822 | 1300 | 224.6414 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 5942569 | 5628 | 135.072 | 5.628 | 5.4 | 5.4 | 3B+1S | 0 | 999 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30725090 | 1268 | 225.3021 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 137 | 5948054 | 5485 | 131.64 | 5.485 | 5.3 | 5.3 | 3B+1S | 0 | 999 | 1125 | 1185 | 1189 | N/A | N/A | N/A | N/A | 30726334 | 1244 | 226.8004 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 5953549 | 5495 | 131.88 | 5.495 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1125 | 1185 | 1189 | N/A | N/A | N/A | N/A | 30727554 | 1220 | 222.02 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 5959047 | 5498 | 131.952 | 5.498 | 5.1 | 5.1 | 3B+1S | 0 | 999 | 1125 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30728800 | 1246 | 226.6279 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 137 | 5964532 | 5485 | 131.64 | 5.485 | 5 | 5 | 3B+1S | 0 | 999 | 1125 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30730020 | 1220 | 222.4248 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 5970007 | 5475 | 131.4 | 5.475 | 4.8 | 4.8 | 3B+1S | 0 | 999 | 1125 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30731198 | 1178 | 215.1598 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 134 | 5975458 | 5451 | 130.824 | 5.451 | 4.5 | 4.5 | 3B+1S | 0 | 999 | 1105 | 1185 | 1130 | N/A | N/A | N/A | N/A | 30732374 | 1176 | 215.7402 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 124 | 131 | 5980795 | 5337 | 128.088 | 5.337 | 4.2 | 4.2 | 3B+1S | 0 | 999 | 1105 | 1185 | 1110 | N/A | N/A | N/A | N/A | 30733522 | 1148 | 215.1021 | 0% | 100% | 100% | 100% | 100% | 0% | 6759400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 130 | 124 | 5985942 | 5147 | 123.528 | 5.147 | 3.8 | 3.8 | 2B+1S | 0 | 1009 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30734550 | 1028 | 199.728 | 0% | 100% | 100% | 0% | 100% | 0% | 6759400 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 101 | 5990245 | 4303 | 103.272 | 4.303 | 4.3 | 4.3 | 2B | 0 | 0 | 1061 | 0 | 1110 | N/A | N/A | N/A | N/A | 30735292 | 742 | 172.4378 | 0% | 0% | 100% | 0% | 100% | 25% | 6760082 | 682 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 92 | 5994226 | 3981 | 95.544 | 3.981 | 4.9 | 4.9 | 2B | 0 | 0 | 1027 | 0 | 1059 | N/A | N/A | N/A | N/A | 30735938 | 646 | 162.2708 | 0% | 0% | 100% | 0% | 100% | 25% | 6760679 | 597 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.875 | 123137 | 123137 | 123.137 | 123.137 | [12 empty] | 25330 | 25330 | 205.7058 | [6 empty] | 4912 | 4912 | 0.98667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 4:01 AM FOR REFILLING
XCV1 CLOSED @ 5:45 AM, WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET PRESSURE
MAGALLANES 0NLINE BOOSTER- VFD CURRENT OVER LOAD / RESET @ 8:30 AM - NORMAL OPERATION @ 8:32 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 9) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 9) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24916 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5994226 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30735938 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6760679 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 107 | 97 | 5998030 | 3804 | 91.296 | 3.804 | 6.1 | 6.1 | 2B | 0 | 0 | 1012 | 0 | 1059 | N/A | N/A | N/A | N/A | 30736510 | 572 | 150.368 | 0% | 0% | 100% | 0% | 100% | 35% | 6761422 | 743 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 84 | 6001722 | 3692 | 88.608 | 3.692 | 7.5 | 7.5 | 2B | 0 | 0 | 932 | 0 | 1059 | N/A | N/A | N/A | N/A | 30737075 | 565 | 153.0336 | 0% | 0% | 100% | 0% | 100% | 35% | 6762373 | 951 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 87 | 6005339 | 3617 | 86.808 | 3.617 | 8.4 | 8.4 | 2B | 0 | 0 | 936 | 0 | 1059 | N/A | N/A | N/A | N/A | 30737633 | 558 | 154.2715 | 0% | 0% | 100% | 0% | 100% | 35% | 6763792 | 1419 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 92 | 6009021 | 3682 | 88.368 | 3.682 | 9.5 | 9.5 | 2B | 0 | 0 | 933 | 0 | 999 | N/A | N/A | N/A | N/A | 30738208 | 575 | 156.1651 | 0% | 0% | 100% | 0% | 100% | 35% | 6765056 | 1264 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 106 | 6013033 | 4012 | 96.288 | 4.012 | 9.5 | 9.5 | 2B | 0 | 0 | 1019 | 0 | 1009 | N/A | N/A | N/A | N/A | 30738732 | 524 | 130.6082 | 0% | 0% | 100% | 0% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 120 | 6017883 | 4850 | 116.4 | 4.85 | 9.5 | 9.5 | 2B | 0 | 0 | 1191 | 0 | 1170 | N/A | N/A | N/A | N/A | 30739522 | 790 | 162.8866 | 0% | 0% | 100% | 0% | 100% | 0% | 6765056 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 143 | 6023917 | 6034 | 144.816 | 6.034 | 9.1 | 9.1 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30740866 | 1344 | 222.7378 | 0% | 0% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 6029920 | 6003 | 144.072 | 6.003 | 8.4 | 8.4 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30742232 | 1366 | 227.5529 | 0% | 0% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 6036157 | 6237 | 149.688 | 6.237 | 7.7 | 7.7 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30743634 | 1402 | 224.7876 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 152 | 6042242 | 6085 | 146.04 | 6.085 | 7 | 7 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30745007 | 1373 | 225.6368 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 136 | 145 | 6048328 | 6086 | 146.064 | 6.086 | 6.5 | 6.5 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30746380 | 1373 | 225.5997 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 6054392 | 6064 | 145.536 | 6.064 | 6 | 6 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30747756 | 1376 | 226.9129 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 141 | 6060153 | 5761 | 138.264 | 5.761 | 5.9 | 5.9 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30749078 | 1322 | 229.474 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 6065718 | 5565 | 133.56 | 5.565 | 5.8 | 5.8 | 3B+1S | 0 | 1005 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30750332 | 1254 | 225.3369 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 6071280 | 5562 | 133.488 | 5.562 | 5.7 | 5.7 | 3B+1S | 0 | 999 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30751562 | 1230 | 221.1435 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 6076602 | 5322 | 127.728 | 5.322 | 5.6 | 5.6 | 3B+1S | 0 | 990 | 1105 | 1185 | 1129 | N/A | N/A | N/A | N/A | 30752710 | 1148 | 215.7084 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 6082040 | 5438 | 130.512 | 5.438 | 5.5 | 5.5 | 3B+1S | 0 | 1010 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30753922 | 1212 | 222.8761 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 6087569 | 5529 | 132.696 | 5.529 | 5.4 | 5.4 | 3B+1S | 0 | 982 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30755136 | 1214 | 219.5695 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 6093068 | 5499 | 131.976 | 5.499 | 5.3 | 5.3 | 3B+1S | 0 | 99 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30756358 | 1222 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 131 | 6098535 | 5467 | 131.208 | 5.467 | 4.6 | 4.6 | 2B+1S | 0 | 1080 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30757446 | 1088 | 199.0123 | 0% | 100% | 100% | 0% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 129 | 6103874 | 5339 | 128.136 | 5.339 | 3.9 | 3.9 | 2B+1S | 0 | 1030 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30758504 | 1058 | 198.1645 | 0% | 100% | 100% | 0% | 100% | 0% | 6765056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 132 | 135 | 6108976 | 5102 | 122.448 | 5.102 | 3.7 | 3.7 | 2B+1S | 0 | 999 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 30759508 | 1004 | 196.7856 | 0% | 100% | 100% | 0% | 100% | 0% | 6765056 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 99 | 6113119 | 4143 | 99.432 | 4.143 | 4.3 | 4.3 | 2B | 0 | 0 | 1056 | 0 | 1099 | N/A | N/A | N/A | N/A | 30760212 | 704 | 169.9252 | 0% | 0% | 100% | 0% | 100% | 25% | 6765560 | 504 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 90 | 6117088 | 3969 | 95.256 | 3.969 | 4.9 | 4.9 | 2B | 0 | 0 | 1029 | 0 | 1038 | N/A | N/A | N/A | N/A | 30760854 | 642 | 161.7536 | 0% | 0% | 100% | 0% | 100% | 25% | 6766175 | 615 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0417 | 122862 | 122862 | 122.862 | 122.862 | [12 empty] | 24916 | 24916 | 202.7966 | [6 empty] | 5496 | 5496 | 0.945 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:46 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 9) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 9) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24656 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6117088 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30760854 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6766175 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 95 | 6120894 | 3806 | 91.344 | 3.806 | 5.9 | 5.9 | 2B | 0 | 0 | 1020 | 0 | 1028 | N/A | N/A | N/A | N/A | 30761460 | 606 | 159.2223 | 0% | 0% | 100% | 0% | 100% | 35% | 6767212 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 91 | 6124656 | 3762 | 90.288 | 3.762 | 7.5 | 7.5 | 2B | 0 | 0 | 981 | 0 | 1018 | N/A | N/A | N/A | N/A | 30762021 | 561 | 149.1228 | 0% | 0% | 100% | 0% | 100% | 35% | 6768294 | 1082 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 88 | 6128405 | 3749 | 89.976 | 3.749 | 8.7 | 8.7 | 2B | 0 | 0 | 974 | 0 | 1018 | N/A | N/A | N/A | N/A | 30762574 | 553 | 147.506 | 0% | 0% | 100% | 0% | 100% | 35% | 6769575 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 91 | 6132039 | 3634 | 87.216 | 3.634 | 9.5 | 9.5 | 2B | 0 | 0 | 975 | 0 | 988 | N/A | N/A | N/A | N/A | 30763094 | 520 | 143.093 | 0% | 0% | 100% | 0% | 100% | 35% | 6770556 | 981 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 101 | 6135961 | 3922 | 94.128 | 3.922 | 9.5 | 9.5 | 2B | 0 | 0 | 990 | 0 | 988 | N/A | N/A | N/A | N/A | 30763598 | 504 | 128.5059 | 0% | 0% | 100% | 0% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 115 | 6141410 | 5449 | 130.776 | 5.449 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30764688 | 1090 | 200.0367 | 0% | 0% | 100% | 0% | 100% | 0% | 6770556 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 6146859 | 5449 | 130.776 | 5.449 | 9.1 | 9.1 | 3B+1S | 0 | 1042 | 1135 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30765778 | 1090 | 200.0367 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 6152870 | 6011 | 144.264 | 6.011 | 8.3 | 8.3 | 3B+1S | 0 | 1143 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30767102 | 1324 | 220.2629 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 6158969 | 6099 | 146.376 | 6.099 | 7.8 | 7.8 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30768466 | 1364 | 223.6432 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 6165083 | 6114 | 146.736 | 6.114 | 7.2 | 7.2 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30769842 | 1376 | 225.0572 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 140 | 141 | 6171158 | 6075 | 145.8 | 6.075 | 6.8 | 6.8 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30771206 | 1364 | 224.5267 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Normal operation schedule
59:00 | 12:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 136 | 6177020 | 5862 | 140.688 | 5.862 | 6.6 | 6.6 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30772536 | 1330 | 226.885 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 115 | 132 | 6182714 | 5694 | 136.656 | 5.694 | 5.8 | 5.8 | 2B+1S | 0 | 1176 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30773712 | 1176 | 206.5332 | 0% | 100% | 100% | 0% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 131 | 6188172 | 5458 | 130.992 | 5.458 | 5.3 | 5.3 | 3B+1S | 0 | 999 | 1125 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30774882 | 1170 | 214.3642 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 132 | 6193428 | 5256 | 126.144 | 5.256 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30776082 | 1200 | 228.3105 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 6198730 | 5302 | 127.248 | 5.302 | 5.1 | 5.1 | 3B+1S | 0 | 999 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30777284 | 1202 | 226.7069 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 6204015 | 5285 | 126.84 | 5.285 | 5 | 5 | 3B+1S | 0 | 999 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30778514 | 1230 | 232.7342 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 6209494 | 5479 | 131.496 | 5.479 | 4.9 | 4.9 | 3B+1S | 0 | 999 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30779706 | 1192 | 217.5579 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 6215025 | 5531 | 132.744 | 5.531 | 4.7 | 4.7 | 3B+1S | 0 | 999 | 1145 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30780942 | 1236 | 223.4677 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 131 | 6220424 | 5399 | 129.576 | 5.399 | 4.6 | 4.6 | 3B+1S | 0 | 980 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 30782126 | 1184 | 219.2999 | 0% | 100% | 100% | 100% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 126 | 6225728 | 5304 | 127.296 | 5.304 | 3.9 | 3.9 | 2B+1S | 0 | 1028 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30783186 | 1060 | 199.8492 | 0% | 100% | 100% | 0% | 100% | 0% | 6770556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 112 | 6230594 | 4866 | 116.784 | 4.866 | 3.7 | 3.7 | 2B+1S | 0 | 1000 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30784154 | 968 | 198.9314 | 0% | 100% | 100% | 0% | 100% | 0% | 6770556 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 100 | 6234896 | 4302 | 103.248 | 4.302 | 4.2 | 4.2 | 2B | 0 | 0 | 1080 | 0 | 1088 | N/A | N/A | N/A | N/A | 30784882 | 728 | 169.2236 | 0% | 0% | 100% | 0% | 100% | 25% | 6770995 | 439 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 98 | 6238777 | 3881 | 93.144 | 3.881 | 4.8 | 4.8 | 2B | 0 | 0 | 1036 | 0 | 1027 | N/A | N/A | N/A | N/A | 30785510 | 628 | 161.814 | 0% | 0% | 100% | 0% | 100% | 25% | 6771568 | 573 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5833 | 121689 | 121689 | 121.689 | 121.689 | [12 empty] | 24656 | 24656 | 202.6149 | [6 empty] | 5393 | 5393 | 0.96667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:54 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:08 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 10) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 12:06 PM
BP2 - RESTART @ 1:24 PM / STOPPED @ 8:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 10) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25044 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6238777 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30785510 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6771568 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 99 | 96 | 6242629 | 3852 | 92.448 | 3.852 | 5.8 | 5.8 | 2B | 0 | 0 | 1022 | 0 | 1028 | N/A | N/A | N/A | N/A | 30786090 | 580 | 150.5711 | 0% | 0% | 100% | 0% | 100% | 35% | 6772568 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 94 | 6246395 | 3766 | 90.384 | 3.766 | 6.9 | 6.9 | 2B | 0 | 0 | 1022 | 0 | 1028 | N/A | N/A | N/A | N/A | 30786625 | 535 | 142.0605 | 0% | 0% | 100% | 0% | 100% | 35% | 6773683 | 1115 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 92 | 6249907 | 3512 | 84.288 | 3.512 | 8.2 | 8.2 | 2B | 0 | 0 | 985 | 0 | 1050 | N/A | N/A | N/A | N/A | 30787160 | 535 | 152.3349 | 0% | 0% | 100% | 0% | 100% | 35% | 6774911 | 1228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 89 | 6253349 | 3442 | 82.608 | 3.442 | 9.5 | 9.5 | 2B | 0 | 0 | 904 | 0 | 907 | N/A | N/A | N/A | N/A | 30787724 | 564 | 163.8582 | 0% | 0% | 100% | 0% | 100% | 35% | 6776022 | 1111 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 102 | 6257014 | 3665 | 87.96 | 3.665 | 9.5 | 9.5 | 2B | 0 | 0 | 983 | 0 | 988 | N/A | N/A | N/A | N/A | 30788176 | 452 | 123.3288 | 0% | 0% | 100% | 0% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 125 | 6261724 | 4710 | 113.04 | 4.71 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1191 | N/A | N/A | N/A | N/A | 30788916 | 740 | 157.1125 | 0% | 0% | 100% | 0% | 100% | 0% | 6776022 | 0 | 0.92 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 144 | 6267795 | 6071 | 145.704 | 6.071 | 9.1 | 9.1 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30790274 | 1358 | 223.6864 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 6273935 | 6140 | 147.36 | 6.14 | 8.6 | 8.6 | 3B+1S | 0 | 1065 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30791645 | 1371 | 223.2899 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 6280103 | 6168 | 148.032 | 6.168 | 7.8 | 7.8 | 3B+1S | 0 | 1084 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30793007 | 1362 | 220.8171 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 6286276 | 6173 | 148.152 | 6.173 | 7.2 | 7.2 | 3B+1S | 0 | 1082 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30794366 | 1359 | 220.1523 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 140 | 142 | 6292429 | 6153 | 147.672 | 6.153 | 6.7 | 6.7 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30795746 | 1380 | 224.2808 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 141 | 6298353 | 5924 | 142.176 | 5.924 | 6.4 | 6.4 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30797095 | 1349 | 227.7178 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 136 | 6304180 | 5827 | 139.848 | 5.827 | 6.2 | 6.2 | 3B+1S | 0 | 993 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 30798418 | 1323 | 227.0465 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 6309846 | 5666 | 135.984 | 5.666 | 6.1 | 6.1 | 3B+1S | 0 | 970 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 30799706 | 1288 | 227.3209 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 134 | 6315305 | 5459 | 131.016 | 5.459 | 6 | 6 | 3B+1S | 0 | 1005 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30800942 | 1236 | 226.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 133 | 6320682 | 5377 | 129.048 | 5.377 | 5.9 | 5.9 | 3B+1S | 0 | 990 | 1125 | 1185 | 1180 | N/A | N/A | N/A | N/A | 30802164 | 1222 | 227.2643 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 134 | 6325973 | 5291 | 126.984 | 5.291 | 5.8 | 5.8 | 3B+1S | 0 | 1012 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30803386 | 1222 | 230.9582 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 6331442 | 5469 | 131.256 | 5.469 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30804616 | 1230 | 224.904 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 6337019 | 5577 | 133.848 | 5.577 | 5.3 | 5.3 | 3B+1S | 0 | 989 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30805878 | 1262 | 226.2865 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 6342439 | 5420 | 130.08 | 5.42 | 5.2 | 5.2 | 3B+1S | 0 | 965 | 1125 | 1185 | 1146 | N/A | N/A | N/A | N/A | 30807080 | 1202 | 221.7712 | 0% | 100% | 100% | 100% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 6347802 | 5363 | 128.712 | 5.363 | 4.6 | 4.6 | 2B+1S | 0 | 1036 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30808170 | 1090 | 203.2445 | 0% | 100% | 100% | 0% | 100% | 0% | 6776022 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 118 | 6352774 | 4972 | 119.328 | 4.972 | 4.1 | 4.1 | 2B+1S | 0 | 898 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30809164 | 994 | 199.9195 | 0% | 100% | 100% | 0% | 100% | 0% | 6776022 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 99 | 6357149 | 4375 | 105 | 4.375 | 4.5 | 4.5 | 2B | 0 | 0 | 1096 | 0 | 1109 | N/A | N/A | N/A | N/A | 30809926 | 762 | 174.1714 | 0% | 0% | 100% | 0% | 100% | 25% | 6776364 | 342 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 98 | 93 | 6360999 | 3850 | 92.4 | 3.85 | 5 | 5 | 2B | 0 | 0 | 1030 | 0 | 1028 | N/A | N/A | N/A | N/A | 30810554 | 628 | 163.1169 | 0% | 0% | 100% | 0% | 100% | 25% | 6776896 | 532 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.6667 | 122222 | 122222 | 122.222 | 122.222 | [12 empty] | 25044 | 25044 | 204.9058 | [6 empty] | 5328 | 5328 | 0.92 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:58 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 12) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 11) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24598 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6360999 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30810554 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6776896 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 91 | 6364729 | 3730 | 89.52 | 3.73 | 6.1 | 6.1 | 2B | 0 | 0 | 1035 | 0 | 1048 | N/A | N/A | N/A | N/A | 30811153 | 599 | 160.5898 | 0% | 0% | 100% | 0% | 100% | 35% | 6777956 | 1060 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 85 | 6368429 | 3700 | 88.8 | 3.7 | 7.2 | 7.2 | 2B | 0 | 0 | 977 | 0 | 1008 | N/A | N/A | N/A | N/A | 30811720 | 567 | 153.2432 | 0% | 0% | 100% | 0% | 100% | 35% | 6779062 | 1106 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 83 | 6372003 | 3574 | 85.776 | 3.574 | 8.4 | 8.4 | 2B | 0 | 0 | 978 | 0 | 1008 | N/A | N/A | N/A | N/A | 30812237 | 517 | 144.6558 | 0% | 0% | 100% | 0% | 100% | 35% | 6780180 | 1118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 82 | 6375602 | 3599 | 86.376 | 3.599 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 0 | 958 | N/A | N/A | N/A | N/A | 30812754 | 517 | 143.651 | 0% | 0% | 100% | 0% | 100% | 35% | 6781183 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 99 | 6379088 | 3486 | 83.664 | 3.486 | 9.5 | 9.5 | 2B | 0 | 0 | 995 | 0 | 978 | N/A | N/A | N/A | N/A | 30813204 | 450 | 129.0878 | 0% | 0% | 100% | 0% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 120 | 6384353 | 5265 | 126.36 | 5.265 | 9.5 | 9.5 | 2B | 0 | 0 | 1149 | 0 | 1199 | N/A | N/A | N/A | N/A | 30814223 | 1019 | 193.5423 | 0% | 0% | 100% | 0% | 100% | 0% | 6781183 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 147 | 6389618 | 5265 | 126.36 | 5.265 | 9.1 | 9.1 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30815242 | 1019 | 193.5423 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 6395687 | 6069 | 145.656 | 6.069 | 8.6 | 8.6 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1179 | N/A | N/A | N/A | N/A | 30816590 | 1348 | 222.1124 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 6401752 | 6065 | 145.56 | 6.065 | 8 | 8 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1181 | N/A | N/A | N/A | N/A | 30817942 | 1352 | 222.9184 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 6407875 | 6123 | 146.952 | 6.123 | 7.4 | 7.4 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 30819306 | 1364 | 222.7666 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 135 | 145 | 6413908 | 6033 | 144.792 | 6.033 | 6.9 | 6.9 | 3B+1S | 0 | 1060 | 1163 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30820658 | 1352 | 224.1008 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Normal operation schedule
59:00 | 12:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 6419992 | 6084 | 146.016 | 6.084 | 6.4 | 6.4 | 3B+1S | 0 | 1060 | 1138 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30822006 | 1348 | 221.5648 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 6425540 | 5548 | 133.152 | 5.548 | 6 | 6 | 3B+1S | 0 | 1019 | 1128 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30823246 | 1240 | 223.504 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 137 | 6431242 | 5702 | 136.848 | 5.702 | 5.8 | 5.8 | 3B+1S | 0 | 1021 | 1107 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30824522 | 1276 | 223.7811 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 135 | 6436659 | 5417 | 130.008 | 5.417 | 5.7 | 5.7 | 3B+1S | 0 | 999 | 1129 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30825744 | 1222 | 225.5861 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 6442075 | 5416 | 129.984 | 5.416 | 5.5 | 5.5 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30826976 | 1232 | 227.4742 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 6447416 | 5341 | 128.184 | 5.341 | 5.4 | 5.4 | 3B+1S | 0 | 999 | 1160 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30828242 | 1266 | 237.0343 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 130 | 6452732 | 5316 | 127.584 | 5.316 | 5.2 | 5.2 | 3B+1S | 0 | 980 | 1110 | 1185 | 1129 | N/A | N/A | N/A | N/A | 30829410 | 1168 | 219.7141 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 6457952 | 5220 | 125.28 | 5.22 | 5.1 | 5.1 | 3B+1S | 0 | 980 | 1115 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30830586 | 1176 | 225.2874 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 130 | 6463240 | 5288 | 126.912 | 5.288 | 5 | 5 | 3B+1S | 0 | 980 | 1093 | 1185 | 1129 | N/A | N/A | N/A | N/A | 30831744 | 1158 | 218.9864 | 0% | 100% | 100% | 100% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 6468437 | 5197 | 124.728 | 5.197 | 4.5 | 4.5 | 2B+1S | 0 | 1022 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30832786 | 1042 | 200.5003 | 0% | 100% | 100% | 0% | 100% | 0% | 6781183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 114 | 6473307 | 4870 | 116.88 | 4.87 | 4.1 | 4.1 | 2B+1S | 0 | 972 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30833772 | 986 | 202.4641 | 0% | 100% | 100% | 0% | 100% | 0% | 6781183 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 101 | 6477747 | 4440 | 106.56 | 4.44 | 4.6 | 4.6 | 2B | 0 | 0 | 1060 | 0 | 1089 | N/A | N/A | N/A | N/A | 30834536 | 764 | 172.0721 | 0% | 0% | 100% | 0% | 100% | 25% | 6781636 | 453 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 96 | 6481561 | 3814 | 91.536 | 3.814 | 5.1 | 5.1 | 2B | 0 | 0 | 1043 | 0 | 1048 | N/A | N/A | N/A | N/A | 30835152 | 616 | 161.5102 | 0% | 0% | 100% | 0% | 100% | 25% | 6782159 | 523 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5 | 120562 | 120562 | 120.562 | 120.562 | [12 empty] | 24598 | 24598 | 204.0278 | [6 empty] | 5263 | 5263 | 0.97833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:01 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 12) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 12) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24458 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6481561 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30835152 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6782159 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 90 | 6485315 | 3754 | 90.096 | 3.754 | 6.1 | 6.1 | 2B | 0 | 0 | 1053 | 0 | 1064 | N/A | N/A | N/A | N/A | 30835750 | 598 | 159.2968 | 0% | 0% | 100% | 0% | 100% | 35% | 6783159 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 111 | 88 | 6488983 | 3668 | 88.032 | 3.668 | 7.2 | 7.2 | 2B | 0 | 0 | 1053 | 0 | 1064 | N/A | N/A | N/A | N/A | 30836331 | 581 | 158.3969 | 0% | 0% | 100% | 0% | 100% | 35% | 6784171 | 1012 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 87 | 6492572 | 3589 | 86.136 | 3.589 | 8.3 | 8.3 | 2B | 0 | 0 | 977 | 0 | 1009 | N/A | N/A | N/A | N/A | 30836906 | 575 | 160.2118 | 0% | 0% | 100% | 0% | 100% | 35% | 6785282 | 1111 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 89 | 6496195 | 3623 | 86.952 | 3.623 | 9.4 | 9.4 | 2B | 0 | 0 | 977 | 0 | 1009 | N/A | N/A | N/A | N/A | 30837466 | 560 | 154.568 | 0% | 0% | 100% | 0% | 100% | 35% | 6786156 | 874 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 92 | 6500126 | 3931 | 94.344 | 3.931 | 9.5 | 9.5 | 2B | 0 | 0 | 968 | 0 | 970 | N/A | N/A | N/A | N/A | 30837980 | 514 | 130.7555 | 0% | 0% | 100% | 0% | 100% | 0% | 6786333 | 177 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 113 | 111 | 6504418 | 4292 | 103.008 | 4.292 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1001 | N/A | N/A | N/A | N/A | 30838562 | 582 | 135.6011 | 0% | 0% | 100% | 0% | 100% | 0% | 6786333 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 148 | 144 | 6510223 | 5805 | 139.32 | 5.805 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30839792 | 1230 | 211.8863 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 6515885 | 5662 | 135.888 | 5.662 | 9.2 | 9.2 | 3B+1S | 0 | 1010 | 1197 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30841046 | 1254 | 221.4765 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 6521990 | 6105 | 146.52 | 6.105 | 8.7 | 8.7 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30842414 | 1368 | 224.0786 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 149 | 6528210 | 6220 | 149.28 | 6.22 | 8 | 8 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30843814 | 1400 | 225.0804 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 133 | 147 | 6534456 | 6246 | 149.904 | 6.246 | 7.1 | 7.1 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1160 | N/A | N/A | N/A | N/A | 30845212 | 1398 | 223.8232 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 145 | 6540516 | 6060 | 145.44 | 6.06 | 6.5 | 6.5 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1180 | N/A | N/A | N/A | N/A | 30846574 | 1362 | 224.7525 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 6546470 | 5954 | 142.896 | 5.954 | 5.8 | 5.8 | 3B+1S | 0 | 1071 | 1161 | 1185 | 1180 | N/A | N/A | N/A | N/A | 30847914 | 1340 | 225.0588 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 6552291 | 5821 | 139.704 | 5.821 | 5.3 | 5.3 | 3B+1S | 0 | 1051 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 30849226 | 1312 | 225.3908 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 124 | 133 | 6557892 | 5601 | 134.424 | 5.601 | 4.9 | 4.9 | 3B+1S | 0 | 999 | 1189 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30850533 | 1307 | 233.3512 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 129 | 6563484 | 5592 | 134.208 | 5.592 | 4.8 | 4.8 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30851826 | 1293 | 231.2232 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 6569075 | 5591 | 134.184 | 5.591 | 4.7 | 4.7 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30853122 | 1296 | 231.8011 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 121 | 125 | 6574463 | 5388 | 129.312 | 5.388 | 4.4 | 4.4 | 3B+1S | 0 | 1010 | 1121 | 1185 | 1129 | N/A | N/A | N/A | N/A | 30854311 | 1189 | 220.6756 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 126 | 6579830 | 5367 | 128.808 | 5.367 | 4.1 | 4.1 | 3B+1S | 0 | 1010 | 1081 | 1185 | 1099 | N/A | N/A | N/A | N/A | 30855490 | 1179 | 219.6758 | 0% | 100% | 100% | 100% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 121 | 6584914 | 5084 | 122.016 | 5.084 | 3.7 | 3.7 | 2B+1S | 0 | 1010 | 1190 | 0 | 1191 | N/A | N/A | N/A | N/A | 30856514 | 1024 | 201.4162 | 0% | 100% | 100% | 0% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 122 | 6589822 | 4908 | 117.792 | 4.908 | 3.4 | 3.4 | 2B+1S | 0 | 1010 | 1154 | 0 | 1160 | N/A | N/A | N/A | N/A | 30857460 | 946 | 192.7465 | 0% | 100% | 100% | 0% | 100% | 0% | 6786333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 112 | 6594564 | 4742 | 113.808 | 4.742 | 3.1 | 3.1 | 2B+1S | 0 | 1010 | 1083 | 0 | 1110 | N/A | N/A | N/A | N/A | 30858318 | 858 | 180.9363 | 0% | 100% | 100% | 0% | 100% | 0% | 6786333 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 97 | 6598622 | 4058 | 97.392 | 4.058 | 3.7 | 3.7 | 2B | 0 | 0 | 1063 | 0 | 1068 | N/A | N/A | N/A | N/A | 30858982 | 664 | 163.6274 | 0% | 0% | 100% | 0% | 100% | 25% | 6786954 | 621 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 93 | 6602541 | 3919 | 94.056 | 3.919 | 4.6 | 4.6 | 2B | 0 | 0 | 1058 | 0 | 1068 | N/A | N/A | N/A | N/A | 30859610 | 628 | 160.245 | 0% | 0% | 100% | 0% | 100% | 25% | 6787653 | 699 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.0833 | 120980 | 120980 | 120.98 | 120.98 | [12 empty] | 24458 | 24458 | 202.1656 | [6 empty] | 5494 | 5494 | 0.955 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:08 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 13) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 13) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22424 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6602541 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30859610 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6787653 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 109 | 81 | 6606150 | 3609 | 86.616 | 3.609 | 5.6 | 5.6 | 2B | 0 | 0 | 1008 | 0 | 998 | N/A | N/A | N/A | N/A | 30860172 | 562 | 155.7218 | 0% | 0% | 100% | 0% | 100% | 35% | 6788479 | 826 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 90 | 6609661 | 3511 | 84.264 | 3.511 | 6.8 | 6.8 | 2B | 0 | 0 | 1009 | 0 | 999 | N/A | N/A | N/A | N/A | 30860723 | 551 | 156.9353 | 0% | 0% | 100% | 0% | 100% | 35% | 6789536 | 1057 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 107 | 82 | 6613109 | 3448 | 82.752 | 3.448 | 7.9 | 7.9 | 2B | 0 | 0 | 1008 | 0 | 968 | N/A | N/A | N/A | N/A | 30861259 | 536 | 155.4524 | 0% | 0% | 100% | 0% | 100% | 35% | 6790644 | 1108 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 78 | 6616574 | 3465 | 83.16 | 3.465 | 9.1 | 9.1 | 2B | 0 | 0 | 1003 | 0 | 935 | N/A | N/A | N/A | N/A | 30861806 | 547 | 157.8644 | 0% | 0% | 100% | 0% | 100% | 35% | 6792057 | 1413 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 85 | 6619946 | 3372 | 80.928 | 3.372 | 9.5 | 9.5 | 2B | 0 | 0 | 888 | 0 | 908 | N/A | N/A | N/A | N/A | 30862335 | 529 | 156.8802 | 0% | 0% | 100% | 0% | 100% | 35% | 6792411 | 354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 29 | 20.4225 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 102 | 107 | 6624457 | 4511 | 108.264 | 4.511 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 968 | N/A | N/A | N/A | N/A | 30862996 | 661 | 146.5307 | 0% | 0% | 100% | 0% | 100% | 0% | 6792411 | 0 | 1.04 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 27 | 19.0141 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 129 | 6628969 | 4512 | 108.288 | 4.512 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1050 | N/A | N/A | N/A | N/A | 30863658 | 662 | 146.7199 | 0% | 0% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 6634405 | 5436 | 130.464 | 5.436 | 9.5 | 9.5 | 3B | 0 | 0 | 1152 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30864732 | 1074 | 197.5717 | 0% | 0% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 148 | 6640407 | 6002 | 144.048 | 6.002 | 9.3 | 9.3 | 3B+1S | 0 | 1093 | 1104 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30866018 | 1286 | 214.2619 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 6646640 | 6233 | 149.592 | 6.233 | 8.5 | 8.5 | 3B+1S | 0 | 1076 | 1164 | 1185 | 1197 | N/A | N/A | N/A | N/A | 30867386 | 1368 | 219.477 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 138 | 147 | 6652808 | 6168 | 148.032 | 6.168 | 7.9 | 7.9 | 3B+1S | 0 | 1050 | 1165 | 1185 | 1197 | N/A | N/A | N/A | N/A | 30868734 | 1348 | 218.5473 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 6658772 | 5964 | 143.136 | 5.964 | 7.5 | 7.5 | 3B+1S | 0 | 1021 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30870042 | 1308 | 219.3159 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 135 | 6664623 | 5851 | 140.424 | 5.851 | 6.9 | 6.9 | 3B+1S | 0 | 1051 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 30871312 | 1270 | 217.0569 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 133 | 6670244 | 5621 | 134.904 | 5.621 | 6.5 | 6.5 | 3B+1S | 0 | 1013 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 30872544 | 1232 | 219.1781 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 129 | 6675763 | 5519 | 132.456 | 5.519 | 6.3 | 6.3 | 3B+1S | 0 | 1013 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 30873749 | 1205 | 218.3367 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 6681145 | 5382 | 129.168 | 5.382 | 6.1 | 6.1 | 3B+1S | 0 | 1008 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 30874936 | 1187 | 220.55 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 128 | 6686613 | 5468 | 131.232 | 5.468 | 5.7 | 5.7 | 3B+1S | 0 | 998 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 30876112 | 1176 | 215.0695 | 0% | 100% | 100% | 100% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 119 | 126 | 6691845 | 5232 | 125.568 | 5.232 | 5.3 | 5.3 | 2B+1S | 0 | 1060 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 30877164 | 1052 | 201.0703 | 0% | 100% | 100% | 0% | 100% | 0% | 6792411 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 117 | 121 | 6697002 | 5157 | 123.768 | 5.157 | 4.8 | 4.8 | 2B+1S | 0 | 1023 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 30878174 | 1010 | 195.8503 | 0% | 100% | 100% | 0% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 119 | 6702039 | 5037 | 120.888 | 5.037 | 4.4 | 4.4 | 2B+1S | 0 | 1027 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 30879154 | 980 | 194.5603 | 0% | 100% | 100% | 0% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 113 | 6707020 | 4981 | 119.544 | 4.981 | 3.9 | 3.9 | 2B+1S | 0 | 989 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 30880105 | 951 | 190.9255 | 0% | 100% | 100% | 0% | 100% | 0% | 6792411 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 100 | 98 | 6711254 | 4234 | 101.616 | 4.234 | 3.8 | 3.8 | 2B+1S | 0 | 999 | 1064 | 0 | 1068 | N/A | N/A | N/A | N/A | 30880862 | 757 | 178.7907 | 0% | 100% | 100% | 0% | 100% | 0% | 6792411 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 89 | 6715196 | 3942 | 94.608 | 3.942 | 4.5 | 4.5 | 2B | 0 | 0 | 991 | 0 | 1053 | N/A | N/A | N/A | N/A | 30881448 | 586 | 148.6555 | 0% | 0% | 100% | 0% | 100% | 25% | 6793069 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 85 | 6718939 | 3743 | 89.832 | 3.743 | 5.2 | 5.2 | 2B | 0 | 0 | 946 | 0 | 1008 | N/A | N/A | N/A | N/A | 30882034 | 586 | 156.5589 | 0% | 0% | 100% | 0% | 100% | 25% | 6793770 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 116 | 116398 | 116398 | 116.398 | 116.398 | [12 empty] | 22424 | 22424 | 192.6494 | [6 empty] | 6117 | 6117 | 0.94667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:19 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 14) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23874 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6718939 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30882034 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6793770 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 83 | 81 | 6722494 | 3555 | 85.32 | 3.555 | 6.7 | 6.7 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 30882589 | 555 | 156.1181 | 0% | 0% | 100% | 0% | 100% | 35% | 6794769 | 999 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 82 | 80 | 6726141 | 3647 | 87.528 | 3.647 | 7.7 | 7.7 | 2B | 0 | 0 | 903 | 0 | 1009 | N/A | N/A | N/A | N/A | 30883129 | 540 | 148.0669 | 0% | 0% | 100% | 0% | 100% | 35% | 6795779 | 1010 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 80 | 79 | 6729729 | 3588 | 86.112 | 3.588 | 8.7 | 8.7 | 2B | 0 | 0 | 903 | 0 | 1009 | N/A | N/A | N/A | N/A | 30883616 | 487 | 135.7302 | 0% | 0% | 100% | 0% | 100% | 35% | 6796877 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 82 | 6733201 | 3472 | 83.328 | 3.472 | 9.5 | 9.5 | 2B | 0 | 0 | 888 | 0 | 907 | N/A | N/A | N/A | N/A | 30884048 | 432 | 124.424 | 0% | 0% | 100% | 0% | 100% | 35% | 6797878 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 91 | 6736533 | 3332 | 79.968 | 3.332 | 9.5 | 9.5 | 2B | 0 | 0 | 913 | 0 | 909 | N/A | N/A | N/A | N/A | 30884442 | 394 | 118.2473 | 0% | 0% | 100% | 0% | 100% | 35% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 107 | 110 | 6740722 | 4189 | 100.536 | 4.189 | 9.5 | 9.5 | 2B | 0 | 0 | 1084 | 0 | 1008 | N/A | N/A | N/A | N/A | 30884976 | 534 | 127.4767 | 0% | 0% | 100% | 0% | 100% | 0% | 6797878 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 131 | 6746176 | 5454 | 130.896 | 5.454 | 9.5 | 9.5 | 3B | 0 | 0 | 1089 | 1185 | 1170 | N/A | N/A | N/A | N/A | 30886078 | 1102 | 202.0535 | 0% | 0% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 142 | 6751869 | 5693 | 136.632 | 5.693 | 9.5 | 9.5 | 3B | 0 | 0 | 1189 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30887262 | 1184 | 207.9747 | 0% | 0% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 142 | 6758023 | 6154 | 147.696 | 6.154 | 9 | 9 | 3B+1S | 0 | 1067 | 1155 | 1185 | 1170 | N/A | N/A | N/A | N/A | 30888606 | 1344 | 218.3945 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 6763900 | 5877 | 141.048 | 5.877 | 8.3 | 8.3 | 3B+1S | 0 | 1084 | 1176 | 1185 | 1189 | N/A | N/A | N/A | N/A | 30889898 | 1292 | 219.8401 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 | 0.93 | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 135 | 147 | 6769969 | 6069 | 145.656 | 6.069 | 7.6 | 7.6 | 3B+1S | 0 | 1056 | 1176 | 1185 | 1189 | N/A | N/A | N/A | N/A | 30891243 | 1345 | 221.6181 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 6776038 | 6069 | 145.656 | 6.069 | 7.3 | 7.3 | 3B+1S | 0 | 1107 | 1181 | 1185 | 1181 | N/A | N/A | N/A | N/A | 30892588 | 1345 | 221.6181 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 6781832 | 5794 | 139.056 | 5.794 | 7 | 7 | 3B+1S | 0 | 1009 | 1154 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30893892 | 1304 | 225.0604 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 6787507 | 5675 | 136.2 | 5.675 | 6.7 | 6.7 | 3B+1S | 0 | 990 | 1155 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30895144 | 1252 | 220.6167 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 132 | 6793057 | 5550 | 133.2 | 5.55 | 6.6 | 6.6 | 3B+1S | 0 | 988 | 1155 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30896392 | 1248 | 224.8649 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 6798418 | 5361 | 128.664 | 5.361 | 6.5 | 6.5 | 3B+1S | 0 | 985 | 1155 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30897606 | 1214 | 226.4503 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 6803820 | 5402 | 129.648 | 5.402 | 6.2 | 6.2 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30898866 | 1260 | 233.2469 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 138 | 6809315 | 5495 | 131.88 | 5.495 | 6 | 6 | 3B+1S | 0 | 980 | 1145 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30900088 | 1222 | 222.384 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 6814761 | 5446 | 130.704 | 5.446 | 5.9 | 5.9 | 3B+1S | 0 | 980 | 1145 | 1185 | 1159 | N/A | N/A | N/A | N/A | 30901306 | 1218 | 223.6504 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 6820167 | 5406 | 129.744 | 5.406 | 5.8 | 5.8 | 3B+1S | 0 | 958 | 1125 | 1185 | 1149 | N/A | N/A | N/A | N/A | 30902506 | 1200 | 221.9756 | 0% | 100% | 100% | 100% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 123 | 6825388 | 5221 | 125.304 | 5.221 | 5.3 | 5.3 | 2B+1S | 0 | 1015 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30903554 | 1048 | 200.7278 | 0% | 100% | 100% | 0% | 100% | 0% | 6797878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 121 | 6830365 | 4977 | 119.448 | 4.977 | 5 | 5 | 2B+1S | 0 | 1017 | 1125 | 0 | 1150 | N/A | N/A | N/A | N/A | 30904526 | 972 | 195.2984 | 0% | 100% | 100% | 0% | 100% | 0% | 6797878 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 96 | 6834731 | 4366 | 104.784 | 4.366 | 5.3 | 5.3 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 30905286 | 760 | 174.0724 | 0% | 0% | 100% | 0% | 100% | 25% | 6798254 | 376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 106 | 89 | 6838558 | 3827 | 91.848 | 3.827 | 5.8 | 5.8 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 30905908 | 622 | 162.5294 | 0% | 0% | 100% | 0% | 100% | 25% | 6798825 | 571 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.4167 | 119619 | 119619 | 119.619 | 119.619 | [12 empty] | 23874 | 23874 | 199.5837 | [6 empty] | 5055 | 5055 | 0.93667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @3:53 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
CONDUCTED GENSET EXCERCISES TO G1 AND G2 FOR 10 MINUTES EACH, NORMAL CONDITION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 15) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24822 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6838558 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30905908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6798825 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 89 | 6842261 | 3703 | 88.872 | 3.703 | 6.8 | 6.8 | 2B | 0 | 0 | 1021 | 0 | 1008 | N/A | N/A | N/A | N/A | 30906488 | 580 | 156.6298 | 0% | 0% | 100% | 0% | 100% | 35% | 6799799 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 86 | 6845969 | 3708 | 88.992 | 3.708 | 7.7 | 7.7 | 2B | 0 | 0 | 1021 | 0 | 1008 | N/A | N/A | N/A | N/A | 30907009 | 521 | 140.507 | 0% | 0% | 100% | 0% | 100% | 35% | 6802353 | 2554 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 106 | 91 | 6849603 | 3634 | 87.216 | 3.634 | 8.6 | 8.6 | 2B | 0 | 0 | 956 | 0 | 983 | N/A | N/A | N/A | N/A | 30907512 | 503 | 138.415 | 0% | 0% | 100% | 0% | 100% | 35% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 108 | 94 | 6853294 | 3691 | 88.584 | 3.691 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 969 | N/A | N/A | N/A | N/A | 30908023 | 511 | 138.4449 | 0% | 0% | 100% | 0% | 100% | 35% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 99 | 6856846 | 3552 | 85.248 | 3.552 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 960 | N/A | N/A | N/A | N/A | 30908518 | 495 | 139.3581 | 0% | 0% | 100% | 0% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 118 | 6861271 | 4425 | 106.2 | 4.425 | 9.5 | 9.5 | 2B | 0 | 0 | 1165 | 0 | 1181 | N/A | N/A | N/A | N/A | 30909206 | 688 | 155.4802 | 0% | 0% | 100% | 0% | 100% | 0% | 6802353 | 0 | 0.92 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 6867199 | 5928 | 142.272 | 5.928 | 9.1 | 9.1 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30910534 | 1328 | 224.0216 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 6873248 | 6049 | 145.176 | 6.049 | 8.5 | 8.5 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30911875 | 1341 | 221.6895 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 151 | 6879443 | 6195 | 148.68 | 6.195 | 7.9 | 7.9 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30913244 | 1369 | 220.9847 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 6885606 | 6163 | 147.912 | 6.163 | 7.1 | 7.1 | 3B+1S | 0 | 1116 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30914661 | 1417 | 229.9205 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 139 | 147 | 6891734 | 6128 | 147.072 | 6.128 | 6.5 | 6.5 | 3B+1S | 0 | 1083 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30916053 | 1392 | 227.154 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 6897810 | 6076 | 145.824 | 6.076 | 6.1 | 6.1 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30917422 | 1369 | 225.3127 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 132 | 6903482 | 5672 | 136.128 | 5.672 | 5.9 | 5.9 | 3B+1S | 0 | 1009 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30918724 | 1302 | 229.5487 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 135 | 6909046 | 5564 | 133.536 | 5.564 | 5.8 | 5.8 | 3B+1S | 0 | 999 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30919992 | 1268 | 227.8936 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 133 | 6914465 | 5419 | 130.056 | 5.419 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30921214 | 1222 | 225.5029 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 6919870 | 5405 | 129.72 | 5.405 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30922442 | 1228 | 227.197 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 6925416 | 5546 | 133.104 | 5.546 | 5.5 | 5.5 | 3B+1S | 0 | 1022 | 119 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30923710 | 1268 | 228.6332 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 132 | 6930975 | 5559 | 133.416 | 5.559 | 5.4 | 5.4 | 3B+1S | 0 | 975 | 1145 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30924972 | 1262 | 227.0192 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 6936443 | 5468 | 131.232 | 5.468 | 5.2 | 5.2 | 3B+1S | 0 | 990 | 1145 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30926208 | 1236 | 226.0424 | 0% | 100% | 100% | 100% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 126 | 6941779 | 5336 | 128.064 | 5.336 | 4.6 | 4.6 | 2B+1S | 0 | 1073 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30927292 | 1084 | 203.1484 | 0% | 100% | 100% | 0% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 6947028 | 5249 | 125.976 | 5.249 | 3.8 | 3.8 | 2B+1S | 0 | 1038 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30928342 | 1050 | 200.0381 | 0% | 100% | 100% | 0% | 100% | 0% | 6802353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 117 | 6951992 | 4964 | 119.136 | 4.964 | 3.5 | 3.5 | 2B+1S | 0 | 989 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30929346 | 1004 | 202.2562 | 0% | 100% | 100% | 0% | 100% | 0% | 6802353 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 110 | 6956532 | 4540 | 108.96 | 4.54 | 3.9 | 3.9 | 2B | 0 | 0 | 1097 | 0 | 1100 | N/A | N/A | N/A | N/A | 30930142 | 796 | 175.3304 | 0% | 0% | 100% | 0% | 100% | 25% | 6802785 | 432 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 87 | 6960168 | 3636 | 87.264 | 3.636 | 4.7 | 4.7 | 2B | 0 | 0 | 1021 | 0 | 1008 | N/A | N/A | N/A | N/A | 30930730 | 588 | 161.7162 | 0% | 0% | 100% | 0% | 100% | 25% | 6803346 | 561 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0417 | 121610 | 121610 | 121.61 | 121.61 | [12 empty] | 24822 | 24822 | 204.1115 | [6 empty] | 4521 | 4521 | 0.975 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:14 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:05 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 16) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 16) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24638 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6960168 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30930730 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6803346 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 85 | 83 | 6963722 | 3554 | 85.296 | 3.554 | 6 | 6 | 2B | 0 | 0 | 1023 | 0 | 1028 | N/A | N/A | N/A | N/A | 30931295 | 565 | 158.9758 | 0% | 0% | 100% | 0% | 100% | 35% | 6804560 | 1214 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 81 | 6967134 | 3412 | 81.888 | 3.412 | 7.4 | 7.4 | 2B | 0 | 0 | 949 | 0 | 987 | N/A | N/A | N/A | N/A | 30931857 | 562 | 164.7128 | 0% | 0% | 100% | 0% | 100% | 35% | 6805888 | 1328 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 82 | 80 | 6970518 | 3384 | 81.216 | 3.384 | 8.9 | 8.9 | 2B | 0 | 0 | 949 | 0 | 987 | N/A | N/A | N/A | N/A | 30932404 | 547 | 161.643 | 0% | 0% | 100% | 0% | 100% | 35% | 6807375 | 1487 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 86 | 6974386 | 3868 | 92.832 | 3.868 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 0 | 908 | N/A | N/A | N/A | N/A | 30932856 | 452 | 116.8563 | 0% | 0% | 100% | 0% | 100% | 35% | 6808030 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 97 | 6977938 | 3552 | 85.248 | 3.552 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 978 | N/A | N/A | N/A | N/A | 30933298 | 442 | 124.4369 | 0% | 0% | 100% | 0% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 112 | 132 | 6983299 | 5361 | 128.664 | 5.361 | 9.5 | 9.5 | 2B | 0 | 0 | 1120 | 0 | 1198 | N/A | N/A | N/A | N/A | 30934339 | 1041 | 194.1802 | 0% | 0% | 100% | 0% | 100% | 0% | 6808030 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 6988661 | 5362 | 128.688 | 5.362 | 9 | 9 | 3B+1S | 0 | 1045 | 1165 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30935380 | 1041 | 194.144 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 6994741 | 6080 | 145.92 | 6.08 | 8.3 | 8.3 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30936728 | 1348 | 221.7105 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 7000926 | 6185 | 148.44 | 6.185 | 7.5 | 7.5 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30938118 | 1390 | 224.7373 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 7007116 | 6190 | 148.56 | 6.19 | 6.8 | 6.8 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30939522 | 1404 | 226.8174 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 143 | 147 | 7013189 | 6073 | 145.752 | 6.073 | 6.3 | 6.3 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30940882 | 1360 | 223.942 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 7019263 | 6074 | 145.776 | 6.074 | 6 | 6 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30942242 | 1360 | 223.9052 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 134 | 7024914 | 5651 | 135.624 | 5.651 | 5.9 | 5.9 | 3B+1S | 0 | 1018 | 1135 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30943530 | 1288 | 227.9243 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 7030490 | 5576 | 133.824 | 5.576 | 5.6 | 5.6 | 3B+1S | 0 | 990 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30944784 | 1254 | 224.8924 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 122 | 129 | 7035857 | 5367 | 128.808 | 5.367 | 5.5 | 5.5 | 3B+1S | 0 | 995 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30946014 | 1230 | 229.1783 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 131 | 7041106 | 5249 | 125.976 | 5.249 | 5.4 | 5.4 | 3B+1S | 0 | 1010 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30947210 | 1196 | 227.8529 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 7046621 | 5515 | 132.36 | 5.515 | 5.3 | 5.3 | 3B+1S | 0 | 1017 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 30948510 | 1300 | 235.7208 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 134 | 7052052 | 5431 | 130.344 | 5.431 | 5.2 | 5.2 | 3B+1S | 0 | 980 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30949732 | 1222 | 225.0046 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 132 | 7057523 | 5471 | 131.304 | 5.471 | 5.1 | 5.1 | 3B+1S | 0 | 990 | 1125 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30950954 | 1222 | 223.3595 | 0% | 100% | 100% | 100% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 125 | 7062812 | 5289 | 126.936 | 5.289 | 4..4 | 4..4 | 2B+1S | 0 | 1060 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30952018 | 1064 | 201.1722 | 0% | 100% | 100% | 0% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 7068040 | 5228 | 125.472 | 5.228 | 3.7 | 3.7 | 2B+1S | 0 | 1021 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30953070 | 1052 | 201.2242 | 0% | 100% | 100% | 0% | 100% | 0% | 6808030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 115 | 7072828 | 4788 | 114.912 | 4.788 | 3.6 | 3.6 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30954038 | 968 | 202.1721 | 0% | 100% | 100% | 0% | 100% | 0% | 6808030 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 95 | 7076938 | 4110 | 98.64 | 4.11 | 4.1 | 4.1 | 2B | 0 | 0 | 1080 | 0 | 1068 | N/A | N/A | N/A | N/A | 30954758 | 720 | 175.1825 | 0% | 0% | 100% | 0% | 100% | 25% | 6808461 | 431 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 106 | 88 | 7080683 | 3745 | 89.88 | 3.745 | 4.8 | 4.8 | 2B | 0 | 0 | 1023 | 0 | 1018 | N/A | N/A | N/A | N/A | 30955368 | 610 | 162.8838 | 0% | 0% | 100% | 0% | 100% | 25% | 6809072 | 611 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.8333 | 120515 | 120515 | 120.515 | 120.515 | [12 empty] | 24638 | 24638 | 204.4393 | [6 empty] | 5726 | 5726 | 0.90833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:40 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 17) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 17) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24262 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7080683 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30955368 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6809072 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 81 | 85 | 7084264 | 3581 | 85.944 | 3.581 | 5.8 | 5.8 | 2B | 0 | 0 | 1017 | 0 | 1028 | N/A | N/A | N/A | N/A | 30955948 | 580 | 161.9659 | 0% | 0% | 100% | 0% | 100% | 35% | 6810081 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 81 | 7087769 | 3505 | 84.12 | 3.505 | 7.1 | 7.1 | 2B | 0 | 0 | 991 | 0 | 1009 | N/A | N/A | N/A | N/A | 30956508 | 560 | 159.7718 | 0% | 0% | 100% | 0% | 100% | 35% | 6811196 | 1115 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 84 | 80 | 7091216 | 3447 | 82.728 | 3.447 | 8.6 | 8.6 | 2B | 0 | 0 | 963 | 0 | 968 | N/A | N/A | N/A | N/A | 30957056 | 548 | 158.9788 | 0% | 0% | 100% | 0% | 100% | 35% | 6812485 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 78 | 7094607 | 3391 | 81.384 | 3.391 | 9.5 | 9.5 | 2B | 0 | 0 | 928 | 0 | 927 | N/A | N/A | N/A | N/A | 30957482 | 426 | 125.6267 | 0% | 0% | 100% | 0% | 100% | 35% | 6813618 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 99 | 7098414 | 3807 | 91.368 | 3.807 | 9.5 | 9.5 | 2B | 0 | 0 | 985 | 0 | 987 | N/A | N/A | N/A | N/A | 30957982 | 500 | 131.337 | 0% | 0% | 100% | 0% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 117 | 7103125 | 4711 | 113.064 | 4.711 | 9.5 | 9.5 | 2B | 0 | 0 | 1143 | 0 | 1160 | N/A | N/A | N/A | N/A | 30958726 | 744 | 157.9283 | 0% | 0% | 100% | 0% | 100% | 0% | 6813618 | 0 | 0.88 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 7108938 | 5813 | 139.512 | 5.813 | 9.2 | 9.2 | 3B+1S | 0 | 986 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30960028 | 1302 | 223.9807 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 138 | 7114837 | 5899 | 141.576 | 5.899 | 8.9 | 8.9 | 3B+1S | 0 | 1006 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30961368 | 1340 | 227.1571 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 141 | 7120859 | 6022 | 144.528 | 6.022 | 8.7 | 8.7 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30962728 | 1360 | 225.8386 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 7126896 | 6037 | 144.888 | 6.037 | 8.1 | 8.1 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30964078 | 1350 | 223.621 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 141 | 148 | 7133060 | 6164 | 147.936 | 6.164 | 7.7 | 7.7 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30965466 | 1388 | 225.1785 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 7138800 | 5740 | 137.76 | 5.74 | 7.5 | 7.5 | 3B+1S | 0 | 983 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30966754 | 1288 | 224.3902 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 133 | 7144404 | 5604 | 134.496 | 5.604 | 7.4 | 7.4 | 3B+1S | 0 | 980 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 30968002 | 1248 | 222.6981 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 132 | 7150050 | 5646 | 135.504 | 5.646 | 7.3 | 7.3 | 3B+1S | 0 | 999 | 1155 | 1185 | 1148 | N/A | N/A | N/A | N/A | 30969250 | 1248 | 221.0414 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 133 | 7155424 | 5374 | 128.976 | 5.374 | 7.2 | 7.2 | 3B+1S | 0 | 975 | 1155 | 1185 | 1148 | N/A | N/A | N/A | N/A | 30970462 | 1212 | 225.5303 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 131 | 7160665 | 5241 | 125.784 | 5.241 | 7.1 | 7.1 | 3B+1S | 0 | 1007 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 30971644 | 1182 | 225.5295 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 131 | 7166159 | 5494 | 131.856 | 5.494 | 6.8 | 6.8 | 3B+1S | 0 | 1025 | 1164 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30972896 | 1252 | 227.885 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 7171583 | 5424 | 130.176 | 5.424 | 6.7 | 6.7 | 3B+1S | 0 | 979 | 1145 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30974124 | 1228 | 226.4012 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 7177006 | 5423 | 130.152 | 5.423 | 6.5 | 6.5 | 3B+1S | 0 | 980 | 1145 | 1185 | 1168 | N/A | N/A | N/A | N/A | 30975350 | 1226 | 226.0741 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 126 | 7182349 | 5343 | 128.232 | 5.343 | 5.8 | 5.8 | 2B+1S | 0 | 1029 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30976412 | 1062 | 198.7647 | 0% | 100% | 100% | 100% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 125 | 7187502 | 5153 | 123.672 | 5.153 | 5.4 | 5.4 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30977438 | 1026 | 199.1073 | 0% | 100% | 100% | 0% | 100% | 0% | 6813618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 115 | 7192250 | 4748 | 113.952 | 4.748 | 5.3 | 5.3 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 30978348 | 910 | 191.6596 | 0% | 100% | 100% | 0% | 100% | 0% | 6813618 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 99 | 7196368 | 4118 | 98.832 | 4.118 | 5.7 | 5.7 | 2B | 0 | 0 | 1046 | 0 | 1068 | N/A | N/A | N/A | N/A | 30979063 | 715 | 173.628 | 0% | 0% | 100% | 0% | 100% | 25% | 6814029 | 411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 89 | 7200128 | 3760 | 90.24 | 3.76 | 6.4 | 6.4 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 30979630 | 567 | 150.7979 | 0% | 0% | 100% | 0% | 100% | 25% | 6814569 | 540 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.6667 | 119445 | 119445 | 119.445 | 119.445 | [12 empty] | 24262 | 24262 | 203.1228 | [6 empty] | 5497 | 5497 | 0.94 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:51 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @9:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 18) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 20792 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7200128 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 30979630 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6814569 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 90 | 88 | 7203800 | 3672 | 88.128 | 3.672 | 7.7 | 7.7 | 2B | 0 | 0 | 1011 | 0 | 1008 | N/A | N/A | N/A | N/A | 30980150 | 520 | 141.6122 | 0% | 0% | 100% | 0% | 100% | 35% | 6815781 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 81 | 7207312 | 3512 | 84.288 | 3.512 | 9 | 9 | 2B | 0 | 0 | 919 | 0 | 1008 | N/A | N/A | N/A | N/A | 30980650 | 500 | 142.369 | 0% | 0% | 100% | 0% | 100% | 35% | 6817081 | 1300 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 85 | 84 | 7210900 | 3588 | 86.112 | 3.588 | 9.5 | 9.5 | 2B | 0 | 0 | 911 | 0 | 907 | N/A | N/A | N/A | N/A | 30981147 | 497 | 138.5173 | 0% | 0% | 100% | 0% | 100% | 35% | 6817624 | 543 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 85 | 7214578 | 3678 | 88.272 | 3.678 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 907 | N/A | N/A | N/A | N/A | 30981622 | 475 | 129.1463 | 0% | 0% | 100% | 0% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 94 | 7217987 | 3409 | 81.816 | 3.409 | 9.5 | 9.5 | 2B | 0 | 0 | 971 | 0 | 907 | N/A | N/A | N/A | N/A | 30982022 | 400 | 117.3365 | 0% | 0% | 100% | 0% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 109 | 7222304 | 4317 | 103.608 | 4.317 | 9.5 | 9.5 | 2B | 0 | 0 | 1028 | 0 | 1003 | N/A | N/A | N/A | N/A | 30982598 | 576 | 133.426 | 0% | 0% | 100% | 0% | 100% | 0% | 6817624 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 21 | 14.7887 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 154 | 7227742 | 5438 | 130.512 | 5.438 | 9.5 | 9.5 | 3B | 0 | 0 | 1024 | 1185 | 1109 | N/A | N/A | N/A | N/A | 30983686 | 1088 | 200.0736 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 131 | 7233180 | 5438 | 130.512 | 5.438 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1139 | N/A | N/A | N/A | N/A | 30984774 | 1088 | 200.0736 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 118 | 134 | 7238844 | 5664 | 135.936 | 5.664 | 8.9 | 8.9 | 2B+1S | 0 | 1156 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 30985886 | 1112 | 196.3277 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 141 | 7244643 | 5799 | 139.176 | 5.799 | 8.1 | 8.1 | 3B+1S | 0 | 1000 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30987062 | 1176 | 202.7936 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 | 1.01 | Normal operation schedule
58:00 | 11:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 120 | 136 | 7250432 | 5789 | 138.936 | 5.789 | 7.9 | 7.9 | 3B+1S | 0 | 994 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 30988310 | 1248 | 215.5813 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Normal operation schedule
59:00 | 12:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 115 | 136 | 7256221 | 5789 | 138.936 | 5.789 | 7.7 | 7.7 | 2B+1S | 0 | 1135 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 30989558 | 1248 | 215.5813 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 113 | 127 | 7261568 | 5347 | 128.328 | 5.347 | 6.8 | 6.8 | 2B+1S | 0 | 1066 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 30990615 | 1057 | 197.6809 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 114 | 125 | 7266915 | 5347 | 128.328 | 5.347 | 6.2 | 6.2 | 2B+1S | 0 | 1066 | 1165 | 0 | 1198 | N/A | N/A | N/A | N/A | 30991672 | 1057 | 197.6809 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 117 | 124 | 7272067 | 5152 | 123.648 | 5.152 | 5.7 | 5.7 | 2B+1S | 0 | 1033 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 30992662 | 990 | 192.1584 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 115 | 125 | 7277229 | 5162 | 123.888 | 5.162 | 5.4 | 5.4 | 2B+1S | 0 | 1025 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 30993662 | 1000 | 193.7234 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 22 | 15.493 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 111 | 126 | 7282392 | 5163 | 123.912 | 5.163 | 4.8 | 4.8 | 2B+1S | 0 | 1108 | 1166 | 0 | 1199 | N/A | N/A | N/A | N/A | 30994662 | 1000 | 193.6858 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 17 | 11.9718 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 116 | 128 | 7287347 | 4955 | 118.92 | 4.955 | 3.9 | 3.9 | 2B+1S | 0 | 1111 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 30995610 | 948 | 191.3219 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 15 | 10.5634 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 | 124 | 7292302 | 4955 | 118.92 | 4.955 | 3.2 | 3.2 | 2B+1S | 0 | 1087 | 1195 | 0 | 1190 | N/A | N/A | N/A | N/A | 30996558 | 948 | 191.3219 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 105 | 124 | 7297203 | 4901 | 117.624 | 4.901 | 2.5 | 2.5 | 2B+1S | 0 | 1109 | 1136 | 0 | 1140 | N/A | N/A | N/A | N/A | 30997504 | 946 | 193.0218 | 0% | 100% | 100% | 100% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 19 | 13.3803 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 114 | 7301955 | 4752 | 114.048 | 4.752 | 1.9 | 1.9 | 2B+1S | 0 | 1121 | 1105 | 0 | 1129 | N/A | N/A | N/A | N/A | 30998363 | 859 | 180.766 | 0% | 100% | 100% | 0% | 100% | 0% | 6817624 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 107 | 7306708 | 4753 | 114.072 | 4.753 | 1.8 | 1.8 | 2B+1S | 0 | 825 | 1100 | 0 | 1109 | N/A | N/A | N/A | N/A | 30999222 | 859 | 180.728 | 0% | 100% | 100% | 0% | 100% | 0% | 6817624 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 90 | 7310656 | 3948 | 94.752 | 3.948 | 3.1 | 3.1 | 2B | 0 | 0 | 1009 | 0 | 1068 | N/A | N/A | N/A | N/A | 30999858 | 636 | 161.0942 | 0% | 0% | 100% | 0% | 100% | 25% | 6818833 | 1209 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 85 | 7314218 | 3562 | 85.488 | 3.562 | 4.5 | 4.5 | 2B | 0 | 0 | 966 | 0 | 1037 | N/A | N/A | N/A | N/A | 31000422 | 564 | 158.338 | 0% | 0% | 100% | 0% | 100% | 25% | 6820185 | 1352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 115.5 | 114090 | 114090 | 114.09 | 114.09 | [12 empty] | 20792 | 20792 | 182.2421 | [6 empty] | 5616 | 5616 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:58 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:09 AM TO MEET 83 PSI TARGET PRESSURE
BP2 - STOPPED @ 8:09 AM
BP2 - RESTART @ 9:40 AM
BP2 - STOPPED @ 11:45 AM
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 19) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
POWER INTERRUPTION @ 5:19 PM / MERALCO POWER RESUMED @ 5:20 PM
RESUMED NORMAL OPERATION @ 5:28 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 20) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25644 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7314218 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31000422 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6820185 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 82 | 7317639 | 3421 | 82.104 | 3.421 | 6 | 6 | 2B | 0 | 0 | 939 | 0 | 1038 | N/A | N/A | N/A | N/A | 31000934 | 512 | 149.6638 | 0% | 0% | 100% | 0% | 100% | 35% | 6821535 | 1350 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 80 | 7321060 | 3421 | 82.104 | 3.421 | 7.4 | 7.4 | 2B | 0 | 0 | 916 | 0 | 1038 | N/A | N/A | N/A | N/A | 31001446 | 512 | 149.6638 | 0% | 0% | 100% | 0% | 100% | 35% | 6822886 | 1351 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 100 | 81 | 7324448 | 3388 | 81.312 | 3.388 | 9.5 | 9.5 | 2B | 0 | 0 | 894 | 0 | 1030 | N/A | N/A | N/A | N/A | 31001946 | 500 | 147.5797 | 0% | 0% | 100% | 0% | 100% | 35% | 6824947 | 2061 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 85 | 7327926 | 3478 | 83.472 | 3.478 | 9.5 | 9.5 | 2B | 0 | 0 | 887 | 0 | 1000 | N/A | N/A | N/A | N/A | 31002356 | 410 | 117.8838 | 0% | 0% | 100% | 0% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 34 | 23.9437 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 91 | 7331135 | 3209 | 77.016 | 3.209 | 9.5 | 9.5 | 2B | 0 | 0 | 820 | 0 | 1010 | N/A | N/A | N/A | N/A | 31002806 | 450 | 140.2306 | 0% | 0% | 100% | 0% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 104 | 7335292 | 4157 | 99.768 | 4.157 | 9.5 | 9.5 | 2B | 0 | 0 | 1000 | 0 | 1030 | N/A | N/A | N/A | N/A | 31003396 | 590 | 141.9293 | 0% | 0% | 100% | 0% | 100% | 0% | 6824947 | 0 | 0.86 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 138 | 7340856 | 5564 | 133.536 | 5.564 | 9.5 | 9.5 | 3B | 0 | 0 | 1128 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31004542 | 1146 | 205.9669 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 146 | 7346778 | 5922 | 142.128 | 5.922 | 9.4 | 9.4 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31005824 | 1282 | 216.4809 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 150 | 7352987 | 6209 | 149.016 | 6.209 | 8.8 | 8.8 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1189 | N/A | N/A | N/A | N/A | 31007204 | 1380 | 222.258 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 147 | 7359084 | 6097 | 146.328 | 6.097 | 7.9 | 7.9 | 3B+1S | 0 | 1185 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31008596 | 1392 | 228.309 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 130 | 130 | 7365408 | 6324 | 151.776 | 6.324 | 6.7 | 6.7 | 3B+1S | 0 | 1165 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31010046 | 1450 | 229.2853 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 150 | 7371780 | 6372 | 152.928 | 6.372 | 5.9 | 5.9 | 3B+1S | 0 | 1178 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31011502 | 1456 | 228.4997 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 149 | 7377779 | 5999 | 143.976 | 5.999 | 4.5 | 4.5 | 3B+1S | 0 | 1130 | 1170 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31012882 | 1380 | 230.0383 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 144 | 7383779 | 6000 | 144 | 6 | 4.2 | 4.2 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31014262 | 1380 | 230 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 138 | 7389752 | 5973 | 143.352 | 5.973 | 3.4 | 3.4 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31015622 | 1360 | 227.6913 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 7395408 | 5656 | 135.744 | 5.656 | 3 | 3 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31017022 | 1400 | 247.5248 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 7401104 | 5696 | 136.704 | 5.696 | 2.5 | 2.5 | 3B+1S | 0 | 1189 | 1194 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31018450 | 1428 | 250.7022 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 115 | 7406763 | 5659 | 135.816 | 5.659 | 2 | 2 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31019894 | 1444 | 255.1688 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 131 | 7412284 | 5521 | 132.504 | 5.521 | 1.9 | 1.9 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1191 | N/A | N/A | N/A | N/A | 31021326 | 1432 | 259.3733 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 114 | 7417524 | 5240 | 125.76 | 5.24 | 1.5 | 1.5 | 2B+1S | 0 | 1031 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 31022446 | 1120 | 213.7405 | 0% | 100% | 100% | 100% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 132 | 124 | 7422549 | 5025 | 120.6 | 5.025 | 1.5 | 1.5 | 3B | 0 | 0 | 1104 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31023512 | 1066 | 212.1393 | 0% | 100% | 100% | 0% | 100% | 0% | 6824947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 119 | 7427611 | 5062 | 121.488 | 5.062 | 1.7 | 1.7 | 3B | 0 | 0 | 1032 | 0 | 1087 | N/A | N/A | N/A | N/A | 31024582 | 1070 | 211.3789 | 0% | 100% | 100% | 0% | 100% | 0% | 6824947 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 103 | 7432056 | 4445 | 106.68 | 4.445 | 2.5 | 2.5 | 2B | 0 | 0 | 1121 | 0 | 1110 | N/A | N/A | N/A | N/A | 31025366 | 784 | 176.378 | 0% | 0% | 100% | 0% | 100% | 25% | 6825803 | 856 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 97 | 7436159 | 4103 | 98.472 | 4.103 | 3.6 | 3.6 | 2B | 0 | 0 | 1032 | 0 | 1109 | N/A | N/A | N/A | N/A | 31026066 | 700 | 170.6069 | 0% | 0% | 100% | 0% | 100% | 25% | 6826861 | 1058 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.5833 | 121941 | 121941 | 121.941 | 121.941 | [12 empty] | 25644 | 25644 | 210.2984 | [6 empty] | 6676 | 6676 | 0.88167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:15 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:42 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @7:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 20) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED @ 3:10 PM (12%) / CLOSED @ 9:26 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:29 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM
SP2 - STOPPED @ 8:11 PM DUE TO LOW WATER LEVEL
BP2 - RESTART @ 8:11 PM
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 21) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25344 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7436159 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31026066 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6826861 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 91 | 7439910 | 3751 | 90.024 | 3.751 | 4.5 | 4.5 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 31026693 | 627 | 167.1554 | 0% | 0% | 100% | 0% | 100% | 35% | 6827870 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 86 | 7443661 | 3751 | 90.024 | 3.751 | 5.9 | 5.9 | 2B | 0 | 0 | 968 | 0 | 1111 | N/A | N/A | N/A | N/A | 31027320 | 627 | 167.1554 | 0% | 0% | 100% | 0% | 100% | 35% | 6828879 | 1009 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 88 | 7447227 | 3566 | 85.584 | 3.566 | 6.5 | 6.5 | 2B | 0 | 0 | 988 | 0 | 1109 | N/A | N/A | N/A | N/A | 31027903 | 583 | 163.4885 | 0% | 0% | 100% | 0% | 100% | 35% | 6830225 | 1346 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 87 | 7450794 | 3567 | 85.608 | 3.567 | 8.7 | 8.7 | 2B | 0 | 0 | 923 | 0 | 1100 | N/A | N/A | N/A | N/A | 31028486 | 583 | 163.4427 | 0% | 0% | 100% | 0% | 100% | 35% | 6831571 | 1346 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 88 | 7454345 | 3551 | 85.224 | 3.551 | 9.5 | 9.5 | 2B | 0 | 0 | 898 | 0 | 1090 | N/A | N/A | N/A | N/A | 31029030 | 544 | 153.1963 | 0% | 0% | 100% | 0% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 102 | 7458482 | 4137 | 99.288 | 4.137 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1110 | N/A | N/A | N/A | N/A | 31029610 | 580 | 140.1982 | 0% | 0% | 100% | 0% | 100% | 0% | 6831571 | 0 | 1.07 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 7464071 | 5589 | 134.136 | 5.589 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31030778 | 1168 | 208.9819 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 7469937 | 5866 | 140.784 | 5.866 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31032022 | 1244 | 212.0696 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 149 | 7475874 | 5937 | 142.488 | 5.937 | 9 | 9 | 3B+1S | 0 | 1077 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31033346 | 1324 | 223.0083 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 147 | 7482109 | 6235 | 149.64 | 6.235 | 8.2 | 8.2 | 3B+1S | 0 | 1153 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31034752 | 1406 | 225.5012 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 133 | 148 | 7488338 | 6229 | 149.496 | 6.229 | 7.2 | 7.2 | 3B+1S | 0 | 1114 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31036174 | 1422 | 228.287 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 139 | 7494542 | 6204 | 148.896 | 6.204 | 6.3 | 6.3 | 3B+1S | 0 | 1153 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31037610 | 1436 | 231.4636 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 138 | 7500426 | 5884 | 141.216 | 5.884 | 5.8 | 5.8 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31038958 | 1348 | 229.0959 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 7506221 | 5795 | 139.08 | 5.795 | 5.4 | 5.4 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31040294 | 1336 | 230.5436 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 133 | 7511928 | 5707 | 136.968 | 5.707 | 5.2 | 5.2 | 3B+1S | 0 | 1017 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31041622 | 1328 | 232.6967 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 7517558 | 5630 | 135.12 | 5.63 | 5 | 5 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31042946 | 1324 | 235.1687 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 132 | 7523264 | 5706 | 136.944 | 5.706 | 4.4 | 4.4 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31044290 | 1344 | 235.5415 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 7528831 | 5567 | 133.608 | 5.567 | 4.3 | 4.3 | 3B+1S | 0 | 985 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31045594 | 1304 | 234.2375 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 7534315 | 5484 | 131.616 | 5.484 | 4.2 | 4.2 | 3B+1S | 0 | 970 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31046890 | 1296 | 236.3239 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 135 | 7539647 | 5332 | 127.968 | 5.332 | 4.1 | 4.1 | 3B+1S | 0 | 980 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31048070 | 1180 | 221.3053 | 0% | 100% | 100% | 100% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 123 | 7544840 | 5193 | 124.632 | 5.193 | 3.6 | 3.6 | 3B+1S | 0 | 1020 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31049102 | 1032 | 198.7291 | 0% | 100% | 100% | 0% | 100% | 0% | 6831571 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 115 | 7549807 | 4967 | 119.208 | 4.967 | 3.3 | 3.3 | 3B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31050100 | 998 | 200.9261 | 0% | 100% | 100% | 0% | 100% | 0% | 6831571 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 98 | 7553928 | 4121 | 98.904 | 4.121 | 3.8 | 3.8 | 2B | 0 | 0 | 1060 | 0 | 1109 | N/A | N/A | N/A | N/A | 31050818 | 718 | 174.2296 | 0% | 0% | 100% | 0% | 100% | 25% | 6832774 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 92 | 7557616 | 3688 | 88.512 | 3.688 | 4.4 | 4.4 | 2B | 0 | 0 | 1040 | 0 | 1017 | N/A | N/A | N/A | N/A | 31051410 | 592 | 160.5206 | 0% | 0% | 100% | 0% | 100% | 25% | 6833352 | 578 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.8333 | 121457 | 121457 | 121.457 | 121.457 | [12 empty] | 25344 | 25344 | 208.6664 | [6 empty] | 6491 | 6491 | 0.99167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:20 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @6:20 AM, NORMAL OPERATION
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 21) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24764 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7557616 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31051410 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6833352 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 98 | 96 | 7561470 | 3854 | 92.496 | 3.854 | 5.5 | 5.5 | 2B | 0 | 0 | 1053 | 0 | 1037 | N/A | N/A | N/A | N/A | 31052002 | 592 | 153.6066 | 0% | 0% | 100% | 0% | 100% | 35% | 6834373 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 93 | 90 | 7565357 | 3887 | 93.288 | 3.887 | 6.8 | 6.8 | 2B | 0 | 0 | 1053 | 0 | 1037 | N/A | N/A | N/A | N/A | 31052587 | 585 | 150.5017 | 0% | 0% | 100% | 0% | 100% | 35% | 6835562 | 1189 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 86 | 85 | 7568865 | 3508 | 84.192 | 3.508 | 8.2 | 8.2 | 2B | 0 | 0 | 1053 | 0 | 1037 | N/A | N/A | N/A | N/A | 31053165 | 578 | 164.7662 | 0% | 0% | 100% | 0% | 100% | 35% | 6836851 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 89 | 7572557 | 3692 | 88.608 | 3.692 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 948 | N/A | N/A | N/A | N/A | 31053738 | 573 | 155.2004 | 0% | 0% | 100% | 0% | 100% | 35% | 6838197 | 1346 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 98 | 7575614 | 3057 | 73.368 | 3.057 | 9.5 | 9.5 | 2B | 0 | 0 | 968 | 0 | 1008 | N/A | N/A | N/A | N/A | 31054124 | 386 | 126.2676 | 0% | 0% | 100% | 0% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 122 | 7580339 | 4725 | 113.4 | 4.725 | 9.5 | 9.5 | 2B | 0 | 0 | 1115 | 0 | 1199 | N/A | N/A | N/A | N/A | 31054870 | 746 | 157.8836 | 0% | 0% | 100% | 0% | 100% | 0% | 6838197 | 0 | 0.88 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 135 | 7586250 | 5911 | 141.864 | 5.911 | 9.2 | 9.2 | 3B+1S | 0 | 998 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31056182 | 1312 | 221.9591 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 7592293 | 6043 | 145.032 | 6.043 | 8.9 | 8.9 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31057568 | 1386 | 229.3563 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 7598164 | 5871 | 140.904 | 5.871 | 8.4 | 8.4 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31058896 | 1328 | 226.1966 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 7604214 | 6050 | 145.2 | 6.05 | 7.8 | 7.8 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31060252 | 1356 | 224.1322 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 134 | 146 | 7610299 | 6085 | 146.04 | 6.085 | 7.2 | 7.2 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31061622 | 1370 | 225.1438 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 7616360 | 6061 | 145.464 | 6.061 | 6.7 | 6.7 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31062988 | 1366 | 225.3754 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 136 | 7622059 | 5699 | 136.776 | 5.699 | 6.6 | 6.6 | 3B+1S | 0 | 980 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31064286 | 1298 | 227.7593 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 7627726 | 5667 | 136.008 | 5.667 | 6.5 | 6.5 | 3B+1S | 0 | 985 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 31065578 | 1292 | 227.9866 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 133 | 7633188 | 5462 | 131.088 | 5.462 | 6.4 | 6.4 | 3B+1S | 0 | 995 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31066790 | 1212 | 221.8967 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 132 | 7638370 | 5182 | 124.368 | 5.182 | 6.3 | 6.3 | 3B+1S | 0 | 991 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31067986 | 1196 | 230.7989 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 7643830 | 5460 | 131.04 | 5.46 | 6.1 | 6.1 | 3B+1S | 0 | 1023 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31069262 | 1276 | 233.6996 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 135 | 7649314 | 5484 | 131.616 | 5.484 | 5.9 | 5.9 | 3B+1S | 0 | 1000 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31070508 | 1246 | 227.2064 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 7654795 | 5481 | 131.544 | 5.481 | 5.8 | 5.8 | 3B+1S | 0 | 970 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31071746 | 1238 | 225.8712 | 0% | 100% | 100% | 100% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 126 | 7660221 | 5426 | 130.224 | 5.426 | 5.2 | 5.2 | 2B+1S | 0 | 1072 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31072826 | 1080 | 199.0417 | 0% | 100% | 100% | 0% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 7665476 | 5255 | 126.12 | 5.255 | 4.5 | 4.5 | 2B+1S | 0 | 1002 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31073882 | 1056 | 200.9515 | 0% | 100% | 100% | 0% | 100% | 0% | 6838197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 127 | 7670466 | 4990 | 119.76 | 4.99 | 4.2 | 4.2 | 2B+1S | 0 | 982 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31074882 | 1000 | 200.4008 | 0% | 100% | 100% | 0% | 100% | 0% | 6838197 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 108 | 96 | 7674463 | 3997 | 95.928 | 3.997 | 4.7 | 4.7 | 2B | 0 | 0 | 1033 | 0 | 1110 | N/A | N/A | N/A | N/A | 31075570 | 688 | 172.1291 | 0% | 0% | 100% | 0% | 100% | 25% | 6838678 | 481 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 85 | 7678073 | 3610 | 86.64 | 3.61 | 5.3 | 5.3 | 2B | 0 | 0 | 925 | 0 | 1110 | N/A | N/A | N/A | N/A | 31076174 | 604 | 167.313 | 0% | 0% | 100% | 0% | 100% | 25% | 6839292 | 614 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.7917 | 120457 | 120457 | 120.457 | 120.457 | [12 empty] | 24764 | 24764 | 205.5837 | [6 empty] | 5940 | 5940 | 0.93667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:01AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 23) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:10PM TO 4:20 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:21PM TO 4:31 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 23) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24818 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7678073 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31076174 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6839292 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 108 | 81 | 7681395 | 3322 | 79.728 | 3.322 | 6.4 | 6.4 | 2B | 0 | 0 | 925 | 0 | 1110 | N/A | N/A | N/A | N/A | 31076746 | 572 | 172.1854 | 0% | 0% | 100% | 0% | 100% | 35% | 6840365 | 1073 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 93 | 7684812 | 3417 | 82.008 | 3.417 | 7.4 | 7.4 | 2B | 0 | 0 | 993 | 0 | 1110 | N/A | N/A | N/A | N/A | 31077282 | 536 | 156.8627 | 0% | 0% | 100% | 0% | 100% | 35% | 6841522 | 1157 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 90 | 7688241 | 3429 | 82.296 | 3.429 | 8.7 | 8.7 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 31077812 | 530 | 154.564 | 0% | 0% | 100% | 0% | 100% | 35% | 6842644 | 1122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 89 | 7691758 | 3517 | 84.408 | 3.517 | 9.5 | 9.5 | 2B | 0 | 0 | 938 | 0 | 960 | N/A | N/A | N/A | N/A | 31078304 | 492 | 139.892 | 0% | 0% | 100% | 0% | 100% | 35% | 6843297 | 653 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 105 | 7695655 | 3897 | 93.528 | 3.897 | 9.5 | 9.5 | 2B | 0 | 0 | 972 | 0 | 1009 | N/A | N/A | N/A | N/A | 31078792 | 488 | 125.2245 | 0% | 0% | 100% | 0% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 116 | 7700168 | 4513 | 108.312 | 4.513 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1197 | N/A | N/A | N/A | N/A | 31079526 | 734 | 162.6413 | 0% | 0% | 100% | 0% | 100% | 0% | 6843297 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 147 | 7706339 | 6171 | 148.104 | 6.171 | 8.9 | 8.9 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31080912 | 1386 | 224.5989 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 147 | 7712408 | 6069 | 145.656 | 6.069 | 8.3 | 8.3 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31082282 | 1370 | 225.7374 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 126 | 148 | 7718654 | 6246 | 149.904 | 6.246 | 7.6 | 7.6 | 3B+1S | 0 | 1184 | 1164 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31083644 | 1362 | 218.0596 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 152 | 7724757 | 6103 | 146.472 | 6.103 | 6.4 | 6.4 | 3B+1S | 0 | 1173 | 1185 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31085070 | 1426 | 233.6556 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 137 | 146 | 7730895 | 6138 | 147.312 | 6.138 | 5.7 | 5.7 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31086462 | 1392 | 226.784 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 7736833 | 5938 | 142.512 | 5.938 | 5.3 | 5.3 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31087806 | 1344 | 226.3388 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 134 | 7742561 | 5728 | 137.472 | 5.728 | 4.9 | 4.9 | 3B+1S | 0 | 1032 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31089105 | 1299 | 226.7807 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 7748275 | 5714 | 137.136 | 5.714 | 4.8 | 4.8 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31090408 | 1303 | 228.0364 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 7753567 | 5292 | 127.008 | 5.292 | 4.7 | 4.7 | 3B+1S | 0 | 999 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31091598 | 1190 | 224.8677 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 7758998 | 5431 | 130.344 | 5.431 | 4.6 | 4.6 | 3B+1S | 0 | 999 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31092806 | 1208 | 222.4268 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 7764411 | 5413 | 129.912 | 5.413 | 4.5 | 4.5 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31094066 | 1260 | 232.773 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 7769835 | 5424 | 130.176 | 5.424 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31095306 | 1240 | 228.6136 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 133 | 7775184 | 5349 | 128.376 | 5.349 | 4.3 | 4.3 | 3B+1S | 0 | 985 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31096546 | 1240 | 231.819 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 130 | 7780346 | 5162 | 123.888 | 5.162 | 4.2 | 4.2 | 3B+1S | 0 | 975 | 1129 | 1185 | 1129 | N/A | N/A | N/A | N/A | 31097712 | 1166 | 225.8814 | 0% | 100% | 100% | 100% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 122 | 7785472 | 5126 | 123.024 | 5.126 | 3.8 | 3.8 | 2B+1S | 0 | 1010 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31098750 | 1038 | 202.4971 | 0% | 100% | 100% | 0% | 100% | 0% | 6843297 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 112 | 7790216 | 4744 | 113.856 | 4.744 | 3.7 | 3.7 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31099714 | 964 | 203.204 | 0% | 100% | 100% | 0% | 100% | 0% | 6843297 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 96 | 7794203 | 3987 | 95.688 | 3.987 | 4.3 | 4.3 | 2B | 0 | 0 | 1050 | 0 | 1088 | N/A | N/A | N/A | N/A | 31100454 | 740 | 185.6032 | 0% | 0% | 100% | 0% | 100% | 25% | 6843779 | 482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 88 | 7797890 | 3687 | 88.488 | 3.687 | 4.9 | 4.9 | 2B | 0 | 0 | 1033 | 0 | 1008 | N/A | N/A | N/A | N/A | 31100992 | 538 | 145.9181 | 0% | 0% | 100% | 0% | 100% | 25% | 6844380 | 601 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5833 | 119817 | 119817 | 119.817 | 119.817 | [12 empty] | 24818 | 24818 | 207.1325 | [6 empty] | 5088 | 5088 | 0.975 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35% VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:40 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:25 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 24) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 23) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24938 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7797890 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31100992 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6844380 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 99 | 82 | 7801591 | 3701 | 88.824 | 3.701 | 6 | 6 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31101570 | 578 | 156.174 | 0% | 0% | 100% | 0% | 100% | 35% | 6845454 | 1074 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 80 | 7805336 | 3745 | 89.88 | 3.745 | 7.2 | 7.2 | 2B | 0 | 0 | 953 | 0 | 1008 | N/A | N/A | N/A | N/A | 31102138 | 568 | 151.6689 | 0% | 0% | 100% | 0% | 100% | 35% | 6846556 | 1102 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 79 | 7809025 | 3689 | 88.536 | 3.689 | 8.7 | 8.7 | 2B | 0 | 0 | 953 | 0 | 1008 | N/A | N/A | N/A | N/A | 31102700 | 562 | 152.3448 | 0% | 0% | 100% | 0% | 100% | 35% | 6847907 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 78 | 7812294 | 3269 | 78.456 | 3.269 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 936 | N/A | N/A | N/A | N/A | 31103204 | 504 | 154.1756 | 0% | 0% | 100% | 0% | 100% | 35% | 6848795 | 888 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 100 | 7815921 | 3627 | 87.048 | 3.627 | 9.5 | 9.5 | 2B | 0 | 0 | 974 | 0 | 1008 | N/A | N/A | N/A | N/A | 31103666 | 462 | 127.378 | 0% | 0% | 100% | 0% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 119 | 7820600 | 4679 | 112.296 | 4.679 | 9.5 | 9.5 | 2B | 0 | 0 | 1184 | 0 | 1198 | N/A | N/A | N/A | N/A | 31104414 | 748 | 159.8632 | 0% | 0% | 100% | 0% | 100% | 0% | 6848795 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 7826730 | 6130 | 147.12 | 6.13 | 9 | 9 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31105790 | 1376 | 224.4698 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 7832979 | 6249 | 149.976 | 6.249 | 8.3 | 8.3 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31107186 | 1396 | 223.3957 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 150 | 7839100 | 6121 | 146.904 | 6.121 | 7.6 | 7.6 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31108558 | 1372 | 224.1464 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 7845289 | 6189 | 148.536 | 6.189 | 6.9 | 6.9 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31109959 | 1401 | 226.3694 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 | 0.93 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 131 | 140 | 7851479 | 6190 | 148.56 | 6.19 | 6.2 | 6.2 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31111360 | 1401 | 226.3328 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 7857444 | 5965 | 143.16 | 5.965 | 5.5 | 5.5 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31112734 | 1374 | 230.3437 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 7863109 | 5665 | 135.96 | 5.665 | 5.3 | 5.3 | 3B+1S | 0 | 1024 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31114022 | 1288 | 227.361 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 7868807 | 5698 | 136.752 | 5.698 | 5.1 | 5.1 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31115310 | 1288 | 226.0442 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 135 | 7874268 | 5461 | 131.064 | 5.461 | 5 | 5 | 3B+1S | 0 | 1003 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31116546 | 1236 | 226.3322 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 7879614 | 5346 | 128.304 | 5.346 | 4.9 | 4.9 | 3B+1S | 0 | 988 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31117786 | 1240 | 231.9491 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 7885080 | 5466 | 131.184 | 5.466 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31119082 | 1296 | 237.1021 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 7890475 | 5395 | 129.48 | 5.395 | 4.7 | 4.7 | 3B+1S | 0 | 1002 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31120304 | 1222 | 226.506 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 132 | 7895764 | 5289 | 126.936 | 5.289 | 4.6 | 4.6 | 3B+1S | 0 | 988 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31121482 | 1178 | 222.7264 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 130 | 7900919 | 5155 | 123.72 | 5.155 | 4.5 | 4.5 | 3B+1S | 0 | 925 | 1105 | 1185 | 1110 | N/A | N/A | N/A | N/A | 31122606 | 1124 | 218.0407 | 0% | 100% | 100% | 100% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 7906160 | 5241 | 125.784 | 5.241 | 4.1 | 4.1 | 2B+1S | 0 | 1020 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31123654 | 1048 | 199.9618 | 0% | 100% | 100% | 0% | 100% | 0% | 6848795 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 116 | 7910994 | 4834 | 116.016 | 4.834 | 3.9 | 3.9 | 2B+1S | 0 | 985 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31124618 | 964 | 199.4208 | 0% | 100% | 100% | 0% | 100% | 0% | 6848795 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 96 | 7915048 | 4054 | 97.296 | 4.054 | 4.4 | 4.4 | 2B | 0 | 0 | 1054 | 0 | 1068 | N/A | N/A | N/A | N/A | 31125359 | 741 | 182.7824 | 0% | 0% | 100% | 0% | 100% | 25% | 6849242 | 447 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 93 | 7918979 | 3931 | 94.344 | 3.931 | 5 | 5 | 2B | 0 | 0 | 1021 | 0 | 1037 | N/A | N/A | N/A | N/A | 31125930 | 571 | 145.2557 | 0% | 0% | 100% | 0% | 100% | 25% | 6849845 | 603 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.4583 | 121089 | 121089 | 121.089 | 121.089 | [12 empty] | 24938 | 24938 | 205.9477 | [6 empty] | 5465 | 5465 | 0.95 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:30 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 25) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 24) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24168 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7918979 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31125930 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6849845 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 90 | 7922699 | 3720 | 89.28 | 3.72 | 6 | 6 | 2B | 0 | 0 | 1040 | 0 | 1038 | N/A | N/A | N/A | N/A | 31126508 | 578 | 155.3763 | 0% | 0% | 100% | 0% | 100% | 35% | 6850934 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 104 | 89 | 7926300 | 3601 | 86.424 | 3.601 | 7.1 | 7.1 | 2B | 0 | 0 | 1040 | 0 | 1038 | N/A | N/A | N/A | N/A | 31127072 | 564 | 156.6232 | 0% | 0% | 100% | 0% | 100% | 35% | 6852093 | 1159 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 88 | 7929891 | 3591 | 86.184 | 3.591 | 8.2 | 8.2 | 2B | 0 | 0 | 944 | 0 | 1038 | N/A | N/A | N/A | N/A | 31127623 | 551 | 153.4392 | 0% | 0% | 100% | 0% | 100% | 35% | 6853291 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 86 | 7933333 | 3442 | 82.608 | 3.442 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 958 | N/A | N/A | N/A | N/A | 31128108 | 485 | 140.9064 | 0% | 0% | 100% | 0% | 100% | 35% | 6854138 | 847 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 95 | 7937197 | 3864 | 92.736 | 3.864 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 978 | N/A | N/A | N/A | N/A | 31128596 | 488 | 126.294 | 0% | 0% | 100% | 0% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 118 | 7941951 | 4754 | 114.096 | 4.754 | 9.5 | 9.5 | 2B | 0 | 0 | 1128 | 0 | 1199 | N/A | N/A | N/A | N/A | 31129356 | 760 | 159.8654 | 0% | 0% | 100% | 0% | 100% | 0% | 6854138 | 0 | 0.94 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 144 | 7947855 | 5904 | 141.696 | 5.904 | 9.1 | 9.1 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31130648 | 1292 | 218.8347 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 7953864 | 6009 | 144.216 | 6.009 | 8.7 | 8.7 | 3B+1S | 0 | 1036 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31132034 | 1386 | 230.654 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 7959889 | 6025 | 144.6 | 6.025 | 8.1 | 8.1 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31133413 | 1379 | 228.8797 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 7965932 | 6043 | 145.032 | 6.043 | 7.6 | 7.6 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31134754 | 1341 | 221.9096 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 135 | 147 | 7971951 | 6019 | 144.456 | 6.019 | 6.9 | 6.9 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31136126 | 1372 | 227.9448 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 138 | 7977937 | 5986 | 143.664 | 5.986 | 6.4 | 6.4 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31137482 | 1356 | 226.5286 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 131 | 7983536 | 5599 | 134.376 | 5.599 | 6.2 | 6.2 | 3B+1S | 0 | 989 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31138754 | 1272 | 227.1834 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 129 | 7988888 | 5352 | 128.448 | 5.352 | 6.1 | 6.1 | 3B+1S | 0 | 989 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31139948 | 1194 | 223.0942 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 124 | 7994176 | 5288 | 126.912 | 5.288 | 5.9 | 5.9 | 3B+1S | 0 | 995 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31141129 | 1181 | 223.3359 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 127 | 7999525 | 5349 | 128.376 | 5.349 | 5.7 | 5.7 | 3B+1S | 0 | 1021 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31142326 | 1197 | 223.7801 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 132 | 8004947 | 5422 | 130.128 | 5.422 | 5.2 | 5.2 | 3B+1S | 0 | 1040 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31143538 | 1212 | 223.5338 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 120 | 125 | 8010312 | 5365 | 128.76 | 5.365 | 5 | 5 | 3B+1S | 0 | 1041 | 1095 | 1185 | 1098 | N/A | N/A | N/A | N/A | 31144730 | 1192 | 222.1808 | 0% | 100% | 100% | 100% | 100% | 0% | 6854138 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 123 | 8015587 | 5275 | 126.6 | 5.275 | 4.1 | 4.1 | 2B+1S | 0 | 1079 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31145802 | 1072 | 203.2227 | 0% | 100% | 100% | 0% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 121 | 8020863 | 5276 | 126.624 | 5.276 | 3.7 | 3.7 | 2B+1S | 0 | 1012 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31146870 | 1068 | 202.4261 | 0% | 100% | 100% | 0% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 119 | 8025952 | 5089 | 122.136 | 5.089 | 3.4 | 3.4 | 2B+1S | 0 | 990 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31147859 | 989 | 194.3407 | 0% | 100% | 100% | 0% | 100% | 0% | 6854138 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 116 | 8030700 | 4748 | 113.952 | 4.748 | 3.3 | 3.3 | 2B+1S | 0 | 989 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31148778 | 919 | 193.5552 | 0% | 100% | 100% | 0% | 100% | 0% | 6854138 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 98 | 8034852 | 4152 | 99.648 | 4.152 | 3.9 | 3.9 | 2B | 0 | 0 | 1071 | 0 | 1088 | N/A | N/A | N/A | N/A | 31149458 | 680 | 163.7765 | 0% | 0% | 100% | 0% | 100% | 25% | 6854592 | 454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 91 | 8038835 | 3983 | 95.592 | 3.983 | 4.7 | 4.7 | 2B | 0 | 0 | 1014 | 0 | 1008 | N/A | N/A | N/A | N/A | 31150098 | 640 | 160.6829 | 0% | 0% | 100% | 0% | 100% | 25% | 6855336 | 744 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.25 | 119856 | 119856 | 119.856 | 119.856 | [12 empty] | 24168 | 24168 | 201.642 | [6 empty] | 5491 | 5491 | 0.95 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:49 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 26) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:00PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 25) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24740 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8038835 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31150098 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6855336 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 94 | 90 | 8042490 | 3655 | 87.72 | 3.655 | 5.7 | 5.7 | 2B | 0 | 0 | 1004 | 0 | 1028 | N/A | N/A | N/A | N/A | 31150658 | 560 | 153.2148 | 0% | 0% | 100% | 0% | 100% | 35% | 6856378 | 1042 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 88 | 8046042 | 3552 | 85.248 | 3.552 | 6.9 | 6.9 | 2B | 0 | 0 | 1004 | 0 | 1028 | N/A | N/A | N/A | N/A | 31151206 | 548 | 154.2793 | 0% | 0% | 100% | 0% | 100% | 35% | 6857592 | 1214 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 89 | 86 | 8049490 | 3448 | 82.752 | 3.448 | 8.4 | 8.4 | 2B | 0 | 0 | 921 | 0 | 1009 | N/A | N/A | N/A | N/A | 31151734 | 528 | 153.1323 | 0% | 0% | 100% | 0% | 100% | 35% | 6858959 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 84 | 8052881 | 3391 | 81.384 | 3.391 | 9.5 | 9.5 | 2B | 0 | 0 | 921 | 0 | 1009 | N/A | N/A | N/A | N/A | 31152170 | 436 | 128.5756 | 0% | 0% | 100% | 0% | 100% | 35% | 6860023 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 96 | 8056608 | 3727 | 89.448 | 3.727 | 9.5 | 9.5 | 2B | 0 | 0 | 943 | 0 | 948 | N/A | N/A | N/A | N/A | 31152608 | 438 | 117.5208 | 0% | 0% | 100% | 0% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 122 | 8061327 | 4719 | 113.256 | 4.719 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1195 | N/A | N/A | N/A | N/A | 31153336 | 728 | 154.27 | 0% | 0% | 100% | 0% | 100% | 0% | 6860023 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 148 | 8067316 | 5989 | 143.736 | 5.989 | 9 | 9 | 3B+1S | 0 | 1081 | 1148 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31154670 | 1334 | 222.7417 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 8073509 | 6193 | 148.632 | 6.193 | 8.3 | 8.3 | 3B+1S | 0 | 1080 | 1188 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31156036 | 1366 | 220.5716 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 8079718 | 6209 | 149.016 | 6.209 | 7.6 | 7.6 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31157430 | 1394 | 224.5128 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 8085718 | 6000 | 144 | 6 | 6.9 | 6.9 | 3B+1S | 0 | 1080 | 1192 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31158792 | 1362 | 227 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 | 0.83 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 135 | 135 | 8091840 | 6122 | 146.928 | 6.122 | 6.4 | 6.4 | 3B+1S | 0 | 1071 | 1169 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31160145 | 1353 | 221.0062 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 135 | 8097728 | 5888 | 141.312 | 5.888 | 5.8 | 5.8 | 3B+1S | 0 | 1070 | 1150 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31161498 | 1353 | 229.7894 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 136 | 8103465 | 5737 | 137.688 | 5.737 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1168 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31162806 | 1308 | 227.9937 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 132 | 8108996 | 5531 | 132.744 | 5.531 | 5.5 | 5.5 | 3B+1S | 0 | 999 | 1098 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31164030 | 1224 | 221.2981 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 134 | 8114366 | 5370 | 128.88 | 5.37 | 5.4 | 5.4 | 3B+1S | 0 | 999 | 1171 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31165238 | 1208 | 224.9534 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 8119865 | 5499 | 131.976 | 5.499 | 5.3 | 5.3 | 3B+1S | 0 | 999 | 1145 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31166492 | 1254 | 228.0415 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 8125293 | 5428 | 130.272 | 5.428 | 5.2 | 5.2 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31167766 | 1274 | 234.7089 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 8130759 | 5466 | 131.184 | 5.466 | 5.1 | 5.1 | 3B+1S | 0 | 950 | 1170 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31169006 | 1240 | 226.8569 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 8136256 | 5497 | 131.928 | 5.497 | 5 | 5 | 3B+1S | 0 | 999 | 1116 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31170282 | 1276 | 232.1266 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 8141737 | 5481 | 131.544 | 5.481 | 4.8 | 4.8 | 3B+1S | 0 | 949 | 1105 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31171470 | 1188 | 216.7488 | 0% | 100% | 100% | 100% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 118 | 8147074 | 5337 | 128.088 | 5.337 | 4.3 | 4.3 | 2B+1S | 0 | 1050 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 31172534 | 1064 | 199.3629 | 0% | 100% | 100% | 0% | 100% | 0% | 6860023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 113 | 8151966 | 4892 | 117.408 | 4.892 | 3.7 | 3.7 | 2B+1S | 0 | 1030 | 1098 | 0 | 1198 | N/A | N/A | N/A | N/A | 31173474 | 940 | 192.1504 | 0% | 100% | 100% | 0% | 100% | 0% | 6860023 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 105 | 101 | 8156764 | 4798 | 115.152 | 4.798 | 4.3 | 4.3 | 2B | 0 | 0 | 1061 | 0 | 1110 | N/A | N/A | N/A | N/A | 31174228 | 754 | 157.1488 | 0% | 0% | 100% | 0% | 100% | 25% | 6860446 | 423 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 97 | 8160243 | 3479 | 83.496 | 3.479 | 4.9 | 4.9 | 2B | 0 | 0 | 1020 | 0 | 1079 | N/A | N/A | N/A | N/A | 31174838 | 610 | 175.3377 | 0% | 0% | 100% | 0% | 100% | 25% | 6861066 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.25 | 121408 | 121408 | 121.408 | 121.408 | [12 empty] | 24740 | 24740 | 203.7757 | [6 empty] | 5730 | 5730 | 0.95333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:46 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 26) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 26) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25660 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8160243 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31174838 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6861066 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 94 | 8164201 | 3958 | 94.992 | 3.958 | 6 | 6 | 2B | 0 | 0 | 1054 | 0 | 1059 | N/A | N/A | N/A | N/A | 31175437 | 599 | 151.3391 | 0% | 0% | 100% | 0% | 100% | 35% | 6862080 | 1014 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 90 | 8167988 | 3787 | 90.888 | 3.787 | 7.2 | 7.2 | 2B | 0 | 0 | 1054 | 0 | 1059 | N/A | N/A | N/A | N/A | 31176021 | 584 | 154.2118 | 0% | 0% | 100% | 0% | 100% | 35% | 6863225 | 1145 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 88 | 8171666 | 3678 | 88.272 | 3.678 | 8.5 | 8.5 | 2B | 0 | 0 | 1054 | 0 | 1059 | N/A | N/A | N/A | N/A | 31176596 | 575 | 156.335 | 0% | 0% | 100% | 0% | 100% | 35% | 6864523 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 84 | 8174927 | 3261 | 78.264 | 3.261 | 9.5 | 9.5 | 2B | 0 | 0 | 911 | 0 | 1059 | N/A | N/A | N/A | N/A | 31177122 | 526 | 161.3002 | 0% | 0% | 100% | 0% | 100% | 35% | 6865579 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 92 | 8178245 | 3318 | 79.632 | 3.318 | 9.5 | 9.5 | 2B | 0 | 0 | 940 | 0 | 948 | N/A | N/A | N/A | N/A | 31177532 | 410 | 123.5684 | 0% | 0% | 100% | 0% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 114 | 8182552 | 4307 | 103.368 | 4.307 | 9.5 | 9.5 | 2B | 0 | 0 | 1101 | 0 | 1190 | N/A | N/A | N/A | N/A | 31178164 | 632 | 146.7379 | 0% | 0% | 100% | 0% | 100% | 0% | 6865579 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 140 | 8188357 | 5805 | 139.32 | 5.805 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31179418 | 1254 | 216.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 8194521 | 6164 | 147.936 | 6.164 | 9.1 | 9.1 | 3B+1S | 0 | 1026 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31180777 | 1359 | 220.4737 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 149 | 8200685 | 6164 | 147.936 | 6.164 | 8.6 | 8.6 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31182136 | 1359 | 220.4737 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 155 | 8206852 | 6167 | 148.008 | 6.167 | 7.7 | 7.7 | 3B+1S | 0 | 1184 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31183542 | 1406 | 227.9877 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 132 | 153 | 8213190 | 6338 | 152.112 | 6.338 | 6.7 | 6.7 | 3B+1S | 0 | 1160 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31184987 | 1445 | 227.9899 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 146 | 8219528 | 6338 | 152.112 | 6.338 | 5.7 | 5.7 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31186432 | 1445 | 227.9899 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 141 | 8225455 | 5927 | 142.248 | 5.927 | 4.9 | 4.9 | 3B+1S | 0 | 1131 | 1135 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31187798 | 1366 | 230.4707 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 8231196 | 5741 | 137.784 | 5.741 | 4.5 | 4.5 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31189133 | 1335 | 232.5379 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 136 | 8236979 | 5783 | 138.792 | 5.783 | 4.3 | 4.3 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31190474 | 1341 | 231.8866 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 8242736 | 5757 | 138.168 | 5.757 | 4.2 | 4.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31191802 | 1328 | 230.6757 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 8248439 | 5703 | 136.872 | 5.703 | 3.8 | 3.8 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31193116 | 1314 | 230.405 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 8254030 | 5591 | 134.184 | 5.591 | 3.5 | 3.5 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31194425 | 1309 | 234.1263 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 131 | 8259607 | 5577 | 133.848 | 5.577 | 3.3 | 3.3 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31195710 | 1285 | 230.4106 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 122 | 8264950 | 5343 | 128.232 | 5.343 | 3.2 | 3.2 | 3B+1S | 0 | 990 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31196916 | 1206 | 225.7159 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 125 | 126 | 8270209 | 5259 | 126.216 | 5.259 | 3.1 | 3.1 | 3B+1S | 0 | 989 | 1090 | 1185 | 1109 | N/A | N/A | N/A | N/A | 31198100 | 1184 | 225.1379 | 0% | 100% | 100% | 100% | 100% | 0% | 6865579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 | 121 | 8275190 | 4981 | 119.544 | 4.981 | 2.9 | 2.9 | 2B+1S | 0 | 1000 | 1190 | 0 | 1199 | N/A | N/A | N/A | N/A | 31199086 | 986 | 197.9522 | 0% | 100% | 100% | 0% | 100% | 0% | 6865579 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 101 | 8279765 | 4575 | 109.8 | 4.575 | 3.5 | 3.5 | 2B | 0 | 0 | 1098 | 0 | 1110 | N/A | N/A | N/A | N/A | 31199814 | 728 | 159.1257 | 0% | 0% | 100% | 0% | 100% | 25% | 6866030 | 451 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 91 | 8283560 | 3795 | 91.08 | 3.795 | 4.1 | 4.1 | 2B | 0 | 0 | 1035 | 0 | 1068 | N/A | N/A | N/A | N/A | 31200498 | 684 | 180.2372 | 0% | 0% | 100% | 0% | 100% | 25% | 6866676 | 646 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.7083 | 123317 | 123317 | 123.317 | 123.317 | [12 empty] | 25660 | 25660 | 208.0816 | [6 empty] | 5610 | 5610 | 0.93333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:01AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 27) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 27) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25192 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8283560 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31200498 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6866676 |  | mg /l |  | Automatic - i2O | AI | REIVIN M. MALLARI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 90 | 8287449 | 3889 | 93.336 | 3.889 | 5.1 | 5.1 | 2B | 0 | 0 | 964 | 0 | 968 | N/A | N/A | N/A | N/A | 31201108 | 610 | 156.8527 | 0% | 0% | 100% | 0% | 100% | 35% | 6867700 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS L. GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 88 | 8291203 | 3754 | 90.096 | 3.754 | 6.2 | 6.2 | 2B | 0 | 0 | 964 | 0 | 968 | N/A | N/A | N/A | N/A | 31201704 | 596 | 158.764 | 0% | 0% | 100% | 0% | 100% | 35% | 6868856 | 1156 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ALEXANDER CABREROS
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 86 | 8294867 | 3664 | 87.936 | 3.664 | 7.6 | 7.6 | 2B | 0 | 0 | 981 | 0 | 988 | N/A | N/A | N/A | N/A | 31202280 | 576 | 157.2052 | 0% | 0% | 100% | 0% | 100% | 35% | 6870068 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY O. REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 82 | 8298294 | 3427 | 82.248 | 3.427 | 8.9 | 8.9 | 2B | 0 | 0 | 981 | 0 | 988 | N/A | N/A | N/A | N/A | 31202838 | 558 | 162.8246 | 0% | 0% | 100% | 0% | 100% | 35% | 6871157 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 85 | 8301526 | 3232 | 77.568 | 3.232 | 9.5 | 9.5 | 2B | 0 | 0 | 936 | 0 | 927 | N/A | N/A | N/A | N/A | 31203294 | 456 | 141.0891 | 0% | 0% | 100% | 0% | 100% | 35% | 6871819 | 662 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 106 | 8305559 | 4033 | 96.792 | 4.033 | 9.5 | 9.5 | 2B | 0 | 0 | 1022 | 0 | 1110 | N/A | N/A | N/A | N/A | 31203838 | 544 | 134.8872 | 0% | 0% | 100% | 0% | 100% | 0% | 6871819 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 126 | 118 | 8311105 | 5546 | 133.104 | 5.546 | 8.9 | 8.9 | 2B+1S | 0 | 1129 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 31204910 | 1072 | 193.2925 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 8317092 | 5987 | 143.688 | 5.987 | 8.5 | 8.5 | 3B+1S | 0 | 1053 | 1135 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31206190 | 1280 | 213.7966 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 153 | 8323298 | 6206 | 148.944 | 6.206 | 7.7 | 7.7 | 3B+1S | 0 | 1142 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31207554 | 1364 | 219.7873 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 148 | 8329553 | 6255 | 150.12 | 6.255 | 6.8 | 6.8 | 3B+1S | 0 | 1170 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31208981 | 1427 | 228.1375 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 128 | 155 | 8335808 | 6255 | 150.12 | 6.255 | 5.8 | 5.8 | 3B+1S | 0 | 1187 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31210408 | 1427 | 228.1375 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 123 | 144 | 8341758 | 5950 | 142.8 | 5.95 | 4.9 | 4.9 | 3B+1S | 0 | 1162 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31211806 | 1398 | 234.958 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 8347732 | 5974 | 143.376 | 5.974 | 4.3 | 4.3 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31213182 | 1376 | 230.3314 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 137 | 8353561 | 5829 | 139.896 | 5.829 | 3.9 | 3.9 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31214524 | 1342 | 230.2282 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 147 | 8359110 | 5549 | 133.176 | 5.549 | 3.9 | 3.9 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31215814 | 1290 | 232.4743 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 132 | 8364579 | 5469 | 131.256 | 5.469 | 3.9 | 3.9 | 3B+1S | 0 | 999 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31217102 | 1288 | 235.5092 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 8370174 | 5595 | 134.28 | 5.595 | 3.6 | 3.6 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31218420 | 1318 | 235.5675 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 132 | 8375660 | 5486 | 131.664 | 5.486 | 3.2 | 3.2 | 3B+1S | 0 | 1104 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31219688 | 1268 | 231.1338 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 131 | 8381292 | 5632 | 135.168 | 5.632 | 3.3 | 3.3 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31221084 | 1396 | 247.8693 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 8386552 | 5260 | 126.24 | 5.26 | 3.4 | 3.4 | 3B | 0 | 0 | 1106 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31222178 | 1094 | 207.9848 | 0% | 100% | 100% | 100% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 123 | 128 | 8391772 | 5220 | 125.28 | 5.22 | 3.4 | 3.4 | 3B | 0 | 0 | 1032 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31223262 | 1084 | 207.6628 | 0% | 100% | 100% | 0% | 100% | 0% | 6871819 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 114 | 8396526 | 4754 | 114.096 | 4.754 | 3.4 | 3.4 | 3B | 0 | 0 | 1032 | 0 | 1139 | N/A | N/A | N/A | N/A | 31224186 | 924 | 194.3626 | 0% | 100% | 100% | 0% | 100% | 0% | 6871819 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 97 | 8401147 | 4621 | 110.904 | 4.621 | 4.1 | 4.1 | 2B | 0 | 0 | 1062 | 0 | 1139 | N/A | N/A | N/A | N/A | 31225061 | 875 | 189.353 | 0% | 0% | 100% | 0% | 100% | 30% | 6872473 | 654 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 87 | 8405281 | 4134 | 99.216 | 4.134 | 5.3 | 5.3 | 2B | 0 | 0 | 1035 | 0 | 1037 | N/A | N/A | N/A | N/A | 31225690 | 629 | 152.1529 | 0% | 0% | 100% | 0% | 100% | 30% | 6873481 | 1008 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.25 | 121721 | 121721 | 121.721 | 121.721 | [12 empty] | 25192 | 25192 | 206.9651 | [6 empty] | 6805 | 6805 | 0.965 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:40 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:16 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED @ 5:46 PM (10%) / CLOSED @ 6:57 PM
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 11) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24752 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8405281 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31225690 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6873481 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 95 | 87 | 8408923 | 3642 | 87.408 | 3.642 | 6.3 | 6.3 | 2B | 0 | 0 | 964 | 0 | 968 | N/A | N/A | N/A | N/A | 31226272 | 582 | 159.8023 | 0% | 0% | 100% | 0% | 100% | 35% | 6874435 | 954 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 86 | 8412439 | 3516 | 84.384 | 3.516 | 7.4 | 7.4 | 2B | 0 | 0 | 964 | 0 | 968 | N/A | N/A | N/A | N/A | 31226822 | 550 | 156.4278 | 0% | 0% | 100% | 0% | 100% | 35% | 6875633 | 1198 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 88 | 85 | 8415928 | 3489 | 83.736 | 3.489 | 8.9 | 8.9 | 2B | 0 | 0 | 964 | 0 | 968 | N/A | N/A | N/A | N/A | 31227340 | 518 | 148.4666 | 0% | 0% | 100% | 0% | 100% | 35% | 6876987 | 1354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 84 | 8419147 | 3219 | 77.256 | 3.219 | 9.5 | 9.5 | 2B | 0 | 0 | 916 | 0 | 897 | N/A | N/A | N/A | N/A | 31227790 | 450 | 139.795 | 0% | 0% | 100% | 0% | 100% | 35% | 6877591 | 604 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 8422550 | 3403 | 81.672 | 3.403 | 9.5 | 9.5 | 2B | 0 | 0 | 964 | 0 | 986 | N/A | N/A | N/A | N/A | 31228214 | 424 | 124.5959 | 0% | 0% | 100% | 0% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 120 | 8427262 | 4712 | 113.088 | 4.712 | 9.5 | 9.5 | 2B | 0 | 0 | 1186 | 0 | 1190 | N/A | N/A | N/A | N/A | 31228958 | 744 | 157.8947 | 0% | 0% | 100% | 0% | 100% | 0% | 6877591 | 0 | 0.92 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 147 | 8433329 | 6067 | 145.608 | 6.067 | 9.1 | 9.1 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31230308 | 1350 | 222.5152 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 8439419 | 6090 | 146.16 | 6.09 | 8.7 | 8.7 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31231664 | 1356 | 222.6601 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 151 | 8445695 | 6276 | 150.624 | 6.276 | 8 | 8 | 3B+1S | 0 | 1087 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31233064 | 1400 | 223.072 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 152 | 8451808 | 6113 | 146.712 | 6.113 | 7.2 | 7.2 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31234454 | 1390 | 227.3843 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 | 0.85 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 132 | 144 | 8457965 | 6157 | 147.768 | 6.157 | 6.7 | 6.7 | 3B+1S | 0 | 1106 | 1197 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31235838 | 1384 | 224.7848 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 8463945 | 5980 | 143.52 | 5.98 | 6 | 6 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31237214 | 1376 | 230.1003 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 132 | 8469691 | 5746 | 137.904 | 5.746 | 5.9 | 5.9 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31238538 | 1324 | 230.4212 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 134 | 8475302 | 5611 | 134.664 | 5.611 | 5.8 | 5.8 | 3B+1S | 0 | 1002 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31239802 | 1264 | 225.2718 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 133 | 8480681 | 5379 | 129.096 | 5.379 | 5.7 | 5.7 | 3B+1S | 0 | 990 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31241010 | 1208 | 224.5771 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 131 | 8485911 | 5230 | 125.52 | 5.23 | 5.6 | 5.6 | 3B+1S | 0 | 985 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31242198 | 1188 | 227.1511 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 8491353 | 5442 | 130.608 | 5.442 | 5.5 | 5.5 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31243470 | 1272 | 233.7376 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 8496850 | 5497 | 131.928 | 5.497 | 5.4 | 5.4 | 3B+1S | 0 | 975 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31244714 | 1244 | 226.3053 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 8502416 | 5566 | 133.584 | 5.566 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1125 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31245964 | 1250 | 224.5778 | 0% | 100% | 100% | 100% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 125 | 8507810 | 5394 | 129.456 | 5.394 | 4.6 | 4.6 | 2B+1S | 0 | 1088 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31247050 | 1086 | 201.3348 | 0% | 100% | 100% | 0% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 123 | 8513179 | 5369 | 128.856 | 5.369 | 3.7 | 3.7 | 2B+1S | 0 | 1014 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31248118 | 1068 | 198.9197 | 0% | 100% | 100% | 0% | 100% | 0% | 6877591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 121 | 8518103 | 4924 | 118.176 | 4.924 | 3.5 | 3.5 | 2B+1S | 0 | 985 | 1165 | 0 | 169 | N/A | N/A | N/A | N/A | 31249094 | 976 | 198.2128 | 0% | 100% | 100% | 0% | 100% | 0% | 6877591 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 97 | 8522317 | 4214 | 101.136 | 4.214 | 4 | 4 | 2B | 0 | 0 | 1041 | 0 | 1110 | N/A | N/A | N/A | N/A | 31249810 | 716 | 169.9098 | 0% | 0% | 100% | 0% | 100% | 0% | 6878081 | 490 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 107 | 91 | 8526182 | 3865 | 92.76 | 3.865 | 4.9 | 4.9 | 2B | 0 | 0 | 945 | 0 | 1110 | N/A | N/A | N/A | N/A | 31250442 | 632 | 163.5188 | 0% | 0% | 100% | 0% | 100% | 0% | 6878723 | 642 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.25 | 120901 | 120901 | 120.901 | 120.901 | [12 empty] | 24752 | 24752 | 204.7295 | [6 empty] | 5242 | 5242 | 0.95167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:30 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 29) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 11) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## SEPT 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-09-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8526182 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31250442 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6878723 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 87 | 8529827 | 3645 | 87.48 | 3.645 | 6 | 6 | 2B | 0 | 0 | 940 | 0 | 1110 | N/A | N/A | N/A | N/A | 31251046 | 604 | 165.7064 | 0% | 0% | 100% | 0% | 100% | 35% | 6879849 | 1126 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 84 | 8533334 | 3507 | 84.168 | 3.507 | 7.2 | 7.2 | 2B | 0 | 0 | 933 | 0 | 1060 | N/A | N/A | N/A | N/A | 31251594 | 548 | 156.2589 | 0% | 0% | 100% | 0% | 100% | 35% | 6881030 | 1181 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 83 | 8536875 | 3541 | 84.984 | 3.541 | 8.5 | 8.5 | 2B | 0 | 0 | 965 | 0 | 998 | N/A | N/A | N/A | N/A | 31252114 | 520 | 146.8512 | 0% | 0% | 100% | 0% | 100% | 35% | 6882226 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 93 | 8540420 | 3545 | 85.08 | 3.545 | 9.5 | 9.5 | 2B | 0 | 0 | 968 | 0 | 970 | N/A | N/A | N/A | N/A | 31252626 | 512 | 144.4288 | 0% | 0% | 100% | 0% | 100% | 35% | 6883234 | 1008 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 105 | 8544406 | 3986 | 95.664 | 3.986 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 999 | N/A | N/A | N/A | N/A | 31253128 | 502 | 125.9408 | 0% | 0% | 100% | 0% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 119 | 8549025 | 4619 | 110.856 | 4.619 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1160 | N/A | N/A | N/A | N/A | 31253878 | 750 | 162.3728 | 0% | 0% | 100% | 0% | 100% | 0% | 6883234 | 0 | 1.01 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 143 | 8555089 | 6064 | 145.536 | 6.064 | 9 | 9 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31255234 | 1356 | 223.6148 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 154 | 8561154 | 6065 | 145.56 | 6.065 | 8.4 | 8.4 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31256590 | 1356 | 223.5779 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 149 | 8567425 | 6271 | 150.504 | 6.271 | 7.7 | 7.7 | 3B+1S | 0 | 1112 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31258010 | 1420 | 226.4392 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 8573546 | 6121 | 146.904 | 6.121 | 6.9 | 6.9 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31259390 | 1380 | 225.4534 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 0 | 19 | A ONG | 17.7 | 138 | 148 | 8579708 | 6162 | 147.888 | 6.162 | 6.2 | 6.2 | 3B+1S | 0 | 1073 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31260770 | 1380 | 223.9533 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 8585631 | 5923 | 142.152 | 5.923 | 5.6 | 5.6 | 3B+1S | 0 | 1065 | 1197 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31262134 | 1364 | 230.2887 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 134 | 8591361 | 5730 | 137.52 | 5.73 | 5.4 | 5.4 | 3B+1S | 0 | 1012 | 1169 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31263430 | 1296 | 226.178 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 129 | 8596922 | 5561 | 133.464 | 5.561 | 5.2 | 5.2 | 3B+1S | 0 | 997 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31264684 | 1254 | 225.499 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 8602469 | 5547 | 133.128 | 5.547 | 5.1 | 5.1 | 3B+1S | 0 | 997 | 1145 | 1185 | 1180 | N/A | N/A | N/A | N/A | 31265930 | 1246 | 224.6259 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 8608031 | 5562 | 133.488 | 5.562 | 5 | 5 | 3B+1S | 0 | 995 | 1186 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31267194 | 1264 | 227.2564 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 8613611 | 5580 | 133.92 | 5.58 | 4.9 | 4.9 | 3B+1S | 0 | 11032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31268510 | 1316 | 235.8423 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 8619158 | 5547 | 133.128 | 5.547 | 4.8 | 4.8 | 3B+1S | 0 | 987 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31269738 | 1228 | 221.3809 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 8624755 | 5597 | 134.328 | 5.597 | 4.7 | 4.7 | 3B+1S | 0 | 980 | 1175 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31271006 | 1268 | 226.5499 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 8630128 | 5373 | 128.952 | 5.373 | 4.6 | 4.6 | 3B+1S | 0 | 935 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31272212 | 1206 | 224.4556 | 0% | 100% | 100% | 100% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 8635449 | 5321 | 127.704 | 5.321 | 3.9 | 3.9 | 2B+1S | 0 | 1032 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31273282 | 1070 | 201.09 | 0% | 100% | 100% | 0% | 100% | 0% | 6883234 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 116 | 8640435 | 4986 | 119.664 | 4.986 | 3.6 | 3.6 | 2B+1S | 0 | 998 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31274286 | 1004 | 201.3638 | 0% | 100% | 100% | 0% | 100% | 0% | 6883234 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 99 | 8644756 | 4321 | 103.704 | 4.321 | 4.1 | 4.1 | 2B | 0 | 0 | 1094 | 0 | 1109 | N/A | N/A | N/A | N/A | 31275160 | 874 | 202.268 | 0% | 0% | 100% | 0% | 100% | 25% | 6883692 | 458 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 92 | 8648718 | 3962 | 95.088 | 3.962 | 4.7 | 4.7 | 2B | 0 | 0 | 1075 | 0 | 1008 | N/A | N/A | N/A | N/A | 31275674 | 514 | 129.7325 | 0% | 0% | 100% | 0% | 100% | 25% | 6884249 | 557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.625 | 122536 | 122536 | 122.536 | 122.536 | [12 empty] | 25232 | 25232 | 205.915 | [6 empty] | 5526 | 5526 | 0.99667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:54 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (SEPT 30) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:20 PM TO 4:30 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:31PM TO 4:41 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (SEPT 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION