## OCT 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24104 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8648718 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31275674 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6884249 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 94 | 88 | 8652372 | 3654 | 87.696 | 3.654 | 5.8 | 5.8 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31276234 | 560 | 153.2567 | 0% | 0% | 100% | 0% | 100% | 35% | 6885303 | 1054 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 86 | 8655893 | 3521 | 84.504 | 3.521 | 6.9 | 6.9 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31276742 | 508 | 144.2772 | 0% | 0% | 100% | 0% | 100% | 35% | 6886462 | 1159 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 84 | 8659307 | 3414 | 81.936 | 3.414 | 8.3 | 8.3 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31277222 | 480 | 140.5975 | 0% | 0% | 100% | 0% | 100% | 35% | 6887783 | 1321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 95 | 8662796 | 3489 | 83.736 | 3.489 | 9.5 | 9.5 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31277682 | 460 | 131.8429 | 0% | 0% | 100% | 0% | 100% | 35% | 6888820 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 106 | 8666687 | 3891 | 93.384 | 3.891 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 999 | N/A | N/A | N/A | N/A | 31278134 | 452 | 116.1655 | 0% | 0% | 100% | 0% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 130 | 127 | 8671021 | 4334 | 104.016 | 4.334 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1189 | N/A | N/A | N/A | N/A | 31278979 | 845 | 194.97 | 0% | 0% | 100% | 0% | 100% | 0% | 6888820 | 0 | 0.88 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 8677009 | 5988 | 143.712 | 5.988 | 9.1 | 9.1 | 3B+1S | 0 | 1078 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31280303 | 1324 | 221.1089 | 0% | 0% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 149 | 8683063 | 6054 | 145.296 | 6.054 | 8.5 | 8.5 | 3B+1S | 0 | 1101 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31281667 | 1364 | 225.3056 | 0% | 0% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 150 | 151 | 8689281 | 6218 | 149.232 | 6.218 | 7.8 | 7.8 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31283044 | 1377 | 221.4538 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 8695570 | 6289 | 150.936 | 6.289 | 7.1 | 7.1 | 3B+1S | 0 | 1089 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31284433 | 1389 | 220.8618 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 | 0.87 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 8701395 | 5825 | 139.8 | 5.825 | 6.5 | 6.5 | 3B+1S | 0 | 1026 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31285822 | 1389 | 238.4549 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 131 | 8707173 | 5778 | 138.672 | 5.778 | 6.4 | 6.4 | 3B+1S | 0 | 1025 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31287142 | 1320 | 228.4528 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 131 | 8712860 | 5687 | 136.488 | 5.687 | 6.2 | 6.2 | 3B+1S | 0 | 1022 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31288372 | 1230 | 216.2828 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 122 | 128 | 8718257 | 5397 | 129.528 | 5.397 | 6 | 6 | 3B+1S | 0 | 1026 | 1105 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31289572 | 1200 | 222.3457 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 121 | 124 | 8723617 | 5360 | 128.64 | 5.36 | 5.7 | 5.7 | 3B+1S | 0 | 1025 | 1104 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31290754 | 1182 | 220.5224 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 120 | 129 | 8728960 | 5343 | 128.232 | 5.343 | 5.2 | 5.2 | 3B+1S | 0 | 1091 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31291949 | 1195 | 223.6571 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 119 | 135 | 8734303 | 5343 | 128.232 | 5.343 | 4.8 | 4.8 | 3B+1S | 0 | 1085 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31293144 | 1195 | 223.6571 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 119 | 126 | 8739673 | 5370 | 128.88 | 5.37 | 4.4 | 4.4 | 3B+1S | 0 | 1038 | 1104 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31294330 | 1186 | 220.8566 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 121 | 8744884 | 5211 | 125.064 | 5.211 | 3.9 | 3.9 | 3B+1S | 0 | 1023 | 1104 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31295482 | 1152 | 221.0708 | 0% | 100% | 100% | 100% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 123 | 8750182 | 5298 | 127.152 | 5.298 | 3.3 | 3.3 | 2B+1S | 0 | 1043 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 31296562 | 1080 | 203.8505 | 0% | 100% | 100% | 0% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 124 | 8755177 | 4995 | 119.88 | 4.995 | 2.9 | 2.9 | 2B+1S | 0 | 1019 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 31297554 | 992 | 198.5986 | 0% | 100% | 100% | 0% | 100% | 0% | 6888820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 105 | 8759893 | 4716 | 113.184 | 4.716 | 2.7 | 2.7 | 2B+1S | 0 | 989 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 31298470 | 916 | 194.2324 | 0% | 100% | 100% | 0% | 100% | 0% | 6888820 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 95 | 8764052 | 4159 | 99.816 | 4.159 | 3.4 | 3.4 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 31299174 | 704 | 169.2715 | 0% | 0% | 100% | 0% | 100% | 25% | 6889516 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 89 | 8767758 | 3706 | 88.944 | 3.706 | 4.4 | 4.4 | 2B | 0 | 0 | 945 | 0 | 1110 | N/A | N/A | N/A | N/A | 31299778 | 604 | 162.979 | 0% | 0% | 100% | 0% | 100% | 25% | 6890382 | 866 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.3333 | 119040 | 119040 | 119.04 | 119.04 | [12 empty] | 24104 | 24104 | 202.4866 | [6 empty] | 6133 | 6133 | 0.88667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @3:59AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 1) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:28 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 1) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8767758 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31299778 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6890382 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 86 | 8771360 | 3602 | 86.448 | 3.602 | 5.9 | 5.9 | 2B | 0 | 0 | 1021 | 0 | 1109 | N/A | N/A | N/A | N/A | 31300359 | 581 | 161.2993 | 0% | 0% | 100% | 0% | 100% | 35% | 6891658 | 1276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 84 | 8774962 | 3602 | 86.448 | 3.602 | 7 | 7 | 2B | 0 | 0 | 1002 | 0 | 1109 | N/A | N/A | N/A | N/A | 31300940 | 581 | 161.2993 | 0% | 0% | 100% | 0% | 100% | 35% | 6892934 | 1276 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 83 | 8778564 | 3602 | 86.448 | 3.602 | 8.3 | 8.3 | 2B | 0 | 0 | 900 | 0 | 1109 | N/A | N/A | N/A | N/A | 31301522 | 582 | 161.5769 | 0% | 0% | 100% | 0% | 100% | 35% | 6894210 | 1276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 85 | 8781906 | 3342 | 80.208 | 3.342 | 9.5 | 9.5 | 2B | 0 | 0 | 878 | 0 | 1088 | N/A | N/A | N/A | N/A | 31302034 | 512 | 153.2017 | 0% | 0% | 100% | 0% | 100% | 35% | 6895274 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 85 | 8785850 | 3944 | 94.656 | 3.944 | 9.5 | 9.5 | 2B | 0 | 0 | 961 | 0 | 1088 | N/A | N/A | N/A | N/A | 31302628 | 594 | 150.6085 | 0% | 0% | 100% | 0% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 119 | 8790286 | 4436 | 106.464 | 4.436 | 9.5 | 9.5 | 2B | 0 | 0 | 1171 | 0 | 1199 | N/A | N/A | N/A | N/A | 31303328 | 700 | 157.7998 | 0% | 0% | 100% | 0% | 100% | 0% | 6895274 | 0 | 0.99 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 8796259 | 5973 | 143.352 | 5.973 | 9.1 | 9.1 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31304652 | 1324 | 221.6642 | 0% | 0% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 8802349 | 6090 | 146.16 | 6.09 | 8.4 | 8.4 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31306033 | 1381 | 226.7652 | 0% | 0% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 146 | 8808439 | 6090 | 146.16 | 6.09 | 7.7 | 7.7 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 31307414 | 1381 | 226.7652 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 8814561 | 6122 | 146.928 | 6.122 | 6.9 | 6.9 | 3B+1S | 0 | 1090 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31308806 | 1392 | 227.3767 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 143 | 8820582 | 6021 | 144.504 | 6.021 | 6.4 | 6.4 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31310178 | 1372 | 227.8691 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 8826425 | 5843 | 140.232 | 5.843 | 5.8 | 5.8 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31311526 | 1348 | 230.7034 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 133 | 8831971 | 5546 | 133.104 | 5.546 | 5.5 | 5.5 | 3B+1S | 0 | 1018 | 1135 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31312775 | 1249 | 225.2074 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 131 | 8837518 | 5547 | 133.128 | 5.547 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1104 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31314024 | 1249 | 225.1668 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 120 | 132 | 8842930 | 5412 | 129.888 | 5.412 | 4.8 | 4.8 | 3B+1S | 0 | 1070 | 1104 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31315230 | 1206 | 222.8381 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 132 | 8848384 | 5454 | 130.896 | 5.454 | 4.3 | 4.3 | 3B+1S | 0 | 1048 | 1135 | 1185 | 1168 | N/A | N/A | N/A | N/A | 31316446 | 1216 | 222.9556 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 131 | 8853897 | 5513 | 132.312 | 5.513 | 3.7 | 3.7 | 3B+1S | 0 | 1073 | 1135 | 1185 | 1168 | N/A | N/A | N/A | N/A | 31317690 | 1244 | 225.6485 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 106 | 8859401 | 5504 | 132.096 | 5.504 | 3.4 | 3.4 | 3B+1S | 0 | 1040 | 1135 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31318910 | 1220 | 221.657 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 136 | 8864903 | 5502 | 132.048 | 5.502 | 2.9 | 2.9 | 3B+1S | 0 | 1056 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31320142 | 1232 | 223.9186 | 0% | 100% | 100% | 100% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 124 | 8870094 | 5191 | 124.584 | 5.191 | 2 | 2 | 2B+1S | 0 | 1097 | 1197 | 0 | 1169 | N/A | N/A | N/A | N/A | 31321177 | 1035 | 199.3835 | 0% | 100% | 100% | 0% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 121 | 8875286 | 5192 | 124.608 | 5.192 | 1.6 | 1.6 | 2B+1S | 0 | 1032 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 31322212 | 1035 | 199.3451 | 0% | 100% | 100% | 0% | 100% | 0% | 6895274 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 114 | 8880169 | 4883 | 117.192 | 4.883 | 1.3 | 1.3 | 2B+1S | 0 | 0 | 1197 | 0 | 1141 | N/A | N/A | N/A | N/A | 31323134 | 922 | 188.8183 | 0% | 100% | 100% | 0% | 100% | 0% | 6895274 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 96 | 8884080 | 3911 | 93.864 | 3.911 | 2.6 | 2.6 | 2B | 0 | 0 | 988 | 0 | 1100 | N/A | N/A | N/A | N/A | 31323806 | 672 | 171.8231 | 0% | 0% | 100% | 0% | 100% | 25% | 6896363 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 91 | 8887992 | 3912 | 93.888 | 3.912 | 3.5 | 3.5 | 2B | 0 | 0 | 988 | 0 | 1100 | N/A | N/A | N/A | N/A | 31324478 | 672 | 171.7791 | 0% | 0% | 100% | 0% | 100% | 25% | 6897452 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.125 | 120234 | 120234 | 120.234 | 120.234 | [12 empty] | 24700 | 24700 | 205.4327 | [6 empty] | 7070 | 7070 | 0.96333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:00AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:16 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 2) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:35 PM DUE TO LOW WATER LEVEL (1.3 M)
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25250 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8887992 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31324478 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6897452 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 92 | 8891753 | 3761 | 90.264 | 3.761 | 5.4 | 5.4 | 2B | 0 | 0 | 999 | 0 | 1099 | N/A | N/A | N/A | N/A | 31325083 | 605 | 160.8615 | 0% | 0% | 100% | 0% | 100% | 35% | 6898620 | 1168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 90 | 8895514 | 3761 | 90.264 | 3.761 | 6.9 | 6.9 | 2B | 0 | 0 | 981 | 0 | 1101 | N/A | N/A | N/A | N/A | 31325688 | 605 | 160.8615 | 0% | 0% | 100% | 0% | 100% | 35% | 6899788 | 1168 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 91 | 8899275 | 3761 | 90.264 | 3.761 | 7.4 | 7.4 | 2B | 0 | 0 | 939 | 0 | 1110 | N/A | N/A | N/A | N/A | 31326293 | 605 | 160.8615 | 0% | 0% | 100% | 0% | 100% | 35% | 6900956 | 1168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 93 | 8903107 | 3832 | 91.968 | 3.832 | 8.8 | 8.8 | 2B | 0 | 0 | 972 | 0 | 1000 | N/A | N/A | N/A | N/A | 31326886 | 593 | 154.7495 | 0% | 0% | 100% | 0% | 100% | 35% | 6901987 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 8906939 | 3832 | 91.968 | 3.832 | 9.5 | 9.5 | 2B | 0 | 0 | 965 | 0 | 1099 | N/A | N/A | N/A | N/A | 31327478 | 592 | 154.4885 | 0% | 0% | 100% | 0% | 100% | 35% | 6903018 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 113 | 8911428 | 4489 | 107.736 | 4.489 | 9.5 | 9.5 | 2B | 0 | 0 | 1139 | 0 | 1194 | N/A | N/A | N/A | N/A | 31328320 | 842 | 187.5696 | 0% | 0% | 100% | 0% | 100% | 0% | 6903018 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 144 | 8917386 | 5958 | 142.992 | 5.958 | 9 | 9 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31329634 | 1314 | 220.5438 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 146 | 8923436 | 6050 | 145.2 | 6.05 | 8.4 | 8.4 | 3B+1S | 0 | 1095 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31330992 | 1358 | 224.4628 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 149 | 8929781 | 6345 | 152.28 | 6.345 | 7.7 | 7.7 | 3B+1S | 0 | 1111 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31332354 | 1362 | 214.6572 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 8935698 | 5917 | 142.008 | 5.917 | 7 | 7 | 3B+1S | 0 | 1100 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31333704 | 1350 | 228.1562 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 8941940 | 6242 | 149.808 | 6.242 | 6.5 | 6.5 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31335099 | 1395 | 223.4861 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Normal operation schedule
59:00 | 12:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 140 | 8947794 | 5854 | 140.496 | 5.854 | 5.8 | 5.8 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31336434 | 1335 | 228.0492 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 137 | 8953427 | 5633 | 135.192 | 5.633 | 5.7 | 5.7 | 3B+1S | 0 | 989 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31337738 | 1304 | 231.493 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 120 | 8958958 | 5531 | 132.744 | 5.531 | 5.6 | 5.6 | 3B+1S | 0 | 989 | 1158 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31339036 | 1298 | 234.6773 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 127 | 8964670 | 5712 | 137.088 | 5.712 | 5.5 | 5.5 | 3B+1S | 0 | 989 | 1172 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31340291 | 1255 | 219.7129 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 121 | 8970000 | 5330 | 127.92 | 5.33 | 5.4 | 5.4 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 31341558 | 1267 | 237.7111 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 8975555 | 5555 | 133.32 | 5.555 | 5.3 | 5.3 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 31342834 | 1276 | 229.703 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 8981096 | 5541 | 132.984 | 5.541 | 5 | 5 | 3B+1S | 0 | 1009 | 1180 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31344059 | 1225 | 221.0792 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 124 | 137 | 8986461 | 5365 | 128.76 | 5.365 | 4.9 | 4.9 | 3B+1S | 0 | 999 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31345284 | 1225 | 228.3318 | 0% | 100% | 100% | 100% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 127 | 8991673 | 5212 | 125.088 | 5.212 | 4.2 | 4.2 | 2B+1S | 0 | 1061 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31346339 | 1055 | 202.4175 | 0% | 100% | 100% | 0% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 122 | 8996773 | 5100 | 122.4 | 5.1 | 3.5 | 3.5 | 2B+1S | 0 | 1022 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31347374 | 1035 | 202.9412 | 0% | 100% | 100% | 0% | 100% | 0% | 6903018 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 130 | 120 | 9001847 | 5074 | 121.776 | 5.074 | 3.4 | 3.4 | 2B+1S | 0 | 989 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31348368 | 994 | 195.9007 | 0% | 100% | 100% | 0% | 100% | 0% | 6903018 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 99 | 9006105 | 4258 | 102.192 | 4.258 | 3.9 | 3.9 | 2B | 0 | 0 | 1056 | 0 | 1100 | N/A | N/A | N/A | N/A | 31349083 | 715 | 167.9192 | 0% | 0% | 100% | 0% | 100% | 25% | 6903496 | 478 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 92 | 9010047 | 3942 | 94.608 | 3.942 | 4.7 | 4.7 | 2B | 0 | 0 | 1013 | 0 | 1028 | N/A | N/A | N/A | N/A | 31349728 | 645 | 163.6225 | 0% | 0% | 100% | 0% | 100% | 25% | 6904149 | 653 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.7083 | 122055 | 122055 | 122.055 | 122.055 | [12 empty] | 25250 | 25250 | 206.874 | [6 empty] | 6697 | 6697 | 0.95 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:16AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 3) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 3) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL (1.3 M)
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24822 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9010047 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31349728 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6904149 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 98 | 90 | 9013801 | 3754 | 90.096 | 3.754 | 5.7 | 5.7 | 2B | 0 | 0 | 1035 | 0 | 1048 | N/A | N/A | N/A | N/A | 31350318 | 590 | 157.1657 | 0% | 0% | 100% | 0% | 100% | 35% | 6905173 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 88 | 9017490 | 3689 | 88.536 | 3.689 | 7 | 7 | 2B | 0 | 0 | 1035 | 0 | 1048 | N/A | N/A | N/A | N/A | 31350880 | 562 | 152.3448 | 0% | 0% | 100% | 0% | 100% | 35% | 6906341 | 1168 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 85 | 9021006 | 3516 | 84.384 | 3.516 | 8.5 | 8.5 | 2B | 0 | 0 | 996 | 0 | 978 | N/A | N/A | N/A | N/A | 31351428 | 548 | 155.8589 | 0% | 0% | 100% | 0% | 100% | 35% | 6907695 | 1354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 83 | 9024281 | 3275 | 78.6 | 3.275 | 9.5 | 9.5 | 2B | 0 | 0 | 996 | 0 | 978 | N/A | N/A | N/A | N/A | 31351922 | 494 | 150.8397 | 0% | 0% | 100% | 0% | 100% | 35% | 6908810 | 1115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 93 | 9028037 | 3756 | 90.144 | 3.756 | 9.5 | 9.5 | 2B | 0 | 0 | 922 | 0 | 908 | N/A | N/A | N/A | N/A | 31352410 | 488 | 129.9255 | 0% | 0% | 100% | 0% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 111 | 9032124 | 4087 | 98.088 | 4.087 | 9.5 | 9.5 | 2B | 0 | 0 | 1083 | 0 | 1089 | N/A | N/A | N/A | N/A | 31352982 | 572 | 139.956 | 0% | 0% | 100% | 0% | 100% | 0% | 6908810 | 0 | 0.89 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 145 | 9037888 | 5764 | 138.336 | 5.764 | 9.5 | 9.5 | 2B+1S | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31354206 | 1224 | 212.3525 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 9044133 | 6245 | 149.88 | 6.245 | 9 | 9 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31355574 | 1368 | 219.0552 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 9050483 | 6350 | 152.4 | 6.35 | 8.1 | 8.1 | 3B+1S | 0 | 1160 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31356958 | 1384 | 217.9528 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 9056446 | 5963 | 143.112 | 5.963 | 7.4 | 7.4 | 3B+1S | 0 | 1128 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31358342 | 1384 | 232.0979 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 9062786 | 6340 | 152.16 | 6.34 | 6.8 | 6.8 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31359746 | 1404 | 221.4511 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 9068727 | 5941 | 142.584 | 5.941 | 6.1 | 6.1 | 3B+1S | 0 | 1100 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31361144 | 1398 | 235.3139 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 143 | 9074578 | 5851 | 140.424 | 5.851 | 5.7 | 5.7 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31362474 | 1330 | 227.3116 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 114 | 9080342 | 5764 | 138.336 | 5.764 | 5.4 | 5.4 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31363803 | 1329 | 230.569 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 9086091 | 5749 | 137.976 | 5.749 | 5.2 | 5.2 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31365124 | 1321 | 229.7791 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 9091842 | 5751 | 138.024 | 5.751 | 5.1 | 5.1 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31366466 | 1342 | 233.3507 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 9097629 | 5787 | 138.888 | 5.787 | 4.8 | 4.8 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31367816 | 1350 | 233.2815 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 129 | 9103051 | 5422 | 130.128 | 5.422 | 4.5 | 4.5 | 3B+1S | 0 | 1003 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31369053 | 1237 | 228.1446 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 127 | 9108435 | 5384 | 129.216 | 5.384 | 4.3 | 4.3 | 3B+1S | 0 | 989 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31370274 | 1221 | 226.7831 | 0% | 100% | 100% | 100% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 122 | 9113547 | 5112 | 122.688 | 5.112 | 3.7 | 3.7 | 2B+1S | 0 | 1054 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 31371287 | 1013 | 198.1612 | 0% | 100% | 100% | 0% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 118 | 9118581 | 5034 | 120.816 | 5.034 | 3.4 | 3.4 | 2B+1S | 0 | 989 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 31372273 | 986 | 195.8681 | 0% | 100% | 100% | 0% | 100% | 0% | 6908810 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 112 | 9123537 | 4956 | 118.944 | 4.956 | 3.1 | 3.1 | 2B+1S | 0 | 1081 | 1061 | 0 | 1079 | N/A | N/A | N/A | N/A | 31373252 | 979 | 197.5383 | 0% | 100% | 100% | 0% | 100% | 0% | 6908810 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 99 | 9127724 | 4187 | 100.488 | 4.187 | 3.5 | 3.5 | 2B | 0 | 0 | 1052 | 0 | 1088 | N/A | N/A | N/A | N/A | 31373942 | 690 | 164.7958 | 0% | 0% | 100% | 0% | 100% | 25% | 6909386 | 576 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 91 | 9131525 | 3801 | 91.224 | 3.801 | 4.3 | 4.3 | 2B | 0 | 0 | 1024 | 0 | 1028 | N/A | N/A | N/A | N/A | 31374550 | 608 | 159.9579 | 0% | 0% | 100% | 0% | 100% | 25% | 6910027 | 641 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.5 | 121478 | 121478 | 121.478 | 121.478 | [12 empty] | 24822 | 24822 | 204.3333 | [6 empty] | 5878 | 5878 | 0.91167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @4:16AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 5) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23658 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9131525 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31374550 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6910027 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 98 | 86 | 9135140 | 3615 | 86.76 | 3.615 | 5.3 | 5.3 | 2B | 0 | 0 | 998 | 0 | 1008 | N/A | N/A | N/A | N/A | 31375089 | 539 | 149.101 | 0% | 0% | 100% | 0% | 100% | 35% | 6911219 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 84 | 9138682 | 3542 | 85.008 | 3.542 | 6.5 | 6.5 | 2B | 0 | 0 | 998 | 0 | 1009 | N/A | N/A | N/A | N/A | 31375623 | 534 | 150.7623 | 0% | 0% | 100% | 0% | 100% | 35% | 6912571 | 1352 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 88 | 9142202 | 3520 | 84.48 | 3.52 | 7.6 | 7.6 | 2B | 0 | 0 | 968 | 0 | 1009 | N/A | N/A | N/A | N/A | 31376139 | 516 | 146.5909 | 0% | 0% | 100% | 0% | 100% | 35% | 6914139 | 1568 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 83 | 9145721 | 3519 | 84.456 | 3.519 | 8.7 | 8.7 | 2B | 0 | 0 | 969 | 0 | 1008 | N/A | N/A | N/A | N/A | 31376647 | 508 | 144.3592 | 0% | 0% | 100% | 0% | 100% | 35% | 6914974 | 835 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 86 | 9149207 | 3486 | 83.664 | 3.486 | 9.5 | 9.5 | 2B | 0 | 0 | 925 | 0 | 927 | N/A | N/A | N/A | N/A | 31377168 | 521 | 149.455 | 0% | 0% | 100% | 0% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 103 | 9153298 | 4091 | 98.184 | 4.091 | 9.5 | 9.5 | 2B | 0 | 0 | 984 | 0 | 1008 | N/A | N/A | N/A | N/A | 31377674 | 506 | 123.6861 | 0% | 0% | 100% | 0% | 100% | 0% | 6914974 | 0 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 133 | 9158539 | 5241 | 125.784 | 5.241 | 9.5 | 9.5 | 3B | 0 | 0 | 1131 | 1185 | 1110 | N/A | N/A | N/A | N/A | 31378761 | 1087 | 207.4032 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 139 | 9164038 | 5499 | 131.976 | 5.499 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31379848 | 1087 | 197.6723 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 148 | 142 | 9169936 | 5898 | 141.552 | 5.898 | 8.8 | 8.8 | 3B+1S | 0 | 1099 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31381222 | 1374 | 232.9603 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 150 | 149 | 9176053 | 6117 | 146.808 | 6.117 | 8.2 | 8.2 | 3B+1S | 0 | 1116 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31382620 | 1398 | 228.5434 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 150 | 149 | 9182309 | 6256 | 150.144 | 6.256 | 7.5 | 7.5 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31383982 | 1362 | 217.711 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 143 | 9188450 | 6141 | 147.384 | 6.141 | 6.7 | 6.7 | 3B+1S | 0 | 1160 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31385352 | 1370 | 223.0907 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 140 | 9194452 | 6002 | 144.048 | 6.002 | 6.5 | 6.5 | 3B+1S | 0 | 1011 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31386750 | 1398 | 232.9224 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 141 | 9200266 | 5814 | 139.536 | 5.814 | 6.4 | 6.4 | 3B+1S | 0 | 980 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31388054 | 1304 | 224.2862 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 9205917 | 5651 | 135.624 | 5.651 | 6.3 | 6.3 | 3B+1S | 0 | 900 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31389318 | 1264 | 223.6772 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 130 | 9211435 | 5518 | 132.432 | 5.518 | 6.2 | 6.2 | 3B+1S | 0 | 995 | 1125 | 1185 | 1150 | N/A | N/A | N/A | N/A | 31390520 | 1202 | 217.8325 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 9216797 | 5362 | 128.688 | 5.362 | 6.1 | 6.1 | 3B+1S | 0 | 995 | 1145 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31391734 | 1214 | 226.4081 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 129 | 9222106 | 5309 | 127.416 | 5.309 | 6 | 6 | 3B+1S | 0 | 977 | 1105 | 1185 | 1110 | N/A | N/A | N/A | N/A | 31392880 | 1146 | 215.8599 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 126 | 9227426 | 5320 | 127.68 | 5.32 | 5.9 | 5.9 | 3B+1S | 0 | 950 | 1105 | 1185 | 1110 | N/A | N/A | N/A | N/A | 31394030 | 1150 | 216.1654 | 0% | 100% | 100% | 100% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 121 | 9232312 | 4886 | 117.264 | 4.886 | 5.8 | 5.8 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31394994 | 964 | 197.2984 | 0% | 100% | 100% | 0% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 121 | 9237404 | 5092 | 122.208 | 5.092 | 5.5 | 5.5 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31395998 | 1004 | 197.172 | 0% | 100% | 100% | 0% | 100% | 0% | 6914974 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 115 | 9242335 | 4931 | 118.344 | 4.931 | 5.4 | 5.4 | 2B+1S | 0 | 1021 | 1090 | 0 | 1099 | N/A | N/A | N/A | N/A | 31396930 | 932 | 189.0083 | 0% | 100% | 100% | 0% | 100% | 0% | 6914974 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 95 | 9246414 | 4079 | 97.896 | 4.079 | 5.9 | 5.9 | 2B | 0 | 0 | 1054 | 0 | 1068 | N/A | N/A | N/A | N/A | 31397614 | 684 | 167.6882 | 0% | 0% | 100% | 0% | 100% | 30% | 6915559 | 585 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 89 | 9250198 | 3784 | 90.816 | 3.784 | 6.7 | 6.7 | 2B | 0 | 0 | 1002 | 0 | 1008 | N/A | N/A | N/A | N/A | 31398208 | 594 | 156.9767 | 0% | 0% | 100% | 0% | 100% | 30% | 6916336 | 777 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.3333 | 118673 | 118673 | 118.673 | 118.673 | [12 empty] | 23658 | 23658 | 199.3545 | [6 empty] | 6309 | 6309 | 0.93667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 5) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24782 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9250198 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31398208 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6916336 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 102 | 92 | 9253960 | 3762 | 90.288 | 3.762 | 7.6 | 7.6 | 2B | 0 | 0 | 1056 | 0 | 998 | N/A | N/A | N/A | N/A | 31398790 | 582 | 154.7049 | 0% | 0% | 100% | 0% | 100% | 30% | 6917117 | 781 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 89 | 9257720 | 3760 | 90.24 | 3.76 | 8.3 | 8.3 | 2B | 0 | 0 | 1014 | 0 | 998 | N/A | N/A | N/A | N/A | 31399354 | 564 | 150 | 0% | 0% | 100% | 0% | 100% | 30% | 6917913 | 796 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 90 | 9261475 | 3755 | 90.12 | 3.755 | 9.1 | 9.1 | 2B | 0 | 0 | 989 | 0 | 998 | N/A | N/A | N/A | N/A | 31399893 | 539 | 143.5419 | 0% | 0% | 100% | 0% | 100% | 30% | 6918861 | 948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 86 | 9265224 | 3749 | 89.976 | 3.749 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 0 | 978 | N/A | N/A | N/A | N/A | 31400404 | 511 | 136.303 | 0% | 0% | 100% | 0% | 100% | 30% | 6919029 | 168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 85 | 9268964 | 3740 | 89.76 | 3.74 | 9.5 | 9.5 | 2B | 0 | 0 | 881 | 0 | 877 | N/A | N/A | N/A | N/A | 31400866 | 462 | 123.5294 | 0% | 0% | 100% | 0% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 105 | 9273081 | 4117 | 98.808 | 4.117 | 9.5 | 9.5 | 2B | 0 | 0 | 1028 | 0 | 1014 | N/A | N/A | N/A | N/A | 31401360 | 494 | 119.9903 | 0% | 0% | 100% | 0% | 100% | 0% | 6919029 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 135 | 9278327 | 5246 | 125.904 | 5.246 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1150 | N/A | N/A | N/A | N/A | 31402549 | 1189 | 226.6489 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 9284016 | 5689 | 136.536 | 5.689 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31403708 | 1159 | 203.7265 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 149 | 148 | 9290324 | 6308 | 151.392 | 6.308 | 9 | 9 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31405086 | 1378 | 218.4528 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 149 | 148 | 9296660 | 6336 | 152.064 | 6.336 | 8.4 | 8.4 | 3B+1S | 0 | 1133 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31406450 | 1364 | 215.2778 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 152 | 150 | 9302672 | 6012 | 144.288 | 6.012 | 7.5 | 7.5 | 3B+1S | 0 | 1133 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31407808 | 1358 | 225.8816 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 152 | 153 | 9308831 | 6159 | 147.816 | 6.159 | 6.6 | 6.6 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31409166 | 1358 | 220.4903 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 144 | 142 | 9314882 | 6051 | 145.224 | 6.051 | 5.9 | 5.9 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31410552 | 1386 | 229.053 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 142 | 9320835 | 5953 | 142.872 | 5.953 | 5.6 | 5.6 | 3B+1S | 0 | 1034 | 1199 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31411910 | 1358 | 228.1203 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 139 | 9326772 | 5937 | 142.488 | 5.937 | 5.4 | 5.4 | 3B+1S | 0 | 992 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31413266 | 1356 | 228.3982 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 9332384 | 5612 | 134.688 | 5.612 | 5.4 | 5.4 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31414554 | 1288 | 229.5082 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 9338064 | 5680 | 136.32 | 5.68 | 4.9 | 4.9 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31415876 | 1322 | 232.7465 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 131 | 9343744 | 5680 | 136.32 | 5.68 | 4.6 | 4.6 | 3B+1S | 0 | 1008 | 1165 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31417198 | 1322 | 232.7465 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 9349393 | 5649 | 135.576 | 5.649 | 4.3 | 4.3 | 3B+1S | 0 | 1023 | 1165 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31418508 | 1310 | 231.8995 | 0% | 100% | 100% | 100% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 9354748 | 5355 | 128.52 | 5.355 | 3.3 | 3.3 | 2B+1S | 0 | 1128 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31419598 | 1090 | 203.5481 | 0% | 100% | 100% | 0% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 9360068 | 5320 | 127.68 | 5.32 | 2.6 | 2.6 | 2B+1S | 0 | 1055 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31420666 | 1068 | 200.7519 | 0% | 100% | 100% | 0% | 100% | 0% | 6919029 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 113 | 9365061 | 4993 | 119.832 | 4.993 | 2.4 | 2.4 | 2B+1S | 0 | 720 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31421638 | 972 | 194.6725 | 0% | 100% | 100% | 0% | 100% | 0% | 6919029 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 |  | 9369364 | 4303 | 103.272 | 4.303 | 3.2 | 3.2 | 2B | 0 | 0 | 1043 | 0 | 1110 | N/A | N/A | N/A | N/A | 31422374 | 736 | 171.0435 | 0% | 0% | 100% | 0% | 100% | 30% | 6919757 | 728 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 |  | 9373094 | 3730 | 89.52 | 3.73 | 4.2 | 4.2 | 2B | 0 | 0 | 935 | 0 | 1110 | N/A | N/A | N/A | N/A | 31422990 | 616 | 165.1475 | 0% | 0% | 100% | 0% | 100% | 30% | 6920645 | 888 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.1364 | 122896 | 122896 | 122.896 | 122.896 | [12 empty] | 24782 | 24782 | 201.6502 | [6 empty] | 4309 | 4309 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 6) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:26 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 7) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NOTE: FLOW METER OF 900MM LINE IS NOT WORKING AS OF 10:10PM. NEED FOR INSPECTION.
NORMAL OPERATION

## OCT 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24734 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9373094 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31422990 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6920645 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 |  | 9376686 | 3592 | 86.208 | 3.592 | 5.5 | 5.5 | 2B | 0 | 0 | 961 | 0 | 1110 | N/A | N/A | N/A | N/A | 31423600 | 610 | 169.8218 | 0% | 0% | 100% | 0% | 100% | 35% | 6921925 | 1280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 |  | 9380231 | 3545 | 85.08 | 3.545 | 6.9 | 6.9 | 2B | 0 | 0 | 940 | 0 | 1110 | N/A | N/A | N/A | N/A | 31424186 | 586 | 165.3032 | 0% | 0% | 100% | 0% | 100% | 35% | 6923283 | 1358 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 |  | 9383783 | 3552 | 85.248 | 3.552 | 8.4 | 8.4 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 31424766 | 580 | 163.2883 | 0% | 0% | 100% | 0% | 100% | 35% | 6924603 | 1320 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 |  | 9387331 | 3548 | 85.152 | 3.548 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 970 | N/A | N/A | N/A | N/A | 31425298 | 532 | 149.9436 | 0% | 0% | 100% | 0% | 100% | 35% | 6925710 | 1107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 |  | 9391235 | 3904 | 93.696 | 3.904 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 1010 | N/A | N/A | N/A | N/A | 31425806 | 508 | 130.123 | 0% | 0% | 100% | 0% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 |  | 9396037 | 4802 | 115.248 | 4.802 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1175 | N/A | N/A | N/A | N/A | 31426588 | 782 | 162.8488 | 0% | 0% | 100% | 0% | 100% | 0% | 6925710 | 0 | 0.89 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 |  | 9401828 | 5791 | 138.984 | 5.791 | 9.2 | 9.2 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31427878 | 1290 | 222.7595 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 |  | 9407924 | 6096 | 146.304 | 6.096 | 8.8 | 8.8 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31429234 | 1356 | 222.4409 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 |  | 9414139 | 6215 | 149.16 | 6.215 | 8.2 | 8.2 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31430586 | 1352 | 217.5382 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 |  | 9420105 | 5966 | 143.184 | 5.966 | 7.6 | 7.6 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31431948 | 1362 | 228.2937 | 0% |  | 100% | 100% | 100% | 0% | 6925710 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 |  | 9426116 | 6011 | 144.264 | 6.011 | 7.1 | 7.1 | 3B+1S | 0 | 1083 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31433328 | 1380 | 229.5791 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 |  | 9432012 | 5896 | 141.504 | 5.896 | 6.6 | 6.6 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31434698 | 1370 | 232.3609 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 |  | 9437885 | 5873 | 140.952 | 5.873 | 6.5 | 6.5 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31436052 | 1354 | 230.5466 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 |  | 9443277 | 5392 | 129.408 | 5.392 | 6.4 | 6.4 | 3B+1S | 0 | 1013 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31437278 | 1226 | 227.3739 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 |  | 9448755 | 5478 | 131.472 | 5.478 | 6.3 | 6.3 | 3B+1S | 0 | 999 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 31438532 | 1254 | 228.9157 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 |  | 9454267 | 5512 | 132.288 | 5.512 | 6.1 | 6.1 | 3B+1S | 0 | 994 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31439796 | 1264 | 229.3179 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 |  | 9459836 | 5569 | 133.656 | 5.569 | 5.8 | 5.8 | 3B+1S | 0 | 1058 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31441074 | 1278 | 229.4846 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 120 |  | 9465325 | 5489 | 131.736 | 5.489 | 5 | 5 | 2B+1S | 0 | 1164 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31442190 | 1116 | 203.3157 | 0% | 100% | 100% | 100% | 100% | 0% | 6925710 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 |  | 9470740 | 5415 | 129.96 | 5.415 | 4 | 4 | 2B+1S | 0 | 1151 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31443306 | 1116 | 206.0942 | 0% | 100% | 100% | 0% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 |  | 9475988 | 5248 | 125.952 | 5.248 | 3.2 | 3.2 | 2B+1S | 0 | 1069 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31444346 | 1040 | 198.1707 | 0% | 100% | 100% | 0% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 |  | 9481083 | 5095 | 122.28 | 5.095 | 2.7 | 2.7 | 2B+1S | 0 | 1064 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31445386 | 1040 | 204.1217 | 0% | 100% | 100% | 0% | 100% | 0% | 6925710 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 |  | 9486016 | 4933 | 118.392 | 4.933 | 2.5 | 2.5 | 2B+1S | 0 | 1000 | 1156 | 0 | 1159 | N/A | N/A | N/A | N/A | 31446364 | 978 | 198.2566 | 0% | 100% | 100% | 0% | 100% | 0% | 6925710 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 |  | 9490174 | 4158 | 99.792 | 4.158 | 3.3 | 3.3 | 2B | 0 | 0 | 1065 | 0 | 1079 | N/A | N/A | N/A | N/A | 31447074 | 710 | 170.7552 | 0% | 0% | 100% | 0% | 100% | 30% | 6926522 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 |  | 9494153 | 3979 | 95.496 | 3.979 | 4.4 | 4.4 | 2B | 0 | 0 | 1017 | 0 | 1037 | N/A | N/A | N/A | N/A | 31447724 | 650 | 163.3576 | 0% | 0% | 100% | 0% | 100% | 30% | 6927411 | 889 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 121059 | 121059 | 121.059 | 121.059 | [12 empty] | 24734 | 24734 | 204.3136 | [6 empty] | 6766 | 6766 | 0.91 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
NOTE: FLOW METER OF 900MM LINE IS NOT WORKING. NEED FOR INSPECTION.
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 6) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
I.M.S. AUDIT ARRIVED @ 1:15 PM
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:20 PM TO 4:30 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:31PM TO 4:41 PM FOR 10 MINUTES RUN
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:38 PM, NORMAL OPERATION
BP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23776 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9494153 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31447724 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6927411 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 |  | 9497566 | 3413 | 81.912 | 3.413 | 5.4 | 5.4 | 2B | 0 | 0 | 1016 | 0 | 1018 | N/A | N/A | N/A | N/A | 31448282 | 558 | 163.4925 | 0% | 0% | 100% | 0% | 100% | 35% | 6928415 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 |  | 9501107 | 3541 | 84.984 | 3.541 | 6.5 | 6.5 | 2B | 0 | 0 | 989 | 0 | 988 | N/A | N/A | N/A | N/A | 31448814 | 532 | 150.24 | 0% | 0% | 100% | 0% | 100% | 35% | 6929781 | 1366 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 |  | 9504664 | 3557 | 85.368 | 3.557 | 7.8 | 7.8 | 2B | 0 | 0 | 986 | 0 | 988 | N/A | N/A | N/A | N/A | 31449341 | 527 | 148.1586 | 0% | 0% | 100% | 0% | 100% | 35% | 6931147 | 1366 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 |  | 9508215 | 3551 | 85.224 | 3.551 | 9.5 | 9.5 | 2B | 0 | 0 | 885 | 0 | 987 | N/A | N/A | N/A | N/A | 31449846 | 505 | 142.2135 | 0% | 0% | 100% | 0% | 100% | 35% | 6932513 | 1366 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 |  | 9511727 | 3512 | 84.288 | 3.512 | 9.5 | 9.5 | 2B | 0 | 0 | 991 | 0 | 989 | N/A | N/A | N/A | N/A | 31450318 | 472 | 134.3964 | 0% | 0% | 100% | 0% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 |  | 9516341 | 4614 | 110.736 | 4.614 | 9.5 | 9.5 | 2B | 0 | 0 | 1180 | 0 | 1199 | N/A | N/A | N/A | N/A | 31451070 | 752 | 162.9822 | 0% | 0% | 100% | 0% | 100% | 0% | 6932513 | 0 | 0.88 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 124 |  | 9522156 | 5815 | 139.56 | 5.815 | 9 | 9 | 3B+1S | 0 | 1007 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31452382 | 1312 | 225.6234 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 |  | 9528143 | 5987 | 143.688 | 5.987 | 8.7 | 8.7 | 3B+1S | 0 | 1053 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31453710 | 1328 | 221.8139 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 126 |  | 9534067 | 5924 | 142.176 | 5.924 | 8.1 | 8.1 | 3B+1S | 0 | 1053 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31455095 | 1385 | 233.7947 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 |  | 9540004 | 5937 | 142.488 | 5.937 | 7.5 | 7.5 | 3B+1S | 0 | 1053 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31456430 | 1335 | 224.861 | 0% |  | 100% | 100% | 100% | 0% | 6932513 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 |  | 9546002 | 5998 | 143.952 | 5.998 | 7 | 7 | 3B+1S | 0 | 1004 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31457752 | 1322 | 220.4068 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 |  | 9551899 | 5897 | 141.528 | 5.897 | 6.7 | 6.7 | 3B+1S | 0 | 1075 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31459082 | 1330 | 225.5384 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 |  | 9557489 | 5590 | 134.16 | 5.59 | 6.5 | 6.5 | 3B+1S | 0 | 999 | 1154 | 1185 | 1154 | N/A | N/A | N/A | N/A | 31460334 | 1252 | 223.9714 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 120 |  | 9562873 | 5384 | 129.216 | 5.384 | 6.5 | 6.5 | 3B+1S | 0 | 1017 | 1053 | 1185 | 1109 | N/A | N/A | N/A | N/A | 31461512 | 1178 | 218.7964 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 17 | 11.9718 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 121 |  | 9568200 | 5327 | 127.848 | 5.327 | 6.1 | 6.1 | 3B+1S | 0 | 1015 | 1054 | 1185 | 1109 | N/A | N/A | N/A | N/A | 31462642 | 1130 | 212.1269 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 17 | 11.9718 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 116 |  | 9573431 | 5231 | 125.544 | 5.231 | 5.8 | 5.8 | 3B+1S | 0 | 1035 | 1054 | 1185 | 1109 | N/A | N/A | N/A | N/A | 31463768 | 1126 | 215.2552 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 |  | 9578662 | 5231 | 125.544 | 5.231 | 5.4 | 5.4 | 3B+1S | 0 | 1051 | 1104 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31464894 | 1126 | 215.2552 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 14 | 9.8592 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 114 |  | 9583498 | 4836 | 116.064 | 4.836 | 4.8 | 4.8 | 3B+1S | 0 | 1058 | 1053 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31466038 | 1144 | 236.5591 | 0% | 100% | 100% | 100% | 100% | 0% | 6932513 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 120 |  | 9589503 | 6005 | 144.12 | 6.005 | 4.1 | 4.1 | 3B+1S | 0 | 1039 | 1105 | 1185 | 1108 | N/A | N/A | N/A | N/A | 31467234 | 1196 | 199.1674 | 0% | 100% | 100% | 0% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 |  | 9594651 | 5148 | 123.552 | 5.148 | 3.5 | 3.5 | 2B+1S | 0 | 1044 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 31468262 | 1028 | 199.6892 | 0% | 100% | 100% | 0% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 |  | 9599800 | 5149 | 123.576 | 5.149 | 3.1 | 3.1 | 2B+1S | 0 | 1004 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31469288 | 1026 | 199.262 | 0% | 100% | 100% | 0% | 100% | 0% | 6932513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 19 | 13.3803 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 |  | 9604614 | 4814 | 115.536 | 4.814 | 2.9 | 2.9 | 2B+1S | 0 | 801 | 1195 | 0 | 1110 | N/A | N/A | N/A | N/A | 31470232 | 944 | 196.0947 | 0% | 100% | 100% | 0% | 100% | 0% | 6932513 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 |  | 9608387 | 3773 | 90.552 | 3.773 | 4.1 | 4.1 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 31470866 | 634 | 168.036 | 0% | 0% | 100% | 0% | 100% | 25% | 6933420 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 |  | 9612160 | 3773 | 90.552 | 3.773 | 5 | 5 | 2B | 0 | 0 | 1026 | 0 | 1109 | N/A | N/A | N/A | N/A | 31471500 | 634 | 168.036 | 0% | 0% | 100% | 0% | 100% | 25% | 6934327 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 118007 | 118007 | 118.007 | 118.007 | [12 empty] | 23776 | 23776 | 201.4796 | [6 empty] | 6916 | 6916 | 0.915 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
XCV1 FAULT @ 5:08 AM NO HOURLY MONITORING RECORD @ FLOWRATE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 8) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 8) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9612160 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31471500 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6934327 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 |  | 9615933 | 3773 | 90.552 | 3.773 | 6.1 | 6.1 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31472134 | 634 | 168.036 | 0% | 0% | 100% | 0% | 100% | 35% | 6935234 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 |  | 9619444 | 3511 | 84.264 | 3.511 | 7.3 | 7.3 | 2B | 0 | 0 | 1034 | 0 | 1008 | N/A | N/A | N/A | N/A | 31472674 | 540 | 153.8023 | 0% | 0% | 100% | 0% | 100% | 35% | 6936080 | 846 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 |  | 9622955 | 3511 | 84.264 | 3.511 | 8.4 | 8.4 | 2B | 0 | 0 | 891 | 0 | 1100 | N/A | N/A | N/A | N/A | 31473213 | 539 | 153.5175 | 0% | 0% | 100% | 0% | 100% | 35% | 6936926 | 846 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 |  | 9626466 | 3511 | 84.264 | 3.511 | 9.5 | 9.5 | 2B | 0 | 0 | 787 | 0 | 1069 | N/A | N/A | N/A | N/A | 31473751 | 538 | 153.2327 | 0% | 0% | 100% | 0% | 100% | 35% | 6937772 | 846 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 |  | 9629977 | 3511 | 84.264 | 3.511 | 9.5 | 9.5 | 2B | 0 | 0 | 889 | 0 | 1069 | N/A | N/A | N/A | N/A | 31474290 | 539 | 153.5175 | 0% | 0% | 100% | 0% | 100% | 35% | 6938618 | 846 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 120 |  | 9634660 | 4683 | 112.392 | 4.683 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1155 | 0 | 1170 | N/A | N/A | N/A | N/A | 31475018 | 728 | 155.4559 | 0% | 0% | 100% | 0% | 100% | 0% | 6938618 | 0 | 1.12 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 |  | 9640580 | 5920 | 142.08 | 5.92 | 9.3 | 9.3 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31476340 | 1322 | 223.3108 | 0% | 0% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 |  | 9646632 | 6052 | 145.248 | 6.052 | 8.7 | 8.7 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31477714 | 1374 | 227.0324 | 0% | 0% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 |  | 9652953 | 6321 | 151.704 | 6.321 | 7.8 | 7.8 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31479080 | 1366 | 216.105 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 |  | 9658919 | 5966 | 143.184 | 5.966 | 7.1 | 7.1 | 3B+1S | 0 | 1128 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31480504 | 1424 | 238.6859 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 |  | 9665129 | 6210 | 149.04 | 6.21 | 6.3 | 6.3 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31481926 | 1422 | 228.9855 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 |  | 9671036 | 5907 | 141.768 | 5.907 | 5.9 | 5.9 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31483270 | 1344 | 227.5267 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 |  | 9676767 | 5731 | 137.544 | 5.731 | 5.7 | 5.7 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31484578 | 1308 | 228.2324 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 |  | 9682264 | 5497 | 131.928 | 5.497 | 5.6 | 5.6 | 3B+1S | 0 | 1009 | 1113 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31485800 | 1222 | 222.3031 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 |  | 9687669 | 5405 | 129.72 | 5.405 | 5.3 | 5.3 | 3B+1S | 0 | 1020 | 1104 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31487006 | 1206 | 223.1267 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 |  | 9692980 | 5311 | 127.464 | 5.311 | 5.1 | 5.1 | 3B+1S | 0 | 1016 | 1104 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31488190 | 1184 | 222.9335 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 117 |  | 9698393 | 5413 | 129.912 | 5.413 | 4.6 | 4.6 | 3B+1S | 0 | 1099 | 1103 | 1185 | 1129 | N/A | N/A | N/A | N/A | 31489388 | 1198 | 221.319 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 119 |  | 9703856 | 5463 | 131.112 | 5.463 | 4 | 4 | 3B+1S | 0 | 1068 | 1104 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31490579 | 1191 | 218.0121 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 121 |  | 9709320 | 5464 | 131.136 | 5.464 | 3.4 | 3.4 | 3B+1S | 0 | 1058 | 1104 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31491774 | 1195 | 218.7042 | 0% | 100% | 100% | 100% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 |  | 9714743 | 5423 | 130.152 | 5.423 | 2.6 | 2.6 | 2B+1S | 0 | 1097 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 31492863 | 1089 | 200.8114 | 0% | 100% | 100% | 0% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 |  | 9719889 | 5146 | 123.504 | 5.146 | 2 | 2 | 2B+1S | 0 | 1039 | 1197 | 0 | 1190 | N/A | N/A | N/A | N/A | 31493886 | 1023 | 198.7952 | 0% | 100% | 100% | 0% | 100% | 0% | 6938618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 |  | 9725483 | 5594 | 134.256 | 5.594 | 1.8 | 1.8 | 2B+1S | 0 | 899 | 1153 | 0 | 1159 | N/A | N/A | N/A | N/A | 31494978 | 1092 | 195.2092 | 0% | 100% | 100% | 0% | 100% | 0% | 6938618 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 |  | 9729231 | 3748 | 89.952 | 3.748 | 2.3 | 2.3 | 2B | 0 | 0 | 1065 | 0 | 1079 | N/A | N/A | N/A | N/A | 31495642 | 664 | 177.1612 | 0% | 0% | 100% | 0% | 100% | 30% | 6939191 | 573 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 |  | 9733085 | 3854 | 92.496 | 3.854 | 3.3 | 3.3 | 2B | 0 | 0 | 1007 | 0 | 1018 | N/A | N/A | N/A | N/A | 31496268 | 626 | 162.4286 | 0% | 0% | 100% | 0% | 100% | 30% | 6940128 | 937 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 120925 | 120925 | 120.925 | 120.925 | [12 empty] | 24768 | 24768 | 204.8212 | [6 empty] | 5801 | 5801 | 0.97667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @3:59AM,WATER ELEVATION 9.5M
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 10) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 8) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24699 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9733085 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31496268 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6940128 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 |  | 9737615 | 4530 | 108.72 | 4.53 | 4.6 | 4.6 | 2B | 0 | 0 | 1019 | 0 | 1028 | N/A | N/A | N/A | N/A | 31496854 | 586 | 129.3598 | 0% | 0% | 100% | 0% | 100% | 35% | 6941280 | 1152 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 |  | 9741036 | 3421 | 82.104 | 3.421 | 5.7 | 5.7 | 2B | 0 | 0 | 998 | 0 | 999 | N/A | N/A | N/A | N/A | 31497416 | 562 | 164.2795 | 0% | 0% | 100% | 0% | 100% | 35% | 6942448 | 1168 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 |  | 9744434 | 3398 | 81.552 | 3.398 | 7.1 | 7.1 | 2B | 0 | 0 | 999 | 0 | 999 | N/A | N/A | N/A | N/A | 31497953 | 537 | 158.0341 | 0% | 0% | 100% | 0% | 100% | 35% | 6943637 | 1189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 106 |  | 9747805 | 3371 | 80.904 | 3.371 | 8.6 | 8.6 | 2B | 0 | 0 | 999 | 0 | 998 | N/A | N/A | N/A | N/A | 31498475 | 522 | 154.8502 | 0% | 0% | 100% | 0% | 100% | 35% | 6944822 | 1185 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 |  | 9751127 | 3322 | 79.728 | 3.322 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 999 | N/A | N/A | N/A | N/A | 31498966 | 491 | 147.8025 | 0% | 0% | 100% | 0% | 100% | 35% | 6945931 | 1109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 |  | 9755782 | 4655 | 111.72 | 4.655 | 9.5 | 9.5 | 2B | 0 | 0 | 1172 | 0 | 1180 | N/A | N/A | N/A | N/A | 31499702 | 736 | 158.1096 | 0% | 0% | 100% | 0% | 100% | 0% | 6945931 | 0 | 0.98 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 128 |  | 9761771 | 5989 | 143.736 | 5.989 | 9.1 | 9.1 | 3B+1S | 0 | 1005 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31501058 | 1356 | 226.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 |  | 9767809 | 6038 | 144.912 | 6.038 | 8.5 | 8.5 | 3B+1S | 0 | 1071 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31502426 | 1368 | 226.5651 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 |  | 9773812 | 6003 | 144.072 | 6.003 | 7.6 | 7.6 | 3B+1S | 0 | 1125 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31503796 | 1370 | 228.2192 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 |  | 9779827 | 6015 | 144.36 | 6.015 | 7 | 7 | 3B+1S | 0 | 1078 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31505176 | 1380 | 229.4264 | 0% |  | 100% | 100% | 100% | 0% | 6945931 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 |  | 9785648 | 5821 | 139.704 | 5.821 | 6.4 | 6.4 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31506506 | 1330 | 228.4831 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 |  | 9791680 | 6032 | 144.768 | 6.032 | 5.8 | 5.8 | 3B+1S | 0 | 1067 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31507898 | 1392 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 |  | 9797403 | 5723 | 137.352 | 5.723 | 5.6 | 5.6 | 3B+1S | 0 | 1004 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31509222 | 1324 | 231.3472 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 124 |  | 9803023 | 5620 | 134.88 | 5.62 | 5.4 | 5.4 | 3B+1S | 0 | 1033 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31510510 | 1288 | 229.1815 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 124 |  | 9808448 | 5425 | 130.2 | 5.425 | 5.1 | 5.1 | 3B+1S | 0 | 1030 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31511718 | 1208 | 222.6728 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 |  | 9813810 | 5362 | 128.688 | 5.362 | 4.9 | 4.9 | 3B+1S | 0 | 1023 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31512918 | 1200 | 223.7971 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 |  | 9819300 | 5490 | 131.76 | 5.49 | 4.3 | 4.3 | 3B+1S | 0 | 1058 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31514164 | 1246 | 226.9581 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 111 |  | 9824795 | 5495 | 131.88 | 5.495 | 3.3 | 3.3 | 2B+1S | 0 | 1169 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31515290 | 1126 | 204.9136 | 0% | 100% | 100% | 100% | 100% | 0% | 6945931 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 |  | 9830378 | 5583 | 133.992 | 5.583 | 2.4 | 2.4 | 2B+1S | 0 | 1131 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31516428 | 1138 | 203.8331 | 0% | 100% | 100% | 0% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 |  | 9835442 | 5064 | 121.536 | 5.064 | 1.8 | 1.8 | 2B+1S | 0 | 1053 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31517434 | 1006 | 198.6572 | 0% | 100% | 100% | 0% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 124 |  | 9840640 | 5198 | 124.752 | 5.198 | 1.8 | 1.8 | 3B | 0 | 0 | 1025 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31518526 | 1092 | 210.0808 | 0% | 100% | 100% | 0% | 100% | 0% | 6945931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 |  | 9845560 | 4920 | 118.08 | 4.92 | 1.8 | 1.8 | 3B | 0 | 0 | 959 | 0 | 1118 | N/A | N/A | N/A | N/A | 31519550 | 1024 | 208.1301 | 0% | 100% | 100% | 0% | 100% | 0% | 6945931 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 |  | 9849746 | 4186 | 100.464 | 4.186 | 2.6 | 2.6 | 2B | 0 | 0 | 1077 | 0 | 1079 | N/A | N/A | N/A | N/A | 31520286 | 736 | 175.8242 | 0% | 0% | 100% | 0% | 100% | 30% | 6946754 | 823 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 |  | 9853820 | 4074 | 97.776 | 4.074 | 4.1 | 4.1 | 2B | 0 | 0 | 1027 | 0 | 1048 | N/A | N/A | N/A | N/A | 31520967 | 681 | 167.1576 | 0% | 0% | 100% | 0% | 100% | 30% | 6948187 | 1433 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 120735 | 120735 | 120.735 | 120.735 | [12 empty] | 24699 | 24699 | 204.572 | [6 empty] | 8059 | 8059 | 0.945 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 10) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 PM, NORMAL OPERATION
BP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
BP2 - RESTARTED @ 8:01 PM
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 7) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25385 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9853820 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31520967 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6948187 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 |  | 9857820 | 4000 | 96 | 4 | 5.1 | 5.1 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 31521584 | 617 | 154.25 | 0% | 0% | 100% | 0% | 100% | 35% | 6949169 | 982 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 |  | 9860874 | 3054 | 73.296 | 3.054 | 6.2 | 6.2 | 2B | 0 | 0 | 993 | 0 | 998 | N/A | N/A | N/A | N/A | 31522068 | 484 | 158.4807 | 0% | 0% | 100% | 0% | 100% | 35% | 6950165 | 996 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 |  | 9864462 | 3588 | 86.112 | 3.588 | 7.4 | 7.4 | 2B | 0 | 0 | 984 | 0 | 988 | N/A | N/A | N/A | N/A | 31522593 | 525 | 146.3211 | 0% | 0% | 100% | 0% | 100% | 35% | 6951394 | 1229 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 |  | 9868032 | 3570 | 85.68 | 3.57 | 8.9 | 8.9 | 2B | 0 | 0 | 985 | 0 | 988 | N/A | N/A | N/A | N/A | 31523112 | 519 | 145.3782 | 0% | 0% | 100% | 0% | 100% | 35% | 6952722 | 1328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 |  | 9871621 | 3589 | 86.136 | 3.589 | 9.5 | 9.5 | 2B | 0 | 0 | 970 | 0 | 977 | N/A | N/A | N/A | N/A | 31523588 | 476 | 132.6275 | 0% | 0% | 100% | 0% | 100% | 0% | 6953227 | 505 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 |  | 9876377 | 4756 | 114.144 | 4.756 | 9.5 | 9.5 | 2B | 0 | 0 | 1082 | 0 | 1088 | N/A | N/A | N/A | N/A | 31524274 | 686 | 144.2389 | 0% | 0% | 100% | 0% | 100% | 0% | 6953227 | 0 | 1.06 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 120 |  | 9881428 | 5051 | 121.224 | 5.051 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31525398 | 1124 | 222.5302 | 0% | 0% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 |  | 9887552 | 6124 | 146.976 | 6.124 | 9.1 | 9.1 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31526776 | 1378 | 225.0163 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 |  | 9893767 | 6215 | 149.16 | 6.215 | 8.2 | 8.2 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31528164 | 1388 | 223.3307 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 |  | 9900111 | 6344 | 152.256 | 6.344 | 7.6 | 7.6 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31529548 | 1384 | 218.1589 | 0% |  | 100% | 100% | 100% | 0% | 6953227 | 0 | 1 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 |  | 9906294 | 6183 | 148.392 | 6.183 | 6.7 | 6.7 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31530938 | 1390 | 224.81 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 |  | 9913030 | 6736 | 161.664 | 6.736 | 6 | 6 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31532330 | 1392 | 206.6508 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 |  | 9918496 | 5466 | 131.184 | 5.466 | 5.4 | 5.4 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31533726 | 1396 | 255.397 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 |  | 9924564 | 6068 | 145.632 | 6.068 | 5 | 5 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31535112 | 1386 | 228.4113 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 |  | 9930639 | 6075 | 145.8 | 6.075 | 4.6 | 4.6 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31536482 | 1370 | 225.5144 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 |  | 9936251 | 5612 | 134.688 | 5.612 | 4.5 | 4.5 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31537788 | 1306 | 232.7156 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 |  | 9941968 | 5717 | 137.208 | 5.717 | 4.4 | 4.4 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31539106 | 1318 | 230.5405 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 |  | 9947587 | 5619 | 134.856 | 5.619 | 4.2 | 4.2 | 3B+1S | 0 | 990 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31540410 | 1304 | 232.0698 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 |  | 9953110 | 5523 | 132.552 | 5.523 | 4.1 | 4.1 | 3B+1S | 0 | 990 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31541710 | 1300 | 235.3793 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 |  | 9958521 | 5411 | 129.864 | 5.411 | 4 | 4 | 3B+1S | 0 | 950 | 1114 | 1185 | 1160 | N/A | N/A | N/A | N/A | 31542924 | 1214 | 224.3578 | 0% | 100% | 100% | 100% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 |  | 9963694 | 5173 | 124.152 | 5.173 | 3.7 | 3.7 | 2B+1S | 0 | 1010 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31543958 | 1034 | 199.884 | 0% | 100% | 100% | 0% | 100% | 0% | 6953227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 |  | 9968679 | 4985 | 119.64 | 4.985 | 3.5 | 3.5 | 2B+1S | 0 | 980 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31544946 | 988 | 198.1946 | 0% | 100% | 100% | 0% | 100% | 0% | 6953227 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 |  | 9973007 | 4328 | 103.872 | 4.328 | 3.9 | 3.9 | 2B | 0 | 0 | 1063 | 0 | 1110 | N/A | N/A | N/A | N/A | 31545698 | 752 | 173.7523 | 0% | 0% | 100% | 0% | 100% | 25% | 6953672 | 445 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 |  | 9976992 | 3985 | 95.64 | 3.985 | 4.6 | 4.6 | 2B | 0 | 0 | 974 | 0 | 1110 | N/A | N/A | N/A | N/A | 31546352 | 654 | 164.1154 | 0% | 0% | 100% | 0% | 100% | 25% | 6954274 | 602 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 123172 | 123172 | 123.172 | 123.172 | [12 empty] | 25385 | 25385 | 206.0939 | [6 empty] | 6087 | 6087 | 1.0367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT11) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 12) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 12) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24550 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9976992 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31546352 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6954274 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 |  | 9980712 | 3720 | 89.28 | 3.72 | 5.4 | 5.4 | 2B | 0 | 0 | 1014 | 0 | 1060 | N/A | N/A | N/A | N/A | 31546968 | 616 | 165.5914 | 0% | 0% | 100% | 0% | 100% | 35% | 6955224 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 |  | 9984285 | 3573 | 85.752 | 3.573 | 6.6 | 6.6 | 2B | 0 | 0 | 975 | 0 | 1060 | N/A | N/A | N/A | N/A | 31547542 | 574 | 160.6493 | 0% | 0% | 100% | 0% | 100% | 35% | 6956261 | 1037 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 |  | 9987894 | 3609 | 86.616 | 3.609 | 7.8 | 7.8 | 2B | 0 | 0 | 952 | 0 | 1060 | N/A | N/A | N/A | N/A | 31548106 | 564 | 156.276 | 0% | 0% | 100% | 0% | 100% | 35% | 6957328 | 1067 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 |  | 9991407 | 3513 | 84.312 | 3.513 | 8.9 | 8.9 | 2B | 0 | 0 | 910 | 0 | 1060 | N/A | N/A | N/A | N/A | 31548642 | 536 | 152.5761 | 0% | 0% | 100% | 0% | 100% | 35% | 6958406 | 1078 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 |  | 9994922 | 3515 | 84.36 | 3.515 | 9.5 | 9.5 | 2B | 0 | 0 | 898 | 0 | 1010 | N/A | N/A | N/A | N/A | 31549108 | 466 | 132.5747 | 0% | 0% | 100% | 0% | 100% | 35% | 6958933 | 527 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 |  | 9999023 | 4101 | 98.424 | 4.101 | 9.5 | 9.5 | 2B | 0 | 0 | 1170 | 0 | 1030 | N/A | N/A | N/A | N/A | 31549638 | 530 | 129.2368 | 0% | 0% | 100% | 0% | 100% | 0% | 6958933 | 0 | 0.99 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 |  | 10004331 | 5308 | 127.392 | 5.308 | 9.5 | 9.5 | 3B | 0 | 0 | 1095 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31550742 | 1104 | 207.9879 | 0% | 0% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 |  | 10010011 | 5680 | 136.32 | 5.68 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31551952 | 1210 | 213.0282 | 0% | 0% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 |  | 10016239 | 6228 | 149.472 | 6.228 | 9 | 9 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31553346 | 1394 | 223.8279 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 |  | 10022363 | 6124 | 146.976 | 6.124 | 8.1 | 8.1 | 3B+1S | 0 | 1132 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31554670 | 1324 | 216.1986 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 | 1 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 |  | 10028561 | 6198 | 148.752 | 6.198 | 7.3 | 7.3 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31556028 | 1358 | 219.1029 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 |  | 10034776 | 6215 | 149.16 | 6.215 | 6.8 | 6.8 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31557414 | 1386 | 223.0088 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 |  | 10040857 | 6081 | 145.944 | 6.081 | 6.3 | 6.3 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31558778 | 1364 | 224.3052 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 |  | 10046656 | 5799 | 139.176 | 5.799 | 6.1 | 6.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31560236 | 1458 | 251.4227 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 |  | 10052425 | 5769 | 138.456 | 5.769 | 6 | 6 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31561556 | 1320 | 228.8092 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 |  | 10058040 | 5615 | 134.76 | 5.615 | 5.9 | 5.9 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31562824 | 1268 | 225.8237 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 |  | 10063588 | 5548 | 133.152 | 5.548 | 5.8 | 5.8 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31564114 | 1290 | 232.5162 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 |  | 10069140 | 5552 | 133.248 | 5.552 | 5.6 | 5.6 | 3B+1S | 0 | 950 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31565378 | 1264 | 227.6657 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 |  | 10074709 | 5569 | 133.656 | 5.569 | 5.5 | 5.5 | 3B+1S | 0 | 950 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 31566646 | 1268 | 227.689 | 0% | 100% | 100% | 100% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 |  | 10080035 | 5326 | 127.824 | 5.326 | 5.1 | 5.1 | 2B+1S | 0 | 1040 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31567706 | 1060 | 199.0237 | 0% | 100% | 100% | 0% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 |  | 10085165 | 5130 | 123.12 | 5.13 | 4.5 | 4.5 | 2B+1S | 0 | 980 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31568718 | 1012 | 197.271 | 0% | 100% | 100% | 0% | 100% | 0% | 6958933 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 |  | 10090058 | 4893 | 117.432 | 4.893 | 4.3 | 4.3 | 2B+1S | 0 | 980 | 1140 | 0 | 1150 | N/A | N/A | N/A | N/A | 31569670 | 952 | 194.5637 | 0% | 100% | 100% | 0% | 100% | 0% | 6958933 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 |  | 10094076 | 4018 | 96.432 | 4.018 | 4.8 | 4.8 | 2B | 0 | 0 | 1038 | 0 | 1050 | N/A | N/A | N/A | N/A | 31570322 | 652 | 162.2698 | 0% | 0% | 100% | 0% | 100% | 0% | 6959451 | 518 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 |  | 10097897 | 3821 | 91.704 | 3.821 | 5.6 | 5.6 | 2B | 0 | 0 | 957 | 0 | 1050 | N/A | N/A | N/A | N/A | 31570902 | 580 | 151.7927 | 0% | 0% | 100% | 0% | 100% | 0% | 6960129 | 678 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 120905 | 120905 | 120.905 | 120.905 | [12 empty] | 24550 | 24550 | 203.052 | [6 empty] | 5855 | 5855 | 1.0433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT12) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 13) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24776 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10097897 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31570902 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6960129 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 |  | 10101572 | 3675 | 88.2 | 3.675 | 6.5 | 6.5 | 2B | 0 | 0 | 1002 | 0 | 1010 | N/A | N/A | N/A | N/A | 31571472 | 570 | 155.102 | 0% | 0% | 100% | 0% | 100% | 35% | 6961161 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 |  | 10105123 | 3551 | 85.224 | 3.551 | 7.6 | 7.6 | 2B | 0 | 0 | 992 | 0 | 960 | N/A | N/A | N/A | N/A | 31571998 | 526 | 148.1273 | 0% | 0% | 100% | 0% | 100% | 35% | 6962151 | 990 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 |  | 10108677 | 3554 | 85.296 | 3.554 | 8.5 | 8.5 | 2B | 0 | 0 | 936 | 0 | 960 | N/A | N/A | N/A | N/A | 31572496 | 498 | 140.1238 | 0% | 0% | 100% | 0% | 100% | 35% | 6963134 | 983 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 |  | 10112190 | 3513 | 84.312 | 3.513 | 9.5 | 9.5 | 2B | 0 | 0 | 905 | 0 | 960 | N/A | N/A | N/A | N/A | 31572966 | 470 | 133.7888 | 0% | 0% | 100% | 0% | 100% | 35% | 6963934 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 |  | 10116200 | 4010 | 96.24 | 4.01 | 9.5 | 9.5 | 2B | 0 | 0 | 965 | 0 | 998 | N/A | N/A | N/A | N/A | 31573466 | 500 | 124.6883 | 0% | 0% | 100% | 0% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 |  | 10120898 | 4698 | 112.752 | 4.698 | 9.5 | 9.5 | 2B | 0 | 0 | 1177 | 0 | 1160 | N/A | N/A | N/A | N/A | 31574210 | 744 | 158.3653 | 0% | 0% | 100% | 0% | 100% | 0% | 6963934 | 0 | 0.99 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 |  | 10126352 | 5454 | 130.896 | 5.454 | 9 | 9 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31575516 | 1306 | 239.4573 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 |  | 10132669 | 6317 | 151.608 | 6.317 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31576822 | 1306 | 206.7437 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 |  | 10138865 | 6196 | 148.704 | 6.196 | 7.9 | 7.9 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31578202 | 1380 | 222.7243 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 |  | 10145080 | 6215 | 149.16 | 6.215 | 7.1 | 7.1 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31579592 | 1390 | 223.6525 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 |  | 10151205 | 6125 | 147 | 6.125 | 6.5 | 6.5 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31580982 | 1390 | 226.9388 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 |  | 10157263 | 6058 | 145.392 | 6.058 | 5.9 | 5.9 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31582384 | 1402 | 231.4295 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 |  | 10163173 | 5910 | 141.84 | 5.91 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31583730 | 1346 | 227.7496 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 124 |  | 10168766 | 5593 | 134.232 | 5.593 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31585008 | 1278 | 228.4999 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 |  | 10174360 | 5594 | 134.256 | 5.594 | 5.1 | 5.1 | 3B+1S | 0 | 1029 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31586210 | 1202 | 214.8731 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 |  | 10179527 | 5167 | 124.008 | 5.167 | 4.8 | 4.8 | 3B+1S | 0 | 1050 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31587420 | 1210 | 234.1784 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 |  | 10185230 | 5703 | 136.872 | 5.703 | 4.2 | 4.2 | 3B+1S | 0 | 1041 | 1165 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31588722 | 1302 | 228.3009 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 123 |  | 10190719 | 5489 | 131.736 | 5.489 | 3.7 | 3.7 | 3B+1S | 0 | 1047 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31589940 | 1218 | 221.8983 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 |  | 10196207 | 5488 | 131.712 | 5.488 | 3.2 | 3.2 | 3B+1S | 0 | 1059 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31591166 | 1226 | 223.3965 | 0% | 100% | 100% | 100% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 |  | 10201630 | 5423 | 130.152 | 5.423 | 2.3 | 2.3 | 2B+1S | 0 | 1123 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31592270 | 1104 | 203.5774 | 0% | 100% | 100% | 0% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 |  | 10206922 | 5292 | 127.008 | 5.292 | 1.7 | 1.7 | 2B+1S | 0 | 1048 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31593328 | 1058 | 199.9244 | 0% | 100% | 100% | 0% | 100% | 0% | 6963934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 |  | 10212103 | 5181 | 124.344 | 5.181 | 1.5 | 1.5 | 2B+1S | 0 | 972 | 1165 | 0 | 1140 | N/A | N/A | N/A | N/A | 31594310 | 982 | 189.5387 | 0% | 100% | 100% | 0% | 100% | 0% | 6963934 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 |  | 10216797 | 4694 | 112.656 | 4.694 | 2.2 | 2.2 | 2B | 0 | 0 | 1053 | 0 | 1110 | N/A | N/A | N/A | N/A | 31595034 | 724 | 154.2395 | 0% | 0% | 100% | 0% | 100% | 30% | 6964652 | 718 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 |  | 10220551 | 3754 | 90.096 | 3.754 | 3.2 | 3.2 | 2B | 0 | 0 | 971 | 0 | 1110 | N/A | N/A | N/A | N/A | 31595678 | 644 | 171.5503 | 0% | 0% | 100% | 0% | 100% | 30% | 6965663 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | 122654 | 122654 | 122.654 | 122.654 | [12 empty] | 24776 | 24776 | 201.9991 | [6 empty] | 5534 | 5534 | 1.03 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT11) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
NOTE: WRONG VALUES INDICATED AT 900MM DISCHARGE TOTALIZER @ 10:00PM. NEED FOR INSPECTION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 13) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24890 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10220551 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31595678 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6965663 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 |  | 10224116 | 3565 | 85.56 | 3.565 | 5.1 | 5.1 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 31596334 | 656 | 184.0112 | 0% | 0% | 100% | 0% | 100% | 40% | 6967354 | 1691 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 |  | 10227728 | 3612 | 86.688 | 3.612 | 6.7 | 6.7 | 2B | 0 | 0 | 942 | 0 | 1110 | N/A | N/A | N/A | N/A | 31596926 | 592 | 163.8981 | 0% | 0% | 100% | 0% | 100% | 40% | 6968991 | 1637 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 |  | 10231248 | 3520 | 84.48 | 3.52 | 8.2 | 8.2 | 2B | 0 | 0 | 950 | 0 | 1008 | N/A | N/A | N/A | N/A | 31597474 | 548 | 155.6818 | 0% | 0% | 100% | 0% | 100% | 40% | 6970548 | 1557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 |  | 10234796 | 3548 | 85.152 | 3.548 | 9.5 | 9.5 | 2B | 0 | 0 | 953 | 0 | 950 | N/A | N/A | N/A | N/A | 31597982 | 508 | 143.1793 | 0% | 0% | 100% | 0% | 100% | 35% | 6971636 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 |  | 10238416 | 3620 | 86.88 | 3.62 | 9.5 | 9.5 | 2B | 0 | 0 | 975 | 0 | 1008 | N/A | N/A | N/A | N/A | 31598486 | 504 | 139.2265 | 0% | 0% | 100% | 0% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 |  | 10243261 | 4845 | 116.28 | 4.845 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31599250 | 764 | 157.6883 | 0% | 0% | 100% | 0% | 100% | 0% | 6971636 | 0 | 0.98 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 |  | 10248818 | 5557 | 133.368 | 5.557 | 9 | 9 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31600554 | 1304 | 234.659 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 |  | 10255016 | 6198 | 148.752 | 6.198 | 8.2 | 8.2 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31601904 | 1350 | 217.8122 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 |  | 10261305 | 6289 | 150.936 | 6.289 | 7.6 | 7.6 | 3B+1S | 0 | 1107 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31603272 | 1368 | 217.5227 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 |  | 10267683 | 6378 | 153.072 | 6.378 | 6.8 | 6.8 | 3B+1S | 0 | 1101 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31604660 | 1388 | 217.6231 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 |  | 10273904 | 6221 | 149.304 | 6.221 | 6.3 | 6.3 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31606054 | 1394 | 224.0797 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 |  | 10279698 | 5794 | 139.056 | 5.794 | 5.8 | 5.8 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31607444 | 1390 | 239.9033 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 |  | 10285429 | 5731 | 137.544 | 5.731 | 5.6 | 5.6 | 3B+1S | 0 | 1032 | 1165 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31608818 | 1374 | 239.7487 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 |  | 10290880 | 5451 | 130.824 | 5.451 | 5.3 | 5.3 | 3B+1S | 0 | 1020 | 1136 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31610018 | 1200 | 220.1431 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 128 | 10296332 | 5452 | 130.848 | 5.452 | 5.1 | 5.1 | 3B+1S | 0 | 1004 | 1104 | 1185 | 1108 | N/A | N/A | N/A | N/A | 31611218 | 1200 | 220.1027 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 126 | 10301624 | 5292 | 127.008 | 5.292 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 31612348 | 1130 | 213.5299 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 130 | 10307083 | 5459 | 131.016 | 5.459 | 4.5 | 4.5 | 3B+1S | 0 | 1071 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31613590 | 1242 | 227.5142 | 0% | 100% | 100% | 100% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 123 | 136 | 10312548 | 5465 | 131.16 | 5.465 | 4.1 | 4.1 | 3B+1S | 0 | 1039 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31614805 | 1215 | 222.3239 | 0% | 100% | 100% | 0% | 100% | 0% | 6971636 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 132 | 10318013 | 5465 | 131.16 | 5.465 | 3.6 | 3.6 | 3B+1S | 0 | 1026 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31616020 | 1215 | 222.3239 | 0% | 100% | 100% | 0% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 10323289 | 5276 | 126.624 | 5.276 | 2.9 | 2.9 | 2B+1S | 0 | 1092 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31617086 | 1066 | 202.047 | 0% | 100% | 100% | 0% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 10328628 | 5339 | 128.136 | 5.339 | 2.2 | 2.2 | 2B+1S | 0 | 1059 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31618162 | 1076 | 201.5359 | 0% | 100% | 100% | 0% | 100% | 0% | 6971636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 111 | 10333631 | 5003 | 120.072 | 5.003 | 2 | 2 | 2B+1S | 0 | 880 | 1197 | 0 | 1110 | N/A | N/A | N/A | N/A | 31619156 | 994 | 198.6808 | 0% | 100% | 100% | 0% | 100% | 0% | 6971636 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 96 | 10337689 | 4058 | 97.392 | 4.058 | 2.6 | 2.6 | 2B | 0 | 0 | 0 | 1185 | 1002 | N/A | N/A | N/A | N/A | 31619890 | 734 | 180.8773 | 0% | 0% | 100% | 0% | 100% | 25% | 6972567 | 931 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 70 | 10341764 | 4075 | 97.8 | 4.075 | 3.6 | 3.6 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 31620568 | 678 | 166.3804 | 0% | 0% | 100% | 0% | 100% | 25% | 6973498 | 931 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.3 | 121213 | 121213 | 121.213 | 121.213 | [12 empty] | 24890 | 24890 | 205.341 | [6 empty] | 7835 | 7835 | 0.96833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: WRONG VALUES INDICATED AT DISCHARGE TOTALIZER @ 10:00PM (OCT. 13). NEED FOR INSPECTION
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 40 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:56 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT14) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 13) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## OCT 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25054 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10341764 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31620568 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6973498 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 88 | 10345473 | 3709 | 89.016 | 3.709 | 4.9 | 4.9 | 2B | 0 | 0 | 1064 | 0 | 1008 | N/A | N/A | N/A | N/A | 31621198 | 630 | 169.8571 | 0% | 0% | 100% | 0% | 100% | 35% | 6974430 | 932 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 74 | 10349151 | 3678 | 88.272 | 3.678 | 6.6 | 6.6 | 2B | 0 | 0 | 982 | 0 | 1059 | N/A | N/A | N/A | N/A | 31621759 | 561 | 152.5285 | 0% | 0% | 100% | 0% | 100% | 35% | 6975808 | 1378 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 82 | 10352829 | 3678 | 88.272 | 3.678 | 8 | 8 | 2B | 0 | 0 | 979 | 0 | 1059 | N/A | N/A | N/A | N/A | 31622320 | 561 | 152.5285 | 0% | 0% | 100% | 0% | 100% | 35% | 6977186 | 1378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 87 | 10356507 | 3678 | 88.272 | 3.678 | 9.2 | 9.2 | 2B | 0 | 0 | 959 | 0 | 1058 | N/A | N/A | N/A | N/A | 31622882 | 562 | 152.8004 | 0% | 0% | 100% | 0% | 100% | 35% | 6978566 | 1380 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 100 | 10360188 | 3681 | 88.344 | 3.681 | 9.5 | 9.5 | 2B | 0 | 0 | 941 | 0 | 1058 | N/A | N/A | N/A | N/A | 31623412 | 530 | 143.9826 | 0% | 0% | 100% | 0% | 100% | 35% | 6978789 | 223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 120 | 10364787 | 4599 | 110.376 | 4.599 | 9.5 | 9.5 | 2B | 0 | 0 | 1129 | 0 | 1199 | N/A | N/A | N/A | N/A | 31624118 | 706 | 153.5116 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.99 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 139 | 10370776 | 5989 | 143.736 | 5.989 | 9.3 | 9.3 | 3B+1S | 0 | 1003 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31625436 | 1318 | 220.0701 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 140 | 10376714 | 5938 | 142.512 | 5.938 | 8.7 | 8.7 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31626743 | 1307 | 220.1078 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 31 | 21.831 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 141 | 10382792 | 6078 | 145.872 | 6.078 | 8.5 | 8.5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31628056 | 1313 | 216.025 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 10388934 | 6142 | 147.408 | 6.142 | 8.2 | 8.2 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31629430 | 1374 | 223.7056 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 146 | 10394774 | 5840 | 140.16 | 5.84 | 8 | 8 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31630720 | 1290 | 220.8904 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 140 | 10400834 | 6060 | 145.44 | 6.06 | 7.8 | 7.8 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31632070 | 1350 | 222.7723 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 137 | 10406497 | 5663 | 135.912 | 5.663 | 7.6 | 7.6 | 3B+1S | 0 | 988 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31633294 | 1224 | 216.1399 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 127 | 10412245 | 5748 | 137.952 | 5.748 | 7.3 | 7.3 | 3B+1S | 0 | 982 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31634562 | 1268 | 220.5985 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 129 | 10417657 | 5412 | 129.888 | 5.412 | 7.2 | 7.2 | 3B+1S | 0 | 984 | 1124 | 1185 | 1148 | N/A | N/A | N/A | N/A | 31635762 | 1200 | 221.7295 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 28 | 19.7183 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 132 | 10422931 | 5274 | 126.576 | 5.274 | 7 | 7 | 3B+1S | 0 | 1006 | 1104 | 1185 | 1149 | N/A | N/A | N/A | N/A | 31636926 | 1164 | 220.7053 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 137 | 10428564 | 5633 | 135.192 | 5.633 | 6.5 | 6.5 | 3B+1S | 0 | 1045 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31638178 | 1252 | 222.2617 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 132 | 10434090 | 5526 | 132.624 | 5.526 | 6.1 | 6.1 | 3B+1S | 0 | 1013 | 1134 | 1185 | 1128 | N/A | N/A | N/A | N/A | 31639390 | 1212 | 219.3268 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 118 | 131 | 10439542 | 5452 | 130.848 | 5.452 | 5.6 | 5.6 | 3B+1S | 0 | 1054 | 1135 | 1185 | 1129 | N/A | N/A | N/A | N/A | 31640610 | 1220 | 223.7711 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 127 | 10444846 | 5304 | 127.296 | 5.304 | 4.8 | 4.8 | 2B+1S | 0 | 1114 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31641702 | 1092 | 205.8824 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 126 | 10450151 | 5305 | 127.32 | 5.305 | 3.6 | 3.6 | 2B+1S | 0 | 1102 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 31642794 | 1092 | 205.8435 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 120 | 10455144 | 4993 | 119.832 | 4.993 | 3.1 | 3.1 | 2B+1S | 0 | 1010 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31643810 | 1016 | 203.4849 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 96 | 10459383 | 4239 | 101.736 | 4.239 | 3.8 | 3.8 | 2B | 0 | 0 | 1194 | 0 | 1199 | N/A | N/A | N/A | N/A | 31644708 | 898 | 211.8424 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 94 | 10463241 | 3858 | 92.592 | 3.858 | 5.4 | 5.4 | 2B | 0 | 0 | 1147 | 0 | 1199 | N/A | N/A | N/A | N/A | 31645622 | 914 | 236.9103 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.5417 | 121477 | 121477 | 121.477 | 121.477 | [12 empty] | 25054 | 25054 | 206.2448 | [6 empty] | 5291 | 5291 | 0.96167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ : AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:05 PM TO 4:15 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:16PM TO 4:26 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 15) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
MOV4 FAULT NEED FOR INSPECTION ASAP
XCV4 - OPENED @ 10:08 PM (15%)
NORMAL OPERATION

## OCT 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26068 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10463241 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31645622 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 89 | 10467023 | 3782 | 90.768 | 3.782 | 6.7 | 6.7 | 2B | 0 | 0 | 1060 | 0 | 1190 | N/A | N/A | N/A | N/A | 31646462 | 840 | 222.1047 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 87 | 10470696 | 3673 | 88.152 | 3.673 | 8.1 | 8.1 | 2B | 0 | 0 | 1058 | 0 | 1190 | N/A | N/A | N/A | N/A | 31647117 | 655 | 178.3283 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 10474369 | 3673 | 88.152 | 3.673 | 9.4 | 9.4 | 2B | 0 | 0 | 1049 | 0 | 1190 | N/A | N/A | N/A | N/A | 31647772 | 655 | 178.3283 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 35 | 24.6479 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 89 | 10478042 | 3673 | 88.152 | 3.673 | 9.5 | 9.5 | 2B | 0 | 0 | 918 | 0 | 1069 | N/A | N/A | N/A | N/A | 31648427 | 655 | 178.3283 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 100 | 10481716 | 3674 | 88.176 | 3.674 | 9.5 | 9.5 | 2B | 0 | 0 | 981 | 0 | 1069 | N/A | N/A | N/A | N/A | 31649082 | 655 | 178.2798 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 121 | 10486514 | 4798 | 115.152 | 4.798 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1140 | N/A | N/A | N/A | N/A | 31649826 | 744 | 155.0646 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.89 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 146 | 10492560 | 6046 | 145.104 | 6.046 | 9.3 | 9.3 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31651164 | 1338 | 221.3033 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 10498699 | 6139 | 147.336 | 6.139 | 8.8 | 8.8 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31652530 | 1366 | 222.5118 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 10504907 | 6208 | 148.992 | 6.208 | 8.2 | 8.2 | 3B+1S | 0 | 1075 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31653922 | 1392 | 224.2268 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 10511054 | 6147 | 147.528 | 6.147 | 7.6 | 7.6 | 3B+1S | 0 | 1056 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31655302 | 1380 | 224.4998 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 10517165 | 6111 | 146.664 | 6.111 | 7.1 | 7.1 | 3B+1S | 0 | 1033 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31656672 | 1370 | 224.1859 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 10523506 | 6341 | 152.184 | 6.341 | 6.9 | 6.9 | 3B+1S | 0 | 995 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31658114 | 1442 | 227.4089 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 10528988 | 5482 | 131.568 | 5.482 | 6.8 | 6.8 | 3B+1S | 0 | 1003 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31659350 | 1236 | 225.4652 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 10534588 | 5600 | 134.4 | 5.6 | 6.7 | 6.7 | 3B+1S | 0 | 995 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31660642 | 1292 | 230.7143 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 10540236 | 5648 | 135.552 | 5.648 | 6.6 | 6.6 | 3B+1S | 0 | 985 | 1145 | 1185 | 1160 | N/A | N/A | N/A | N/A | 31661902 | 1260 | 223.0878 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 10545719 | 5483 | 131.592 | 5.483 | 6.5 | 6.5 | 3B+1S | 0 | 990 | 1145 | 1185 | 1160 | N/A | N/A | N/A | N/A | 31663122 | 1220 | 222.5059 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 10551243 | 5524 | 132.576 | 5.524 | 6.4 | 6.4 | 3B+1S | 0 | 1009 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31664378 | 1256 | 227.3715 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 10556807 | 5564 | 133.536 | 5.564 | 6.3 | 6.3 | 3B+1S | 0 | 985 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31665630 | 1252 | 225.018 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 139 | 10562358 | 5551 | 133.224 | 5.551 | 6.1 | 6.1 | 3B+1S | 0 | 968 | 1185 | 1185 | 1190 | N/A | N/A | N/A | N/A | 31666912 | 1282 | 230.9494 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 123 | 10567794 | 5436 | 130.464 | 5.436 | 5.4 | 5.4 | 2B+1S | 0 | 1079 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31668014 | 1102 | 202.7226 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 10573134 | 5340 | 128.16 | 5.34 | 4.8 | 4.8 | 2B+1S | 0 | 1040 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31669078 | 1064 | 199.2509 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 129 | 10578057 | 4923 | 118.152 | 4.923 | 4.5 | 4.5 | 2B+1S | 0 | 968 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31670070 | 992 | 201.5031 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 99 | 10582372 | 4315 | 103.56 | 4.315 | 5.1 | 5.1 | 2B | 0 | 0 | 1115 | 0 | 1140 | N/A | N/A | N/A | N/A | 31670922 | 852 | 197.4508 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 96 | 10586361 | 3989 | 95.736 | 3.989 | 5.9 | 5.9 | 2B | 0 | 0 | 1070 | 0 | 1130 | N/A | N/A | N/A | N/A | 31671690 | 768 | 192.5295 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.7917 | 123120 | 123120 | 123.12 | 123.12 | [12 empty] | 26068 | 26068 | 211.7284 | [6 empty] | 0 | 0 | 1.0067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: MOV4 FAULT NEED FOR INSPECTION ASAP
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 OPENING INCREASED TO 20 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV4 CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 15) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED @ 10:01 PM (15%)
NORMAL OPERATION

## OCT 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25498 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10586361 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31671690 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 90 | 10590159 | 3798 | 91.152 | 3.798 | 6.8 | 6.8 | 2B | 0 | 0 | 1050 | 0 | 1110 | N/A | N/A | N/A | N/A | 31672446 | 756 | 199.0521 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 89 | 10593945 | 3786 | 90.864 | 3.786 | 8 | 8 | 2B | 0 | 0 | 1018 | 0 | 1060 | N/A | N/A | N/A | N/A | 31673152 | 706 | 186.4765 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 | 86 | 10597530 | 3585 | 86.04 | 3.585 | 8.6 | 8.6 | 2B | 0 | 0 | 1006 | 0 | 1060 | N/A | N/A | N/A | N/A | 31673782 | 630 | 175.7322 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 89 | 10601154 | 3624 | 86.976 | 3.624 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1060 | N/A | N/A | N/A | N/A | 31674402 | 620 | 171.0817 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 104 | 10605113 | 3959 | 95.016 | 3.959 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 958 | N/A | N/A | N/A | N/A | 31674930 | 528 | 133.367 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 128 | 10609895 | 4782 | 114.768 | 4.782 | 9.5 | 9.5 | 2B | 0 | 0 | 1167 | 0 | 1199 | N/A | N/A | N/A | N/A | 31675684 | 754 | 157.6746 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.95 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 10615796 | 5901 | 141.624 | 5.901 | 9.2 | 9.2 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31676986 | 1302 | 220.6406 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 10621838 | 6042 | 145.008 | 6.042 | 8.7 | 8.7 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31678334 | 1348 | 223.1049 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 10628109 | 6271 | 150.504 | 6.271 | 8.2 | 8.2 | 3B+1S | 0 | 1059 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31679734 | 1400 | 223.2499 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 10634191 | 6082 | 145.968 | 6.082 | 7.6 | 7.6 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31681109 | 1375 | 226.0769 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 10640273 | 6082 | 145.968 | 6.082 | 7.2 | 7.2 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31682458 | 1349 | 221.802 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 140 | 10646336 | 6063 | 145.512 | 6.063 | 7 | 7 | 3B+1S | 0 | 902 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31683810 | 1352 | 222.9919 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 139 | 10651993 | 5657 | 135.768 | 5.657 | 6.8 | 6.8 | 3B+1S | 0 | 1001 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31685010 | 1200 | 212.1266 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 131 | 10657745 | 5752 | 138.048 | 5.752 | 6 | 6 | 3B+1S | 0 | 1035 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31686254 | 1244 | 216.2726 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 137 | 10663498 | 5753 | 138.072 | 5.753 | 5.8 | 5.8 | 3B+1S | 0 | 1010 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31687498 | 1244 | 216.235 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 132 | 10668941 | 5443 | 130.632 | 5.443 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1136 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31688712 | 1214 | 223.0388 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 135 | 10674383 | 5442 | 130.608 | 5.442 | 5.1 | 5.1 | 3B+1S | 0 | 1080 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31689926 | 1214 | 223.0798 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 128 | 10679844 | 5461 | 131.064 | 5.461 | 4.8 | 4.8 | 3B+1S | 0 | 1014 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31691134 | 1208 | 221.2049 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 128 | 10685320 | 5476 | 131.424 | 5.476 | 4.4 | 4.4 | 3B+1S | 0 | 1013 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31692342 | 1208 | 220.599 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 130 | 10690659 | 5339 | 128.136 | 5.339 | 3.5 | 3.5 | 2B+1S | 0 | 1096 | 1197 | 0 | 1169 | N/A | N/A | N/A | N/A | 31693402 | 1060 | 198.5391 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 120 | 10695729 | 5070 | 121.68 | 5.07 | 3.3 | 3.3 | 2B+1S | 0 | 1049 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 31694393 | 991 | 195.4635 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 115 | 10700800 | 5071 | 121.704 | 5.071 | 2.8 | 2.8 | 2B+1S | 0 | 987 | 1196 | 0 | 1169 | N/A | N/A | N/A | N/A | 31695384 | 991 | 195.425 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 94 | 10704797 | 3997 | 95.928 | 3.997 | 4.3 | 4.3 | 2B | 0 | 0 | 1175 | 0 | 1195 | N/A | N/A | N/A | N/A | 31696286 | 902 | 225.6693 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 101 | 10708794 | 3997 | 95.928 | 3.997 | 5.3 | 5.3 | 2B | 0 | 0 | 1170 | 0 | 1190 | N/A | N/A | N/A | N/A | 31697188 | 902 | 225.6693 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.75 | 122433 | 122433 | 122.433 | 122.433 | [12 empty] | 25498 | 25498 | 208.2608 | [6 empty] | 0 | 0 | 0.96833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: MOV4 FAULT NEED FOR INSPECTION ASAP
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 OPENING INCREASED TO 17 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV4 CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT17) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 17) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED @ 10:01 PM (17%)
NORMAL OPERATION

## OCT 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | DENNIS L. GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26326 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10708794 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31697188 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 91 | 10712791 | 3997 | 95.928 | 3.997 | 6.9 | 6.9 | 2B | 0 | 0 | 1165 | 0 | 1160 | N/A | N/A | N/A | N/A | 31698090 | 902 | 225.6693 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 87 | 10716789 | 3998 | 95.952 | 3.998 | 7.9 | 7.9 | 2B | 0 | 0 | 1166 | 0 | 1160 | N/A | N/A | N/A | N/A | 31698992 | 902 | 225.6128 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 | 87 | 10720438 | 3649 | 87.576 | 3.649 | 9.5 | 9.5 | 2B | 0 | 0 | 1014 | 0 | 1069 | N/A | N/A | N/A | N/A | 31699838 | 846 | 231.8443 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 107 | 90 | 10724293 | 3855 | 92.52 | 3.855 | 9.5 | 9.5 | 2B | 0 | 0 | 975 | 0 | 1069 | N/A | N/A | N/A | N/A | 31700368 | 530 | 137.4838 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 97 | 10728148 | 3855 | 92.52 | 3.855 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 1069 | N/A | N/A | N/A | N/A | 31700898 | 530 | 137.4838 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 108 | 10732004 | 3856 | 92.544 | 3.856 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 1070 | N/A | N/A | N/A | N/A | 31701430 | 532 | 137.9668 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.97 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 131 | 10737706 | 5702 | 136.848 | 5.702 | 9.5 | 9.5 | 3B | 0 | 0 | 1083 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31702596 | 1166 | 204.4897 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 143 | 10743467 | 5761 | 138.264 | 5.761 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31703834 | 1238 | 214.8932 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 146 | 144 | 10749479 | 6012 | 144.288 | 6.012 | 9.1 | 9.1 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31705188 | 1354 | 225.2162 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 10755653 | 6174 | 148.176 | 6.174 | 8.7 | 8.7 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31706542 | 1354 | 219.3068 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 10761867 | 6214 | 149.136 | 6.214 | 8.2 | 8.2 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31707924 | 1382 | 222.401 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 10768367 | 6500 | 156 | 6.5 | 7.5 | 7.5 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31709382 | 1458 | 224.3077 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 138 | 10774122 | 5755 | 138.12 | 5.755 | 7.2 | 7.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31710694 | 1312 | 227.9757 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 10779942 | 5820 | 139.68 | 5.82 | 6.8 | 6.8 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31712002 | 1308 | 224.7423 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 10785851 | 5909 | 141.816 | 5.909 | 6.3 | 6.3 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31713354 | 1352 | 228.8035 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 10791727 | 5876 | 141.024 | 5.876 | 6 | 6 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31714694 | 1340 | 228.0463 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 10797408 | 5681 | 136.344 | 5.681 | 5.6 | 5.6 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31716022 | 1328 | 233.7617 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 132 | 10803175 | 5767 | 138.408 | 5.767 | 5.3 | 5.3 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31717354 | 1332 | 230.9693 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 130 | 10808711 | 5536 | 132.864 | 5.536 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31718642 | 1288 | 232.659 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 124 | 10814149 | 5438 | 130.512 | 5.438 | 4.6 | 4.6 | 2B+1S | 0 | 1102 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31719734 | 1092 | 200.8091 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 123 | 10819388 | 5239 | 125.736 | 5.239 | 3.7 | 3.7 | 2B+1S | 0 | 1034 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31720764 | 1030 | 196.6024 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 118 | 10824493 | 5105 | 122.52 | 5.105 | 3.5 | 3.5 | 2B+1S | 0 | 998 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31721794 | 1030 | 201.763 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 106 | 10829391 | 4898 | 117.552 | 4.898 | 4.4 | 4.4 | 2B | 0 | 0 | 1151 | 0 | 1199 | N/A | N/A | N/A | N/A | 31722754 | 960 | 195.9984 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 97 | 10832810 | 3419 | 82.056 | 3.419 | 5.4 | 5.4 | 2B | 0 | 0 | 1117 | 0 | 1140 | N/A | N/A | N/A | N/A | 31723514 | 760 | 222.2872 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.6667 | 124016 | 124016 | 124.016 | 124.016 | [12 empty] | 26326 | 26326 | 212.2791 | [6 empty] | 0 | 0 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: MOV4 FAULT NEED FOR INSPECTION ASAP
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 OPENING INCREASED TO 17 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV4 CLOSED @ 3:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 17) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED @ 10:01 PM (17%)
NORMAL OPERATION

## OCT 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26236 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10832810 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31723514 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 106 | 94 | 10836894 | 4084 | 98.016 | 4.084 | 6.5 | 6.5 | 2B | 0 | 0 | 1146 | 0 | 1140 | N/A | N/A | N/A | N/A | 31724309 | 795 | 194.6621 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 107 | 92 | 10840849 | 3955 | 94.92 | 3.955 | 7.6 | 7.6 | 2B | 0 | 0 | 1146 | 0 | 1140 | N/A | N/A | N/A | N/A | 31725081 | 772 | 195.196 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 | 90 | 10844748 | 3899 | 93.576 | 3.899 | 8.7 | 8.7 | 2B | 0 | 0 | 980 | 0 | 1059 | N/A | N/A | N/A | N/A | 31725832 | 751 | 192.6135 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 87 | 10848546 | 3798 | 91.152 | 3.798 | 9.4 | 9.4 | 2B | 0 | 0 | 960 | 0 | 1059 | N/A | N/A | N/A | N/A | 31726572 | 740 | 194.8394 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 86 | 10851524 | 2978 | 71.472 | 2.978 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 0 | 927 | N/A | N/A | N/A | N/A | 31726970 | 398 | 133.6467 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 105 | 10855749 | 4225 | 101.4 | 4.225 | 9.5 | 9.5 | 2B | 0 | 0 | 1019 | 0 | 1009 | N/A | N/A | N/A | N/A | 31727490 | 520 | 123.0769 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.88 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 130 | 10861247 | 5498 | 131.952 | 5.498 | 9.5 | 9.5 | 3B | 0 | 0 | 1055 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31728637 | 1147 | 208.6213 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 139 | 10867153 | 5906 | 141.744 | 5.906 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31729886 | 1249 | 211.4799 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 143 | 10873275 | 6122 | 146.928 | 6.122 | 9 | 9 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31731246 | 1360 | 222.1496 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 153 | 10879569 | 6294 | 151.056 | 6.294 | 8.1 | 8.1 | 3B+1S | 0 | 1164 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31732640 | 1394 | 221.4808 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 10885821 | 6252 | 150.048 | 6.252 | 7.3 | 7.3 | 3B+1S | 0 | 1081 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31734080 | 1440 | 230.3263 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 10891995 | 6174 | 148.176 | 6.174 | 6.6 | 6.6 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31735478 | 1398 | 226.4334 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 10897939 | 5944 | 142.656 | 5.944 | 6.1 | 6.1 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31736842 | 1364 | 229.4751 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 139 | 10903884 | 5945 | 142.68 | 5.945 | 5.7 | 5.7 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31738202 | 1360 | 228.7637 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 126 | 10909659 | 5775 | 138.6 | 5.775 | 5.6 | 5.6 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31739518 | 1316 | 227.8788 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 139 | 10915409 | 5750 | 138 | 5.75 | 5.5 | 5.5 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31740846 | 1328 | 230.9565 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 133 | 10921186 | 5777 | 138.648 | 5.777 | 5.1 | 5.1 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 31742190 | 1344 | 232.6467 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 148 | 10926848 | 5662 | 135.888 | 5.662 | 5 | 5 | 3B+1S | 0 | 980 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31743510 | 1320 | 233.1332 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 130 | 10932391 | 5543 | 133.032 | 5.543 | 5 | 5 | 3B+1S | 0 | 973 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31744798 | 1288 | 232.3651 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 128 | 10937698 | 5307 | 127.368 | 5.307 | 4.4 | 4.4 | 2B+1S | 0 | 1046 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31745846 | 1048 | 197.475 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 125 | 10943006 | 5308 | 127.392 | 5.308 | 3.7 | 3.7 | 2B+1S | 0 | 1023 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31746894 | 1048 | 197.4378 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 115 | 10948076 | 5070 | 121.68 | 5.07 | 3.6 | 3.6 | 2B+1S | 0 | 5800 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31747888 | 994 | 196.0552 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 102 | 10952109 | 4033 | 96.792 | 4.033 | 4.5 | 4.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 31748819 | 931 | 230.8455 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 99 | 10956142 | 4033 | 96.792 | 4.033 | 5.9 | 5.9 | 2B | 0 | 0 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31749750 | 931 | 230.8455 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.375 | 123332 | 123332 | 123.332 | 123.332 | [12 empty] | 26236 | 26236 | 212.7266 | [6 empty] | 0 | 0 | 0.94333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: MOV4 FAULT NEED FOR INSPECTION ASAP
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT19) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:28 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 19) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED @ 10:01 PM (17%)
NORMAL OPERATION

## OCT 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26830 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10956142 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31749750 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 93 | 10960175 | 4033 | 96.792 | 4.033 | 7.6 | 7.6 | 2B | 0 | 0 | 1180 | 0 | 1190 | N/A | N/A | N/A | N/A | 31750681 | 931 | 230.8455 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 89 | 10964211 | 4036 | 96.864 | 4.036 | 9.2 | 9.2 | 2B | 0 | 0 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31751614 | 933 | 231.1695 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 81 | 10967967 | 3756 | 90.144 | 3.756 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1197 | N/A | N/A | N/A | N/A | 31752178 | 564 | 150.1597 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 97 | 10971723 | 3756 | 90.144 | 3.756 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 1100 | N/A | N/A | N/A | N/A | 31752742 | 564 | 150.1597 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 98 | 10975481 | 3758 | 90.192 | 3.758 | 9.5 | 9.5 | 2B | 0 | 0 | 874 | 0 | 1100 | N/A | N/A | N/A | N/A | 31753308 | 566 | 150.612 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 124 | 10980139 | 4658 | 111.792 | 4.658 | 9.5 | 9.5 | 2B | 0 | 0 | 1197 | 0 | 1109 | N/A | N/A | N/A | N/A | 31754030 | 722 | 155.0021 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 142 | 10986251 | 6112 | 146.688 | 6.112 | 9.1 | 9.1 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31755370 | 1340 | 219.2408 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 10992449 | 6198 | 148.752 | 6.198 | 8.5 | 8.5 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31756750 | 1380 | 222.6525 | 0% | 0% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 10998659 | 6210 | 149.04 | 6.21 | 8.3 | 8.3 | 3B+1S | 0 | 1092 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31758148 | 1398 | 225.1208 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 11004900 | 6241 | 149.784 | 6.241 | 6.9 | 6.9 | 3B+1S | 0 | 1114 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31759544 | 1396 | 223.6821 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 11010935 | 6035 | 144.84 | 6.035 | 6.3 | 6.3 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31760934 | 1390 | 230.3231 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 11017099 | 6164 | 147.936 | 6.164 | 5.8 | 5.8 | 3B+1S | 0 | 1105 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31762342 | 1408 | 228.4231 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 11022823 | 5724 | 137.376 | 5.724 | 5.4 | 5.4 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31763658 | 1316 | 229.9092 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 138 | 11028722 | 5899 | 141.576 | 5.899 | 5.1 | 5.1 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31765016 | 1358 | 230.2085 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 137 | 11034445 | 5723 | 137.352 | 5.723 | 4.9 | 4.9 | 3B+1S | 0 | 909 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31766334 | 1318 | 230.2988 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 11040115 | 5670 | 136.08 | 5.67 | 4.9 | 4.9 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31767651 | 1317 | 232.2751 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 11045785 | 5670 | 136.08 | 5.67 | 4.6 | 4.6 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31768968 | 1317 | 232.2751 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 11051423 | 5638 | 135.312 | 5.638 | 4.5 | 4.5 | 3B+1S | 0 | 998 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31770279 | 1311 | 232.5293 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 135 | 11057062 | 5639 | 135.336 | 5.639 | 4.3 | 4.3 | 3B+1S | 0 | 997 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31771590 | 1311 | 232.488 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 130 | 11062559 | 5497 | 131.928 | 5.497 | 3.2 | 3.2 | 2B+1S | 0 | 1165 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31772720 | 1130 | 205.5667 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 11067937 | 5378 | 129.072 | 5.378 | 2.4 | 2.4 | 2B+1S | 0 | 1080 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31773810 | 1090 | 202.6776 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 130 | 11073186 | 5249 | 125.976 | 5.249 | 2 | 2 | 2B+1S | 0 | 999 | 1199 | 0 | 1199 | N/A | N/A | N/A | N/A | 31774854 | 1044 | 198.895 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 92 | 11077481 | 4295 | 103.08 | 4.295 | 2.7 | 2.7 | 2B | 0 | 0 | 1146 | 0 | 1170 | N/A | N/A | N/A | N/A | 31775754 | 900 | 209.546 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 90 | 11081481 | 4000 | 96 | 4 | 3.6 | 3.6 | 2B | 0 | 0 | 1107 | 0 | 1140 | N/A | N/A | N/A | N/A | 31776580 | 826 | 206.5 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4167 | 125339 | 125339 | 125.339 | 125.339 | [12 empty] | 26830 | 26830 | 214.0595 | [6 empty] | 0 | 0 | 0.97333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: MOV4 FAULT NEED FOR INSPECTION ASAP
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 CLOSED @ 2:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT20) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 20) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED @ 10:01 PM (17%)
NORMAL OPERATION

## OCT 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26940 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11081481 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31776580 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6978789 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 93 | 11085316 | 3835 | 92.04 | 3.835 | 5.1 | 5.1 | 2B | 0 | 0 | 1133 | 0 | 1140 | N/A | N/A | N/A | N/A | 31777434 | 854 | 222.6858 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 11089050 | 3734 | 89.616 | 3.734 | 6.5 | 6.5 | 2B | 0 | 0 | 1090 | 0 | 1140 | N/A | N/A | N/A | N/A | 31778234 | 800 | 214.2475 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 11092729 | 3679 | 88.296 | 3.679 | 7.8 | 7.8 | 2B | 0 | 0 | 1070 | 0 | 1140 | N/A | N/A | N/A | N/A | 31779002 | 768 | 208.7524 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 93 | 11096436 | 3707 | 88.968 | 3.707 | 9 | 9 | 2B | 0 | 0 | 1132 | 0 | 1110 | N/A | N/A | N/A | N/A | 31779754 | 752 | 202.8595 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 105 | 11100447 | 4011 | 96.264 | 4.011 | 9.5 | 9.5 | 2B | 0 | 0 | 935 | 0 | 1008 | N/A | N/A | N/A | N/A | 31780382 | 628 | 156.5694 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 124 | 11105066 | 4619 | 110.856 | 4.619 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1150 | N/A | N/A | N/A | N/A | 31781082 | 700 | 151.548 | 0% | 0% | 100% | 0% | 100% | 0% | 6978789 | 0 | 1.02 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 148 | 11111193 | 6127 | 147.048 | 6.127 | 9.2 | 9.2 | 3B+1S | 0 | 998 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31782471 | 1389 | 226.7015 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 150 | 11117294 | 6101 | 146.424 | 6.101 | 8.8 | 8.8 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31783866 | 1395 | 228.651 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 140 | 11123930 | 6636 | 159.264 | 6.636 | 8.2 | 8.2 | 3B+1S | 0 | 1067 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31785250 | 1384 | 208.5594 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 140 | 11130030 | 6100 | 146.4 | 6.1 | 7.5 | 7.5 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31786639 | 1389 | 227.7049 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 1 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 153 | 11135999 | 5969 | 143.256 | 5.969 | 7 | 7 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31787980 | 1341 | 224.6607 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 11142051 | 6052 | 145.248 | 6.052 | 6.6 | 6.6 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31789338 | 1358 | 224.3886 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 11148117 | 6066 | 145.584 | 6.066 | 5.7 | 5.7 | 3B+1S | 0 | 1087 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31790732 | 1394 | 229.8055 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 11154074 | 5957 | 142.968 | 5.957 | 5.1 | 5.1 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31792087 | 1355 | 227.4635 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 145 | 11160032 | 5958 | 142.992 | 5.958 | 4.8 | 4.8 | 3B+1S | 0 | 1031 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31793442 | 1355 | 227.4253 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 11165857 | 5825 | 139.8 | 5.825 | 4.6 | 4.6 | 3B+1S | 0 | 1022 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31794776 | 1334 | 229.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 141 | 11171599 | 5742 | 137.808 | 5.742 | 4 | 4 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31796118 | 1342 | 233.7165 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 141 | 11177226 | 5627 | 135.048 | 5.627 | 3.8 | 3.8 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31797438 | 1320 | 234.5833 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 11182832 | 5606 | 134.544 | 5.606 | 3.6 | 3.6 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31798744 | 1306 | 232.9647 | 0% | 100% | 100% | 100% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 129 | 11188284 | 5452 | 130.848 | 5.452 | 2.7 | 2.7 | 2B+1S | 0 | 1174 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 31799874 | 1130 | 207.2634 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 11193613 | 5329 | 127.896 | 5.329 | 1.8 | 1.8 | 2B+1S | 0 | 1078 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 31800962 | 1088 | 204.1659 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 122 | 11199027 | 5414 | 129.936 | 5.414 | 1.4 | 1.4 | 2B+1S | 0 | 1015 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31802046 | 1084 | 200.2216 | 0% | 100% | 100% | 0% | 100% | 0% | 6978789 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 101 | 11203341 | 4314 | 103.536 | 4.314 | 2.1 | 2.1 | 2B | 0 | 0 | 1094 | 0 | 1099 | N/A | N/A | N/A | N/A | 31802826 | 780 | 180.8067 | 0% | 0% | 100% | 0% | 100% | 30% | 6979501 | 712 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 89 | 11207570 | 4229 | 101.496 | 4.229 | 3.2 | 3.2 | 2B | 0 | 0 | 1035 | 0 | 1049 | N/A | N/A | N/A | N/A | 31803520 | 694 | 164.105 | 0% | 0% | 100% | 0% | 100% | 30% | 6980356 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.1667 | 126089 | 126089 | 126.089 | 126.089 | [12 empty] | 26940 | 26940 | 213.6586 | [6 empty] | 1567 | 1567 | 0.97 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 22) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 22) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (30%)
NORMAL OPERATION

## OCT 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25694 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11207570 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31803520 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6980356 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 88 | 11211231 | 3661 | 87.864 | 3.661 | 4.1 | 4.1 | 2B | 0 | 0 | 1044 | 0 | 1049 | N/A | N/A | N/A | N/A | 31804138 | 618 | 168.8063 | 0% | 0% | 100% | 0% | 100% | 35% | 6981373 | 1017 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 85 | 11214944 | 3713 | 89.112 | 3.713 | 5.4 | 5.4 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 31804730 | 592 | 159.4398 | 0% | 0% | 100% | 0% | 100% | 35% | 6982536 | 1163 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 81 | 11218625 | 3681 | 88.344 | 3.681 | 6.7 | 6.7 | 2B | 0 | 0 | 1024 | 0 | 1028 | N/A | N/A | N/A | N/A | 31805311 | 581 | 157.8375 | 0% | 0% | 100% | 0% | 100% | 35% | 6983721 | 1185 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 87 | 11222231 | 3606 | 86.544 | 3.606 | 8.1 | 8.1 | 2B | 0 | 0 | 1002 | 0 | 999 | N/A | N/A | N/A | N/A | 31805871 | 560 | 155.2967 | 0% | 0% | 100% | 0% | 100% | 35% | 6984945 | 1224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 131 | 98 | 11227202 | 4971 | 119.304 | 4.971 | 9.1 | 9.1 | 2B | 0 | 0 | 1054 | 0 | 1059 | N/A | N/A | N/A | N/A | 31806564 | 693 | 139.4086 | 0% | 0% | 100% | 0% | 100% | 35% | 6986214 | 1269 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 121 | 11230804 | 3602 | 86.448 | 3.602 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31807170 | 606 | 168.2399 | 0% | 0% | 100% | 0% | 100% | 35% | 6986575 | 361 | 0.92 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 142 | 11236791 | 5987 | 143.688 | 5.987 | 9.1 | 9.1 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31808535 | 1365 | 227.994 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 11242849 | 6058 | 145.392 | 6.058 | 8.4 | 8.4 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31809913 | 1378 | 227.4678 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 11248997 | 6148 | 147.552 | 6.148 | 7.6 | 7.6 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31811302 | 1389 | 225.9271 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 25 | 17.6056 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 11255226 | 6229 | 149.496 | 6.229 | 6.8 | 6.8 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31812664 | 1362 | 218.6547 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 11261434 | 6208 | 148.992 | 6.208 | 6.3 | 6.3 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31814059 | 1395 | 224.7101 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 11267602 | 6168 | 148.032 | 6.168 | 5.9 | 5.9 | 3B+1S | 0 | 1065 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31815454 | 1395 | 226.1673 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 138 | 11273425 | 5823 | 139.752 | 5.823 | 5.8 | 5.8 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31816782 | 1328 | 228.0611 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 23 | 16.1972 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 137 | 11279348 | 5923 | 142.152 | 5.923 | 5.6 | 5.6 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31818138 | 1356 | 228.938 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 135 | 11285231 | 5883 | 141.192 | 5.883 | 5.5 | 5.5 | 3B+1S | 0 | 998 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31819480 | 1342 | 228.1149 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 11290853 | 5622 | 134.928 | 5.622 | 5.3 | 5.3 | 3B+1S | 0 | 1044 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31820790 | 1310 | 233.0132 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 11296420 | 5567 | 133.608 | 5.567 | 5.1 | 5.1 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31822078 | 1288 | 231.3634 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 11302013 | 5593 | 134.232 | 5.593 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31823369 | 1291 | 230.8242 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 11307588 | 5575 | 133.8 | 5.575 | 4.5 | 4.5 | 3B+1S | 0 | 993 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31824644 | 1275 | 228.6996 | 0% | 100% | 100% | 100% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 11313048 | 5460 | 131.04 | 5.46 | 3.5 | 3.5 | 2B+1S | 0 | 1118 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31825748 | 1104 | 202.1978 | 0% | 100% | 100% | 0% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 124 | 11318431 | 5383 | 129.192 | 5.383 | 2.8 | 2.8 | 2B+1S | 0 | 1059 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31826836 | 1088 | 202.1178 | 0% | 100% | 100% | 0% | 100% | 0% | 6986575 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 120 | 11323338 | 4907 | 117.768 | 4.907 | 2.5 | 2.5 | 2B+1S | 0 | 1002 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31827818 | 982 | 200.1223 | 0% | 100% | 100% | 0% | 100% | 0% | 6986575 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 102 | 11327583 | 4245 | 101.88 | 4.245 | 3.1 | 3.1 | 2B | 0 | 0 | 1058 | 0 | 1069 | N/A | N/A | N/A | N/A | 31828530 | 712 | 167.7267 | 0% | 0% | 100% | 0% | 100% | 25% | 6987046 | 471 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 94 | 11331758 | 4175 | 100.2 | 4.175 | 3.7 | 3.7 | 2B | 0 | 0 | 1021 | 0 | 1028 | N/A | N/A | N/A | N/A | 31829214 | 684 | 163.8323 | 0% | 0% | 100% | 0% | 100% | 25% | 6987778 | 732 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0833 | 124188 | 124188 | 124.188 | 124.188 | [12 empty] | 25694 | 25694 | 206.896 | [6 empty] | 7422 | 7422 | 0.955 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 5:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT. 23) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:18 PM TO 4:28 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:29 PM TO 4:39 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 23) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24940 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11331758 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31829214 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6987778 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 85 | 11335670 | 3912 | 93.888 | 3.912 | 6.3 | 6.3 | 2B | 0 | 0 | 1003 | 0 | 988 | N/A | N/A | N/A | N/A | 31829830 | 616 | 157.4642 | 0% | 0% | 100% | 0% | 100% | 35% | 6988719 | 941 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 11339475 | 3805 | 91.32 | 3.805 | 7.4 | 7.4 | 2B | 0 | 0 | 998 | 0 | 988 | N/A | N/A | N/A | N/A | 31830412 | 582 | 152.9566 | 0% | 0% | 100% | 0% | 100% | 35% | 6989900 | 1181 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 88 | 11343266 | 3791 | 90.984 | 3.791 | 8.2 | 8.2 | 2B | 0 | 0 | 983 | 0 | 978 | N/A | N/A | N/A | N/A | 31830986 | 574 | 151.4112 | 0% | 0% | 100% | 0% | 100% | 35% | 6991226 | 1326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 89 | 11346921 | 3655 | 87.72 | 3.655 | 9.1 | 9.1 | 2B | 0 | 0 | 981 | 0 | 978 | N/A | N/A | N/A | N/A | 31831512 | 526 | 143.9124 | 0% | 0% | 100% | 0% | 100% | 35% | 6992720 | 1494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 94 | 11350106 | 3185 | 76.44 | 3.185 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 0 | 978 | N/A | N/A | N/A | N/A | 31831946 | 434 | 136.2637 | 0% | 0% | 100% | 0% | 100% | 35% | 6993188 | 468 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 119 | 11354622 | 4516 | 108.384 | 4.516 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1140 | 0 | 1160 | N/A | N/A | N/A | N/A | 31832634 | 688 | 152.3472 | 0% | 0% | 100% | 0% | 100% | 0% | 6993188 | 0 | 1.17 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 146 | 11360509 | 5887 | 141.288 | 5.887 | 9.4 | 9.4 | 3B+1S | 0 | 970 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31833946 | 1312 | 222.8639 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 11366555 | 6046 | 145.104 | 6.046 | 9.2 | 9.2 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31835298 | 1352 | 223.6189 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 145 | 11372699 | 6144 | 147.456 | 6.144 | 8.6 | 8.6 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31836672 | 1374 | 223.6328 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 147 | 11378836 | 6137 | 147.288 | 6.137 | 8.5 | 8.5 | 3B+1S | 0 | 984 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31838030 | 1358 | 221.2808 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 | 1.03 | Normal operation schedule
58:00 | 11:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 144 | 11384649 | 5813 | 139.512 | 5.813 | 8.3 | 8.3 | 3B+1S | 0 | 990 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31839338 | 1308 | 225.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Normal operation schedule
59:00 | 12:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 11390557 | 5908 | 141.792 | 5.908 | 8.2 | 8.2 | 3B+1S | 0 | 988 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31840668 | 1330 | 225.1185 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 11396397 | 5840 | 140.16 | 5.84 | 7.9 | 7.9 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31841996 | 1328 | 227.3973 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 11402124 | 5727 | 137.448 | 5.727 | 7.5 | 7.5 | 3B+1S | 0 | 972 | 1165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31843316 | 1320 | 230.4872 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 133 | 11407689 | 5565 | 133.56 | 5.565 | 7.2 | 7.2 | 3B+1S | 0 | 1018 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31844563 | 1247 | 224.0791 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 131 | 11413270 | 5581 | 133.944 | 5.581 | 6.9 | 6.9 | 3B+1S | 0 | 1006 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31845824 | 1261 | 225.9452 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 11418871 | 5601 | 134.424 | 5.601 | 6.6 | 6.6 | 3B+1S | 0 | 1044 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31847114 | 1290 | 230.316 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 137 | 11424441 | 5570 | 133.68 | 5.57 | 6.3 | 6.3 | 3B+1S | 0 | 998 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31848380 | 1266 | 227.289 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 11429973 | 5532 | 132.768 | 5.532 | 6.1 | 6.1 | 3B+1S | 0 | 981 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31849620 | 1240 | 224.1504 | 0% | 100% | 100% | 100% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 133 | 11435377 | 5404 | 129.696 | 5.404 | 5.4 | 5.4 | 2B+1S | 0 | 1076 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31850712 | 1092 | 202.0725 | 0% | 100% | 100% | 0% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 126 | 11440754 | 5377 | 129.048 | 5.377 | 4.7 | 4.7 | 2B+1S | 0 | 1035 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31851762 | 1050 | 195.2762 | 0% | 100% | 100% | 0% | 100% | 0% | 6993188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 118 | 11445819 | 5065 | 121.56 | 5.065 | 4.5 | 4.5 | 2B+1S | 0 | 979 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31852764 | 1002 | 197.8282 | 0% | 100% | 100% | 0% | 100% | 0% | 6993188 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 96 | 11450035 | 4216 | 101.184 | 4.216 | 4.9 | 4.9 | 2B | 0 | 0 | 1015 | 0 | 1018 | N/A | N/A | N/A | N/A | 31853485 | 721 | 171.0152 | 0% | 0% | 100% | 0% | 100% | 25% | 6993604 | 416 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 89 | 11454031 | 3996 | 95.904 | 3.996 | 5.4 | 5.4 | 2B | 0 | 0 | 1018 | 0 | 1018 | N/A | N/A | N/A | N/A | 31854154 | 669 | 167.4174 | 0% | 0% | 100% | 0% | 100% | 25% | 6994084 | 480 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5417 | 122273 | 122273 | 122.273 | 122.273 | [12 empty] | 24940 | 24940 | 203.9698 | [6 empty] | 6306 | 6306 | 1.0117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 4:34 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 24) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 24) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24492 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11454031 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31854154 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6994084 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 91 | 86 | 11457597 | 3566 | 85.584 | 3.566 | 6.5 | 6.5 | 2B | 0 | 0 | 1011 | 0 | 1018 | N/A | N/A | N/A | N/A | 31854745 | 591 | 165.7319 | 0% | 0% | 100% | 0% | 100% | 35% | 6994829 | 745 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 84 | 11461114 | 3517 | 84.408 | 3.517 | 7.6 | 7.6 | 2B | 0 | 0 | 1009 | 0 | 1018 | N/A | N/A | N/A | N/A | 31855308 | 563 | 160.0796 | 0% | 0% | 100% | 0% | 100% | 35% | 6996024 | 1195 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 81 | 11464572 | 3458 | 82.992 | 3.458 | 8.3 | 8.3 | 2B | 0 | 0 | 985 | 0 | 989 | N/A | N/A | N/A | N/A | 31855820 | 512 | 148.0625 | 0% | 0% | 100% | 0% | 100% | 35% | 6997280 | 1256 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 80 | 11467864 | 3292 | 79.008 | 3.292 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 0 | 918 | N/A | N/A | N/A | N/A | 31856202 | 382 | 116.0389 | 0% | 0% | 100% | 0% | 100% | 35% | 6998034 | 754 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 92 | 11471524 | 3660 | 87.84 | 3.66 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 958 | N/A | N/A | N/A | N/A | 31856658 | 456 | 124.5902 | 0% | 0% | 100% | 0% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 113 | 11475748 | 4224 | 101.376 | 4.224 | 9.5 | 9.5 | 2B | 0 | 0 | 1103 | 0 | 1109 | N/A | N/A | N/A | N/A | 31857288 | 630 | 149.1477 | 0% | 0% | 100% | 0% | 100% | 0% | 6998034 | 0 | 0.99 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 148 | 143 | 11481750 | 6002 | 144.048 | 6.002 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31858556 | 1268 | 211.2629 | 0% | 0% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 11487808 | 6058 | 145.392 | 6.058 | 9 | 9 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31859945 | 1389 | 229.2836 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 11493991 | 6183 | 148.392 | 6.183 | 8.3 | 8.3 | 3B+1S | 0 | 1076 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31861335 | 1390 | 224.81 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 11500365 | 6374 | 152.976 | 6.374 | 7.7 | 7.7 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31862724 | 1389 | 217.9165 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 | 1.01 | Normal operation schedule
58:00 | 11:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 11506463 | 6098 | 146.352 | 6.098 | 7.1 | 7.1 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31864089 | 1365 | 223.8439 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Normal operation schedule
59:00 | 12:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 11512513 | 6050 | 145.2 | 6.05 | 6.7 | 6.7 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31865454 | 1365 | 225.6198 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 11518105 | 5592 | 134.208 | 5.592 | 6.6 | 6.6 | 3B+1S | 0 | 1019 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31866764 | 1310 | 234.2632 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 11523471 | 5366 | 128.784 | 5.366 | 6.1 | 6.1 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31867947 | 1183 | 220.4622 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 126 | 136 | 11528837 | 5366 | 128.784 | 5.366 | 5.9 | 5.9 | 3B+1S | 0 | 1042 | 1164 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31869130 | 1183 | 220.4622 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 134 | 11534497 | 5660 | 135.84 | 5.66 | 5.4 | 5.4 | 3B+1S | 0 | 1046 | 1165 | 1185 | 1138 | N/A | N/A | N/A | N/A | 31870386 | 1256 | 221.9081 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 137 | 11540100 | 5603 | 134.472 | 5.603 | 4.9 | 4.9 | 3B+1S | 0 | 1070 | 1164 | 1185 | 1170 | N/A | N/A | N/A | N/A | 31871666 | 1280 | 228.449 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 134 | 11545680 | 5580 | 133.92 | 5.58 | 4.5 | 4.5 | 3B+1S | 0 | 1023 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31872938 | 1272 | 227.957 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 128 | 11551261 | 5581 | 133.944 | 5.581 | 4.1 | 4.1 | 3B+1S | 0 | 999 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31874214 | 1276 | 228.6329 | 0% | 100% | 100% | 100% | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 124 | 11556432 | 5171 | 124.104 | 5.171 | 3.5 | 3.5 | 2B+1S | 0 | 1054 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31875284 | 1070 | 206.9232 | 0% | 100% | 100% |  | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 121 | 11561554 | 5122 | 122.928 | 5.122 | 3.1 | 3.1 | 2B+1S | 0 | 996 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31876306 | 1022 | 199.5314 | 0% | 100% | 100% |  | 100% | 0% | 6998034 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 115 | 11566530 | 4976 | 119.424 | 4.976 | 3.1 | 3.1 | 2B+1S | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31877276 | 970 | 194.9357 | 0% |  | 100% |  | 100% | 0% | 6998034 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 97 | 11570758 | 4228 | 101.472 | 4.228 | 3.6 | 3.6 | 2B | 0 | 0 | 1071 | 0 | 1079 | N/A | N/A | N/A | N/A | 31878008 | 732 | 173.1315 | 0% |  | 100% |  | 100% | 25% | 6998532 | 498 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 90 | 11574705 | 3947 | 94.728 | 3.947 | 4.4 | 4.4 | 2B | 0 | 0 | 1035 | 0 | 1038 | N/A | N/A | N/A | N/A | 31878646 | 638 | 161.6418 | 0% |  | 100% |  | 100% | 25% | 6999152 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.1667 | 120674 | 120674 | 120.674 | 120.674 | [12 empty] | 24492 | 24492 | 202.96 | [6 empty] | 5068 | 5068 | 0.94333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 25) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
POWER FLUCTUATION @ 1:08 PM / POWER RESUMED @ 1:09 PM
RESUMED NORMAL OPERATION @ 1:15 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:10 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 25) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:38 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25220 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11574705 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31878646 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 6999152 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 87 | 11578427 | 3722 | 89.328 | 3.722 | 5.5 | 5.5 | 2B | 0 | 0 | 1002 | 0 | 998 | N/A | N/A | N/A | N/A | 31879242 | 596 | 160.129 | 0% | 0% | 100% | 0% | 100% | 35% | 7000103 | 951 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 85 | 11582017 | 3590 | 86.16 | 3.59 | 6.7 | 6.7 | 2B | 0 | 0 | 996 | 0 | 998 | N/A | N/A | N/A | N/A | 31879804 | 562 | 156.546 | 0% | 0% | 100% | 0% | 100% | 35% | 7001218 | 1115 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 107 | 82 | 11585598 | 3581 | 85.944 | 3.581 | 7.9 | 7.9 | 2B | 0 | 0 | 965 | 0 | 979 | N/A | N/A | N/A | N/A | 31880350 | 546 | 152.4714 | 0% | 0% | 100% | 0% | 100% | 35% | 7002540 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 85 | 11589031 | 3433 | 82.392 | 3.433 | 9.1 | 9.1 | 2B | 0 | 0 | 980 | 0 | 978 | N/A | N/A | N/A | N/A | 31880830 | 480 | 139.8194 | 0% | 0% | 100% | 0% | 100% | 35% | 7003817 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 92 | 11592670 | 3639 | 87.336 | 3.639 | 9.5 | 9.5 | 2B | 0 | 0 | 954 | 0 | 959 | N/A | N/A | N/A | N/A | 31881308 | 478 | 131.3548 | 0% | 0% | 100% | 0% | 100% | 35% | 7004077 | 260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 108 | 11596973 | 4303 | 103.272 | 4.303 | 9.5 | 9.5 | 2B | 0 | 0 | 1112 | 0 | 1118 | N/A | N/A | N/A | N/A | 31881894 | 586 | 136.1841 | 0% | 0% | 100% | 0% | 100% | 0% | 7004077 | 0 | 0.9 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 141 | 11602769 | 5796 | 139.104 | 5.796 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31883110 | 1216 | 209.7999 | 0% | 0% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 11608689 | 5920 | 142.08 | 5.92 | 9.1 | 9.1 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31884414 | 1304 | 220.2703 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 11614913 | 6224 | 149.376 | 6.224 | 8.6 | 8.6 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31885788 | 1374 | 220.7584 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 11621074 | 6161 | 147.864 | 6.161 | 7.9 | 7.9 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31887162 | 1374 | 223.0157 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 11627324 | 6250 | 150 | 6.25 | 7.3 | 7.3 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31888558 | 1396 | 223.36 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 11633474 | 6150 | 147.6 | 6.15 | 6.6 | 6.6 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31889954 | 1396 | 226.9919 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 138 | 11639572 | 6098 | 146.352 | 6.098 | 6.2 | 6.2 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31891302 | 1348 | 221.0561 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 11645324 | 5752 | 138.048 | 5.752 | 5.9 | 5.9 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31892666 | 1364 | 237.1349 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 11651144 | 5820 | 139.68 | 5.82 | 5.6 | 5.6 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31893998 | 1332 | 228.866 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 143 | 11656783 | 5639 | 135.336 | 5.639 | 5.4 | 5.4 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31895294 | 1296 | 229.828 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 11662628 | 5845 | 140.28 | 5.845 | 5 | 5 | 3B+1S | 0 | 980 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31896646 | 1352 | 231.3088 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 142 | 11668370 | 5742 | 137.808 | 5.742 | 4.8 | 4.8 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31897966 | 1320 | 229.8851 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 144 | 11674047 | 5677 | 136.248 | 5.677 | 4.7 | 4.7 | 3B+1S | 0 | 980 | 1177 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31899286 | 1320 | 232.5172 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 135 | 11679437 | 5390 | 129.36 | 5.39 | 4.6 | 4.6 | 3B+1S | 0 | 940 | 1153 | 1185 | 1150 | N/A | N/A | N/A | N/A | 31900494 | 1208 | 224.1187 | 0% | 100% | 100% | 100% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 119 | 11684640 | 5203 | 124.872 | 5.203 | 4.1 | 4.1 | 2B+1S | 0 | 1050 | 1156 | 0 | 1170 | N/A | N/A | N/A | N/A | 31901550 | 1056 | 202.9598 | 0% | 100% | 100% | 0% | 100% | 0% | 7004077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 121 | 11689552 | 4912 | 117.888 | 4.912 | 3.5 | 3.5 | 2B+1S | 0 | 1050 | 1131 | 0 | 1129 | N/A | N/A | N/A | N/A | 31902484 | 934 | 190.1466 | 0% | 100% | 100% | 0% | 100% | 0% | 7004077 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 92 | 11693969 | 4417 | 106.008 | 4.417 | 3.9 | 3.9 | 2B | 0 | 0 | 1059 | 0 | 1110 | N/A | N/A | N/A | N/A | 31903216 | 732 | 165.7233 | 0% | 0% | 100% | 0% | 100% | 25% | 7004573 | 496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 89 | 11697812 | 3843 | 92.232 | 3.843 | 4.6 | 4.6 | 2B | 0 | 0 | 1024 | 0 | 1028 | N/A | N/A | N/A | N/A | 31903866 | 650 | 169.1387 | 0% | 0% | 100% | 0% | 100% | 25% | 7005161 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5417 | 123107 | 123107 | 123.107 | 123.107 | [12 empty] | 25220 | 25220 | 204.8624 | [6 empty] | 6009 | 6009 | 1.0167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 4:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 26) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 25) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24698 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11697812 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31903866 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7005161 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 107 | 90 | 11701620 | 3808 | 91.392 | 3.808 | 5.4 | 5.4 | 2B | 0 | 0 | 1035 | 0 | 1038 | N/A | N/A | N/A | N/A | 31904488 | 622 | 163.3403 | 0% | 0% | 100% | 0% | 100% | 35% | 7006056 | 895 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 | 86 | 11705397 | 3777 | 90.648 | 3.777 | 6.9 | 6.9 | 2B | 0 | 0 | 1025 | 0 | 1038 | N/A | N/A | N/A | N/A | 31905092 | 604 | 159.9153 | 0% | 0% | 100% | 0% | 100% | 35% | 7007077 | 1021 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 87 | 11709149 | 3752 | 90.048 | 3.752 | 7.9 | 7.9 | 2B | 0 | 0 | 979 | 0 | 989 | N/A | N/A | N/A | N/A | 31905663 | 571 | 152.1855 | 0% | 0% | 100% | 0% | 100% | 35% | 7008366 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 85 | 11712852 | 3703 | 88.872 | 3.703 | 9.2 | 9.2 | 2B | 0 | 0 | 965 | 0 | 978 | N/A | N/A | N/A | N/A | 31906214 | 551 | 148.7983 | 0% | 0% | 100% | 0% | 100% | 35% | 7009520 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 89 | 11715864 | 3012 | 72.288 | 3.012 | 9.5 | 9.5 | 2B | 0 | 0 | 935 | 0 | 937 | N/A | N/A | N/A | N/A | 31906630 | 416 | 138.1142 | 0% | 0% | 100% | 0% | 100% | 35% | 7009822 | 302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 104 | 11719947 | 4083 | 97.992 | 4.083 | 9.5 | 9.5 | 2B | 0 | 0 | 1039 | 0 | 1048 | N/A | N/A | N/A | N/A | 31907170 | 540 | 132.2557 | 0% | 0% | 100% | 0% | 100% | 0% | 7009822 | 0 | 0.97 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 132 | 11725446 | 5499 | 131.976 | 5.499 | 9.5 | 9.5 | 3B | 0 | 0 | 1140 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31908310 | 1140 | 207.3104 | 0% | 0% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 138 | 11731281 | 5835 | 140.04 | 5.835 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31909542 | 1232 | 211.1397 | 0% | 0% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 146 | 11737409 | 6128 | 147.072 | 6.128 | 8.9 | 8.9 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31910940 | 1398 | 228.1332 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 154 | 11743677 | 6268 | 150.432 | 6.268 | 8.2 | 8.2 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31912335 | 1395 | 222.559 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 24 | 16.9014 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 11749906 | 6229 | 149.496 | 6.229 | 7.5 | 7.5 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31913734 | 1399 | 224.5946 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Normal operation schedule
59:00 | 12:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 11756062 | 6156 | 147.744 | 6.156 | 6.9 | 6.9 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31915150 | 1416 | 230.0195 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 11761967 | 5905 | 141.72 | 5.905 | 6.5 | 6.5 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31916462 | 1312 | 222.1846 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 133 | 11767782 | 5815 | 139.56 | 5.815 | 6.1 | 6.1 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31917789 | 1327 | 228.2029 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 11773554 | 5772 | 138.528 | 5.772 | 5.9 | 5.9 | 3B+1S | 0 | 1028 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31919120 | 1331 | 230.596 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 11779242 | 5688 | 136.512 | 5.688 | 5.7 | 5.7 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31920444 | 1324 | 232.7707 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 132 | 11785036 | 5794 | 139.056 | 5.794 | 5.4 | 5.4 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31921804 | 1360 | 234.7256 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 131 | 11790574 | 5538 | 132.912 | 5.538 | 5.2 | 5.2 | 3B+1S | 0 | 996 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31923052 | 1248 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 11796030 | 5456 | 130.944 | 5.456 | 5.1 | 5.1 | 3B+1S | 0 | 899 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31924266 | 1214 | 222.5073 | 0% | 100% | 100% | 100% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 127 | 11801332 | 5302 | 127.248 | 5.302 | 4.7 | 4.7 | 2B+1S | 0 | 1047 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31925324 | 1058 | 199.5473 | 0% | 100% | 100% | 0% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 123 | 11806588 | 5256 | 126.144 | 5.256 | 4.2 | 4.2 | 2B+1S | 0 | 1019 | 1155 | 0 | 1159 | N/A | N/A | N/A | N/A | 31926334 | 1010 | 192.1613 | 0% | 100% | 100% | 0% | 100% | 0% | 7009822 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 35 | 24.6479 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 101 | 109 | 11811495 | 4907 | 117.768 | 4.907 | 3.9 | 3.9 | 2B+1S | 0 | 1021 | 1075 | 0 | 1079 | N/A | N/A | N/A | N/A | 31927258 | 924 | 188.3024 | 0% | 100% | 100% | 0% | 100% | 0% | 7009822 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 98 | 11815616 | 4121 | 98.904 | 4.121 | 4.4 | 4.4 | 2B | 0 | 0 | 1056 | 0 | 1068 | N/A | N/A | N/A | N/A | 31927952 | 694 | 168.4057 | 0% | 0% | 100% | 0% | 100% | 25% | 7010311 | 489 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 86 | 11819471 | 3855 | 92.52 | 3.855 | 5.1 | 5.1 | 2B | 0 | 0 | 1004 | 0 | 1008 | N/A | N/A | N/A | N/A | 31928564 | 612 | 158.7549 | 0% | 0% | 100% | 0% | 100% | 25% | 7010934 | 623 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.5 | 121659 | 121659 | 121.659 | 121.659 | [12 empty] | 24698 | 24698 | 203.0101 | [6 empty] | 5773 | 5773 | 0.995 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 20) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24970 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11819471 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31928564 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7010934 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 102 | 88 | 11823148 | 3677 | 88.248 | 3.677 | 6.2 | 6.2 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 31929153 | 589 | 160.1849 | 0% | 0% | 100% | 0% | 100% | 35% | 7011889 | 955 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 87 | 11826751 | 3603 | 86.472 | 3.603 | 7.4 | 7.4 | 2B | 0 | 0 | 1004 | 0 | 1009 | N/A | N/A | N/A | N/A | 31929713 | 560 | 155.426 | 0% | 0% | 100% | 0% | 100% | 35% | 7013048 | 1159 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 89 | 11830340 | 3589 | 86.136 | 3.589 | 8.6 | 8.6 | 2B | 0 | 0 | 9005 | 0 | 9008 | N/A | N/A | N/A | N/A | 31930215 | 502 | 139.8718 | 0% | 0% | 100% | 0% | 100% | 35% | 7014430 | 1382 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 85 | 11833822 | 3482 | 83.568 | 3.482 | 9.5 | 9.5 | 2B | 0 | 0 | 893 | 0 | 9008 | N/A | N/A | N/A | N/A | 31930686 | 471 | 135.2671 | 0% | 0% | 100% | 0% | 100% | 35% | 7015159 | 729 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 11837652 | 3830 | 91.92 | 3.83 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 0 | 978 | N/A | N/A | N/A | N/A | 31931156 | 470 | 122.7154 | 0% | 0% | 100% | 0% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 117 | 11842216 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 2B | 0 | 0 | 1123 | 0 | 1129 | N/A | N/A | N/A | N/A | 31931828 | 672 | 147.2393 | 0% | 0% | 100% | 0% | 100% | 0% | 7015159 | 0 | 0.96 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 147 | 11848203 | 5987 | 143.688 | 5.987 | 9 | 9 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31933139 | 1311 | 218.9744 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 150 | 11854399 | 6196 | 148.704 | 6.196 | 8.5 | 8.5 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31934450 | 1311 | 211.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 151 | 11860679 | 6280 | 150.72 | 6.28 | 8 | 8 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31935846 | 1396 | 222.293 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 11866720 | 6041 | 144.984 | 6.041 | 7.3 | 7.3 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31937206 | 1360 | 225.1283 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 11873052 | 6332 | 151.968 | 6.332 | 6.7 | 6.7 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31938622 | 1416 | 223.626 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 11879331 | 6279 | 150.696 | 6.279 | 6.1 | 6.1 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31940038 | 1416 | 225.5136 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 11885101 | 5770 | 138.48 | 5.77 | 5.8 | 5.8 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31941360 | 1322 | 229.1161 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 137 | 11890937 | 5836 | 140.064 | 5.836 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31942706 | 1346 | 230.6374 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 128 | 11896421 | 5484 | 131.616 | 5.484 | 5.5 | 5.5 | 3B+1S | 0 | 1014 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31943963 | 1257 | 229.2123 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 132 | 11902008 | 5587 | 134.088 | 5.587 | 5.3 | 5.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31945220 | 1257 | 224.9866 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 11907616 | 5608 | 134.592 | 5.608 | 5 | 5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31946510 | 1290 | 230.0285 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 11913337 | 5721 | 137.304 | 5.721 | 4.9 | 4.9 | 3B+1S | 0 | 989 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31947852 | 1342 | 234.5744 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 117 | 11918873 | 5536 | 132.864 | 5.536 | 4.3 | 4.3 | 3B+1S | 0 | 999 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 31949034 | 1182 | 213.5116 | 0% | 100% | 100% | 100% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 11924123 | 5250 | 126 | 5.25 | 3.6 | 3.6 | 2B+1S | 0 | 1072 | 1199 | 0 | 1199 | N/A | N/A | N/A | N/A | 31950080 | 1046 | 199.2381 | 0% | 100% | 100% | 0% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 122 | 11929857 | 5734 | 137.616 | 5.734 | 3 | 3 | 2B+1S | 0 | 1018 | 1199 | 0 | 1199 | N/A | N/A | N/A | N/A | 31951114 | 1034 | 180.3279 | 0% | 100% | 100% | 0% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 123 | 11934718 | 4861 | 116.664 | 4.861 | 2.8 | 2.8 | 2B+1S | 0 | 850 | 1160 | 0 | 1170 | N/A | N/A | N/A | N/A | 31952140 | 1026 | 211.0677 | 0% | 100% | 100% | 0% | 100% | 0% | 7015159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 98 | 11938783 | 4065 | 97.56 | 4.065 | 3.3 | 3.3 | 2B | 0 | 0 | 1051 | 0 | 1110 | N/A | N/A | N/A | N/A | 31952882 | 742 | 182.5338 | 0% | 0% | 100% | 0% | 100% | 25% | 7015673 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 94 | 11942750 | 3967 | 95.208 | 3.967 | 4.1 | 4.1 | 2B | 0 | 0 | 948 | 0 | 1110 | N/A | N/A | N/A | N/A | 31953534 | 652 | 164.3559 | 0% | 0% | 100% | 0% | 100% | 25% | 7016433 | 760 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.6667 | 123279 | 123279 | 123.279 | 123.279 | [12 empty] | 24970 | 24970 | 202.5487 | [6 empty] | 5499 | 5499 | 1.01 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP3 - STOPPED@ 6:01 PM DUE TO REPAIR OF THE CHECK VALVE LEAK
BP3 - RESTARTED @ 6:31 PM
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:17 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 28) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11942750 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31953534 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7016433 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 89 | 112 | 11946312 | 3562 | 85.488 | 3.562 | 5.7 | 5.7 | 2B | 0 | 0 | 1032 | 0 | 1110 | N/A | N/A | N/A | N/A | 31954144 | 610 | 171.2521 | 0% | 0% | 100% | 0% | 100% | 35% | 7017701 | 1268 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 87 | 110 | 11949884 | 3572 | 85.728 | 3.572 | 6.7 | 6.7 | 2B | 0 | 0 | 948 | 0 | 1010 | N/A | N/A | N/A | N/A | 31954686 | 542 | 151.7357 | 0% | 0% | 100% | 0% | 100% | 35% | 7018965 | 1264 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 86 | 98 | 11953394 | 3510 | 84.24 | 3.51 | 7.9 | 7.9 | 2B | 0 | 0 | 935 | 0 | 1010 | N/A | N/A | N/A | N/A | 31955224 | 538 | 153.2764 | 0% | 0% | 100% | 0% | 100% | 35% | 7020218 | 1253 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 99 | 11956842 | 3448 | 82.752 | 3.448 | 9.5 | 9.5 | 2B | 0 | 0 | 865 | 0 | 990 | N/A | N/A | N/A | N/A | 31955678 | 454 | 131.6705 | 0% | 0% | 100% | 0% | 100% | 35% | 7021485 | 1267 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 97 | 11960609 | 3767 | 90.408 | 3.767 | 9.5 | 9.5 | 2B | 0 | 0 | 942 | 0 | 990 | N/A | N/A | N/A | N/A | 31956150 | 472 | 125.2986 | 0% | 0% | 100% | 0% | 100% | 35% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 118 | 11965222 | 4613 | 110.712 | 4.613 | 9.5 | 9.5 | 2B | 0 | 0 | 1152 | 0 | 1170 | N/A | N/A | N/A | N/A | 31956842 | 692 | 150.0108 | 0% | 0% | 100% | 0% | 100% | 0% | 7021485 | 0 | 0 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 151 | 11971420 | 6198 | 148.752 | 6.198 | 9.1 | 9.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31958181 | 1339 | 216.0374 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 11977433 | 6013 | 144.312 | 6.013 | 8.6 | 8.6 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31959520 | 1339 | 222.6842 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 11983697 | 6264 | 150.336 | 6.264 | 8 | 8 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31960920 | 1400 | 223.4994 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 11989946 | 6249 | 149.976 | 6.249 | 7.3 | 7.3 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31962310 | 1390 | 222.4356 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 | 0 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 11995942 | 5996 | 143.904 | 5.996 | 6.8 | 6.8 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31963678 | 1368 | 228.1521 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 12002026 | 6084 | 146.016 | 6.084 | 6.5 | 6.5 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31965026 | 1348 | 221.5648 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 139 | 12007904 | 5878 | 141.072 | 5.878 | 6.2 | 6.2 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31966374 | 1348 | 229.3297 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 133 | 12013744 | 5840 | 140.16 | 5.84 | 5.8 | 5.8 | 3B+1S | 0 | 1011 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31967730 | 1356 | 232.1918 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 126 | 135 | 12019340 | 5596 | 134.304 | 5.596 | 5.7 | 5.7 | 3B+1S | 0 | 1045 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31969006 | 1276 | 228.02 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 132 | 12024962 | 5622 | 134.928 | 5.622 | 5.2 | 5.2 | 3B+1S | 0 | 1043 | 1164 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31970246 | 1240 | 220.5621 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 12030642 | 5680 | 136.32 | 5.68 | 4.7 | 4.7 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1168 | N/A | N/A | N/A | N/A | 31971542 | 1296 | 228.169 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 12036303 | 5661 | 135.864 | 5.661 | 4.5 | 4.5 | 3B+1S | 0 | 997 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 31972858 | 1316 | 232.4678 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 132 | 12041876 | 5573 | 133.752 | 5.573 | 4.4 | 4.4 | 3B+1S | 0 | 972 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31974158 | 1300 | 233.2675 | 0% | 100% | 100% | 100% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 129 | 12047319 | 5443 | 130.632 | 5.443 | 3.6 | 3.6 | 2B+1S | 0 | 1081 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31975250 | 1092 | 200.6247 | 0% | 100% | 100% | 0% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 12052547 | 5228 | 125.472 | 5.228 | 3 | 3 | 2B+1S | 0 | 1020 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 31976294 | 1044 | 199.694 | 0% | 100% | 100% | 0% | 100% | 0% | 7021485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 111 | 12057576 | 5029 | 120.696 | 5.029 | 2.8 | 2.8 | 2B+1S | 0 | 1001 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 31977294 | 1000 | 198.8467 | 0% | 100% | 100% | 0% | 100% | 0% | 7021485 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 96 | 12061797 | 4221 | 101.304 | 4.221 | 3.4 | 3.4 | 2B | 0 | 0 | 1074 | 0 | 1100 | N/A | N/A | N/A | N/A | 31978028 | 734 | 173.8924 | 0% | 0% | 100% | 0% | 100% | 30% | 7022560 | 1075 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 93 | 12065604 | 3807 | 91.368 | 3.807 | 4.4 | 4.4 | 2B | 0 | 0 | 1048 | 0 | 1109 | N/A | N/A | N/A | N/A | 31978670 | 642 | 168.6367 | 0% | 0% | 100% | 0% | 100% | 30% | 7023635 | 1075 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.625 | 122854 | 122854 | 122.854 | 122.854 | [12 empty] | 25136 | 25136 | 204.6006 | [6 empty] | 7202 | 7202 | 0 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 3:52 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 29) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24605 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12065604 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 31978670 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7023635 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 86 | 12069411 | 3807 | 91.368 | 3.807 | 6.3 | 6.3 | 2B | 0 | 0 | 952 | 0 | 1110 | N/A | N/A | N/A | N/A | 31979312 | 642 | 168.6367 | 0% | 0% | 100% | 0% | 100% | 35% | 7024711 | 1076 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 81 | 12072942 | 3531 | 84.744 | 3.531 | 8.9 | 8.9 | 2B | 0 | 0 | 943 | 0 | 1109 | N/A | N/A | N/A | N/A | 31979891 | 579 | 163.9762 | 0% | 0% | 100% | 0% | 100% | 35% | 7026255 | 1544 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 86 | 84 | 12076474 | 3532 | 84.768 | 3.532 | 9.5 | 9.5 | 2B | 0 | 0 | 803 | 0 | 1110 | N/A | N/A | N/A | N/A | 31980470 | 579 | 163.9298 | 0% | 0% | 100% | 0% | 100% | 35% | 7027801 | 1546 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 85 | 12080072 | 3598 | 86.352 | 3.598 | 9.5 | 9.5 | 2B | 0 | 0 | 899 | 0 | 1069 | N/A | N/A | N/A | N/A | 31980969 | 499 | 138.6882 | 0% | 0% | 100% | 0% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 94 | 12083670 | 3598 | 86.352 | 3.598 | 9.5 | 9.5 | 2B | 0 | 0 | 918 | 0 | 1069 | N/A | N/A | N/A | N/A | 31981468 | 499 | 138.6882 | 0% | 0% | 100% | 0% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 112 | 12088198 | 4528 | 108.672 | 4.528 | 9.5 | 9.5 | 2B | 0 | 0 | 1105 | 0 | 1109 | N/A | N/A | N/A | N/A | 31982142 | 674 | 148.8516 | 0% | 0% | 100% | 0% | 100% | 0% | 7027801 | 0 | 0 | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 142 | 12094318 | 6120 | 146.88 | 6.12 | 9.2 | 9.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31983516 | 1374 | 224.5098 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 12100251 | 5933 | 142.392 | 5.933 | 8.9 | 8.9 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31984806 | 1290 | 217.4279 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 12106490 | 6239 | 149.736 | 6.239 | 8.5 | 8.5 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31986180 | 1374 | 220.2276 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 12112626 | 6136 | 147.264 | 6.136 | 7.9 | 7.9 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31987560 | 1380 | 224.9022 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 | 0 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 12118724 | 6098 | 146.352 | 6.098 | 7.5 | 7.5 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 31988900 | 1340 | 219.7442 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 12124701 | 5977 | 143.448 | 5.977 | 7.3 | 7.3 | 3B+1S | 0 | 999 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 31990240 | 1340 | 224.1927 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 141 | 12130240 | 5539 | 132.936 | 5.539 | 6.9 | 6.9 | 3B+1S | 0 | 1036 | 1134 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31991440 | 1200 | 216.6456 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 124 | 132 | 12136062 | 5822 | 139.728 | 5.822 | 6.3 | 6.3 | 3B+1S | 0 | 1056 | 1135 | 1185 | 1140 | N/A | N/A | N/A | N/A | 31992718 | 1278 | 219.5122 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 12141545 | 5483 | 131.592 | 5.483 | 6 | 6 | 3B+1S | 0 | 963 | 1195 | 1185 | 1169 | N/A | N/A | N/A | N/A | 31993938 | 1220 | 222.5059 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 12147122 | 5577 | 133.848 | 5.577 | 5.9 | 5.9 | 3B+1S | 0 | 987 | 1165 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31995202 | 1264 | 226.6451 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 132 | 12152622 | 5500 | 132 | 5.5 | 5.7 | 5.7 | 3B+1S | 0 | 1022 | 1165 | 1185 | 1181 | N/A | N/A | N/A | N/A | 31996462 | 1260 | 229.0909 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 131 | 12158069 | 5447 | 130.728 | 5.447 | 5.6 | 5.6 | 3B+1S | 0 | 983 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31997708 | 1246 | 228.7498 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 127 | 12163513 | 5444 | 130.656 | 5.444 | 5.4 | 5.4 | 3B+1S | 0 | 993 | 1126 | 1185 | 1139 | N/A | N/A | N/A | N/A | 31998902 | 1194 | 219.324 | 0% | 100% | 100% | 100% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 12168853 | 5340 | 128.16 | 5.34 | 4.9 | 4.9 | 2B+1S | 0 | 1033 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 31999956 | 1054 | 197.3783 | 0% | 100% | 100% | 0% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 121 | 12174020 | 5167 | 124.008 | 5.167 | 4.5 | 4.5 | 2B+1S | 0 | 991 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32000978 | 1022 | 197.7937 | 0% | 100% | 100% | 0% | 100% | 0% | 7027801 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 113 | 12178986 | 4966 | 119.184 | 4.966 | 4.2 | 4.2 | 2B+1S | 0 | 974 | 1166 | 0 | 1140 | N/A | N/A | N/A | N/A | 32001938 | 960 | 193.3145 | 0% | 100% | 100% | 0% | 100% | 0% | 7027801 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 98 | 12183050 | 4064 | 97.536 | 4.064 | 4.8 | 4.8 | 2B | 0 | 0 | 1114 | 0 | 1109 | N/A | N/A | N/A | N/A | 32002640 | 702 | 172.7362 | 0% | 0% | 100% | 0% | 100% | 25% | 7028371 | 570 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 89 | 12186858 | 3808 | 91.392 | 3.808 | 5.9 | 5.9 | 2B | 0 | 0 | 968 | 0 | 1110 | N/A | N/A | N/A | N/A | 32003275 | 635 | 166.7542 | 0% | 0% | 100% | 0% | 100% | 25% | 7029404 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.7083 | 121254 | 121254 | 121.254 | 121.254 | [12 empty] | 24605 | 24605 | 202.9211 | [6 empty] | 5769 | 5769 | 0 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 2:56 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT29) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY O. REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25065 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12186858 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32003275 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7029404 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 89 | 12190667 | 3809 | 91.416 | 3.809 | 7.1 | 7.1 | 2B | 0 | 0 | 943 | 0 | 1110 | N/A | N/A | N/A | N/A | 32003910 | 635 | 166.7104 | 0% | 0% | 100% | 0% | 100% | 35% | 7030393 | 989 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 85 | 12194188 | 3521 | 84.504 | 3.521 | 8.8 | 8.8 | 2B | 0 | 0 | 920 | 0 | 1109 | N/A | N/A | N/A | N/A | 32004478 | 568 | 161.3178 | 0% | 0% | 100% | 0% | 100% | 35% | 7031626 | 1233 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 83 | 12197709 | 3521 | 84.504 | 3.521 | 9.5 | 9.5 | 2B | 0 | 0 | 805 | 0 | 1079 | N/A | N/A | N/A | N/A | 32005046 | 568 | 161.3178 | 0% | 0% | 100% | 0% | 100% | 35% | 7032859 | 1233 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 86 | 12201346 | 3637 | 87.288 | 3.637 | 9.5 | 9.5 | 2B | 0 | 0 | 826 | 0 | 1109 | N/A | N/A | N/A | N/A | 32005545 | 499 | 137.201 | 0% | 0% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 92 | 12204984 | 3638 | 87.312 | 3.638 | 9.5 | 9.5 | 2B | 0 | 0 | 866 | 0 | 1079 | N/A | N/A | N/A | N/A | 32006044 | 499 | 137.1633 | 0% | 0% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 114 | 12209470 | 4486 | 107.664 | 4.486 | 9.5 | 9.5 | 2B | 0 | 0 | 1094 | 0 | 1110 | N/A | N/A | N/A | N/A | 32006716 | 672 | 149.7994 | 0% | 0% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 146 | 12215449 | 5979 | 143.496 | 5.979 | 9.3 | 9.3 | 3B+1S | 0 | 981 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32008038 | 1322 | 221.1072 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 12221510 | 6061 | 145.464 | 6.061 | 9 | 9 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32009386 | 1348 | 222.4055 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 12227732 | 6222 | 149.328 | 6.222 | 8.5 | 8.5 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32010778 | 1392 | 223.7223 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 12233845 | 6113 | 146.712 | 6.113 | 7.9 | 7.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32012160 | 1382 | 226.0756 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 12240083 | 6238 | 149.712 | 6.238 | 7.3 | 7.3 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32013542 | 1382 | 221.5454 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 148 | 12246071 | 5988 | 143.712 | 5.988 | 6.9 | 6.9 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32014874 | 1332 | 222.4449 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 12251733 | 5662 | 135.888 | 5.662 | 6.8 | 6.8 | 3B+1S | 0 | 1000 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32016176 | 1302 | 229.9541 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 137 | 12257396 | 5663 | 135.912 | 5.663 | 6.6 | 6.6 | 3B+1S | 0 | 1033 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32017478 | 1302 | 229.9135 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 12263025 | 5629 | 135.096 | 5.629 | 6.3 | 6.3 | 3B+1S | 0 | 920 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32018782 | 1304 | 231.6575 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 12268686 | 5661 | 135.864 | 5.661 | 6.1 | 6.1 | 3B+1S | 0 | 969 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32020072 | 1290 | 227.8749 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 12274347 | 5661 | 135.864 | 5.661 | 5.9 | 5.9 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1191 | N/A | N/A | N/A | N/A | 32021362 | 1290 | 227.8749 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 12280032 | 5685 | 136.44 | 5.685 | 5.6 | 5.6 | 3B+1S | 0 | 983 | 1164 | 1185 | 1181 | N/A | N/A | N/A | N/A | 32022654 | 1292 | 227.2647 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 132 | 12285541 | 5509 | 132.216 | 5.509 | 5.5 | 5.5 | 3B+1S | 0 | 1001 | 1135 | 1185 | 1140 | N/A | N/A | N/A | N/A | 32023894 | 1240 | 225.0862 | 0% | 100% | 100% | 100% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 126 | 12290774 | 5233 | 125.592 | 5.233 | 4.9 | 4.9 | 2B+1S | 0 | 1035 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32024938 | 1044 | 199.5032 | 0% | 100% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 117 | 12295836 | 5062 | 121.488 | 5.062 | 4.5 | 4.5 | 2B+1S | 0 | 990 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32025938 | 1000 | 197.5504 | 0% | 100% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 117 | 12300899 | 5063 | 121.512 | 5.063 | 4.2 | 4.2 | 2B+1S | 0 | 973 | 1166 | 0 | 1170 | N/A | N/A | N/A | N/A | 32026938 | 1000 | 197.5114 | 0% | 100% | 100% | 0% | 100% | 0% | 7032859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 95 | 12305196 | 4297 | 103.128 | 4.297 | 4.8 | 4.8 | 2B | 0 | 0 | 1098 | 0 | 1110 | N/A | N/A | N/A | N/A | 32027688 | 750 | 174.5404 | 0% | 0% | 100% | 0% | 100% | 25% | 7033432 | 573 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 86 | 12309086 | 3890 | 93.36 | 3.89 | 5.8 | 5.8 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 32028340 | 652 | 167.6093 | 0% | 0% | 100% | 0% | 100% | 25% | 7034331 | 899 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.7917 | 122228 | 122228 | 122.228 | 122.228 | [12 empty] | 25065 | 25065 | 205.0676 | [6 empty] | 4927 | 4927 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 2:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT 31) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION

## OCT 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS L. GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS L. GUANZON
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-10-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24998 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12309086 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32028340 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7034331 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 91 | 12312761 | 3675 | 88.2 | 3.675 | 7 | 7 | 2B | 0 | 0 | 957 | 0 | 1110 | N/A | N/A | N/A | N/A | 32028952 | 612 | 166.5306 | 0% | 0% | 100% | 0% | 100% | 35% | 7035528 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 84 | 12316315 | 3554 | 85.296 | 3.554 | 8.4 | 8.4 | 2B | 0 | 0 | 915 | 0 | 1110 | N/A | N/A | N/A | N/A | 32029536 | 584 | 164.3219 | 0% | 0% | 100% | 0% | 100% | 35% | 7036818 | 1290 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 81 | 12319870 | 3555 | 85.32 | 3.555 | 9.5 | 9.5 | 2B | 0 | 0 | 820 | 0 | 1069 | N/A | N/A | N/A | N/A | 32030065 | 529 | 148.8045 | 0% | 0% | 100% | 0% | 100% | 35% | 7037881 | 1063 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 82 | 12323425 | 3555 | 85.32 | 3.555 | 9.5 | 9.5 | 2B | 0 | 0 | 810 | 0 | 1069 | N/A | N/A | N/A | N/A | 32030594 | 529 | 148.8045 | 0% | 0% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 98 | 12326981 | 3556 | 85.344 | 3.556 | 9.5 | 9.5 | 2B | 0 | 0 | 907 | 0 | 1068 | N/A | N/A | N/A | N/A | 32031124 | 530 | 149.0439 | 0% | 0% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 116 | 12331157 | 4176 | 100.224 | 4.176 | 9.5 | 9.5 | 2B | 0 | 0 | 1165 | 0 | 1064 | N/A | N/A | N/A | N/A | 32031690 | 566 | 135.5364 | 0% | 0% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 12336920 | 5763 | 138.312 | 5.763 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32032938 | 1248 | 216.5539 | 0% | 0% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 134 | 12343204 | 6284 | 150.816 | 6.284 | 8.8 | 8.8 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32034233 | 1295 | 206.0789 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 12349228 | 6024 | 144.576 | 6.024 | 8.3 | 8.3 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32035649 | 1416 | 235.0598 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 12355397 | 6169 | 148.056 | 6.169 | 7.4 | 7.4 | 3B+1S | 0 | 1107 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32037066 | 1417 | 229.6969 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 12361711 | 6314 | 151.536 | 6.314 | 6.8 | 6.8 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32038482 | 1416 | 224.2635 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 12367996 | 6285 | 150.84 | 6.285 | 6.3 | 6.3 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32039898 | 1416 | 225.2983 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 136 | 12374292 | 6296 | 151.104 | 6.296 | 5.9 | 5.9 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32041240 | 1342 | 213.1512 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 12379674 | 5382 | 129.168 | 5.382 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 32042515 | 1275 | 236.9008 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 12385034 | 5360 | 128.64 | 5.36 | 5.4 | 5.4 | 3B+1S | 0 | 1004 | 1155 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32043790 | 1275 | 237.8731 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 134 | 12390710 | 5676 | 136.224 | 5.676 | 5.1 | 5.1 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32045066 | 1276 | 224.8062 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 130 | 12396419 | 5709 | 137.016 | 5.709 | 4.9 | 4.9 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32046386 | 1320 | 231.2139 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 135 | 12402098 | 5679 | 136.296 | 5.679 | 4.7 | 4.7 | 3B+1S | 0 | 984 | 1176 | 1185 | 1160 | N/A | N/A | N/A | N/A | 32047678 | 1292 | 227.5048 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 12407664 | 5566 | 133.584 | 5.566 | 4.6 | 4.6 | 2B+1S | 0 | 992 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 32048942 | 1264 | 227.0931 | 0% | 100% | 100% | 100% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 12413011 | 5347 | 128.328 | 5.347 | 4 | 4 | 2B+1S | 0 | 1047 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32050006 | 1064 | 198.9901 | 0% | 100% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 118 | 12418043 | 5032 | 120.768 | 5.032 | 3.6 | 3.6 | 2B+1S | 0 | 987 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32051002 | 996 | 197.9332 | 0% | 100% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 112 | 12423061 | 5018 | 120.432 | 5.018 | 3.5 | 3.5 | 2B+1S | 0 | 980 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 32051910 | 908 | 180.9486 | 0% | 100% | 100% | 0% | 100% | 0% | 7037881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 98 | 12427412 | 4351 | 104.424 | 4.351 | 4.1 | 4.1 | 2B | 0 | 0 | 1068 | 0 | 1079 | N/A | N/A | N/A | N/A | 32052720 | 810 | 186.1641 | 0% | 0% | 100% | 0% | 100% | 25% | 7038372 | 491 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 89 | 12431257 | 3845 | 92.28 | 3.845 | 4.9 | 4.9 | 2B | 0 | 0 | 1011 | 0 | 1018 | N/A | N/A | N/A | N/A | 32053338 | 618 | 160.7282 | 0% | 0% | 100% | 0% | 100% | 25% | 7038983 | 611 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.625 | 122171 | 122171 | 122.171 | 122.171 | [12 empty] | 24998 | 24998 | 204.6148 | [6 empty] | 4652 | 4652 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1- OPENED @ 12:01 AM (35%) / CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (OCT28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (OCT 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1- OPENED @ 10:01 PM (25%)
NORMAL OPERATION