## NOV 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23552 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12431257 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32053338 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7038983 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 87 | 12434979 | 3722 | 89.328 | 3.722 | 6.1 | 6.1 | 2B | 0 | 0 | 1008 | 0 | 1018 | N/A | N/A | N/A | N/A | 32053934 | 596 | 160.129 | 0% | 0% | 100% | 0% | 100% | 35% | 7039955 | 972 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 86 | 12438585 | 3606 | 86.544 | 3.606 | 8.1 | 8.1 | 2B | 0 | 0 | 960 | 0 | 968 | N/A | N/A | N/A | N/A | 32054476 | 542 | 150.305 | 0% | 0% | 100% | 0% | 100% | 35% | 7041339 | 1384 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 83 | 12442173 | 3588 | 86.112 | 3.588 | 8.9 | 8.9 | 2B | 0 | 0 | 959 | 0 | 968 | N/A | N/A | N/A | N/A | 32055004 | 528 | 147.1572 | 0% | 0% | 100% | 0% | 100% | 35% | 7042542 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 85 | 12445610 | 3437 | 82.488 | 3.437 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 0 | 899 | N/A | N/A | N/A | N/A | 32055430 | 426 | 123.9453 | 0% | 0% | 100% | 0% | 100% | 35% | 7043452 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 89 | 12449136 | 3526 | 84.624 | 3.526 | 9.5 | 9.5 | 2B | 0 | 0 | 898 | 0 | 899 | N/A | N/A | N/A | N/A | 32055852 | 422 | 119.6824 | 0% | 0% | 100% | 0% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 102 | 12453150 | 4014 | 96.336 | 4.014 | 9.5 | 9.5 | 2B | 0 | 0 | 991 | 0 | 1002 | N/A | N/A | N/A | N/A | 32056370 | 518 | 129.0483 | 0% | 0% | 100% | 0% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 12458495 | 5345 | 128.28 | 5.345 | 9.5 | 9.5 | 3B | 0 | 0 | 1075 | 1185 | 1079 | N/A | N/A | N/A | N/A | 32057430 | 1060 | 198.3162 | 0% | 0% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 142 | 12464274 | 5779 | 138.696 | 5.779 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1170 | N/A | N/A | N/A | N/A | 32058610 | 1180 | 204.1876 | 0% | 0% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 146 | 12470309 | 6035 | 144.84 | 6.035 | 9.3 | 9.3 | 3B+1S | 0 | 994 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32059942 | 1332 | 220.7125 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 147 | 12476478 | 6169 | 148.056 | 6.169 | 8.9 | 8.9 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32061306 | 1364 | 221.1055 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 145 | 12482651 | 6173 | 148.152 | 6.173 | 8.6 | 8.6 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32062675 | 1369 | 221.7722 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 142 | 12488816 | 6165 | 147.96 | 6.165 | 8.3 | 8.3 | 3B+1S | 0 | 1017 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32064024 | 1349 | 218.8159 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 123 | 136 | 12494614 | 5798 | 139.152 | 5.798 | 7.6 | 7.6 | 3B+1S | 0 | 1124 | 1104 | 1185 | 1109 | N/A | N/A | N/A | N/A | 32065274 | 1250 | 215.5916 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 140 | 138 | 12500361 | 5747 | 137.928 | 5.747 | 6.8 | 6.8 | 3B+1S | 0 | 981 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32066510 | 1236 | 215.0687 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 12506094 | 5733 | 137.592 | 5.733 | 6.7 | 6.7 | 3B+1S | 0 | 997 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 32067802 | 1292 | 225.3619 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 127 | 12511688 | 5594 | 134.256 | 5.594 | 6.6 | 6.6 | 3B+1S | 0 | 979 | 1197 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32069098 | 1296 | 231.6768 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 12517352 | 5664 | 135.936 | 5.664 | 6.4 | 6.4 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32070410 | 1312 | 231.6384 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 137 | 12522970 | 5618 | 134.832 | 5.618 | 6.1 | 6.1 | 3B+1S | 0 | 975 | 1165 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32071638 | 1228 | 218.5831 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 124 | 12528411 | 5441 | 130.584 | 5.441 | 6 | 6 | 3B+1S | 0 | 1004 | 165 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32072838 | 1200 | 220.5477 | 0% | 100% | 100% | 100% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 121 | 12533454 | 5043 | 121.032 | 5.043 | 5.8 | 5.8 | 2B+1S | 0 | 978 | 1165 | 0 | 1199 | N/A | N/A | N/A | N/A | 32073804 | 966 | 191.5526 | 0% | 100% | 100% | 0% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 118 | 12538497 | 5043 | 121.032 | 5.043 | 5.7 | 5.7 | 2B+1S | 0 | 959 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 32074770 | 966 | 191.5526 | 0% | 100% | 100% | 0% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 115 | 12543335 | 4838 | 116.112 | 4.838 | 5.6 | 5.6 | 2B+1S | 0 | 938 | 1165 | 0 | 1110 | N/A | N/A | N/A | N/A | 32075644 | 874 | 180.6532 | 0% | 100% | 100% | 0% | 100% | 0% | 7043452 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 93 | 12547341 | 4006 | 96.144 | 4.006 | 6.2 | 6.2 | 2B | 0 | 0 | 981 | 0 | 1110 | N/A | N/A | N/A | N/A | 32076298 | 654 | 163.2551 | 0% | 0% | 100% | 0% | 100% | 25% | 7043984 | 532 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 107 | 89 | 12551063 | 3722 | 89.328 | 3.722 | 6.8 | 6.8 | 2B | 0 | 0 | 933 | 0 | 1060 | N/A | N/A | N/A | N/A | 32076890 | 592 | 159.0543 | 0% | 0% | 100% | 0% | 100% | 25% | 7044627 | 643 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.3333 | 119806 | 119806 | 119.806 | 119.806 | [12 empty] | 23552 | 23552 | 196.5845 | [6 empty] | 5644 | 5644 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:41 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 2) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:13 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 2) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12551063 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32076890 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7044627 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 86 | 12554658 | 3595 | 86.28 | 3.595 | 7.8 | 7.8 | 2B | 0 | 0 | 965 | 0 | 1018 | N/A | N/A | N/A | N/A | 32077438 | 548 | 152.4339 | 0% | 0% | 100% | 0% | 100% | 30% | 7045543 | 916 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 | 84 | 12558155 | 3497 | 83.928 | 3.497 | 8.8 | 8.8 | 2B | 0 | 0 | 942 | 0 | 987 | N/A | N/A | N/A | N/A | 32077954 | 516 | 147.555 | 0% | 0% | 100% | 0% | 100% | 30% | 7046541 | 998 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 83 | 12561686 | 3531 | 84.744 | 3.531 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 948 | N/A | N/A | N/A | N/A | 32078432 | 478 | 135.3724 | 0% | 0% | 100% | 0% | 100% | 30% | 7047172 | 631 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 82 | 83 | 12565152 | 3466 | 83.184 | 3.466 | 9.5 | 9.5 | 2B | 0 | 0 | 852 | 0 | 948 | N/A | N/A | N/A | N/A | 32078862 | 430 | 124.0623 | 0% | 0% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 85 | 12568660 | 3508 | 84.192 | 3.508 | 9.5 | 9.5 | 2B | 0 | 0 | 840 | 0 | 948 | N/A | N/A | N/A | N/A | 32079278 | 416 | 118.5861 | 0% | 0% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 110 | 12572687 | 4027 | 96.648 | 4.027 | 9.5 | 9.5 | 2B | 0 | 0 | 988 | 0 | 989 | N/A | N/A | N/A | N/A | 32079750 | 472 | 117.2088 | 0% | 0% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 136 | 12578024 | 5337 | 128.088 | 5.337 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1088 | N/A | N/A | N/A | N/A | 32080746 | 996 | 186.6217 | 0% | 0% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 12584420 | 6396 | 153.504 | 6.396 | 9.5 | 9.5 | 3B | 0 | 0 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 32082068 | 1322 | 206.6917 | 0% | 0% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 143 | 12590222 | 5802 | 139.248 | 5.802 | 9.3 | 9.3 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32083337 | 1269 | 218.7177 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 12596074 | 5852 | 140.448 | 5.852 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32084614 | 1277 | 218.216 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 12602199 | 6125 | 147 | 6.125 | 8.5 | 8.5 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32085986 | 1372 | 224 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 12608298 | 6099 | 146.376 | 6.099 | 8.1 | 8.1 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32087334 | 1348 | 221.0198 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 139 | 12614224 | 5926 | 142.224 | 5.926 | 7.8 | 7.8 | 3B+1S | 0 | 1054 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32088648 | 1314 | 221.7347 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 12620122 | 5898 | 141.552 | 5.898 | 7.1 | 7.1 | 3B+1S | 0 | 1051 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32089944 | 1296 | 219.7355 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 12625793 | 5671 | 136.104 | 5.671 | 6.5 | 6.5 | 3B+1S | 0 | 1044 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32091214 | 1270 | 223.9464 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 12631445 | 5652 | 135.648 | 5.652 | 6.1 | 6.1 | 3B+1S | 0 | 1044 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32092470 | 1256 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 136 | 12637158 | 5713 | 137.112 | 5.713 | 5.4 | 5.4 | 3B+1S | 0 | 1084 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32093768 | 1298 | 227.2011 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 135 | 12642839 | 5681 | 136.344 | 5.681 | 5.1 | 5.1 | 3B+1S | 0 | 1021 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32095032 | 1264 | 222.496 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 134 | 12648354 | 5515 | 132.36 | 5.515 | 4.9 | 4.9 | 3B+1S | 0 | 975 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32096262 | 1230 | 223.0281 | 0% | 100% | 100% | 100% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 123 | 12653618 | 5264 | 126.336 | 5.264 | 4.4 | 4.4 | 2B+1S | 0 | 1020 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32097314 | 1052 | 199.848 | 0% | 100% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 125 | 12658786 | 5168 | 124.032 | 5.168 | 4.1 | 4.1 | 2B+1S | 0 | 975 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32098332 | 1018 | 196.9814 | 0% | 100% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 120 | 12663630 | 4844 | 116.256 | 4.844 | 3.9 | 3.9 | 2B+1S | 0 | 980 | 1145 | 0 | 1150 | N/A | N/A | N/A | N/A | 32099250 | 918 | 189.5128 | 0% | 100% | 100% | 0% | 100% | 0% | 7047172 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 99 | 12667885 | 4255 | 102.12 | 4.255 | 4.6 | 4.6 | 2B | 0 | 0 | 1023 | 0 | 1110 | N/A | N/A | N/A | N/A | 32099962 | 712 | 167.3325 | 0% | 0% | 100% | 0% | 100% | 25% | 7047713 | 541 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 97 | 12671779 | 3894 | 93.456 | 3.894 | 5.3 | 5.3 | 2B | 0 | 0 | 998 | 0 | 1110 | N/A | N/A | N/A | N/A | 32100590 | 628 | 161.2738 | 0% | 0% | 100% | 0% | 100% | 25% | 7048378 | 665 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.25 | 120716 | 120716 | 120.716 | 120.716 | [12 empty] | 23700 | 23700 | 196.3286 | [6 empty] | 3751 | 3751 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 30 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 2:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 3) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 3) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25560 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12671779 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32100590 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7048378 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 90 | 12675455 | 3676 | 88.224 | 3.676 | 6.3 | 6.3 | 2B | 0 | 0 | 973 | 0 | 1050 | N/A | N/A | N/A | N/A | 32101174 | 584 | 158.8683 | 0% | 0% | 100% | 0% | 100% | 35% | 7049425 | 1047 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 88 | 12679021 | 3566 | 85.584 | 3.566 | 7.4 | 7.4 | 2B | 0 | 0 | 980 | 0 | 988 | N/A | N/A | N/A | N/A | 32101706 | 532 | 149.1868 | 0% | 0% | 100% | 0% | 100% | 35% | 7050538 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 86 | 12682485 | 3464 | 83.136 | 3.464 | 8.7 | 8.7 | 2B | 0 | 0 | 947 | 0 | 988 | N/A | N/A | N/A | N/A | 32102206 | 500 | 144.3418 | 0% | 0% | 100% | 0% | 100% | 35% | 7051662 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 86 | 12686070 | 3585 | 86.04 | 3.585 | 9.5 | 9.5 | 2B | 0 | 0 | 880 | 0 | 948 | N/A | N/A | N/A | N/A | 32102698 | 492 | 137.2385 | 0% | 0% | 100% | 0% | 100% | 35% | 7052435 | 773 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 98 | 12689860 | 3790 | 90.96 | 3.79 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 988 | N/A | N/A | N/A | N/A | 32103172 | 474 | 125.066 | 0% | 0% | 100% | 0% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 124 | 12694397 | 4537 | 108.888 | 4.537 | 9.5 | 9.5 | 2B | 0 | 0 | 1131 | 0 | 1170 | N/A | N/A | N/A | N/A | 32103858 | 686 | 151.2012 | 0% | 0% | 100% | 0% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 12700496 | 6099 | 146.376 | 6.099 | 9.3 | 9.3 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32105154 | 1296 | 212.4939 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 12706731 | 6235 | 149.64 | 6.235 | 8.8 | 8.8 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32106542 | 1388 | 222.6143 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 12712883 | 6152 | 147.648 | 6.152 | 8.1 | 8.1 | 3B+1S | 0 | 1094 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32107939 | 1397 | 227.0806 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 12719067 | 6184 | 148.416 | 6.184 | 7.4 | 7.4 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32109352 | 1413 | 228.4929 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 12725275 | 6208 | 148.992 | 6.208 | 6.7 | 6.7 | 3B+1S | 0 | 1089 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32110760 | 1408 | 226.8041 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 12731476 | 6201 | 148.824 | 6.201 | 6.1 | 6.1 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32112154 | 1394 | 224.8025 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 12737396 | 5920 | 142.08 | 5.92 | 5.5 | 5.5 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32113510 | 1356 | 229.0541 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 12743190 | 5794 | 139.056 | 5.794 | 5.1 | 5.1 | 3B+1S | 0 | 1034 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32114840 | 1330 | 229.5478 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 12748961 | 5771 | 138.504 | 5.771 | 4.8 | 4.8 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32116168 | 1328 | 230.1161 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 12754682 | 5721 | 137.304 | 5.721 | 4.7 | 4.7 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32117492 | 1324 | 231.4281 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 142 | 12760421 | 5739 | 137.736 | 5.739 | 4.3 | 4.3 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32118834 | 1342 | 233.8386 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 12766105 | 5684 | 136.416 | 5.684 | 3.9 | 3.9 | 3B+1S | 0 | 1035 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32120123 | 1289 | 226.7769 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 136 | 12771762 | 5657 | 135.768 | 5.657 | 3.5 | 3.5 | 3B+1S | 0 | 1033 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32121390 | 1267 | 223.9703 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 131 | 12777274 | 5512 | 132.288 | 5.512 | 3.3 | 3.3 | 3B+1S | 0 | 998 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32122614 | 1224 | 222.061 | 0% | 100% | 100% | 100% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 12782571 | 5297 | 127.128 | 5.297 | 2.7 | 2.7 | 2B+1S | 0 | 1056 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32123686 | 1072 | 202.3787 | 0% | 100% | 100% | 0% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 127 | 12787563 | 4992 | 119.808 | 4.992 | 2.4 | 2.4 | 2B+1S | 0 | 995 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32124686 | 1000 | 200.3205 | 0% | 100% | 100% | 0% | 100% | 0% | 7052435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 102 | 12791944 | 4381 | 105.144 | 4.381 | 3 | 3 | 2B | 0 | 0 | 1076 | 0 | 1139 | N/A | N/A | N/A | N/A | 32125480 | 794 | 181.2372 | 0% | 0% | 100% | 0% | 100% | 35% | 7053299 | 864 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 88 | 12795841 | 3897 | 93.528 | 3.897 | 4.3 | 4.3 | 2B | 0 | 0 | 995 | 0 | 1109 | N/A | N/A | N/A | N/A | 32126150 | 670 | 171.9271 | 0% | 0% | 100% | 0% | 100% | 35% | 7054164 | 865 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7917 | 124062 | 124062 | 124.062 | 124.062 | [12 empty] | 25560 | 25560 | 206.026 | [6 empty] | 5786 | 5786 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 OPENING INCREASED TO 35 % VALVE OPENING @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:50 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 4) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 4) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24712 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12795841 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32126150 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7054164 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 99 | 12799540 | 3699 | 88.776 | 3.699 | 5.1 | 5.1 | 2B | 0 | 0 | 968 | 0 | 1099 | N/A | N/A | N/A | N/A | 32126744 | 594 | 160.5839 | 0% | 0% | 100% | 0% | 100% | 35% | 7055674 | 1510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 86 | 12803239 | 3699 | 88.776 | 3.699 | 7.3 | 7.3 | 2B | 0 | 0 | 939 | 0 | 1100 | N/A | N/A | N/A | N/A | 32127338 | 594 | 160.5839 | 0% | 0% | 100% | 0% | 100% | 35% | 7057185 | 1511 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 | 90 | 12806779 | 3540 | 84.96 | 3.54 | 9 | 9 | 2B | 0 | 0 | 920 | 0 | 1100 | N/A | N/A | N/A | N/A | 32127886 | 548 | 154.8023 | 0% | 0% | 100% | 0% | 100% | 35% | 7058181 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 88 | 12810320 | 3541 | 84.984 | 3.541 | 9.5 | 9.5 | 2B | 0 | 0 | 817 | 0 | 1100 | N/A | N/A | N/A | N/A | 32128434 | 548 | 154.7585 | 0% | 0% | 100% | 0% | 100% | 35% | 7059178 | 997 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 98 | 12814207 | 3887 | 93.288 | 3.887 | 9.5 | 9.5 | 2B | 0 | 0 | 928 | 0 | 1069 | N/A | N/A | N/A | N/A | 32128950 | 516 | 132.7502 | 0% | 0% | 100% | 0% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 117 | 12818884 | 4677 | 112.248 | 4.677 | 9.5 | 9.5 | 2B | 0 | 0 | 1164 | 0 | 1169 | N/A | N/A | N/A | N/A | 32129698 | 748 | 159.9316 | 0% | 0% | 100% | 0% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 147 | 12824804 | 5920 | 142.08 | 5.92 | 9.2 | 9.2 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32131026 | 1328 | 224.3243 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 12830798 | 5994 | 143.856 | 5.994 | 8.7 | 8.7 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32132385 | 1359 | 226.7267 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 145 | 12836883 | 6085 | 146.04 | 6.085 | 8.2 | 8.2 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32133753 | 1368 | 224.8151 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 142 | 12843061 | 6178 | 148.272 | 6.178 | 7.7 | 7.7 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32135123 | 1370 | 221.7546 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 12849073 | 6012 | 144.288 | 6.012 | 7.4 | 7.4 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32136479 | 1356 | 225.5489 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 12854976 | 5903 | 141.672 | 5.903 | 7.2 | 7.2 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32137808 | 1329 | 225.1398 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 12860693 | 5717 | 137.208 | 5.717 | 6.8 | 6.8 | 3B+1S | 0 | 1024 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32139110 | 1302 | 227.7418 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 135 | 12866279 | 5586 | 134.064 | 5.586 | 6.6 | 6.6 | 3B+1S | 0 | 1002 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32140381 | 1271 | 227.5331 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 121 | 127 | 12871714 | 5435 | 130.44 | 5.435 | 6.4 | 6.4 | 3B+1S | 0 | 1029 | 1095 | 1185 | 1099 | N/A | N/A | N/A | N/A | 32141574 | 1193 | 219.5032 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 136 | 12877222 | 5508 | 132.192 | 5.508 | 6 | 6 | 3B+1S | 0 | 1041 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 32142779 | 1205 | 218.7727 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 138 | 12882782 | 5560 | 133.44 | 5.56 | 5.5 | 5.5 | 3B+1S | 0 | 1071 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32144006 | 1227 | 220.6835 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 135 | 12888378 | 5596 | 134.304 | 5.596 | 5.3 | 5.3 | 3B+1S | 0 | 998 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32145264 | 1258 | 224.8034 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 110 | 123 | 12893920 | 5542 | 133.008 | 5.542 | 4.3 | 4.3 | 3B+1S | 0 | 1158 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32146406 | 1142 | 206.0628 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 127 | 12899299 | 5379 | 129.096 | 5.379 | 3.5 | 3.5 | 3B+1S | 0 | 1080 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32147482 | 1076 | 200.0372 | 0% | 100% | 100% | 100% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 121 | 12904590 | 5291 | 126.984 | 5.291 | 2.9 | 2.9 | 2B+1S | 0 | 170 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32148534 | 1052 | 198.8282 | 0% | 100% | 100% | 0% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 124 | 12909552 | 4962 | 119.088 | 4.962 | 2.7 | 2.7 | 2B+1S | 0 | 1015 | 1155 | 0 | 1160 | N/A | N/A | N/A | N/A | 32149518 | 984 | 198.3071 | 0% | 100% | 100% | 0% | 100% | 0% | 7059178 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 97 | 12913766 | 4214 | 101.136 | 4.214 | 3.4 | 3.4 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 32150226 | 708 | 168.0114 | 0% | 0% | 100% | 0% | 100% | 25% | 7059823 | 645 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 95 | 12917596 | 3830 | 91.92 | 3.83 | 4.1 | 4.1 | 2B | 0 | 0 | 952 | 0 | 1110 | N/A | N/A | N/A | N/A | 32150862 | 636 | 166.0574 | 0% | 0% | 100% | 0% | 100% | 25% | 7060572 | 749 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.125 | 121755 | 121755 | 121.755 | 121.755 | [12 empty] | 24712 | 24712 | 202.965 | [6 empty] | 6408 | 6408 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 5) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 5) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25238 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12917596 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32150862 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7060572 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 85 | 12921167 | 3571 | 85.704 | 3.571 | 5.3 | 5.3 | 2B | 0 | 0 | 980 | 0 | 1048 | N/A | N/A | N/A | N/A | 32151442 | 580 | 162.4195 | 0% | 0% | 100% | 0% | 100% | 35% | 7061748 | 1176 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 84 | 12924703 | 3536 | 84.864 | 3.536 | 6.8 | 6.8 | 2B | 0 | 0 | 975 | 0 | 1008 | N/A | N/A | N/A | N/A | 32151980 | 538 | 152.1493 | 0% | 0% | 100% | 0% | 100% | 35% | 7063012 | 1264 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 84 | 12928196 | 3493 | 83.832 | 3.493 | 8.1 | 8.1 | 2B | 0 | 0 | 951 | 0 | 1008 | N/A | N/A | N/A | N/A | 32152490 | 510 | 146.0063 | 0% | 0% | 100% | 0% | 100% | 35% | 7064291 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 85 | 12931720 | 3524 | 84.576 | 3.524 | 9.2 | 9.2 | 2B | 0 | 0 | 949 | 0 | 1008 | N/A | N/A | N/A | N/A | 32152998 | 508 | 144.1544 | 0% | 0% | 100% | 0% | 100% | 35% | 7065489 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 101 | 12935651 | 3931 | 94.344 | 3.931 | 9.5 | 9.5 | 2B | 0 | 0 | 1012 | 0 | 1008 | N/A | N/A | N/A | N/A | 32153504 | 506 | 128.7204 | 0% | 0% | 100% | 0% | 100% | 35% | 7065652 | 163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 116 | 12940324 | 4673 | 112.152 | 4.673 | 9.5 | 9.5 | 2B | 0 | 0 | 1174 | 0 | 1191 | N/A | N/A | N/A | N/A | 32154250 | 746 | 159.6405 | 0% | 0% | 100% | 0% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 146 | 12946422 | 6098 | 146.352 | 6.098 | 9.1 | 9.1 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32155540 | 1290 | 211.5448 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 12952569 | 6147 | 147.528 | 6.147 | 8.3 | 8.3 | 3B+1S | 0 | 1088 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32156984 | 1444 | 234.9113 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 12958817 | 6248 | 149.952 | 6.248 | 7.5 | 7.5 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32158393 | 1409 | 225.5122 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 12965072 | 6255 | 150.12 | 6.255 | 6.8 | 6.8 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32159816 | 1423 | 227.498 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 12971107 | 6035 | 144.84 | 6.035 | 6.2 | 6.2 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32161198 | 1382 | 228.9975 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 12977071 | 5964 | 143.136 | 5.964 | 5.9 | 5.9 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32162522 | 1324 | 221.9987 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 12982775 | 5704 | 136.896 | 5.704 | 5.7 | 5.7 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 32163837 | 1315 | 230.54 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 12988426 | 5651 | 135.624 | 5.651 | 5.5 | 5.5 | 3B+1S | 0 | 999 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 32165139 | 1302 | 230.4017 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 12994035 | 5609 | 134.616 | 5.609 | 5.4 | 5.4 | 3B+1S | 0 | 994 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 32166430 | 1291 | 230.1658 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 12999662 | 5627 | 135.048 | 5.627 | 5.3 | 5.3 | 3B+1S | 0 | 1024 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32167724 | 1294 | 229.9627 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 138 | 13005264 | 5602 | 134.448 | 5.602 | 4.8 | 4.8 | 3B+1S | 0 | 1085 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32169002 | 1278 | 228.1328 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 134 | 13010818 | 5554 | 133.296 | 5.554 | 4.4 | 4.4 | 3B+1S | 0 | 1011 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32170265 | 1263 | 227.4037 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 13016309 | 5491 | 131.784 | 5.491 | 4.2 | 4.2 | 3B+1S | 0 | 1001 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32171510 | 1245 | 226.7347 | 0% | 100% | 100% | 100% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 130 | 13021804 | 5495 | 131.88 | 5.495 | 3.4 | 3.4 | 3B+1S | 0 | 1099 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32172620 | 1110 | 202.0018 | 0% | 100% | 100% | 0% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 128 | 13027129 | 5325 | 127.8 | 5.325 | 2.8 | 2.8 | 2B+1S | 0 | 1048 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32173666 | 1046 | 196.4319 | 0% | 100% | 100% | 0% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 130 | 13032198 | 5069 | 121.656 | 5.069 | 2.6 | 2.6 | 2B+1S | 0 | 977 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32174674 | 1008 | 198.8558 | 0% | 100% | 100% | 0% | 100% | 0% | 7065652 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 98 | 13036483 | 4285 | 102.84 | 4.285 | 3.1 | 3.1 | 2B | 0 | 0 | 1090 | 0 | 1100 | N/A | N/A | N/A | N/A | 32175426 | 752 | 175.4959 | 0% | 0% | 100% | 0% | 100% | 25% | 7066206 | 554 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 99 | 13040530 | 4047 | 97.128 | 4.047 | 4 | 4 | 2B | 0 | 0 | 1029 | 0 | 1100 | N/A | N/A | N/A | N/A | 32176100 | 674 | 166.5431 | 0% | 0% | 100% | 0% | 100% | 25% | 7066940 | 734 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.6667 | 122934 | 122934 | 122.934 | 122.934 | [12 empty] | 25238 | 25238 | 205.2972 | [7 empty] | 6368 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 6) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25412 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13040530 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32176100 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7066940 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 94 | 13044507 | 3977 | 95.448 | 3.977 | 5.1 | 5.1 | 2B | 0 | 0 | 1048 | 0 | 1048 | N/A | N/A | N/A | N/A | 32176756 | 656 | 164.9485 | 0% | 0% | 100% | 0% | 100% | 35% | 7067987 | 1047 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 89 | 13048346 | 3839 | 92.136 | 3.839 | 6.3 | 6.3 | 2B | 0 | 0 | 1009 | 0 | 1028 | N/A | N/A | N/A | N/A | 32177362 | 606 | 157.8536 | 0% | 0% | 100% | 0% | 100% | 35% | 7069124 | 1137 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 13052179 | 3833 | 91.992 | 3.833 | 7.5 | 7.5 | 2B | 0 | 0 | 998 | 0 | 1008 | N/A | N/A | N/A | N/A | 32177926 | 564 | 147.1432 | 0% | 0% | 100% | 0% | 100% | 35% | 7070302 | 1178 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 95 | 13056066 | 3887 | 93.288 | 3.887 | 8.7 | 8.7 | 2B | 0 | 0 | 989 | 0 | 1008 | N/A | N/A | N/A | N/A | 32178504 | 578 | 148.7008 | 0% | 0% | 100% | 0% | 100% | 35% | 7071431 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 105 | 13060040 | 3974 | 95.376 | 3.974 | 9.5 | 9.5 | 2B | 0 | 0 | 1015 | 0 | 1008 | N/A | N/A | N/A | N/A | 32179090 | 586 | 147.4585 | 0% | 0% | 100% | 0% | 100% | 35% | 7072182 | 751 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 120 | 13064735 | 4695 | 112.68 | 4.695 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1153 | 0 | 1161 | N/A | N/A | N/A | N/A | 32179852 | 762 | 162.3003 | 0% | 0% | 100% | 0% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 142 | 13070768 | 6033 | 144.792 | 6.033 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32181196 | 1344 | 222.7747 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 13076879 | 6111 | 146.664 | 6.111 | 8.6 | 8.6 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32182562 | 1366 | 223.5313 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 13083117 | 6238 | 149.712 | 6.238 | 7.8 | 7.8 | 3B+1S | 0 | 1087 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32183968 | 1406 | 225.3928 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 13089221 | 6104 | 146.496 | 6.104 | 7.1 | 7.1 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32185342 | 1374 | 225.0983 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 142 | 13095323 | 6102 | 146.448 | 6.102 | 6.6 | 6.6 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32186718 | 1376 | 225.4998 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 13101282 | 5959 | 143.016 | 5.959 | 6 | 6 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32188094 | 1376 | 230.9112 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 13107022 | 5740 | 137.76 | 5.74 | 5.8 | 5.8 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32189418 | 1324 | 230.662 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 13112729 | 5707 | 136.968 | 5.707 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32190726 | 1308 | 229.1922 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 129 | 13118252 | 5523 | 132.552 | 5.523 | 5.6 | 5.6 | 3B+1S | 0 | 987 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32192000 | 1274 | 230.6717 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 13123207 | 4955 | 118.92 | 4.955 | 5.4 | 5.4 | 3B+1S | 0 | 994 | 1176 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32193242 | 1242 | 250.6559 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 13129032 | 5825 | 139.8 | 5.825 | 5.2 | 5.2 | 3B+1S | 0 | 1042 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32194504 | 1262 | 216.6524 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 13134858 | 5826 | 139.824 | 5.826 | 4.9 | 4.9 | 3B+1S | 0 | 1024 | 1145 | 1185 | 1140 | N/A | N/A | N/A | N/A | 32195766 | 1262 | 216.6152 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 13140443 | 5585 | 134.04 | 5.585 | 4.7 | 4.7 | 3B+1S | 0 | 985 | 1135 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32197020 | 1254 | 224.53 | 0% | 100% | 100% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 132 | 13145730 | 5287 | 126.888 | 5.287 | 4.2 | 4.2 | 2B+1S | 0 | 1059 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32198073 | 1053 | 199.1678 | 0% | 100% | 100% | 0% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 125 | 13151018 | 5288 | 126.912 | 5.288 | 3.6 | 3.6 | 2B+1S | 0 | 1027 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32199126 | 1053 | 199.1301 | 0% | 100% | 100% | 0% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 127 | 13156121 | 5103 | 122.472 | 5.103 | 3.5 | 3.5 | 2B+1S | 0 | 983 | 0 | 1185 | 1130 | N/A | N/A | N/A | N/A | 32200122 | 996 | 195.1793 | 0% | 100% | 0% | 100% | 100% | 0% | 7072182 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 97 | 13160306 | 4185 | 100.44 | 4.185 | 4.1 | 4.1 | 2B | 0 | 0 | 0 | 1185 | 963 | N/A | N/A | N/A | N/A | 32200858 | 736 | 175.8662 | 0% | 0% | 0% | 100% | 100% | 25% | 7072686 | 504 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 90 | 13164163 | 3857 | 92.568 | 3.857 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 880 | N/A | N/A | N/A | N/A | 32201512 | 654 | 169.5618 | 0% | 0% | 0% | 100% | 100% | 25% | 7073401 | 715 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124 | 123633 | 123633 | 123.633 | 123.633 | [12 empty] | 25412 | 25412 | 205.5438 | [7 empty] | 6461 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 7) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:22 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
ENGR. A. TRINIDAD AND MAINTENANCE TEAM ARRIVED @ 7:08PM FOR MONTHLY PREVENTIVE MAINTENANCE
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 7) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
BP1 - STOPPED @ 9:36 PM FOR PREVENTIVE MAINTENANCE
BP2 - STARTED @ 9:37 PM
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | R. MALLARI / R. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25206 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13164163 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32201512 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7073401 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 90 | 13167811 | 3648 | 87.552 | 3.648 | 5.9 | 5.9 | 2B | 0 | 0 | 893 | 1185 | 0 | N/A | N/A | N/A | N/A | 32202158 | 646 | 177.0833 | 0% | 0% | 100% | 100% | 0% | 35% | 7074526 | 1125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 89 | 13171374 | 3563 | 85.512 | 3.563 | 7.2 | 7.2 | 2B | 0 | 0 | 955 | 0 | 1028 | N/A | N/A | N/A | N/A | 32202706 | 548 | 153.803 | 0% | 0% | 100% | 0% | 100% | 35% | 7075756 | 1230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 87 | 13174842 | 3468 | 83.232 | 3.468 | 8.5 | 8.5 | 2B | 0 | 0 | 969 | 0 | 978 | N/A | N/A | N/A | N/A | 32203214 | 508 | 146.4821 | 0% | 0% | 100% | 0% | 100% | 35% | 7076997 | 1241 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 92 | 13178387 | 3545 | 85.08 | 3.545 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 978 | N/A | N/A | N/A | N/A | 32203698 | 484 | 136.5303 | 0% | 0% | 100% | 0% | 100% | 35% | 7077906 | 909 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 103 | 13182257 | 3870 | 92.88 | 3.87 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 978 | N/A | N/A | N/A | N/A | 32204178 | 480 | 124.031 | 0% | 0% | 100% | 0% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. MALLARI / R. REGENCIA
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 125 | 13186818 | 4561 | 109.464 | 4.561 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1199 | N/A | N/A | N/A | N/A | 32204890 | 712 | 156.1061 | 0% | 0% | 100% | 0% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 147 | 13192922 | 6104 | 146.496 | 6.104 | 9.1 | 9.1 | 3B+1S | 0 | 1019 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32206211 | 1321 | 216.4155 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 143 | 13199114 | 6192 | 148.608 | 6.192 | 8.6 | 8.6 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32207628 | 1417 | 228.8437 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 151 | 13205345 | 6231 | 149.544 | 6.231 | 8.1 | 8.1 | 3B+1S | 0 | 1072 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32209014 | 1386 | 222.4362 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 13211553 | 6208 | 148.992 | 6.208 | 7.3 | 7.3 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32210406 | 1392 | 224.2268 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 13217658 | 6105 | 146.52 | 6.105 | 6.8 | 6.8 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32211777 | 1371 | 224.57 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 140 | 13223734 | 6076 | 145.824 | 6.076 | 6.6 | 6.6 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32213122 | 1345 | 221.3627 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 142 | 13229602 | 5868 | 140.832 | 5.868 | 6.2 | 6.2 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32214458 | 1336 | 227.6755 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 132 | 13235406 | 5804 | 139.296 | 5.804 | 6 | 6 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32215776 | 1318 | 227.0848 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 130 | 13241014 | 5608 | 134.592 | 5.608 | 5.9 | 5.9 | 3B+1S | 0 | 998 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32217057 | 1281 | 228.4237 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 13246556 | 5542 | 133.008 | 5.542 | 5.7 | 5.7 | 3B+1S | 0 | 1012 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32218330 | 1273 | 229.7005 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 139 | 13252216 | 5660 | 135.84 | 5.66 | 5.1 | 5.1 | 3B+1S | 0 | 1099 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32219620 | 1290 | 227.9152 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 133 | 13257828 | 5612 | 134.688 | 5.612 | 4.6 | 4.6 | 3B+1S | 0 | 1022 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32220903 | 1283 | 228.6172 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 136 | 13263397 | 5569 | 133.656 | 5.569 | 4.4 | 4.4 | 3B+1S | 0 | 989 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32222154 | 1251 | 224.6364 | 0% | 100% | 100% | 100% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 125 | 13268762 | 5365 | 128.76 | 5.365 | 3.6 | 3.6 | 2B+1S | 0 | 1065 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32223226 | 1072 | 199.8136 | 0% | 100% | 100% | 0% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 124 | 13274105 | 5343 | 128.232 | 5.343 | 3.1 | 3.1 | 2B+1S | 0 | 1003 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32224290 | 1064 | 199.1391 | 0% | 100% | 100% | 0% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 129 | 13279156 | 5051 | 121.224 | 5.051 | 3 | 3 | 2B+1S | 0 | 973 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32225290 | 1000 | 197.9806 | 0% | 100% | 100% | 0% | 100% | 0% | 7077906 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 101 | 13283494 | 4338 | 104.112 | 4.338 | 3.4 | 3.4 | 2B | 0 | 0 | 1084 | 0 | 1110 | N/A | N/A | N/A | N/A | 32226046 | 756 | 174.2739 | 0% | 0% | 100% | 0% | 100% | 25% | 7078359 | 453 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 97 | 13287556 | 4062 | 97.488 | 4.062 | 4.1 | 4.1 | 2B | 0 | 0 | 1048 | 0 | 1059 | N/A | N/A | N/A | N/A | 32226718 | 672 | 165.4357 | 0% | 0% | 100% | 0% | 100% | 25% | 7078977 | 618 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.2917 | 123393 | 123393 | 123.393 | 123.393 | [12 empty] | 25206 | 25206 | 204.2741 | [7 empty] | 5576 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 12:02 AM
BP1 - STARTED @ 12:03 AM
BP2 - STOPPED @ 1:01 AM
BP3 - STARTED @ 1:02 AM
XCV1 CLOSED @ 3:37 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:55 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 8) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
GENSET # 2 EXERCISED WITHOUT LOAD @ 3:20 PM TO 3:30 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 3:31 PM TO 3:41 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 8) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25812 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13287556 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32226718 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7078977 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 93 | 13291395 | 3839 | 92.136 | 3.839 | 5.3 | 5.3 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 32227342 | 624 | 162.5423 | 0% | 0% | 100% | 0% | 100% | 35% | 7080073 | 1096 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 88 | 13294976 | 3581 | 85.944 | 3.581 | 6.5 | 6.5 | 2B | 0 | 0 | 995 | 0 | 998 | N/A | N/A | N/A | N/A | 32227902 | 560 | 156.3809 | 0% | 0% | 100% | 0% | 100% | 35% | 7081264 | 1191 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 85 | 13298451 | 3475 | 83.4 | 3.475 | 7.8 | 7.8 | 2B | 0 | 0 | 967 | 0 | 998 | N/A | N/A | N/A | N/A | 32228422 | 520 | 149.6403 | 0% | 0% | 100% | 0% | 100% | 35% | 7082488 | 1224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 87 | 13301991 | 3540 | 84.96 | 3.54 | 9 | 9 | 2B | 0 | 0 | 970 | 0 | 998 | N/A | N/A | N/A | N/A | 32228936 | 514 | 145.1977 | 0% | 0% | 100% | 0% | 100% | 35% | 7083670 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 95 | 13305693 | 3702 | 88.848 | 3.702 | 9.5 | 9.5 | 2B | 0 | 0 | 933 | 0 | 938 | N/A | N/A | N/A | N/A | 32229404 | 468 | 126.4182 | 0% | 0% | 100% | 0% | 100% | 35% | 7084041 | 371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 114 | 13309978 | 4285 | 102.84 | 4.285 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1080 | N/A | N/A | N/A | N/A | 32229982 | 578 | 134.8891 | 0% | 0% | 100% | 0% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 140 | 13315691 | 5713 | 137.112 | 5.713 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32231214 | 1232 | 215.6485 | 0% | 0% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 13321804 | 6113 | 146.712 | 6.113 | 9.1 | 9.1 | 3B+1S | 0 | 1047 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32232562 | 1348 | 220.5137 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 13328125 | 6321 | 151.704 | 6.321 | 8.4 | 8.4 | 3B+1S | 0 | 1104 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32233974 | 1412 | 223.3824 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 13334481 | 6356 | 152.544 | 6.356 | 7.5 | 7.5 | 3B+1S | 0 | 1149 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32235410 | 1436 | 225.9283 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 13340719 | 6238 | 149.712 | 6.238 | 6.7 | 6.7 | 3B+1S | 0 | 1109 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32236840 | 1430 | 229.2401 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 146 | 13347072 | 6353 | 152.472 | 6.353 | 5.9 | 5.9 | 3B+1S | 0 | 1138 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32238252 | 1412 | 222.2572 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 133 | 13353074 | 6002 | 144.048 | 6.002 | 5.3 | 5.3 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32239630 | 1378 | 229.5901 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 13359033 | 5959 | 143.016 | 5.959 | 4.6 | 4.6 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32241002 | 1372 | 230.24 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 13364957 | 5924 | 142.176 | 5.924 | 3.7 | 3.7 | 3B+1S | 0 | 1075 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32242376 | 1374 | 231.9379 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 13370881 | 5924 | 142.176 | 5.924 | 3.4 | 3.4 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32243750 | 1374 | 231.9379 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 140 | 13376703 | 5822 | 139.728 | 5.822 | 2.7 | 2.7 | 3B+1S | 0 | 1134 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32245126 | 1376 | 236.3449 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 135 | 13382334 | 5631 | 135.144 | 5.631 | 2.3 | 2.3 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32246446 | 1320 | 234.4166 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 13388022 | 5688 | 136.512 | 5.688 | 2 | 2 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32247784 | 1338 | 235.2321 | 0% | 100% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 129 | 13393410 | 5388 | 129.312 | 5.388 | 1.5 | 1.5 | 3B | 0 | 0 | 1054 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32248950 | 1166 | 216.4068 | 0% | 0% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 122 | 13398603 | 5193 | 124.632 | 5.193 | 1.5 | 1.5 | 3B | 0 | 0 | 1047 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32250074 | 1124 | 216.4452 | 0% | 0% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 117 | 13403609 | 5006 | 120.144 | 5.006 | 1.5 | 1.5 | 3B | 0 | 0 | 1000 | 1185 | 1049 | N/A | N/A | N/A | N/A | 32251098 | 1024 | 204.5545 | 0% | 0% | 100% | 100% | 100% | 0% | 7084041 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 104 | 13407895 | 4286 | 102.864 | 4.286 | 2.3 | 2.3 | 2B | 0 | 0 | 1089 | 0 | 1110 | N/A | N/A | N/A | N/A | 32251858 | 760 | 177.3215 | 0% | 0% | 100% | 0% | 100% | 30% | 7084733 | 692 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 98 | 13411909 | 4014 | 96.336 | 4.014 | 3.3 | 3.3 | 2B | 0 | 0 | 1040 | 0 | 1049 | N/A | N/A | N/A | N/A | 32252530 | 672 | 167.4141 | 0% | 0% | 100% | 0% | 100% | 30% | 7085613 | 880 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.1667 | 124353 | 124353 | 124.353 | 124.353 | [12 empty] | 25812 | 25812 | 207.5704 | [7 empty] | 6636 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 9) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 / RESTART @ 7:34PM
SP2 - STOPPED @ 7:35 PM DUE TO LOW WATER LEVEL
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24469 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13411909 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32252530 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7085613 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 93 | 13415715 | 3806 | 91.344 | 3.806 | 4.7 | 4.7 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 32253164 | 634 | 166.5791 | 0% | 0% | 100% | 0% | 100% | 38% | 7086990 | 1377 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 13419316 | 3601 | 86.424 | 3.601 | 6.2 | 6.2 | 2B | 0 | 0 | 990 | 0 | 1048 | N/A | N/A | N/A | N/A | 32253748 | 584 | 162.1772 | 0% | 0% | 100% | 0% | 100% | 38% | 7088398 | 1408 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 89 | 13422874 | 3558 | 85.392 | 3.558 | 7.8 | 7.8 | 2B | 0 | 0 | 974 | 0 | 1008 | N/A | N/A | N/A | N/A | 32254314 | 566 | 159.0781 | 0% | 0% | 100% | 0% | 100% | 38% | 7089793 | 1395 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 87 | 13426360 | 3486 | 83.664 | 3.486 | 9 | 9 | 2B | 0 | 0 | 959 | 0 | 1008 | N/A | N/A | N/A | N/A | 32254822 | 508 | 145.7258 | 0% | 0% | 100% | 0% | 100% | 38% | 7091195 | 1402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 88 | 87 | 13429900 | 3540 | 84.96 | 3.54 | 9.5 | 9.5 | 2B | 0 | 0 | 906 | 0 | 950 | N/A | N/A | N/A | N/A | 32255304 | 482 | 136.1582 | 0% | 0% | 100% | 0% | 100% | 38% | 7091581 | 386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 105 | 102 | 13433877 | 3977 | 95.448 | 3.977 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 998 | N/A | N/A | N/A | N/A | 32255802 | 498 | 125.22 | 0% | 0% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 135 | 13438979 | 5102 | 122.448 | 5.102 | 9.5 | 9.5 | 2B | 0 | 0 | 1105 | 0 | 1109 | N/A | N/A | N/A | N/A | 32256736 | 934 | 183.0655 | 0% | 0% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 147 | 13444841 | 5862 | 140.688 | 5.862 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32257932 | 1196 | 204.0259 | 0% | 0% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 13450962 | 6121 | 146.904 | 6.121 | 9.2 | 9.2 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32259258 | 1326 | 216.6313 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 13457164 | 6202 | 148.848 | 6.202 | 8.6 | 8.6 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32260668 | 1410 | 227.346 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 13463340 | 6176 | 148.224 | 6.176 | 7.9 | 7.9 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32262055 | 1387 | 224.579 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 13469491 | 6151 | 147.624 | 6.151 | 7.4 | 7.4 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32263434 | 1379 | 224.1912 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 13475495 | 6004 | 144.096 | 6.004 | 6.9 | 6.9 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32264805 | 1371 | 228.3478 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 13481481 | 5986 | 143.664 | 5.986 | 6.3 | 6.3 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32266169 | 1364 | 227.865 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 13487448 | 5967 | 143.208 | 5.967 | 5.8 | 5.8 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32267518 | 1349 | 226.0768 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 13493189 | 5741 | 137.784 | 5.741 | 5.5 | 5.5 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32268850 | 1332 | 232.0153 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 142 | 13498964 | 5775 | 138.6 | 5.775 | 5.1 | 5.1 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32270198 | 1348 | 233.4199 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 133 | 13504572 | 5608 | 134.592 | 5.608 | 4.7 | 4.7 | 3B+1S | 0 | 1008 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32271478 | 1280 | 228.2454 | 0% | 100% | 100% | 100% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 | 125 | 13509954 | 5382 | 129.168 | 5.382 | 3.8 | 3.8 | 3B+1S | 0 | 1144 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32272580 | 1102 | 204.7566 | 0% | 100% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 123 | 13515250 | 5296 | 127.104 | 5.296 | 3.2 | 3.2 | 3B+1S | 0 | 1024 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32273626 | 1046 | 197.5076 | 0% | 100% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 125 | 13520528 | 5278 | 126.672 | 5.278 | 2.9 | 2.9 | 2B+1S | 0 | 1008 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32274652 | 1026 | 194.3918 | 0% | 100% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 115 | 13525576 | 5048 | 121.152 | 5.048 | 2.8 | 2.8 | 2B+1S | 0 | 991 | 1145 | 0 | 1150 | N/A | N/A | N/A | N/A | 32275614 | 962 | 190.5705 | 0% | 100% | 100% | 0% | 100% | 0% | 7091581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 97 | 13529841 | 4265 | 102.36 | 4.265 | 3.3 | 3.3 | 2B | 0 | 0 | 1056 | 0 | 1110 | N/A | N/A | N/A | N/A | 32276342 | 728 | 170.6917 | 0% | 0% | 100% | 0% | 100% | 25% | 7092172 | 591 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 94 | 13533816 | 3975 | 95.4 | 3.975 | 4.2 | 4.2 | 2B | 0 | 0 | 973 | 0 | 1110 | N/A | N/A | N/A | N/A | 32276999 | 657 | 165.283 | 0% | 0% | 100% | 0% | 100% | 25% | 7092922 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5 | 121907 | 121907 | 121.907 | 121.907 | [12 empty] | 24469 | 24469 | 200.7186 | [7 empty] | 7309 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:19 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 10) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 10) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25539 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13533816 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32276999 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7092922 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 87 | 13537528 | 3712 | 89.088 | 3.712 | 5.4 | 5.4 | 2B | 0 | 0 | 1018 | 0 | 1028 | N/A | N/A | N/A | N/A | 32277596 | 597 | 160.8297 | 0% | 0% | 100% | 0% | 100% | 35% | 7094017 | 1095 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 86 | 13541121 | 3593 | 86.232 | 3.593 | 6.6 | 6.6 | 2B | 0 | 0 | 997 | 0 | 1028 | N/A | N/A | N/A | N/A | 32278152 | 556 | 154.7453 | 0% | 0% | 100% | 0% | 100% | 35% | 7095201 | 1184 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 13544674 | 3553 | 85.272 | 3.553 | 7.8 | 7.8 | 2B | 0 | 0 | 973 | 0 | 1028 | N/A | N/A | N/A | N/A | 32278698 | 546 | 153.673 | 0% | 0% | 100% | 0% | 100% | 35% | 7096407 | 1206 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 85 | 13548279 | 3605 | 86.52 | 3.605 | 9 | 9 | 2B | 0 | 0 | 954 | 0 | 1008 | N/A | N/A | N/A | N/A | 32279228 | 530 | 147.018 | 0% | 0% | 100% | 0% | 100% | 35% | 7097572 | 1165 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 105 | 13552175 | 3896 | 93.504 | 3.896 | 9.5 | 9.5 | 2B | 0 | 0 | 935 | 0 | 1008 | N/A | N/A | N/A | N/A | 32279762 | 534 | 137.0637 | 0% | 0% | 100% | 0% | 100% | 35% | 7097979 | 407 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 126 | 13556851 | 4676 | 112.224 | 4.676 | 9.5 | 9.5 | 2B | 0 | 0 | 1172 | 0 | 1190 | N/A | N/A | N/A | N/A | 32280516 | 754 | 161.2489 | 0% | 0% | 100% | 0% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 149 | 13562945 | 6094 | 146.256 | 6.094 | 9.1 | 9.1 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32281838 | 1322 | 216.9347 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 13569101 | 6156 | 147.744 | 6.156 | 8.6 | 8.6 | 3B+1S | 0 | 1072 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32283246 | 1408 | 228.7199 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 13575398 | 6297 | 151.128 | 6.297 | 7.8 | 7.8 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32284658 | 1412 | 224.2338 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 13581663 | 6265 | 150.36 | 6.265 | 7.1 | 7.1 | 3B+1S | 0 | 1097 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32286064 | 1406 | 224.4214 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 13587820 | 6157 | 147.768 | 6.157 | 6.5 | 6.5 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32287446 | 1382 | 224.46 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 13593950 | 6130 | 147.12 | 6.13 | 6.1 | 6.1 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32288814 | 1368 | 223.1648 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 13599768 | 5818 | 139.632 | 5.818 | 5.8 | 5.8 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32290149 | 1335 | 229.4603 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 136 | 13605510 | 5742 | 137.808 | 5.742 | 5.6 | 5.6 | 3B+1S | 0 | 1001 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32291460 | 1311 | 228.3177 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 13611154 | 5644 | 135.456 | 5.644 | 5.5 | 5.5 | 3B+1S | 0 | 994 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32292768 | 1308 | 231.7505 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 13616852 | 5698 | 136.752 | 5.698 | 5.4 | 5.4 | 3B+1S | 0 | 1001 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32294087 | 1319 | 231.4847 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 13622570 | 5718 | 137.232 | 5.718 | 5.1 | 5.1 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32295418 | 1331 | 232.7737 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 13628184 | 5614 | 134.736 | 5.614 | 4.8 | 4.8 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32296687 | 1269 | 226.042 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 13633776 | 5592 | 134.208 | 5.592 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32297946 | 1259 | 225.1431 | 0% | 100% | 100% | 100% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 129 | 13639178 | 5402 | 129.648 | 5.402 | 3.7 | 3.7 | 2B+1S | 0 | 1077 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32299050 | 1104 | 204.3688 | 0% | 100% | 100% | 0% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 125 | 13644486 | 5308 | 127.392 | 5.308 | 3.1 | 3.1 | 2B+1S | 0 | 1027 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32300082 | 1032 | 194.4235 | 0% | 100% | 100% | 0% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 119 | 13649556 | 5070 | 121.68 | 5.07 | 2.8 | 2.8 | 2B+1S | 0 | 1008 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32301094 | 1012 | 199.6055 | 0% | 100% | 100% | 0% | 100% | 0% | 7097979 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 103 | 13653840 | 4284 | 102.816 | 4.284 | 3.5 | 3.5 | 2B | 0 | 0 | 1112 | 0 | 1109 | N/A | N/A | N/A | N/A | 32301858 | 764 | 178.338 | 0% | 0% | 100% | 0% | 100% | 25% | 7098668 | 689 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 91 | 13657870 | 4030 | 96.72 | 4.03 | 4.7 | 4.7 | 2B | 0 | 0 | 1004 | 0 | 1109 | N/A | N/A | N/A | N/A | 32302538 | 680 | 168.7345 | 0% | 0% | 100% | 0% | 100% | 25% | 7099686 | 1018 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.9167 | 124054 | 124054 | 124.054 | 124.054 | [12 empty] | 25539 | 25539 | 205.87 | [7 empty] | 6764 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:25 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 11) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 11) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25460 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13657870 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32302538 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7099686 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 84 | 13661475 | 3605 | 86.52 | 3.605 | 6.1 | 6.1 | 2B | 0 | 0 | 989 | 0 | 1088 | N/A | N/A | N/A | N/A | 32303146 | 608 | 168.6546 | 0% | 0% | 100% | 0% | 100% | 35% | 7100975 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 84 | 13665032 | 3557 | 85.368 | 3.557 | 7.4 | 7.4 | 2B | 0 | 0 | 935 | 0 | 1089 | N/A | N/A | N/A | N/A | 32303718 | 572 | 160.8097 | 0% | 0% | 100% | 0% | 100% | 35% | 7102319 | 1344 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 13668473 | 3441 | 82.584 | 3.441 | 8.9 | 8.9 | 2B | 0 | 0 | 906 | 0 | 1088 | N/A | N/A | N/A | N/A | 32304270 | 552 | 160.4185 | 0% | 0% | 100% | 0% | 100% | 35% | 7103715 | 1396 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 89 | 13672114 | 3641 | 87.384 | 3.641 | 9.5 | 9.5 | 2B | 0 | 0 | 798 | 0 | 1088 | N/A | N/A | N/A | N/A | 32304806 | 536 | 147.2123 | 0% | 0% | 100% | 0% | 100% | 35% | 7104280 | 565 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 100 | 13675926 | 3812 | 91.488 | 3.812 | 9.5 | 9.5 | 2B | 0 | 0 | 928 | 0 | 1038 | N/A | N/A | N/A | N/A | 32305306 | 500 | 131.1647 | 0% | 0% | 100% | 0% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 122 | 13680687 | 4761 | 114.264 | 4.761 | 9.5 | 9.5 | 2B | 0 | 0 | 1179 | 0 | 1168 | N/A | N/A | N/A | N/A | 32306074 | 768 | 161.3106 | 0% | 0% | 100% | 0% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 143 | 13686782 | 6095 | 146.28 | 6.095 | 9 | 9 | 3B+1S | 0 | 1036 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32307435 | 1361 | 223.2978 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 13692939 | 6157 | 147.768 | 6.157 | 8.4 | 8.4 | 3B+1S | 0 | 1067 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32308822 | 1387 | 225.272 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 13699115 | 6176 | 148.224 | 6.176 | 7.7 | 7.7 | 3B+1S | 0 | 1089 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32310216 | 1394 | 225.7124 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 13705354 | 6239 | 149.736 | 6.239 | 7 | 7 | 3B+1S | 0 | 1093 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32311616 | 1400 | 224.3949 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 13711564 | 6210 | 149.04 | 6.21 | 6.4 | 6.4 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32313014 | 1398 | 225.1208 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 142 | 13717597 | 6033 | 144.792 | 6.033 | 6 | 6 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32314362 | 1348 | 223.4378 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 81 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 138 | 13723457 | 5860 | 140.64 | 5.86 | 5.8 | 5.8 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32315702 | 1340 | 228.6689 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 13729161 | 5704 | 136.896 | 5.704 | 5.6 | 5.6 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32317014 | 1312 | 230.014 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 134 | 13734692 | 5531 | 132.744 | 5.531 | 5.4 | 5.4 | 3B+1S | 0 | 1018 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32318316 | 1302 | 235.4005 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 13740387 | 5695 | 136.68 | 5.695 | 5.2 | 5.2 | 3B+1S | 0 | 1029 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32319614 | 1298 | 227.9192 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 13746071 | 5684 | 136.416 | 5.684 | 4.7 | 4.7 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32320902 | 1288 | 226.601 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 13751724 | 5653 | 135.672 | 5.653 | 4.4 | 4.4 | 3B+1S | 0 | 1017 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32322181 | 1279 | 226.2515 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 134 | 13757351 | 5627 | 135.048 | 5.627 | 4.1 | 4.1 | 3B+1S | 0 | 1001 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32323446 | 1265 | 224.809 | 0% | 100% | 100% | 100% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 125 | 13762724 | 5373 | 128.952 | 5.373 | 3.3 | 3.3 | 2B+1S | 0 | 1077 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32324536 | 1090 | 202.8662 | 0% | 100% | 100% | 0% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 124 | 13768004 | 5280 | 126.72 | 5.28 | 2.7 | 2.7 | 2B+1S | 0 | 1025 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32325586 | 1050 | 198.8636 | 0% | 100% | 100% | 0% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 126 | 13773117 | 5113 | 122.712 | 5.113 | 2.5 | 2.5 | 2B+1S | 0 | 889 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32326590 | 1004 | 196.3622 | 0% | 100% | 100% | 0% | 100% | 0% | 7104280 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 97 | 13777509 | 4392 | 105.408 | 4.392 | 3.1 | 3.1 | 2B | 0 | 0 | 1063 | 0 | 1110 | N/A | N/A | N/A | N/A | 32327370 | 780 | 177.5956 | 0% | 0% | 100% | 0% | 100% | 25% | 7104839 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 89 | 13781298 | 3789 | 90.936 | 3.789 | 3.9 | 3.9 | 2B | 0 | 0 | 1000 | 0 | 1028 | N/A | N/A | N/A | N/A | 32327998 | 628 | 165.7429 | 0% | 0% | 100% | 0% | 100% | 25% | 7105572 | 733 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0833 | 123428 | 123428 | 123.428 | 123.428 | [12 empty] | 25460 | 25460 | 206.2741 | [7 empty] | 5886 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 12) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 6) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25708 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13781298 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32327998 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7105572 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 85 | 13784886 | 3588 | 86.112 | 3.588 | 5.2 | 5.2 | 2B | 0 | 0 | 997 | 0 | 1028 | N/A | N/A | N/A | N/A | 32328580 | 582 | 162.2074 | 0% | 0% | 100% | 0% | 100% | 35% | 7106749 | 1177 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 13788364 | 3478 | 83.472 | 3.478 | 6.4 | 6.4 | 2B | 0 | 0 | 981 | 0 | 1008 | N/A | N/A | N/A | N/A | 32329120 | 540 | 155.2616 | 0% | 0% | 100% | 0% | 100% | 35% | 7107974 | 1225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 85 | 13791835 | 3471 | 83.304 | 3.471 | 7.7 | 7.7 | 2B | 0 | 0 | 965 | 0 | 1008 | N/A | N/A | N/A | N/A | 32329646 | 526 | 151.5413 | 0% | 0% | 100% | 0% | 100% | 35% | 7109204 | 1230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 88 | 13795382 | 3547 | 85.128 | 3.547 | 8.9 | 8.9 | 2B | 0 | 0 | 983 | 0 | 1008 | N/A | N/A | N/A | N/A | 32330170 | 524 | 147.7305 | 0% | 0% | 100% | 0% | 100% | 35% | 7110369 | 1165 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 13799334 | 3952 | 94.848 | 3.952 | 9.5 | 9.5 | 2B | 0 | 0 | 988 | 0 | 1008 | N/A | N/A | N/A | N/A | 32330710 | 540 | 136.6397 | 0% | 0% | 100% | 0% | 100% | 35% | 7110912 | 543 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 126 | 13804020 | 4686 | 112.464 | 4.686 | 9.5 | 9.5 | 2B | 0 | 0 | 1162 | 0 | 1199 | N/A | N/A | N/A | N/A | 32331476 | 766 | 163.4656 | 0% | 0% | 100% | 0% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 142 | 13810132 | 6112 | 146.688 | 6.112 | 9.1 | 9.1 | 3B+1S | 0 | 1022 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32332858 | 1382 | 226.1126 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 13816101 | 5969 | 143.256 | 5.969 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32334146 | 1288 | 215.7815 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 151 | 13822389 | 6288 | 150.912 | 6.288 | 7.8 | 7.8 | 3B+1S | 0 | 1105 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32335610 | 1464 | 232.8244 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 13828526 | 6137 | 147.288 | 6.137 | 7 | 7 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32337012 | 1402 | 228.4504 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 146 | 13834561 | 6035 | 144.84 | 6.035 | 6.5 | 6.5 | 3B+1S | 0 | 1052 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32338370 | 1358 | 225.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 13840619 | 6058 | 145.392 | 6.058 | 6.1 | 6.1 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32339742 | 1372 | 226.4774 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 13846515 | 5896 | 141.504 | 5.896 | 5.5 | 5.5 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32341112 | 1370 | 232.3609 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 13852242 | 5727 | 137.448 | 5.727 | 5.1 | 5.1 | 3B+1S | 0 | 1027 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32342430 | 1318 | 230.1379 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 13858048 | 5806 | 139.344 | 5.806 | 5 | 5 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32343770 | 1340 | 230.7957 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 13863549 | 5501 | 132.024 | 5.501 | 4.9 | 4.9 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32345062 | 1292 | 234.8664 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 132 | 13869331 | 5782 | 138.768 | 5.782 | 4.5 | 4.5 | 3B+1S | 0 | 1078 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32346414 | 1352 | 233.8291 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 13875031 | 5700 | 136.8 | 5.7 | 4.2 | 4.2 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32347734 | 1320 | 231.5789 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 13880667 | 5636 | 135.264 | 5.636 | 4.1 | 4.1 | 3B+1S | 0 | 974 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32349062 | 1328 | 235.6281 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 130 | 13885919 | 5252 | 126.048 | 5.252 | 4 | 4 | 2B+1S | 0 | 988 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 32350226 | 1164 | 221.6299 | 0% | 100% | 100% | 100% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 122 | 13891219 | 5300 | 127.2 | 5.3 | 3.3 | 3.3 | 2B+1S | 0 | 1050 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32351298 | 1072 | 202.2642 | 0% | 100% | 100% | 0% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 125 | 13896164 | 4945 | 118.68 | 4.945 | 2.9 | 2.9 | 2B+1S | 0 | 992 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32352310 | 1012 | 204.6512 | 0% | 100% | 100% | 0% | 100% | 0% | 7110912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 97 | 13900462 | 4298 | 103.152 | 4.298 | 3.4 | 3.4 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 32353054 | 744 | 173.1038 | 0% | 0% | 100% | 0% | 100% | 25% | 7111480 | 568 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 90 | 13904394 | 3932 | 94.368 | 3.932 | 4.2 | 4.2 | 2B | 0 | 0 | 1020 | 0 | 1018 | N/A | N/A | N/A | N/A | 32353706 | 652 | 165.8189 | 0% | 0% | 100% | 0% | 100% | 25% | 7112215 | 735 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.8333 | 123096 | 123096 | 123.096 | 123.096 | [12 empty] | 25708 | 25708 | 208.8451 | [7 empty] | 6643 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 13) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:17 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 13) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25622 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13904394 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32353706 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7112215 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 90 | 13908055 | 3661 | 87.864 | 3.661 | 5.4 | 5.4 | 2B | 0 | 0 | 1025 | 0 | 1028 | N/A | N/A | N/A | N/A | 32354302 | 596 | 162.797 | 0% | 0% | 100% | 0% | 100% | 35% | 7113209 | 994 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 86 | 13911654 | 3599 | 86.376 | 3.599 | 6.8 | 6.8 | 2B | 0 | 0 | 987 | 0 | 1008 | N/A | N/A | N/A | N/A | 32354842 | 540 | 150.0417 | 0% | 0% | 100% | 0% | 100% | 35% | 7114534 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 88 | 13915312 | 3658 | 87.792 | 3.658 | 7.9 | 7.9 | 2B | 0 | 0 | 1017 | 0 | 1028 | N/A | N/A | N/A | N/A | 32355398 | 556 | 151.9956 | 0% | 0% | 100% | 0% | 100% | 35% | 7115654 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 87 | 13918859 | 3547 | 85.128 | 3.547 | 8.9 | 8.9 | 2B | 0 | 0 | 992 | 0 | 998 | N/A | N/A | N/A | N/A | 32355942 | 544 | 153.369 | 0% | 0% | 100% | 0% | 100% | 35% | 7116621 | 967 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 100 | 13922779 | 3920 | 94.08 | 3.92 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 998 | N/A | N/A | N/A | N/A | 32356488 | 546 | 139.2857 | 0% | 0% | 100% | 0% | 100% | 35% | 7117155 | 534 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 118 | 13927362 | 4583 | 109.992 | 4.583 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1109 | N/A | N/A | N/A | N/A | 32357226 | 738 | 161.0299 | 0% | 0% | 100% | 0% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 148 | 13933384 | 6022 | 144.528 | 6.022 | 9.1 | 9.1 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32358576 | 1350 | 224.178 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 13939556 | 6172 | 148.128 | 6.172 | 8.5 | 8.5 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32359954 | 1378 | 223.2664 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 13945733 | 6177 | 148.248 | 6.177 | 7.7 | 7.7 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32361342 | 1388 | 224.7045 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 13951910 | 6177 | 148.248 | 6.177 | 7.2 | 7.2 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32362730 | 1388 | 224.7045 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 13957974 | 6064 | 145.536 | 6.064 | 6.7 | 6.7 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32364098 | 1368 | 225.5937 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 150 | 13964188 | 6214 | 149.136 | 6.214 | 5.9 | 5.9 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32365518 | 1420 | 228.5163 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 13970085 | 5897 | 141.528 | 5.897 | 5.4 | 5.4 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32366872 | 1354 | 229.6083 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 13975798 | 5713 | 137.112 | 5.713 | 5.1 | 5.1 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32368190 | 1318 | 230.7019 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 132 | 13981437 | 5639 | 135.336 | 5.639 | 5 | 5 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32369504 | 1314 | 233.02 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 13986983 | 5546 | 133.104 | 5.546 | 4.9 | 4.9 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32370802 | 1298 | 234.0426 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 13992694 | 5711 | 137.064 | 5.711 | 4.7 | 4.7 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32372132 | 1330 | 232.8839 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 13998401 | 5707 | 136.968 | 5.707 | 4.5 | 4.5 | 3B+1S | 0 | 991 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32373450 | 1318 | 230.9445 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 131 | 14004073 | 5672 | 136.128 | 5.672 | 4.4 | 4.4 | 3B+1S | 0 | 1000 | 1165 | 1185 | 1168 | N/A | N/A | N/A | N/A | 32374734 | 1284 | 226.3752 | 0% | 100% | 100% | 100% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 126 | 14009436 | 5363 | 128.712 | 5.363 | 3.7 | 3.7 | 2B+1S | 0 | 1070 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32375802 | 1068 | 199.1423 | 0% | 100% | 100% | 0% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 125 | 14014749 | 5313 | 127.512 | 5.313 | 3 | 3 | 2B+1S | 0 | 1018 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32376854 | 1052 | 198.0049 | 0% | 100% | 100% | 0% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 129 | 14019837 | 5088 | 122.112 | 5.088 | 2.8 | 2.8 | 2B+1S | 0 | 997 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32377862 | 1008 | 198.1132 | 0% | 100% | 100% | 0% | 100% | 0% | 7117155 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 103 | 14024288 | 4451 | 106.824 | 4.451 | 3.2 | 3.2 | 2B | 0 | 0 | 1118 | 0 | 1110 | N/A | N/A | N/A | N/A | 32378654 | 792 | 177.9375 | 0% | 0% | 100% | 0% | 100% | 25% | 7117597 | 442 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 95 | 14028339 | 4051 | 97.224 | 4.051 | 3.9 | 3.9 | 2B | 0 | 0 | 1044 | 0 | 1048 | N/A | N/A | N/A | N/A | 32379328 | 674 | 166.3787 | 0% | 0% | 100% | 0% | 100% | 25% | 7118223 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5 | 123945 | 123945 | 123.945 | 123.945 | [12 empty] | 25622 | 25622 | 206.7207 | [7 empty] | 6008 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 14) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:16 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 14) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14028339 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32379328 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7118223 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 89 | 14032076 | 3737 | 89.688 | 3.737 | 5.2 | 5.2 | 2B | 0 | 0 | 1026 | 0 | 1048 | N/A | N/A | N/A | N/A | 32379950 | 622 | 166.4437 | 0% | 0% | 100% | 0% | 100% | 35% | 7119332 | 1109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 87 | 14035626 | 3550 | 85.2 | 3.55 | 6.4 | 6.4 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 32380520 | 570 | 160.5634 | 0% | 0% | 100% | 0% | 100% | 35% | 7120538 | 1206 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 86 | 14039170 | 3544 | 85.056 | 3.544 | 7.7 | 7.7 | 2B | 0 | 0 | 994 | 0 | 998 | N/A | N/A | N/A | N/A | 32381062 | 542 | 152.9345 | 0% | 0% | 100% | 0% | 100% | 35% | 7121769 | 1231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 90 | 14042800 | 3630 | 87.12 | 3.63 | 8.9 | 8.9 | 2B | 0 | 0 | 1016 | 0 | 1008 | N/A | N/A | N/A | N/A | 32381602 | 540 | 148.7603 | 0% | 0% | 100% | 0% | 100% | 35% | 7122898 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 104 | 14046829 | 4029 | 96.696 | 4.029 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 32382182 | 580 | 143.9563 | 0% | 0% | 100% | 0% | 100% | 35% | 7123496 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 124 | 14051504 | 4675 | 112.2 | 4.675 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1199 | N/A | N/A | N/A | N/A | 32382946 | 764 | 163.4225 | 0% | 0% | 100% | 0% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 148 | 14057485 | 5981 | 143.544 | 5.981 | 9 | 9 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32384294 | 1348 | 225.3804 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 14063705 | 6220 | 149.28 | 6.22 | 8.4 | 8.4 | 3B+1S | 0 | 1083 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32385644 | 1350 | 217.0418 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 14069907 | 6202 | 148.848 | 6.202 | 7.6 | 7.6 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32387053 | 1409 | 227.1848 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 14076142 | 6235 | 149.64 | 6.235 | 6.9 | 6.9 | 3B+1S | 0 | 1110 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32388486 | 1433 | 229.8316 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 14082255 | 6113 | 146.712 | 6.113 | 6.2 | 6.2 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32389784 | 1298 | 212.3344 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 14088357 | 6102 | 146.448 | 6.102 | 5.6 | 5.6 | 3B+1S | 0 | 1084 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32391254 | 1470 | 240.9046 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 14094264 | 5907 | 141.768 | 5.907 | 5.1 | 5.1 | 3B+1S | 0 | 1059 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32392614 | 1360 | 230.2353 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 14100031 | 5767 | 138.408 | 5.767 | 4.7 | 4.7 | 3B+1S | 0 | 1033 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32393946 | 1332 | 230.9693 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 14105747 | 5716 | 137.184 | 5.716 | 4.6 | 4.6 | 3B+1S | 0 | 1003 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32395274 | 1328 | 232.3303 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 14111350 | 5603 | 134.472 | 5.603 | 4.5 | 4.5 | 3B+1S | 0 | 104 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32396574 | 1300 | 232.0186 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 139 | 14117031 | 5681 | 136.344 | 5.681 | 4.2 | 4.2 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32397906 | 1332 | 234.4658 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 14122709 | 5678 | 136.272 | 5.678 | 3.9 | 3.9 | 3B+1S | 0 | 1007 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32399228 | 1322 | 232.8285 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 14128228 | 5519 | 132.456 | 5.519 | 3.8 | 3.8 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32400514 | 1286 | 233.0132 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 132 | 14133591 | 5363 | 128.712 | 5.363 | 3.6 | 3.6 | 3B+1S | 0 | 998 | 1125 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32401698 | 1184 | 220.772 | 0% | 100% | 100% | 100% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 120 | 14138857 | 5266 | 126.384 | 5.266 | 3.3 | 3.3 | 2B+1S | 0 | 1035 | 1196 | 0 | 1 | N/A | N/A | N/A | N/A | 32402766 | 1068 | 202.8105 | 0% | 100% | 100% | 0% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 121 | 14143921 | 5064 | 121.536 | 5.064 | 3 | 3 | 2B+1S | 0 | 985 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32403728 | 962 | 189.9684 | 0% | 100% | 100% | 0% | 100% | 0% | 7123496 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 101 | 14148269 | 4348 | 104.352 | 4.348 | 3.4 | 3.4 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 32404536 | 808 | 185.8326 | 0% | 0% | 100% | 0% | 100% | 25% | 7123958 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 97 | 14152316 | 4047 | 97.128 | 4.047 | 4 | 4 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 32405208 | 672 | 166.0489 | 0% | 0% | 100% | 0% | 100% | 25% | 7124550 | 592 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.9583 | 123977 | 123977 | 123.977 | 123.977 | [12 empty] | 25880 | 25880 | 208.7484 | [7 empty] | 6327 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:19 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 15) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25064 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14152316 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32405208 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7124550 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 90 | 14156144 | 3828 | 91.872 | 3.828 | 5.2 | 5.2 | 2B | 0 | 0 | 1034 | 0 | 1048 | N/A | N/A | N/A | N/A | 32405842 | 634 | 165.6217 | 0% | 0% | 100% | 0% | 100% | 35% | 7125561 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 14159843 | 3699 | 88.776 | 3.699 | 6.4 | 6.4 | 2B | 0 | 0 | 1004 | 0 | 1008 | N/A | N/A | N/A | N/A | 32406430 | 588 | 158.9619 | 0% | 0% | 100% | 0% | 100% | 35% | 7126652 | 1091 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 89 | 14163465 | 3622 | 86.928 | 3.622 | 7.5 | 7.5 | 2B | 0 | 0 | 996 | 0 | 1008 | N/A | N/A | N/A | N/A | 32406994 | 564 | 155.7151 | 0% | 0% | 100% | 0% | 100% | 35% | 7127762 | 1110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 90 | 14167089 | 3624 | 86.976 | 3.624 | 8.6 | 8.6 | 2B | 0 | 0 | 991 | 0 | 1008 | N/A | N/A | N/A | N/A | 32407538 | 544 | 150.1104 | 0% | 0% | 100% | 0% | 100% | 35% | 7128828 | 1066 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 94 | 14170888 | 3799 | 91.176 | 3.799 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 1008 | N/A | N/A | N/A | N/A | 32408086 | 548 | 144.2485 | 0% | 0% | 100% | 0% | 100% | 35% | 7129708 | 880 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 113 | 115 | 14175179 | 4291 | 102.984 | 4.291 | 9.5 | 9.5 | 2B | 0 | 0 | 1093 | 0 | 1110 | N/A | N/A | N/A | N/A | 32408706 | 620 | 144.4885 | 0% | 0% | 100% | 0% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 138 | 14180712 | 5533 | 132.792 | 5.533 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1181 | N/A | N/A | N/A | N/A | 32409882 | 1176 | 212.5429 | 0% | 0% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 147 | 14186628 | 5916 | 141.984 | 5.916 | 9.3 | 9.3 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32411178 | 1296 | 219.0669 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 14192652 | 6024 | 144.576 | 6.024 | 9 | 9 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32412520 | 1342 | 222.7756 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 14198785 | 6133 | 147.192 | 6.133 | 8.4 | 8.4 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32413908 | 1388 | 226.3166 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 14204891 | 6106 | 146.544 | 6.106 | 7.9 | 7.9 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32415280 | 1372 | 224.697 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 14210979 | 6088 | 146.112 | 6.088 | 7.5 | 7.5 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32416638 | 1358 | 223.0618 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 139 | 14216695 | 5716 | 137.184 | 5.716 | 7.3 | 7.3 | 3B+1S | 0 | 1018 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32417948 | 1310 | 229.1812 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 14222576 | 5881 | 141.144 | 5.881 | 6.7 | 6.7 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32419282 | 1334 | 226.8322 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 14228274 | 5698 | 136.752 | 5.698 | 6.3 | 6.3 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32420598 | 1316 | 230.9582 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 14234037 | 5763 | 138.312 | 5.763 | 6 | 6 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32421934 | 1336 | 231.8237 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 132 | 14239704 | 5667 | 136.008 | 5.667 | 5.6 | 5.6 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32423260 | 1326 | 233.9862 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 132 | 14245357 | 5653 | 135.672 | 5.653 | 5.5 | 5.5 | 3B+1S | 0 | 973 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32424578 | 1318 | 233.1505 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 132 | 14250863 | 5506 | 132.144 | 5.506 | 5.4 | 5.4 | 3B+1S | 0 | 974 | 1165 | 1185 | 1138 | N/A | N/A | N/A | N/A | 32425834 | 1256 | 228.1148 | 0% | 100% | 100% | 100% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 124 | 14256142 | 5279 | 126.696 | 5.279 | 5 | 5 | 2B+1S | 0 | 1019 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32426884 | 1050 | 198.9013 | 0% | 100% | 100% | 0% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 122 | 14261216 | 5074 | 121.776 | 5.074 | 4.5 | 4.5 | 2B+1S | 0 | 993 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32427894 | 1010 | 199.054 | 0% | 100% | 100% | 0% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 123 | 14266237 | 5021 | 120.504 | 5.021 | 4.4 | 4.4 | 2B+1S | 0 | 920 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 32428878 | 984 | 195.9769 | 0% | 100% | 100% | 0% | 100% | 0% | 7129708 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 101 | 14270556 | 4319 | 103.656 | 4.319 | 4.8 | 4.8 | 2B | 0 | 0 | 1097 | 0 | 1110 | N/A | N/A | N/A | N/A | 32429618 | 740 | 171.336 | 0% | 0% | 100% | 0% | 100% | 0% | 7130147 | 439 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 95 | 14274594 | 4038 | 96.912 | 4.038 | 5.3 | 5.3 | 2B | 0 | 0 | 1026 | 0 | 1059 | N/A | N/A | N/A | N/A | 32430272 | 654 | 161.9614 | 0% | 0% | 100% | 0% | 100% | 0% | 7130693 | 546 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.75 | 122278 | 122278 | 122.278 | 122.278 | [12 empty] | 25064 | 25064 | 204.9755 | [7 empty] | 6143 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 16) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:45 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:16 PM TO 4:26 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:28 PM TO 4:38 PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 16) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | R. MALLARI / R. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25244 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14274594 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32430272 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7130693 |  | mg /l |  | Automatic - i2O | AI | REIVIN M. MALLARI (O.T.)
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 111 | 91 | 14278431 | 3837 | 92.088 | 3.837 | 6.2 | 6.2 | 2B | 0 | 0 | 1028 | 0 | 1028 | N/A | N/A | N/A | N/A | 32430890 | 618 | 161.0633 | 0% | 0% | 100% | 0% | 100% | 32% | 7131515 | 822 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 111 | 89 | 14282066 | 3635 | 87.24 | 3.635 | 7.2 | 7.2 | 2B | 0 | 0 | 1005 | 0 | 1018 | N/A | N/A | N/A | N/A | 32431462 | 572 | 157.359 | 0% | 0% | 100% | 0% | 100% | 32% | 7132392 | 877 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS L. GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 87 | 14285731 | 3665 | 87.96 | 3.665 | 8.2 | 8.2 | 2B | 0 | 0 | 973 | 0 | 987 | N/A | N/A | N/A | N/A | 32432012 | 550 | 150.0682 | 0% | 0% | 100% | 0% | 100% | 32% | 7133338 | 946 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | ALEXANDER CABREROS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 86 | 14289312 | 3581 | 85.944 | 3.581 | 9.1 | 9.1 | 2B | 0 | 0 | 978 | 0 | 987 | N/A | N/A | N/A | N/A | 32432560 | 548 | 153.0299 | 0% | 0% | 100% | 0% | 100% | 32% | 7134266 | 928 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | R. MALLARI / R. REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 91 | 14292922 | 3610 | 86.64 | 3.61 | 9.5 | 9.5 | 2B | 0 | 0 | 958 | 0 | 978 | N/A | N/A | N/A | N/A | 32433028 | 468 | 129.6399 | 0% | 0% | 100% | 0% | 100% | 32% | 7134676 | 410 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY O. REGENCIA
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 110 | 103 | 14297237 | 4315 | 103.56 | 4.315 | 9.5 | 9.5 | 2B | 0 | 0 | 1024 | 0 | 1028 | N/A | N/A | N/A | N/A | 32433558 | 530 | 122.8273 | 0% | 0% | 100% | 0% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA (O.T.)
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 136 | 14302522 | 5285 | 126.84 | 5.285 | 9.5 | 9.5 | 3B | 0 | 0 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32434660 | 1102 | 208.5147 | 0% | 0% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 14308429 | 5907 | 141.768 | 5.907 | 9.4 | 9.4 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32435954 | 1294 | 219.0621 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 147 | 14314655 | 6226 | 149.424 | 6.226 | 8.8 | 8.8 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32437348 | 1394 | 223.8998 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 153 | 14320976 | 6321 | 151.704 | 6.321 | 7.9 | 7.9 | 3B+1S | 0 | 1138 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32438764 | 1416 | 224.0152 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 14327215 | 6239 | 149.736 | 6.239 | 7.2 | 7.2 | 3B+1S | 0 | 1088 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32440177 | 1413 | 226.4786 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 140 | 14333420 | 6205 | 148.92 | 6.205 | 6.5 | 6.5 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32441578 | 1401 | 225.7857 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 14339361 | 5941 | 142.584 | 5.941 | 6.1 | 6.1 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32442939 | 1361 | 229.086 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 143 | 14345296 | 5935 | 142.44 | 5.935 | 5.5 | 5.5 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32444296 | 1357 | 228.6436 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 14351227 | 5931 | 142.344 | 5.931 | 4.9 | 4.9 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32445656 | 1360 | 229.3037 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 14357046 | 5819 | 139.656 | 5.819 | 4.5 | 4.5 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32447006 | 1350 | 231.9986 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 14362802 | 5756 | 138.144 | 5.756 | 3.9 | 3.9 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32448358 | 1352 | 234.8853 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 139 | 14368488 | 5686 | 136.464 | 5.686 | 3.6 | 3.6 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32449668 | 1310 | 230.3904 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 137 | 14374106 | 5618 | 134.832 | 5.618 | 3.5 | 3.5 | 3B+1S | 0 | 1010 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 32450942 | 1274 | 226.7711 | 0% | 100% | 100% | 100% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 128 | 14379514 | 5408 | 129.792 | 5.408 | 3.2 | 3.2 | 2B+1S | 0 | 1078 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32452066 | 1124 | 207.8402 | 0% | 100% | 100% | 0% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 127 | 14384739 | 5225 | 125.4 | 5.225 | 2.6 | 2.6 | 2B+1S | 0 | 1018 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32453108 | 1042 | 199.4258 | 0% | 100% | 100% | 0% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 125 | 14389696 | 4957 | 118.968 | 4.957 | 2.5 | 2.5 | 2B+1S | 0 | 919 | 1176 | 0 | 1199 | N/A | N/A | N/A | N/A | 32454098 | 990 | 199.7176 | 0% | 100% | 100% | 0% | 100% | 0% | 7134676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 103 | 14393988 | 4292 | 103.008 | 4.292 | 2.9 | 2.9 | 2B | 0 | 0 | 1092 | 0 | 1110 | N/A | N/A | N/A | N/A | 32454846 | 748 | 174.2777 | 0% | 0% | 100% | 0% | 100% | 25% | 7135150 | 474 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 98 | 14398027 | 4039 | 96.936 | 4.039 | 3.6 | 3.6 | 2B | 0 | 0 | 991 | 0 | 1110 | N/A | N/A | N/A | N/A | 32455516 | 670 | 165.8826 | 0% | 0% | 100% | 0% | 100% | 25% | 7135775 | 625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.875 | 123433 | 123433 | 123.433 | 123.433 | [12 empty] | 25244 | 25244 | 204.5158 | [7 empty] | 5082 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 17) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 17) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25806 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14398027 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32455516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7135775 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 88 | 14401739 | 3712 | 89.088 | 3.712 | 4.9 | 4.9 | 2B | 0 | 0 | 1024 | 0 | 1028 | N/A | N/A | N/A | N/A | 32456134 | 618 | 166.4871 | 0% | 0% | 100% | 0% | 100% | 35% | 7136926 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 87 | 14405337 | 3598 | 86.352 | 3.598 | 6.3 | 6.3 | 2B | 0 | 0 | 996 | 0 | 1028 | N/A | N/A | N/A | N/A | 32456702 | 568 | 157.8655 | 0% | 0% | 100% | 0% | 100% | 35% | 7138223 | 1297 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 87 | 14408825 | 3488 | 83.712 | 3.488 | 7.6 | 7.6 | 2B | 0 | 0 | 976 | 0 | 1008 | N/A | N/A | N/A | N/A | 32457246 | 544 | 155.9633 | 0% | 0% | 100% | 0% | 100% | 35% | 7139524 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 86 | 14412456 | 3631 | 87.144 | 3.631 | 8.9 | 8.9 | 2B | 0 | 0 | 991 | 0 | 1008 | N/A | N/A | N/A | N/A | 32457828 | 582 | 160.2864 | 0% | 0% | 100% | 0% | 100% | 35% | 7140721 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 100 | 14416275 | 3819 | 91.656 | 3.819 | 9.5 | 9.5 | 2B | 0 | 0 | 995 | 0 | 1008 | N/A | N/A | N/A | N/A | 32458309 | 481 | 125.9492 | 0% | 0% | 100% | 0% | 100% | 35% | 7141340 | 619 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 141 | 14421002 | 4727 | 113.448 | 4.727 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1159 | 0 | 1169 | N/A | N/A | N/A | N/A | 32459072 | 763 | 161.4132 | 0% | 0% | 100% | 0% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 149 | 14427261 | 6259 | 150.216 | 6.259 | 9.1 | 9.1 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32460458 | 1386 | 221.4411 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 147 | 14433503 | 6242 | 149.808 | 6.242 | 8.3 | 8.3 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32461864 | 1406 | 225.2483 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 151 | 14439611 | 6108 | 146.592 | 6.108 | 7.6 | 7.6 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32463228 | 1364 | 223.3137 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 148 | 14445901 | 6290 | 150.96 | 6.29 | 6.9 | 6.9 | 3B+1S | 0 | 1136 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32464578 | 1350 | 214.6264 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 143 | 14451922 | 6021 | 144.504 | 6.021 | 6.3 | 6.3 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32465940 | 1362 | 226.2083 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 145 | 14458043 | 6121 | 146.904 | 6.121 | 5.8 | 5.8 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32467314 | 1374 | 224.4731 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 140 | 14463884 | 5841 | 140.184 | 5.841 | 5.3 | 5.3 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32468670 | 1356 | 232.152 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 138 | 14469676 | 5792 | 139.008 | 5.792 | 4.8 | 4.8 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32470012 | 1342 | 231.6989 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 134 | 14475417 | 5741 | 137.784 | 5.741 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32471340 | 1328 | 231.3186 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 14481171 | 5754 | 138.096 | 5.754 | 4.5 | 4.5 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32472681 | 1341 | 233.0553 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 14486864 | 5693 | 136.632 | 5.693 | 4.1 | 4.1 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32474006 | 1325 | 232.742 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 14492536 | 5672 | 136.128 | 5.672 | 3.8 | 3.8 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32475318 | 1312 | 231.3117 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 14498184 | 5648 | 135.552 | 5.648 | 3.7 | 3.7 | 3B+1S | 0 | 1013 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32476622 | 1304 | 230.8782 | 0% | 100% | 100% | 100% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 128 | 14503587 | 5403 | 129.672 | 5.403 | 3.3 | 3.3 | 2B+1S | 0 | 1127 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32477794 | 1172 | 216.9165 | 0% | 100% | 100% | 0% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 14508916 | 5329 | 127.896 | 5.329 | 2.5 | 2.5 | 2B+1S | 0 | 1138 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32478876 | 1082 | 203.04 | 0% | 100% | 100% | 0% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 121 | 14514036 | 5120 | 122.88 | 5.12 | 1.9 | 1.9 | 2B+1S | 0 | 997 | 1195 | 0 | 1190 | N/A | N/A | N/A | N/A | 32479902 | 1026 | 200.3906 | 0% | 100% | 100% | 0% | 100% | 0% | 7141340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 106 | 14518271 | 4235 | 101.64 | 4.235 | 2.9 | 2.9 | 2B | 0 | 0 | 1130 | 0 | 1100 | N/A | N/A | N/A | N/A | 32480612 | 710 | 167.6505 | 0% | 0% | 100% | 0% | 100% | 25% | 7142409 | 1069 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 90 | 14522506 | 4235 | 101.64 | 4.235 | 4.3 | 4.3 | 2B | 0 | 0 | 1017 | 0 | 1100 | N/A | N/A | N/A | N/A | 32481322 | 710 | 167.6505 | 0% | 0% | 100% | 0% | 100% | 25% | 7143477 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.8333 | 124479 | 124479 | 124.479 | 124.479 | [12 empty] | 25806 | 25806 | 207.3121 | [7 empty] | 7702 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:13 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
BP2 - STOPPED @ 9:40 AM DUE TO EXCESS CAPACITY
BP2 - RESTARTED @ 10:00 AM
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:30 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 18) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27000 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14522506 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32481322 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7143477 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 93 | 14526282 | 3776 | 90.624 | 3.776 | 5.5 | 5.5 | 2B | 0 | 0 | 1007 | 0 | 1100 | N/A | N/A | N/A | N/A | 32481966 | 644 | 170.5508 | 0% | 0% | 100% | 0% | 100% | 35% | 7144617 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 85 | 14529986 | 3704 | 88.896 | 3.704 | 6.8 | 6.8 | 2B | 0 | 0 | 1011 | 0 | 1059 | N/A | N/A | N/A | N/A | 32482580 | 614 | 165.7667 | 0% | 0% | 100% | 0% | 100% | 35% | 7145835 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 91 | 14533655 | 3669 | 88.056 | 3.669 | 8.1 | 8.1 | 2B | 0 | 0 | 978 | 0 | 1059 | N/A | N/A | N/A | N/A | 32483160 | 580 | 158.0812 | 0% | 0% | 100% | 0% | 100% | 35% | 7147079 | 1244 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 90 | 14537274 | 3619 | 86.856 | 3.619 | 9.3 | 9.3 | 2B | 0 | 0 | 1033 | 0 | 1008 | N/A | N/A | N/A | N/A | 32483714 | 554 | 153.081 | 0% | 0% | 100% | 0% | 100% | 35% | 7148184 | 1105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 14541398 | 4124 | 98.976 | 4.124 | 9.5 | 9.5 | 2B | 0 | 0 | 1023 | 0 | 1059 | N/A | N/A | N/A | N/A | 32484320 | 606 | 146.9447 | 0% | 0% | 100% | 0% | 100% | 35% | 7148447 | 263 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 121 | 14546237 | 4839 | 116.136 | 4.839 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1199 | N/A | N/A | N/A | N/A | 32485122 | 802 | 165.7367 | 0% | 0% | 100% | 0% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 149 | 14552468 | 6231 | 149.544 | 6.231 | 8.9 | 8.9 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32486526 | 1404 | 225.325 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 14558532 | 6064 | 145.536 | 6.064 | 8.1 | 8.1 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32487878 | 1352 | 222.9551 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 14564756 | 6224 | 149.376 | 6.224 | 7.3 | 7.3 | 3B+1S | 0 | 1128 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32489299 | 1421 | 228.3098 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 14570959 | 6203 | 148.872 | 6.203 | 6.5 | 6.5 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32490712 | 1413 | 227.793 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 14577131 | 6172 | 148.128 | 6.172 | 5.6 | 5.6 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32492123 | 1411 | 228.6131 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 149 | 14583331 | 6200 | 148.8 | 6.2 | 4.7 | 4.7 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32493570 | 1447 | 233.3871 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 14589338 | 6007 | 144.168 | 6.007 | 4 | 4 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32494955 | 1385 | 230.5643 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 14595214 | 5876 | 141.024 | 5.876 | 3.5 | 3.5 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32496318 | 1363 | 231.9605 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 14600974 | 5760 | 138.24 | 5.76 | 3.2 | 3.2 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32497768 | 1450 | 251.7361 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 14606692 | 5718 | 137.232 | 5.718 | 3 | 3 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32499220 | 1452 | 253.9349 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 142 | 14612478 | 5786 | 138.864 | 5.786 | 2.5 | 2.5 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32500646 | 1426 | 246.457 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 14618180 | 5702 | 136.848 | 5.702 | 2.2 | 2.2 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32502002 | 1356 | 237.8113 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 132 | 14623867 | 5687 | 136.488 | 5.687 | 2.2 | 2.2 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32503352 | 1350 | 237.3835 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 129 | 14629345 | 5478 | 131.472 | 5.478 | 2.1 | 2.1 | 3B+1S | 0 | 1021 | 1135 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32504682 | 1330 | 242.7893 | 0% | 100% | 100% | 100% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 122 | 127 | 14634716 | 5371 | 128.904 | 5.371 | 2 | 2 | 3B+1S | 0 | 996 | 1135 | 0 | 1139 | N/A | N/A | N/A | N/A | 32505800 | 1118 | 208.1549 | 0% | 100% | 100% | 0% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 119 | 14640001 | 5285 | 126.84 | 5.285 | 1.8 | 1.8 | 2B+1S | 0 | 989 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32506864 | 1064 | 201.3245 | 0% | 100% | 100% | 0% | 100% | 0% | 7148447 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 101 | 14644236 | 4235 | 101.64 | 4.235 | 2.3 | 2.3 | 2B | 0 | 0 | 1115 | 0 | 1110 | N/A | N/A | N/A | N/A | 32507624 | 760 | 179.4569 | 0% | 0% | 100% | 0% | 100% | 27% | 7148984 | 537 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 98 | 14648388 | 4152 | 99.648 | 4.152 | 3.1 | 3.1 | 2B | 0 | 0 | 975 | 0 | 1110 | N/A | N/A | N/A | N/A | 32508322 | 698 | 168.1118 | 0% | 0% | 100% | 0% | 100% | 27% | 7149712 | 728 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 125882 | 125882 | 125.882 | 125.882 | [12 empty] | 27000 | 27000 | 214.4866 | [7 empty] | 6235 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 19) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED @ 2:00 PM - DUE TO LOW RESERVOIR WATER LEVEL / CLOSED @ 7:01 PM
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 19) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26376 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14648388 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32508322 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7149712 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 96 | 14652386 | 3998 | 95.952 | 3.998 | 4.4 | 4.4 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 32509004 | 682 | 170.5853 | 0% | 0% | 100% | 0% | 100% | 35% | 7150815 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 14656346 | 3960 | 95.04 | 3.96 | 5.8 | 5.8 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 32509652 | 648 | 163.6364 | 0% | 0% | 100% | 0% | 100% | 35% | 7152093 | 1278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 98 | 14660300 | 3954 | 94.896 | 3.954 | 6.9 | 6.9 | 2B | 0 | 0 | 998 | 0 | 1110 | N/A | N/A | N/A | N/A | 32510288 | 636 | 160.8498 | 0% | 0% | 100% | 0% | 100% | 35% | 7153347 | 1254 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 99 | 14664224 | 3924 | 94.176 | 3.924 | 8 | 8 | 2B | 0 | 0 | 947 | 0 | 1110 | N/A | N/A | N/A | N/A | 32510910 | 622 | 158.5117 | 0% | 0% | 100% | 0% | 100% | 35% | 7154564 | 1217 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 103 | 14668277 | 4053 | 97.272 | 4.053 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1110 | N/A | N/A | N/A | N/A | 32511570 | 660 | 162.8423 | 0% | 0% | 100% | 0% | 100% | 35% | 7155738 | 1174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 124 | 14672885 | 4608 | 110.592 | 4.608 | 9.5 | 9.5 | 2B | 0 | 0 | 1170 | 0 | 1169 | N/A | N/A | N/A | N/A | 32512334 | 764 | 165.7986 | 0% | 0% | 100% | 0% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 141 | 14678805 | 5920 | 142.08 | 5.92 | 9.1 | 9.1 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32513662 | 1328 | 224.3243 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 152 | 14685107 | 6302 | 151.248 | 6.302 | 8.4 | 8.4 | 3B+1S | 0 | 1112 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32515074 | 1412 | 224.0559 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 14691328 | 6221 | 149.304 | 6.221 | 7.6 | 7.6 | 3B+1S | 0 | 1119 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32516492 | 1418 | 227.9376 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 14697537 | 6209 | 149.016 | 6.209 | 6.7 | 6.7 | 3B+1S | 0 | 1118 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32517898 | 1406 | 226.4455 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 148 | 14703715 | 6178 | 148.272 | 6.178 | 6 | 6 | 3B+1S | 0 | 1154 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32519310 | 1412 | 228.5529 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 14709764 | 6049 | 145.176 | 6.049 | 5.2 | 5.2 | 3B+1S | 0 | 1120 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32520712 | 1402 | 231.7738 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 139 | 14715623 | 5859 | 140.616 | 5.859 | 4.7 | 4.7 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32522076 | 1364 | 232.8042 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 14721448 | 5825 | 139.8 | 5.825 | 4.6 | 4.6 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32523426 | 1350 | 231.7597 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 14727074 | 5626 | 135.024 | 5.626 | 4.4 | 4.4 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32524714 | 1288 | 228.9371 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 14732703 | 5629 | 135.096 | 5.629 | 4.3 | 4.3 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32526033 | 1319 | 234.3223 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 14738346 | 5643 | 135.432 | 5.643 | 3.8 | 3.8 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32527366 | 1333 | 236.2219 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 14743927 | 5581 | 133.944 | 5.581 | 3.5 | 3.5 | 3B+1S | 0 | 1012 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32528672 | 1306 | 234.0082 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 14749472 | 5545 | 133.08 | 5.545 | 3.4 | 3.4 | 3B+1S | 0 | 998 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32529956 | 1284 | 231.56 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 129 | 14754862 | 5390 | 129.36 | 5.39 | 3.2 | 3.2 | 3B+1S | 0 | 1021 | 1136 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32531166 | 1210 | 224.4898 | 0% | 100% | 100% | 100% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 128 | 14760208 | 5346 | 128.304 | 5.346 | 2.5 | 2.5 | 2B+1S | 0 | 1044 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32532252 | 1086 | 203.1425 | 0% | 100% | 100% | 0% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 127 | 14765320 | 5112 | 122.688 | 5.112 | 2.3 | 2.3 | 2B+1S | 0 | 995 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32533262 | 1010 | 197.5743 | 0% | 100% | 100% | 0% | 100% | 0% | 7155738 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 102 | 14769637 | 4317 | 103.608 | 4.317 | 2.8 | 2.8 | 2B | 0 | 0 | 1092 | 0 | 1110 | N/A | N/A | N/A | N/A | 32534012 | 750 | 173.7318 | 0% | 0% | 100% | 0% | 100% | 0% | 7156245 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 100 | 14773710 | 4073 | 97.752 | 4.073 | 3.5 | 3.5 | 2B | 0 | 0 | 1028 | 0 | 1110 | N/A | N/A | N/A | N/A | 32534698 | 686 | 168.4262 | 0% | 0% | 100% | 0% | 100% | 0% | 7156887 | 642 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.4167 | 125322 | 125322 | 125.322 | 125.322 | [12 empty] | 26376 | 26376 | 210.4658 | [7 empty] | 7175 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 20) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 20) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26066 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14773710 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32534698 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7156887 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 95 | 14777645 | 3935 | 94.44 | 3.935 | 4.8 | 4.8 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 32535402 | 704 | 178.9072 | 0% | 0% | 100% | 0% | 100% | 35% | 7157989 | 1102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 93 | 14781534 | 3889 | 93.336 | 3.889 | 5.9 | 5.9 | 2B | 0 | 0 | 1010 | 0 | 1059 | N/A | N/A | N/A | N/A | 32536010 | 608 | 156.3384 | 0% | 0% | 100% | 0% | 100% | 35% | 7159109 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 94 | 14785404 | 3870 | 92.88 | 3.87 | 7.1 | 7.1 | 2B | 0 | 0 | 998 | 0 | 1059 | N/A | N/A | N/A | N/A | 32536616 | 606 | 156.5891 | 0% | 0% | 100% | 0% | 100% | 35% | 7160387 | 1278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 92 | 14789318 | 3914 | 93.936 | 3.914 | 8.9 | 8.9 | 2B | 0 | 0 | 947 | 0 | 1059 | N/A | N/A | N/A | N/A | 32537234 | 618 | 157.8947 | 0% | 0% | 100% | 0% | 100% | 35% | 7161643 | 1256 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 103 | 14793373 | 4055 | 97.32 | 4.055 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1059 | N/A | N/A | N/A | N/A | 32537830 | 596 | 146.979 | 0% | 0% | 100% | 0% | 100% | 35% | 7162754 | 1111 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 123 | 14797957 | 4584 | 110.016 | 4.584 | 9.5 | 9.5 | 2B | 0 | 0 | 1161 | 0 | 1199 | N/A | N/A | N/A | N/A | 32538590 | 760 | 165.7941 | 0% | 0% | 100% | 0% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 144 | 14803936 | 5979 | 143.496 | 5.979 | 9 | 9 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32539926 | 1336 | 223.4487 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 14810083 | 6147 | 147.528 | 6.147 | 8.4 | 8.4 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32541300 | 1374 | 223.5237 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 152 | 14816348 | 6265 | 150.36 | 6.265 | 7.3 | 7.3 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32542718 | 1418 | 226.3368 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 14822479 | 6131 | 147.144 | 6.131 | 6.8 | 6.8 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32544112 | 1394 | 227.3691 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 141 | 14828610 | 6131 | 147.144 | 6.131 | 6.4 | 6.4 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32545506 | 1394 | 227.3691 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 142 | 14834682 | 6072 | 145.728 | 6.072 | 5.7 | 5.7 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32546878 | 1372 | 225.9552 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 14840527 | 5845 | 140.28 | 5.845 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32548226 | 1348 | 230.6245 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 14846307 | 5780 | 138.72 | 5.78 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32549564 | 1338 | 231.4879 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 14851932 | 5625 | 135 | 5.625 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1165 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32550870 | 1306 | 232.1778 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 14857487 | 5555 | 133.32 | 5.555 | 4.6 | 4.6 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32552150 | 1280 | 230.423 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 14863239 | 5752 | 138.048 | 5.752 | 4.1 | 4.1 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32553494 | 1344 | 233.6579 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 134 | 14868931 | 5692 | 136.608 | 5.692 | 4 | 4 | 3B+1S | 0 | 993 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32554806 | 1312 | 230.4989 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 129 | 14874516 | 5585 | 134.04 | 5.585 | 3.8 | 3.8 | 3B+1S | 0 | 1011 | 1164 | 1185 | 1140 | N/A | N/A | N/A | N/A | 32556074 | 1268 | 227.0367 | 0% | 100% | 100% | 100% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 127 | 14879918 | 5402 | 129.648 | 5.402 | 3.1 | 3.1 | 2B+1S | 0 | 1184 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32557160 | 1086 | 201.0367 | 0% | 100% | 100% | 0% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 126 | 14885284 | 5366 | 128.784 | 5.366 | 2.5 | 2.5 | 2B+1S | 0 | 1026 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32558228 | 1068 | 199.0309 | 0% | 100% | 100% | 0% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 125 | 14890345 | 5061 | 121.464 | 5.061 | 2.3 | 2.3 | 2B+1S | 0 | 950 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32559234 | 1006 | 198.7749 | 0% | 100% | 100% | 0% | 100% | 0% | 7162754 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 104 | 14894770 | 4425 | 106.2 | 4.425 | 2.8 | 2.8 | 2B | 0 | 0 | 1144 | 0 | 1110 | N/A | N/A | N/A | N/A | 32560026 | 792 | 178.9831 | 0% | 0% | 100% | 0% | 100% | 28% | 7163065 | 311 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 100 | 14899077 | 4307 | 103.368 | 4.307 | 3.5 | 3.5 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 32560764 | 738 | 171.349 | 0% | 0% | 100% | 0% | 100% | 28% | 7163723 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125 | 125367 | 125367 | 125.367 | 125.367 | [12 empty] | 26066 | 26066 | 207.9176 | [7 empty] | 6836 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 21) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:39 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 21) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (28%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26236 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14899077 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32560764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7163723 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 98 | 14903148 | 4071 | 97.704 | 4.071 | 4.9 | 4.9 | 2B | 0 | 0 | 1043 | 0 | 1110 | N/A | N/A | N/A | N/A | 32561458 | 694 | 170.4741 | 0% | 0% | 100% | 0% | 100% | 40% | 7164886 | 1163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 96 | 14907066 | 3918 | 94.032 | 3.918 | 6.2 | 6.2 | 2B | 0 | 0 | 1045 | 0 | 1059 | N/A | N/A | N/A | N/A | 32562118 | 660 | 168.4533 | 0% | 0% | 100% | 0% | 100% | 40% | 7166240 | 1354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 14910924 | 3858 | 92.592 | 3.858 | 7.6 | 7.6 | 2B | 0 | 0 | 1009 | 0 | 1059 | N/A | N/A | N/A | N/A | 32562730 | 612 | 158.6314 | 0% | 0% | 100% | 0% | 100% | 40% | 7167507 | 1267 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 97 | 14914832 | 3908 | 93.792 | 3.908 | 8.9 | 8.9 | 2B | 0 | 0 | 1034 | 0 | 1029 | N/A | N/A | N/A | N/A | 32563330 | 600 | 153.5312 | 0% | 0% | 100% | 0% | 100% | 40% | 7168777 | 1270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 14918905 | 4073 | 97.752 | 4.073 | 9.5 | 9.5 | 2B | 0 | 0 | 1004 | 0 | 1029 | N/A | N/A | N/A | N/A | 32563914 | 584 | 143.3833 | 0% | 0% | 100% | 0% | 100% | 40% | 7169401 | 624 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 124 | 14923652 | 4747 | 113.928 | 4.747 | 9.5 | 9.5 | 2B | 0 | 0 | 1162 | 0 | 1029 | N/A | N/A | N/A | N/A | 32564690 | 776 | 163.4717 | 0% | 0% | 100% | 0% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 148 | 14929642 | 5990 | 143.76 | 5.99 | 9 | 9 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32566030 | 1340 | 223.7062 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 14935814 | 6172 | 148.128 | 6.172 | 8.3 | 8.3 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32567418 | 1388 | 224.8866 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 14941998 | 6184 | 148.416 | 6.184 | 7.5 | 7.5 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32568815 | 1397 | 225.9056 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 14948194 | 6196 | 148.704 | 6.196 | 6.9 | 6.9 | 3B+1S | 0 | 1094 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32570224 | 1409 | 227.4048 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 14954323 | 6129 | 147.096 | 6.129 | 6.3 | 6.3 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32571596 | 1372 | 223.8538 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 14960423 | 6100 | 146.4 | 6.1 | 5.6 | 5.6 | 3B+1S | 0 | 1114 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32572994 | 1398 | 229.1803 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 14966309 | 5886 | 141.264 | 5.886 | 5.1 | 5.1 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32574355 | 1361 | 231.2266 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 14972111 | 5802 | 139.248 | 5.802 | 4.7 | 4.7 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32575700 | 1345 | 231.8166 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 132 | 14977824 | 5713 | 137.112 | 5.713 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32577030 | 1330 | 232.8024 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 14983499 | 5675 | 136.2 | 5.675 | 4.2 | 4.2 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32578381 | 1351 | 238.0617 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 14989117 | 5618 | 134.832 | 5.618 | 3.7 | 3.7 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32579688 | 1307 | 232.6451 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 135 | 14994709 | 5592 | 134.208 | 5.592 | 3.5 | 3.5 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32580989 | 1301 | 232.6538 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 131 | 15000274 | 5565 | 133.56 | 5.565 | 3.4 | 3.4 | 3B+1S | 0 | 1009 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32582278 | 1289 | 231.6262 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 126 | 15005712 | 5438 | 130.512 | 5.438 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 1094 | 1185 | 1099 | N/A | N/A | N/A | N/A | 32583438 | 1160 | 213.3137 | 0% | 100% | 100% | 100% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 121 | 15010934 | 5222 | 125.328 | 5.222 | 2.6 | 2.6 | 2B+1S | 0 | 1052 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32584498 | 1060 | 202.9874 | 0% | 100% | 100% | 0% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 114 | 15015904 | 4970 | 119.28 | 4.97 | 2.3 | 2.3 | 2B+1S | 0 | 994 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32585502 | 1004 | 202.0121 | 0% | 100% | 100% | 0% | 100% | 0% | 7169401 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 103 | 15020322 | 4418 | 106.032 | 4.418 | 2.9 | 2.9 | 2B | 0 | 0 | 1141 | 0 | 1129 | N/A | N/A | N/A | N/A | 32586306 | 804 | 181.9828 | 0% | 0% | 100% | 0% | 100% | 25% | 7170022 | 621 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 101 | 15024394 | 4072 | 97.728 | 4.072 | 3.9 | 3.9 | 2B | 0 | 0 | 1114 | 0 | 1110 | N/A | N/A | N/A | N/A | 32587000 | 694 | 170.4322 | 0% | 0% | 100% | 0% | 100% | 25% | 7170949 | 927 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 125317 | 125317 | 125.317 | 125.317 | [12 empty] | 26236 | 26236 | 209.3571 | [7 empty] | 7226 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:33 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 22) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:05 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 22) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25494 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15024394 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32587000 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7170949 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 96 | 15028466 | 4072 | 97.728 | 4.072 | 4.8 | 4.8 | 2B | 0 | 0 | 1029 | 0 | 1110 | N/A | N/A | N/A | N/A | 32587694 | 694 | 170.4322 | 0% | 0% | 100% | 0% | 100% | 35% | 7171876 | 927 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 15032539 | 4073 | 97.752 | 4.073 | 5.9 | 5.9 | 2B | 0 | 0 | 997 | 0 | 1110 | N/A | N/A | N/A | N/A | 32588390 | 696 | 170.8814 | 0% | 0% | 100% | 0% | 100% | 35% | 7172803 | 927 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 89 | 15036332 | 3793 | 91.032 | 3.793 | 7.4 | 7.4 | 2B | 0 | 0 | 966 | 0 | 1110 | N/A | N/A | N/A | N/A | 32589014 | 624 | 164.5136 | 0% | 0% | 100% | 0% | 100% | 35% | 7174056 | 1253 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 96 | 15040435 | 4103 | 98.472 | 4.103 | 8.8 | 8.8 | 2B | 0 | 0 | 1005 | 0 | 1080 | N/A | N/A | N/A | N/A | 32589632 | 618 | 150.6215 | 0% | 0% | 100% | 0% | 100% | 35% | 7175494 | 1438 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 101 | 15044538 | 4103 | 98.472 | 4.103 | 9.5 | 9.5 | 2B | 0 | 0 | 1010 | 0 | 1080 | N/A | N/A | N/A | N/A | 32590250 | 618 | 150.6215 | 0% | 0% | 100% | 0% | 100% | 35% | 7176215 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 114 | 114 | 15048643 | 4105 | 98.52 | 4.105 | 9.5 | 9.5 | 2B | 0 | 0 | 1114 | 0 | 1080 | N/A | N/A | N/A | N/A | 32590870 | 620 | 151.0353 | 0% | 0% | 100% | 0% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 15054522 | 5879 | 141.096 | 5.879 | 9.3 | 9.3 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32592162 | 1292 | 219.7653 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 15060742 | 6220 | 149.28 | 6.22 | 8.8 | 8.8 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32593542 | 1380 | 221.865 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 15066997 | 6255 | 150.12 | 6.255 | 8.1 | 8.1 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32594948 | 1406 | 224.7802 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 155 | 15073301 | 6304 | 151.296 | 6.304 | 7.2 | 7.2 | 3B+1S | 0 | 1173 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32596382 | 1434 | 227.4746 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 153 | 15079659 | 6358 | 152.592 | 6.358 | 6.2 | 6.2 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32597830 | 1448 | 227.7446 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 148 | 15085847 | 6188 | 148.512 | 6.188 | 5.3 | 5.3 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32599266 | 1436 | 232.0621 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 145 | 15091902 | 6055 | 145.32 | 6.055 | 4.5 | 4.5 | 3B+1S | 0 | 1132 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32600666 | 1400 | 231.2139 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 146 | 15097821 | 5919 | 142.056 | 5.919 | 3.4 | 3.4 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32602054 | 1388 | 234.4991 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 146 | 15103740 | 5919 | 142.056 | 5.919 | 2.8 | 2.8 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32603442 | 1388 | 234.4991 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 15109661 | 5921 | 142.104 | 5.921 | 2.2 | 2.2 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32604830 | 1388 | 234.4199 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 136 | 15115417 | 5756 | 138.144 | 5.756 | 1.6 | 1.6 | 3B+1S | 0 | 1193 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32606210 | 1380 | 239.7498 | 0% | 100% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 128 | 15121117 | 5700 | 136.8 | 5.7 | 1.5 | 1.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32607498 | 1288 | 225.9649 | 0% | 0% | 100% | 100% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A ONG | 16.6 | 119 | 117 | 15126118 | 5001 | 120.024 | 5.001 | 1.5 | 1.5 | 2B | 0 | 0 | 1167 | 0 | 1182 | N/A | N/A | N/A | N/A | 32608428 | 930 | 185.9628 | 0% | 0% | 100% | 0% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A ONG | 16.6 | 119 | 112 | 15131078 | 4960 | 119.04 | 4.96 | 1.5 | 1.5 | 2B | 0 | 0 | 1185 | 0 | 1150 | N/A | N/A | N/A | N/A | 32609322 | 894 | 180.2419 | 0% | 0% | 100% | 0% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A ONG | 16.1 | 115 | 111 | 15135837 | 4759 | 114.216 | 4.759 | 1.5 | 1.5 | 2B | 0 | 0 | 1114 | 0 | 1110 | N/A | N/A | N/A | N/A | 32610154 | 832 | 174.8266 | 0% | 0% | 100% | 0% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 12.6 | 110 | 103 | 15140510 | 4673 | 112.152 | 4.673 | 1.5 | 1.5 | 2B | 0 | 0 | 1054 | 0 | 1110 | N/A | N/A | N/A | N/A | 32610912 | 758 | 162.2084 | 0% | 0% | 100% | 0% | 100% | 0% | 7176215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 105 | 15145091 | 4581 | 109.944 | 4.581 | 2.2 | 2.2 | 2B | 0 | 0 | 1115 | 0 | 1160 | N/A | N/A | N/A | N/A | 32611730 | 818 | 178.5636 | 0% | 0% | 100% | 0% | 100% | 30% | 7176817 | 602 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 104 | 15149452 | 4361 | 104.664 | 4.361 | 3 | 3 | 2B | 0 | 0 | 1065 | 0 | 1110 | N/A | N/A | N/A | N/A | 32612494 | 764 | 175.1892 | 0% | 0% | 100% | 0% | 100% | 30% | 7177596 | 779 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.125 | 125058 | 125058 | 125.058 | 125.058 | [12 empty] | 25494 | 25494 | 203.8574 | [7 empty] | 6647 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:21 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 23) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 5:12 PM DUE TO LOW WATER LEVEL 1.5M AND LOW SUCTION PRESSURE
BP2 - STOPPED @ 6:01 PM DUE TO LOW WATER LEVEL 1.5M AND LOW SUCTION PRESSURE
Target Discharge Pressure set to 66 psi @ 6:01 pm due to low suction pressure
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:38 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
ABNORMAL OPERATION

## NOV 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26012 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15149452 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32612494 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7177596 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 101 | 15153591 | 4139 | 99.336 | 4.139 | 4.4 | 4.4 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 32613202 | 708 | 171.0558 | 0% | 0% | 100% | 0% | 100% | 40% | 7178812 | 1216 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 98 | 15157606 | 4015 | 96.36 | 4.015 | 5.8 | 5.8 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 32613882 | 680 | 169.3649 | 0% | 0% | 100% | 0% | 100% | 40% | 7180096 | 1284 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 96 | 15161529 | 3923 | 94.152 | 3.923 | 7.1 | 7.1 | 2B | 0 | 0 | 1007 | 0 | 1110 | N/A | N/A | N/A | N/A | 32614536 | 654 | 166.7092 | 0% | 0% | 100% | 0% | 100% | 40% | 7181386 | 1290 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 93 | 15165387 | 3858 | 92.592 | 3.858 | 8.4 | 8.4 | 2B | 0 | 0 | 1010 | 0 | 1029 | N/A | N/A | N/A | N/A | 32615166 | 630 | 163.297 | 0% | 0% | 100% | 0% | 100% | 40% | 7182666 | 1280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 93 | 15169134 | 3747 | 89.928 | 3.747 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1009 | N/A | N/A | N/A | N/A | 32615746 | 580 | 154.7905 | 0% | 0% | 100% | 0% | 100% | 40% | 7183736 | 1070 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 110 | 107 | 15173242 | 4108 | 98.592 | 4.108 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1009 | N/A | N/A | N/A | N/A | 32616286 | 540 | 131.4508 | 0% | 0% | 100% | 0% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 139 | 15178758 | 5516 | 132.384 | 5.516 | 9.5 | 9.5 | 3B | 0 | 0 | 1142 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32617430 | 1144 | 207.3967 | 0% | 0% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 15184750 | 5992 | 143.808 | 5.992 | 9.4 | 9.4 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32618750 | 1320 | 220.2937 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 150 | 15191033 | 6283 | 150.792 | 6.283 | 8.7 | 8.7 | 3B+1S | 0 | 1112 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32620154 | 1404 | 223.4601 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 152 | 15197355 | 6322 | 151.728 | 6.322 | 7.8 | 7.8 | 3B+1S | 0 | 1159 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32621592 | 1438 | 227.4597 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 15203573 | 6218 | 149.232 | 6.218 | 6.9 | 6.9 | 3B+1S | 0 | 1103 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32623010 | 1418 | 228.0476 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 15209821 | 6248 | 149.952 | 6.248 | 6 | 6 | 3B+1S | 0 | 1168 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32624452 | 1442 | 230.7939 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 15215824 | 6003 | 144.072 | 6.003 | 5.3 | 5.3 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32625833 | 1381 | 230.0516 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 15221688 | 5864 | 140.736 | 5.864 | 4.7 | 4.7 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32627197 | 1364 | 232.6057 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 15227413 | 5725 | 137.4 | 5.725 | 4.4 | 4.4 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32628546 | 1349 | 235.6332 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 15233080 | 5667 | 136.008 | 5.667 | 4.2 | 4.2 | 3B+1S | 0 | 1006 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32629873 | 1327 | 234.1627 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 140 | 15238774 | 5694 | 136.656 | 5.694 | 3.5 | 3.5 | 3B+1S | 0 | 1102 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32631228 | 1355 | 237.9698 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 15244411 | 5637 | 135.288 | 5.637 | 3.3 | 3.3 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32632538 | 1310 | 232.3931 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 15250096 | 5685 | 136.44 | 5.685 | 3.2 | 3.2 | 3B+1S | 0 | 1022 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32633854 | 1316 | 231.4864 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 125 | 15255505 | 5409 | 129.816 | 5.409 | 3 | 3 | 3B+1S | 0 | 998 | 1084 | 1185 | 1088 | N/A | N/A | N/A | N/A | 32634998 | 1144 | 211.4994 | 0% | 100% | 100% | 100% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 125 | 15260654 | 5149 | 123.576 | 5.149 | 2.5 | 2.5 | 2B+1S | 0 | 1036 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32636035 | 1037 | 201.3983 | 0% | 100% | 100% | 0% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 122 | 15265782 | 5128 | 123.072 | 5.128 | 2.2 | 2.2 | 2B+1S | 0 | 1014 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 32637046 | 1011 | 197.1529 | 0% | 100% | 100% | 0% | 100% | 0% | 7183736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 99 | 15270130 | 4348 | 104.352 | 4.348 | 2.8 | 2.8 | 2B | 0 |  | 1125 | 0 | 1110 | N/A | N/A | N/A | N/A | 32637818 | 772 | 177.5529 | 0% | 0% | 100% | 0% | 100% | 30% | 7184362 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 94 | 15274157 | 4027 | 96.648 | 4.027 | 3.6 | 3.6 | 2B | 0 |  | 1003 | 0 | 1110 | N/A | N/A | N/A | N/A | 32638506 | 688 | 170.8468 | 0% | 0% | 100% | 0% | 100% | 30% | 7185153 | 791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7917 | 124705 | 124705 | 124.705 | 124.705 | [12 empty] | 26012 | 26012 | 208.5883 | [7 empty] | 7557 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:05 PM TO 4:15 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:16 PM TO 4:26PM FOR 10 MINUTES RUN
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 24) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 24) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25952 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15274157 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32638506 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7185153 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 89 | 15277833 | 3676 | 88.224 | 3.676 | 5.1 | 5.1 | 2B | 0 | 0 | 1025 | 0 | 1048 | N/A | N/A | N/A | N/A | 32639134 | 628 | 170.8379 | 0% | 0% | 100% | 0% | 100% | 40% | 7186429 | 1276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 88 | 15281476 | 3643 | 87.432 | 3.643 | 6.4 | 6.4 | 2B | 0 | 0 | 1008 | 0 | 1048 | N/A | N/A | N/A | N/A | 32639746 | 612 | 167.9934 | 0% | 0% | 100% | 0% | 100% | 40% | 7187762 | 1333 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 86 | 15285031 | 3555 | 85.32 | 3.555 | 7.8 | 7.8 | 2B | 0 | 0 | 932 | 0 | 1028 | N/A | N/A | N/A | N/A | 32640286 | 540 | 151.8987 | 0% | 0% | 100% | 0% | 100% | 40% | 7189092 | 1330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 87 | 15288653 | 3622 | 86.928 | 3.622 | 9.1 | 9.1 | 2B | 0 | 0 | 927 | 0 | 1028 | N/A | N/A | N/A | N/A | 32640816 | 530 | 146.328 | 0% | 0% | 100% | 0% | 100% | 40% | 7190112 | 1020 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 102 | 15292443 | 3790 | 90.96 | 3.79 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 1008 | N/A | N/A | N/A | N/A | 32641360 | 544 | 143.5356 | 0% | 0% | 100% | 0% | 100% | 40% | 7190658 | 546 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 118 | 15297078 | 4635 | 111.24 | 4.635 | 9.5 | 9.5 | 2B | 0 | 0 | 1164 | 0 | 1170 | N/A | N/A | N/A | N/A | 32642120 | 760 | 163.9698 | 0% | 0% | 100% | 0% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 15303052 | 5974 | 143.376 | 5.974 | 9.1 | 9.1 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32643462 | 1342 | 224.6401 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 15309244 | 6192 | 148.608 | 6.192 | 8.5 | 8.5 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32644846 | 1384 | 223.5142 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 15315452 | 6208 | 148.992 | 6.208 | 7.8 | 7.8 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32646238 | 1392 | 224.2268 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 15321630 | 6178 | 148.272 | 6.178 | 7 | 7 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32647642 | 1404 | 227.258 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 15327684 | 6054 | 145.296 | 6.054 | 6.4 | 6.4 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32649034 | 1392 | 229.9306 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 147 | 15333704 | 6020 | 144.48 | 6.02 | 5.8 | 5.8 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32650402 | 1368 | 227.2425 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 144 | 15339526 | 5822 | 139.728 | 5.822 | 5.2 | 5.2 | 3B+1S | 0 | 1067 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32651755 | 1353 | 232.3944 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 15345291 | 5765 | 138.36 | 5.765 | 4.7 | 4.7 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32653094 | 1339 | 232.2637 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 15351003 | 5712 | 137.088 | 5.712 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32654422 | 1328 | 232.493 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 132 | 15356634 | 5631 | 135.144 | 5.631 | 4.5 | 4.5 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32655736 | 1314 | 233.3511 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 139 | 15362293 | 5659 | 135.816 | 5.659 | 3.9 | 3.9 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32657062 | 1326 | 234.317 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 15367938 | 5645 | 135.48 | 5.645 | 3.5 | 3.5 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32658380 | 1318 | 233.481 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 132 | 15373562 | 5624 | 134.976 | 5.624 | 3.4 | 3.4 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32659664 | 1284 | 228.3073 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 | 128 | 15378934 | 5372 | 128.928 | 5.372 | 3.3 | 3.3 | 3B+1S | 0 | 997 | 1126 | 1185 | 1129 | N/A | N/A | N/A | N/A | 32660866 | 1202 | 223.7528 | 0% | 100% | 100% | 100% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 15384259 | 5325 | 127.8 | 5.325 | 2.7 | 2.7 | 2B+1S | 0 | 1071 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32661934 | 1068 | 200.5634 | 0% | 100% | 100% | 0% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 113 | 15389339 | 5080 | 121.92 | 5.08 | 2.3 | 2.3 | 2B+1S | 0 | 997 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32662948 | 1014 | 199.6063 | 0% | 100% | 100% | 0% | 100% | 0% | 7190658 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 105 | 15393792 | 4453 | 106.872 | 4.453 | 3 | 3 | 2B | 0 | 0 | 1154 | 0 | 1100 | N/A | N/A | N/A | N/A | 32663746 | 798 | 179.205 | 0% | 0% | 100% | 0% | 100% | 35% | 7191346 | 688 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 92 | 15397942 | 4150 | 99.6 | 4.15 | 4 | 4 | 2B | 0 | 0 | 1035 | 0 | 1100 | N/A | N/A | N/A | N/A | 32664458 | 712 | 171.5663 | 0% | 0% | 100% | 0% | 100% | 35% | 7192259 | 913 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.875 | 123785 | 123785 | 123.785 | 123.785 | [12 empty] | 25952 | 25952 | 209.6538 | [7 empty] | 7106 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:17AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 25) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 25) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26126 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15297942 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32664458 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7192259 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 93 | 15301859 | 3917 | 94.008 | 3.917 | 5.2 | 5.2 | 2B | 0 | 0 | 1025 | 0 | 1110 | N/A | N/A | N/A | N/A | 32665106 | 648 | 165.4327 | 0% | 0% | 100% | 0% | 100% | 40% | 7193264 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 94 | 15305700 | 3841 | 92.184 | 3.841 | 6.5 | 6.5 | 2B | 0 | 0 | 1027 | 0 | 1059 | N/A | N/A | N/A | N/A | 32665726 | 620 | 161.4163 | 0% | 0% | 100% | 0% | 100% | 40% | 7194517 | 1253 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ORLANDO L. OCAMPO
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 89 | 15309505 | 3805 | 91.32 | 3.805 | 8 | 8 | 2B | 0 | 0 | 1010 | 0 | 1059 | N/A | N/A | N/A | N/A | 32666322 | 596 | 156.636 | 0% | 0% | 100% | 0% | 100% | 40% | 7195964 | 1447 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 99 | 15313470 | 3965 | 95.16 | 3.965 | 9.5 | 9.5 | 2B | 0 | 0 | 934 | 0 | 1059 | N/A | N/A | N/A | N/A | 32666902 | 580 | 146.2799 | 0% | 0% | 100% | 0% | 100% | 40% | 7197481 | 1517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 15317435 | 3965 | 95.16 | 3.965 | 9.5 | 9.5 | 2B | 0 | 0 | 990 | 0 | 1059 | N/A | N/A | N/A | N/A | 32667482 | 580 | 146.2799 | 0% | 0% | 100% | 0% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 122 | 15322221 | 4786 | 114.864 | 4.786 | 9.5 | 9.5 | 2B | 0 | 0 | 1170 | 0 | 1198 | N/A | N/A | N/A | N/A | 32668258 | 776 | 162.1396 | 0% | 0% | 100% | 0% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 149 | 15328305 | 6084 | 146.016 | 6.084 | 8.9 | 8.9 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32669599 | 1341 | 220.4142 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 151 | 15334406 | 6101 | 146.424 | 6.101 | 8.4 | 8.4 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32670992 | 1393 | 228.3232 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 15340548 | 6142 | 147.408 | 6.142 | 7.6 | 7.6 | 3B+1S | 0 | 1099 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32672397 | 1405 | 228.7528 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 15346712 | 6164 | 147.936 | 6.164 | 7 | 7 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32673790 | 1393 | 225.9896 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 15352864 | 6152 | 147.648 | 6.152 | 6.3 | 6.3 | 3B+1S | 0 | 1097 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32675198 | 1408 | 228.8687 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 148 | 15359011 | 6147 | 147.528 | 6.147 | 5.7 | 5.7 | 3B+1S | 0 | 1148 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32676578 | 1380 | 224.4998 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 15364907 | 5896 | 141.504 | 5.896 | 5.2 | 5.2 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32677941 | 1363 | 231.1737 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 15370710 | 5803 | 139.272 | 5.803 | 4.9 | 4.9 | 3B+1S | 0 | 1022 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32679282 | 1341 | 231.0874 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 15376421 | 5711 | 137.064 | 5.711 | 4.7 | 4.7 | 3B+1S | 0 | 1001 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32680602 | 1320 | 231.1329 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 15382119 | 5698 | 136.752 | 5.698 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32681951 | 1349 | 236.7497 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 139 | 15387794 | 5675 | 136.2 | 5.675 | 4.1 | 4.1 | 3B+1S | 0 | 1094 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32683274 | 1323 | 233.1278 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 15393434 | 5640 | 135.36 | 5.64 | 3.7 | 3.7 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32684593 | 1319 | 233.8652 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 131 | 15399057 | 5623 | 134.952 | 5.623 | 3.6 | 3.6 | 3B+1S | 0 | 989 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32685908 | 1315 | 233.8609 | 0% | 100% | 100% | 100% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 129 | 15404434 | 5377 | 129.048 | 5.377 | 2.8 | 2.8 | 2B+1S | 0 | 1142 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32687023 | 1115 | 207.3647 | 0% | 100% | 100% | 0% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 15409672 | 5238 | 125.712 | 5.238 | 2.1 | 2.1 | 2B+1S | 0 | 1059 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32688082 | 1059 | 202.1764 | 0% | 100% | 100% | 0% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 122 | 15414741 | 5069 | 121.656 | 5.069 | 1.9 | 1.9 | 2B+1S | 0 | 1000 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32689098 | 1016 | 200.434 | 0% | 100% | 100% | 0% | 100% | 0% | 7197481 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 98 | 15419081 | 4340 | 104.16 | 4.34 | 2.4 | 2.4 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 32689880 | 782 | 180.1843 | 0% | 0% | 100% | 0% | 100% | 30% | 7198074 | 593 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 100 | 15423206 | 4125 | 99 | 4.125 | 3.3 | 3.3 | 2B | 0 | 0 | 1037 | 0 | 1110 | N/A | N/A | N/A | N/A | 32690584 | 704 | 170.6667 | 0% | 0% | 100% | 0% | 100% | 30% | 7198898 | 824 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.875 | 125264 | 125264 | 125.264 | 125.264 | [12 empty] | 26126 | 26126 | 208.5675 | [7 empty] | 6639 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 26) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:17 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 26) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | A. CABREROS / R. REGENCIA
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26214 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15423206 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32690584 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7198898 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 93 | 15427168 | 3962 | 95.088 | 3.962 | 4.8 | 4.8 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 32691262 | 678 | 171.1257 | 0% | 0% | 100% | 0% | 100% | 40% | 7200128 | 1230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 15430887 | 3719 | 89.256 | 3.719 | 6.1 | 6.1 | 2B | 0 | 0 | 1017 | 0 | 1049 | N/A | N/A | N/A | N/A | 32691888 | 626 | 168.3248 | 0% | 0% | 100% | 0% | 100% | 40% | 7201425 | 1297 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | A. CABREROS / R. REGENCIA
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 91 | 15434665 | 3778 | 90.672 | 3.778 | 7.5 | 7.5 | 2B | 0 | 0 | 999 | 0 | 1049 | N/A | N/A | N/A | N/A | 32692482 | 594 | 157.226 | 0% | 0% | 100% | 0% | 100% | 40% | 7202792 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 93 | 15438396 | 3731 | 89.544 | 3.731 | 8.7 | 8.7 | 2B | 0 | 0 | 998 | 0 | 1049 | N/A | N/A | N/A | N/A | 32693058 | 576 | 154.3822 | 0% | 0% | 100% | 0% | 100% | 40% | 7204007 | 1215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 107 | 15442484 | 4088 | 98.112 | 4.088 | 9.5 | 9.5 | 2B | 0 | 0 | 999 | 0 | 1049 | N/A | N/A | N/A | N/A | 32693658 | 600 | 146.771 | 0% | 0% | 100% | 0% | 100% | 40% | 7204776 | 769 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 122 | 15447140 | 4656 | 111.744 | 4.656 | 9.5 | 9.5 | 2B | 0 | 0 | 1169 | 0 | 1180 | N/A | N/A | N/A | N/A | 32694418 | 760 | 163.2302 | 0% | 0% | 100% | 0% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 148 | 15453275 | 6135 | 147.24 | 6.135 | 9 | 9 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32695790 | 1372 | 223.6349 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 15459427 | 6152 | 147.648 | 6.152 | 8.3 | 8.3 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32697178 | 1388 | 225.6177 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 15465548 | 6121 | 146.904 | 6.121 | 7.6 | 7.6 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32698562 | 1384 | 226.1068 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 15471746 | 6198 | 148.752 | 6.198 | 6.8 | 6.8 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32699970 | 1408 | 227.1701 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 15477876 | 6130 | 147.12 | 6.13 | 6.2 | 6.2 | 3B+1S | 0 | 1088 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32701366 | 1396 | 227.7325 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 146 | 15483994 | 6118 | 146.832 | 6.118 | 5.5 | 5.5 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32702754 | 1388 | 226.8715 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 15489742 | 5748 | 137.952 | 5.748 | 5.1 | 5.1 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32704104 | 1350 | 234.8643 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 15495434 | 5692 | 136.608 | 5.692 | 4.7 | 4.7 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32705436 | 1332 | 234.0126 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 131 | 15501071 | 5637 | 135.288 | 5.637 | 4.5 | 4.5 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32706752 | 1316 | 233.4575 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 15506646 | 5575 | 133.8 | 5.575 | 4.3 | 4.3 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32708062 | 1310 | 234.9776 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 134 | 15512237 | 5591 | 134.184 | 5.591 | 3.7 | 3.7 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 32709390 | 1328 | 237.5246 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 15517874 | 5637 | 135.288 | 5.637 | 3.5 | 3.5 | 3B+1S | 0 | 1012 | 1186 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32710706 | 1316 | 233.4575 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 15523371 | 5497 | 131.928 | 5.497 | 3.4 | 3.4 | 3B+1S | 0 | 958 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32712002 | 1296 | 235.765 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 135 | 15528628 | 5257 | 126.168 | 5.257 | 3.3 | 3.3 | 3B+1S | 0 | 980 | 1155 | 1185 | 1150 | N/A | N/A | N/A | N/A | 32713202 | 1200 | 228.2671 | 0% | 100% | 100% | 100% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 15533856 | 5228 | 125.472 | 5.228 | 3 | 3 | 2B+1S | 0 | 1019 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32714250 | 1048 | 200.4591 | 0% | 100% | 100% | 0% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 121 | 15539007 | 5151 | 123.624 | 5.151 | 2.6 | 2.6 | 2B+1S | 0 | 1004 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32715274 | 1024 | 198.7964 | 0% | 100% | 100% | 0% | 100% | 0% | 7204776 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 104 | 15543471 | 4464 | 107.136 | 4.464 | 3.1 | 3.1 | 2B | 0 | 0 | 1143 | 0 | 1110 | N/A | N/A | N/A | N/A | 32716084 | 810 | 181.4516 | 0% | 0% | 100% | 0% | 100% | 30% | 7205264 | 488 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 99 | 15547660 | 4189 | 100.536 | 4.189 | 3.8 | 3.8 | 2B | 0 | 0 | 1043 | 0 | 1110 | N/A | N/A | N/A | N/A | 32716798 | 714 | 170.4464 | 0% | 0% | 100% | 0% | 100% | 30% | 7206005 | 741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.1667 | 124454 | 124454 | 124.454 | 124.454 | [12 empty] | 26214 | 26214 | 210.632 | [7 empty] | 7107 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:21 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 27) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 27) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25586 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15547660 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32716798 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7206005 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 97 | 15551721 | 4061 | 97.464 | 4.061 | 5.1 | 5.1 | 2B | 0 | 0 | 1036 | 0 | 1110 | N/A | N/A | N/A | N/A | 32717490 | 692 | 170.4014 | 0% | 0% | 100% | 0% | 100% | 40% | 7207115 | 1110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 95 | 15555613 | 3892 | 93.408 | 3.892 | 6.4 | 6.4 | 2B | 0 | 0 | 992 | 0 | 1110 | N/A | N/A | N/A | N/A | 32718138 | 648 | 166.4954 | 0% | 0% | 100% | 0% | 100% | 40% | 7208327 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | A. CABREROS / R. REGENCIA
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 15559447 | 3834 | 92.016 | 3.834 | 7.8 | 7.8 | 2B | 0 | 0 | 1025 | 0 | 1050 | N/A | N/A | N/A | N/A | 32718742 | 604 | 157.5378 | 0% | 0% | 100% | 0% | 100% | 40% | 7209549 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 90 | 15563233 | 3786 | 90.864 | 3.786 | 9 | 9 | 2B | 0 | 0 | 992 | 0 | 1028 | N/A | N/A | N/A | N/A | 32719328 | 586 | 154.7808 | 0% | 0% | 100% | 0% | 100% | 40% | 7210785 | 1236 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 15567181 | 3948 | 94.752 | 3.948 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 1009 | N/A | N/A | N/A | N/A | 32719894 | 566 | 143.3637 | 0% | 0% | 100% | 0% | 100% | 40% | 7211338 | 553 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 121 | 15571788 | 4607 | 110.568 | 4.607 | 9.5 | 9.5 | 2B | 0 | 0 | 1164 | 0 | 1170 | N/A | N/A | N/A | N/A | 32720642 | 748 | 162.3616 | 0% | 0% | 100% | 0% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 149 | 15577736 | 5948 | 142.752 | 5.948 | 9 | 9 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32721978 | 1336 | 224.6133 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 147 | 15583978 | 6242 | 149.808 | 6.242 | 8.3 | 8.3 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32723392 | 1414 | 226.53 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 146 | 15590231 | 6253 | 150.072 | 6.253 | 7.5 | 7.5 | 3B+1S | 0 | 1128 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32724810 | 1418 | 226.7711 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 15596267 | 6036 | 144.864 | 6.036 | 6.8 | 6.8 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32726182 | 1372 | 227.3028 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 15602197 | 5930 | 142.32 | 5.93 | 6.4 | 6.4 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32727533 | 1351 | 227.8246 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 139 | 15608127 | 5930 | 142.32 | 5.93 | 6 | 6 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32728884 | 1351 | 227.8246 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 15613835 | 5708 | 136.992 | 5.708 | 5.7 | 5.7 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32730210 | 1326 | 232.3055 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 132 | 15619454 | 5619 | 134.856 | 5.619 | 5.4 | 5.4 | 3B+1S | 0 | 996 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32731530 | 1320 | 234.9172 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 15625001 | 5547 | 133.128 | 5.547 | 5.3 | 5.3 | 3B+1S | 0 | 991 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32732826 | 1296 | 233.6398 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 131 | 15630405 | 5404 | 129.696 | 5.404 | 5.2 | 5.2 | 3B+1S | 0 | 1079 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32734066 | 1240 | 229.4597 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 133 | 15635914 | 5509 | 132.216 | 5.509 | 4.6 | 4.6 | 3B+1S | 0 | 1046 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32735346 | 1280 | 232.3471 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 131 | 15641356 | 5442 | 130.608 | 5.442 | 4.4 | 4.4 | 3B+1S | 0 | 1008 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32736592 | 1246 | 228.9599 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 132 | 15646799 | 5443 | 130.632 | 5.443 | 4.3 | 4.3 | 3B+1S | 0 | 904 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32737838 | 1246 | 228.9179 | 0% | 100% | 100% | 100% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 123 | 15652134 | 5335 | 128.04 | 5.335 | 3.6 | 3.6 | 2B+1S | 0 | 1061 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32738914 | 1076 | 201.687 | 0% | 100% | 100% | 0% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 121 | 15657227 | 5093 | 122.232 | 5.093 | 3.1 | 3.1 | 2B+1S | 0 | 1014 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32739934 | 1020 | 200.2749 | 0% | 100% | 100% | 0% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 124 | 15662241 | 5014 | 120.336 | 5.014 | 2.9 | 2.9 | 2B+1S | 0 | 900 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32740938 | 1004 | 200.2393 | 0% | 100% | 100% | 0% | 100% | 0% | 7211338 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 102 | 15666555 | 4314 | 103.536 | 4.314 | 3.4 | 3.4 | 2B | 0 | 0 | 1094 | 0 | 1110 | N/A | N/A | N/A | N/A | 32741698 | 760 | 176.1706 | 0% | 0% | 100% | 0% | 100% | 28% | 7211844 | 506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 97 | 15670675 | 4120 | 98.88 | 4.12 | 4.2 | 4.2 | 2B | 0 | 0 | 1016 | 0 | 1110 | N/A | N/A | N/A | N/A | 32742384 | 686 | 166.5049 | 0% | 0% | 100% | 0% | 100% | 28% | 7212542 | 698 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.3333 | 123015 | 123015 | 123.015 | 123.015 | [12 empty] | 25586 | 25586 | 207.9909 | [7 empty] | 6537 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:26 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 28) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (28%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25808 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15670675 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32742384 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7212542 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 93 | 15674597 | 3922 | 94.128 | 3.922 | 5.5 | 5.5 | 2B | 0 | 0 | 1040 | 0 | 1048 | N/A | N/A | N/A | N/A | 32743046 | 662 | 168.7914 | 0% | 0% | 100% | 0% | 100% | 38% | 7213655 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 90 | 15678328 | 3731 | 89.544 | 3.731 | 6.7 | 6.7 | 2B | 0 | 0 | 1012 | 0 | 1008 | N/A | N/A | N/A | N/A | 32743642 | 596 | 159.7427 | 0% | 0% | 100% | 0% | 100% | 38% | 7214863 | 1208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | A. CABREROS / R. REGENCIA
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 15682032 | 3704 | 88.896 | 3.704 | 7.9 | 7.9 | 2B | 0 | 0 | 1002 | 0 | 1008 | N/A | N/A | N/A | N/A | 32744216 | 574 | 154.9676 | 0% | 0% | 100% | 0% | 100% | 38% | 7216098 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 91 | 15685752 | 3720 | 89.28 | 3.72 | 9.1 | 9.1 | 2B | 0 | 0 | 1012 | 0 | 1008 | N/A | N/A | N/A | N/A | 32744770 | 554 | 148.9247 | 0% | 0% | 100% | 0% | 100% | 38% | 7217187 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 15689633 | 3881 | 93.144 | 3.881 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 1008 | N/A | N/A | N/A | N/A | 32745306 | 536 | 138.1087 | 0% | 0% | 100% | 0% | 100% | 38% | 7217591 | 404 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 118 | 15694247 | 4614 | 110.736 | 4.614 | 9.5 | 9.5 | 2B | 0 | 0 | 1153 | 0 | 1169 | N/A | N/A | N/A | N/A | 32746052 | 746 | 161.6818 | 0% | 0% | 100% | 0% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 149 | 15700211 | 5964 | 143.136 | 5.964 | 9.2 | 9.2 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32747382 | 1330 | 223.0047 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 15706309 | 6098 | 146.352 | 6.098 | 8.7 | 8.7 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32748746 | 1364 | 223.6799 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 15712510 | 6201 | 148.824 | 6.201 | 7.9 | 7.9 | 3B+1S | 0 | 1095 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32750138 | 1392 | 224.4799 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 15718725 | 6215 | 149.16 | 6.215 | 7.1 | 7.1 | 3B+1S | 0 | 1113 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32751554 | 1416 | 227.8359 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 15724818 | 6093 | 146.232 | 6.093 | 6.5 | 6.5 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32752930 | 1376 | 225.8329 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 15730926 | 6108 | 146.592 | 6.108 | 5.9 | 5.9 | 3B+1S | 0 | 1095 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32754320 | 1390 | 227.5704 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 15736695 | 5769 | 138.456 | 5.769 | 5.4 | 5.4 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32755664 | 1344 | 232.9693 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 15742464 | 5769 | 138.456 | 5.769 | 5 | 5 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32757002 | 1338 | 231.9293 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 131 | 15748042 | 5578 | 133.872 | 5.578 | 4.9 | 4.9 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32758312 | 1310 | 234.8512 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 15753572 | 5530 | 132.72 | 5.53 | 4.8 | 4.8 | 3B+1S | 0 | 1028 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32759618 | 1306 | 236.1664 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 15759160 | 5588 | 134.112 | 5.588 | 4.5 | 4.5 | 3B+1S | 0 | 1038 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32760930 | 1312 | 234.7888 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 15764847 | 5687 | 136.488 | 5.687 | 4.1 | 4.1 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32762218 | 1288 | 226.4814 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 15770419 | 5572 | 133.728 | 5.572 | 3.9 | 3.9 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32763510 | 1292 | 231.8737 | 0% | 100% | 100% | 100% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 127 | 15775718 | 5299 | 127.176 | 5.299 | 3.2 | 3.2 | 2B+1S | 0 | 1109 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32764610 | 1100 | 207.5863 | 0% | 100% | 100% | 0% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 123 | 15781006 | 5288 | 126.912 | 5.288 | 2.6 | 2.6 | 2B+1S | 0 | 1034 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32765662 | 1052 | 198.941 | 0% | 100% | 100% | 0% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 125 | 15786014 | 5008 | 120.192 | 5.008 | 2.3 | 2.3 | 2B+1S | 0 | 991 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32766678 | 1016 | 202.8754 | 0% | 100% | 100% | 0% | 100% | 0% | 7217591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 104 | 15790548 | 4534 | 108.816 | 4.534 | 2.9 | 2.9 | 2B | 0 | 0 | 1142 | 0 | 1110 | N/A | N/A | N/A | N/A | 32767486 | 808 | 178.2091 | 0% | 0% | 100% | 0% | 100% | 28% | 7218101 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 101 | 15794651 | 4103 | 98.472 | 4.103 | 3.5 | 3.5 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 32768192 | 706 | 172.0692 | 0% | 0% | 100% | 0% | 100% | 28% | 7218754 | 653 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.9583 | 123976 | 123976 | 123.976 | 123.976 | [12 empty] | 25808 | 25808 | 208.1693 | [7 empty] | 6212 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - INCREASED OPENING TO 38% @ 12:01AM FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:05 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 29) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:21 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 29) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (28%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26498 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15794651 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32768192 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7218754 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 94 | 15798792 | 4141 | 99.384 | 4.141 | 4.9 | 4.9 | 2B | 0 | 0 | 1028 | 0 | 1110 | N/A | N/A | N/A | N/A | 32768910 | 718 | 173.3881 | 0% | 0% | 100% | 0% | 100% | 38% | 7219875 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 94 | 15802541 | 3749 | 89.976 | 3.749 | 6 | 6 | 2B | 0 | 0 | 1042 | 0 | 1048 | N/A | N/A | N/A | N/A | 32769534 | 624 | 166.4444 | 0% | 0% | 100% | 0% | 100% | 38% | 7221003 | 1128 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | A. CABREROS / R. REGENCIA
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 15806386 | 3845 | 92.28 | 3.845 | 7.3 | 7.3 | 2B | 0 | 0 | 1010 | 0 | 1048 | N/A | N/A | N/A | N/A | 32770146 | 612 | 159.1678 | 0% | 0% | 100% | 0% | 100% | 38% | 7222200 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 90 | 15810126 | 3740 | 89.76 | 3.74 | 8.4 | 8.4 | 2B | 0 | 0 | 1002 | 0 | 1028 | N/A | N/A | N/A | N/A | 32770728 | 582 | 155.615 | 0% | 0% | 100% | 0% | 100% | 38% | 7223314 | 1114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 102 | 15814015 | 3889 | 93.336 | 3.889 | 9.5 | 9.5 | 2B | 0 | 0 | 962 | 0 | 1028 | N/A | N/A | N/A | N/A | 32771292 | 564 | 145.0244 | 0% | 0% | 100% | 0% | 100% | 38% | 7224377 | 1063 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 119 | 15818205 | 4190 | 100.56 | 4.19 | 9.5 | 9.5 | 2B | 0 | 0 | 1074 | 0 | 1098 | N/A | N/A | N/A | N/A | 32771890 | 598 | 142.7208 | 0% | 0% | 100% | 0% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 141 | 15823909 | 5704 | 136.896 | 5.704 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32773130 | 1240 | 217.3913 | 0% | 0% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 15830122 | 6213 | 149.112 | 6.213 | 9 | 9 | 3B+1S | 0 | 1071 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32774522 | 1392 | 224.0464 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 151 | 15836373 | 6251 | 150.024 | 6.251 | 8.1 | 8.1 | 3B+1S | 0 | 1143 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32775931 | 1409 | 225.4039 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 15842662 | 6289 | 150.936 | 6.289 | 7.2 | 7.2 | 3B+1S | 0 | 1174 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32777358 | 1427 | 226.9041 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 15848857 | 6195 | 148.68 | 6.195 | 6.3 | 6.3 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32778799 | 1441 | 232.6069 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 15855039 | 6182 | 148.368 | 6.182 | 5.4 | 5.4 | 3B+1S | 0 | 1137 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32780230 | 1431 | 231.4785 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 143 | 15860974 | 5935 | 142.44 | 5.935 | 4.7 | 4.7 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32781616 | 1386 | 233.5299 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 144 | 15866886 | 5912 | 141.888 | 5.912 | 3.8 | 3.8 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32783000 | 1384 | 234.1001 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 139 | 15872754 | 5868 | 140.832 | 5.868 | 3.3 | 3.3 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32784370 | 1370 | 233.4697 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 15878439 | 5685 | 136.44 | 5.685 | 3.1 | 3.1 | 3B+1S | 0 | 1187 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32785828 | 1458 | 256.4644 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 143 | 15884106 | 5667 | 136.008 | 5.667 | 2.6 | 2.6 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32787245 | 1417 | 250.0441 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 133 | 15889773 | 5667 | 136.008 | 5.667 | 2.4 | 2.4 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32788662 | 1417 | 250.0441 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 127 | 15895270 | 5497 | 131.928 | 5.497 | 2.3 | 2.3 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32790046 | 1384 | 251.7737 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 128 | 15900555 | 5285 | 126.84 | 5.285 | 2.2 | 2.2 | 3B+1S | 0 | 990 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 32791254 | 1208 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 120 | 15905697 | 5142 | 123.408 | 5.142 | 1.9 | 1.9 | 2B+1S | 0 | 1020 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32792296 | 1042 | 202.6449 | 0% | 100% | 100% | 0% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 119 | 15910724 | 5027 | 120.648 | 5.027 | 1.8 | 1.8 | 2B+1S | 0 | 0 | 1152 | 0 | 1199 | N/A | N/A | N/A | N/A | 32793282 | 986 | 196.1408 | 0% | 0% | 100% | 0% | 100% | 0% | 7224377 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 99 | 15914942 | 4218 | 101.232 | 4.218 | 2.5 | 2.5 | 2B | 0 | 0 | 1102 | 0 | 1110 | N/A | N/A | N/A | N/A | 32794014 | 732 | 173.542 | 0% | 0% | 100% | 0% | 100% | 0% | 7225109 | 732 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 94 | 15918965 | 4023 | 96.552 | 4.023 | 3.4 | 3.4 | 2B | 0 | 0 | 1018 | 0 | 1110 | N/A | N/A | N/A | N/A | 32794690 | 676 | 168.0338 | 0% | 0% | 100% | 0% | 100% | 0% | 7225942 | 833 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0417 | 124314 | 124314 | 124.314 | 124.314 | [12 empty] | 26498 | 26498 | 213.1538 | [7 empty] | 7188 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (NOV 30) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV-4 OPENED @ 3:00 PM / CLOSED @ 7:00 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:21 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:45 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## NOV 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRIS DIO
[13 empty] | 10pm - 6am | RANDY O. REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-11-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24905 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15918965 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32794690 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7225942 |  | mg /l |  | Automatic - i2O | AI | CHRIS DIO
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 15922716 | 3751 | 90.024 | 3.751 | 4.8 | 4.8 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 32795338 | 648 | 172.7539 | 0% | 0% | 100% | 0% | 100% | 40% | 7227196 | 1254 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 85 | 15926353 | 3637 | 87.288 | 3.637 | 6.1 | 6.1 | 2B | 0 | 0 | 1014 | 0 | 1028 | N/A | N/A | N/A | N/A | 32795926 | 588 | 161.6717 | 0% | 0% | 100% | 0% | 100% | 40% | 7228513 | 1317 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | A. CABREROS / R. REGENCIA
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 84 | 15929831 | 3478 | 83.472 | 3.478 | 7.6 | 7.6 | 2B | 0 | 0 | 996 | 0 | 1008 | N/A | N/A | N/A | N/A | 32796474 | 548 | 157.5618 | 0% | 0% | 100% | 0% | 100% | 40% | 7229855 | 1342 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | DENNIS L. GUANZON
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 81 | 15933340 | 3509 | 84.216 | 3.509 | 8.8 | 8.8 | 2B | 0 | 0 | 985 | 0 | 1008 | N/A | N/A | N/A | N/A | 32797014 | 540 | 153.89 | 0% | 0% | 100% | 0% | 100% | 40% | 7231133 | 1278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | ALEXANDER CABREROS
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 92 | 15937024 | 3684 | 88.416 | 3.684 | 9.5 | 9.5 | 2B | 0 | 0 | 921 | 0 | 1008 | N/A | N/A | N/A | N/A | 32797550 | 536 | 145.494 | 0% | 0% | 100% | 0% | 100% | 40% | 7232055 | 922 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | O. OCAMPO / D. GUANZON
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 105 | 105 | 15940806 | 3782 | 90.768 | 3.782 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 987 | N/A | N/A | N/A | N/A | 32798036 | 486 | 128.5034 | 0% | 0% | 100% | 0% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule | Error - General | E | RANDY O. REGENCIA
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 134 | 15946077 | 5271 | 126.504 | 5.271 | 9.5 | 9.5 | 3B | 0 | 0 | 1115 | 1185 | 1119 | N/A | N/A | N/A | N/A | 32799014 | 978 | 185.5435 | 0% | 0% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 143 | 15951896 | 5819 | 139.656 | 5.819 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32800236 | 1222 | 210.0017 | 0% | 0% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 145 | 15958000 | 6104 | 146.496 | 6.104 | 9.2 | 9.2 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32801587 | 1351 | 221.3303 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 15964133 | 6133 | 147.192 | 6.133 | 8.6 | 8.6 | 3B+1S | 0 | 1077 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32802968 | 1381 | 225.1753 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 15970309 | 6176 | 148.224 | 6.176 | 7.9 | 7.9 | 3B+1S | 0 | 1074 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32804365 | 1397 | 226.1982 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 146 | 15976512 | 6203 | 148.872 | 6.203 | 6.9 | 6.9 | 3B+1S | 0 | 1147 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32805780 | 1415 | 228.1154 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 144 | 15982516 | 6004 | 144.096 | 6.004 | 6.3 | 6.3 | 3B+1S | 0 | 1094 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32807158 | 1378 | 229.5137 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 144 | 15988542 | 6026 | 144.624 | 6.026 | 5.7 | 5.7 | 3B+1S | 0 | 1072 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32808538 | 1380 | 229.0076 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 15994347 | 5805 | 139.32 | 5.805 | 5.1 | 5.1 | 3B+1S | 0 | 1043 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32809882 | 1344 | 231.5245 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 15999910 | 5563 | 133.512 | 5.563 | 4.8 | 4.8 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32811190 | 1308 | 235.1249 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 16005473 | 5563 | 133.512 | 5.563 | 4.5 | 4.5 | 3B+1S | 0 | 1046 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32812504 | 1314 | 236.2035 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 129 | 16010934 | 5461 | 131.064 | 5.461 | 4.2 | 4.2 | 3B+1S | 0 | 1020 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32813772 | 1268 | 232.1919 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 129 | 16016547 | 5613 | 134.712 | 5.613 | 4.1 | 4.1 | 3B+1S | 0 | 1003 | 1154 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32815060 | 1288 | 229.4673 | 0% | 100% | 100% | 100% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 16021826 | 5279 | 126.696 | 5.279 | 3.4 | 3.4 | 2B+1S | 0 | 1067 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 32816122 | 1062 | 201.1745 | 0% | 100% | 100% | 0% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 127 | 16027031 | 5205 | 124.92 | 5.205 | 2.9 | 2.9 | 2B+1S | 0 | 1018 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 32817146 | 1024 | 196.7339 | 0% | 100% | 100% | 0% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 126 | 16032092 | 5061 | 121.464 | 5.061 | 2.8 | 2.8 | 2B+1S | 0 | 991 | 1155 | 0 | 1198 | N/A | N/A | N/A | N/A | 32818146 | 1000 | 197.5894 | 0% | 100% | 100% | 0% | 100% | 0% | 7232055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 102 | 16036500 | 4408 | 105.792 | 4.408 | 3.3 | 3.3 | 2B | 0 | 0 | 1120 | 0 | 1110 | N/A | N/A | N/A | N/A | 32818920 | 774 | 175.5898 | 0% | 0% | 100% | 0% | 100% | 25% | 7232513 | 458 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 100 | 16040714 | 4214 | 101.136 | 4.214 | 3.9 | 3.9 | 2B | 0 | 0 | 1011 | 0 | 1110 | N/A | N/A | N/A | N/A | 32819595 | 675 | 160.1804 | 0% | 0% | 100% | 0% | 100% | 25% | 7233186 | 673 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.625 | 121749 | 121749 | 121.749 | 121.749 | [12 empty] | 24905 | 24905 | 204.5602 | [7 empty] | 7244 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
XCV1 - OPENED @ 12:01AM (40%) FOR REFILLING
NOTE:NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 1) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:00 PM, NORMAL OPERATION
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:05 PM TO 4:15 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:16 PM TO 4:26PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure @ 10:01 pm to 5am (NOV 30) as per request of Engr. Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION