## DEC 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25317 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16040714 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32819595 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7233186 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 94 | 16044607 | 3893 | 93.432 | 3.893 | 5 | 5 | 2B | 0 | 0 | 1042 | 0 | 1048 | N/A | N/A | N/A | N/A | 32820260 | 665 | 170.8194 | 0% | 0% | 100% | 0% | 100% | 35% | 7234109 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 92 | 16048419 | 3812 | 91.488 | 3.812 | 6.2 | 6.2 | 2B | 0 | 0 | 1026 | 0 | 1048 | N/A | N/A | N/A | N/A | 32820880 | 620 | 162.6443 | 0% | 0% | 100% | 0% | 100% | 35% | 7235356 | 1247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 16052197 | 3778 | 90.672 | 3.778 | 7.4 | 7.4 | 2B | 0 | 0 | 1007 | 0 | 1028 | N/A | N/A | N/A | N/A | 32821462 | 582 | 154.0498 | 0% | 0% | 100% | 0% | 100% | 35% | 7236627 | 1271 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 92 | 16055974 | 3777 | 90.648 | 3.777 | 8.6 | 8.6 | 2B | 0 | 0 | 1010 | 0 | 1018 | N/A | N/A | N/A | N/A | 32822030 | 568 | 150.3839 | 0% | 0% | 100% | 0% | 100% | 35% | 7237760 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 105 | 16059875 | 3901 | 93.624 | 3.901 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 1018 | N/A | N/A | N/A | N/A | 32822584 | 554 | 142.0149 | 0% | 0% | 100% | 0% | 100% | 35% | 7238601 | 841 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 117 | 16064453 | 4578 | 109.872 | 4.578 | 9.5 | 9.5 | 2B | 0 | 0 | 1133 | 0 | 1110 | N/A | N/A | N/A | N/A | 32823286 | 702 | 153.3421 | 0% | 0% | 100% | 0% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 143 | 16070209 | 5756 | 138.144 | 5.756 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32824522 | 1236 | 214.7325 | 0% | 0% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 144 | 16076087 | 5878 | 141.072 | 5.878 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32825774 | 1252 | 212.9976 | 0% | 0% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 16082156 | 6069 | 145.656 | 6.069 | 9.1 | 9.1 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32827130 | 1356 | 223.4305 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 16088151 | 5995 | 143.88 | 5.995 | 8.6 | 8.6 | 3B+1S | 0 | 1034 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32828482 | 1352 | 225.5213 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 16094294 | 6143 | 147.432 | 6.143 | 8.1 | 8.1 | 3B+1S | 0 | 1053 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32829870 | 1388 | 225.9482 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 16100203 | 5909 | 141.816 | 5.909 | 7.5 | 7.5 | 3B+1S | 0 | 1082 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32831222 | 1352 | 228.8035 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 16106064 | 5861 | 140.664 | 5.861 | 7.1 | 7.1 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32832562 | 1340 | 228.6299 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 16111755 | 5691 | 136.584 | 5.691 | 7.1 | 7.1 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32833866 | 1304 | 229.1337 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 16117320 | 5565 | 133.56 | 5.565 | 6.9 | 6.9 | 3B+1S | 0 | 989 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32835162 | 1296 | 232.8841 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 134 | 16122899 | 5579 | 133.896 | 5.579 | 6.8 | 6.8 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32836442 | 1280 | 229.4318 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 16128580 | 5681 | 136.344 | 5.681 | 6.4 | 6.4 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32837758 | 1316 | 231.6494 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 139 | 16134563 | 5983 | 143.592 | 5.983 | 5.6 | 5.6 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32839154 | 1396 | 233.3278 | 0% | 100% | 100% | 100% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 109 | 132 | 16139725 | 5162 | 123.888 | 5.162 | 4.9 | 4.9 | 2B+1S | 0 | 1189 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32840210 | 1056 | 204.5719 | 0% | 100% | 100% | 0% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 16145148 | 5423 | 130.152 | 5.423 | 3.9 | 3.9 | 2B+1S | 0 | 1120 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32841298 | 1088 | 200.627 | 0% | 100% | 100% | 0% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 123 | 16150529 | 5381 | 129.144 | 5.381 | 3.1 | 3.1 | 2B+1S | 0 | 1042 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32842374 | 1076 | 199.9628 | 0% | 100% | 100% | 0% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 117 | 16155548 | 5019 | 120.456 | 5.019 | 2.8 | 2.8 | 2B+1S | 0 | 999 | 1129 | 0 | 1199 | N/A | N/A | N/A | N/A | 32843382 | 1008 | 200.8368 | 0% | 100% | 100% | 0% | 100% | 0% | 7238601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 101 | 16160091 | 4543 | 109.032 | 4.543 | 3.3 | 3.3 | 2B | 0 | 0 | 1137 | 0 | 1109 | N/A | N/A | N/A | N/A | 32844204 | 822 | 180.9377 | 0% | 0% | 100% | 0% | 100% | 35% | 7239107 | 506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 94 | 16164229 | 4138 | 99.312 | 4.138 | 4.4 | 4.4 | 2B | 0 | 0 | 1033 | 0 | 1109 | N/A | N/A | N/A | N/A | 32844912 | 708 | 171.0971 | 0% | 0% | 100% | 0% | 100% | 35% | 7240043 | 936 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124 | 123515 | 123515 | 123.515 | 123.515 | [12 empty] | 25317 | 25317 | 204.9711 | [6 empty] | 6857 | 6857 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 2) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @3:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / C. DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25650 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16164229 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32844912 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7240043 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 91 | 16168169 | 3940 | 94.56 | 3.94 | 5.7 | 5.7 | 2B | 0 | 0 | 1011 | 0 | 1109 | N/A | N/A | N/A | N/A | 32845574 | 662 | 168.0203 | 0% | 0% | 100% | 0% | 100% | 40% | 7241294 | 1251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 90 | 16171916 | 3747 | 89.928 | 3.747 | 6.9 | 6.9 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 32846162 | 588 | 156.9255 | 0% | 0% | 100% | 0% | 100% | 40% | 7242504 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 | 89 | 16175663 | 3747 | 89.928 | 3.747 | 8.7 | 8.7 | 2B | 0 | 0 | 919 | 0 | 1089 | N/A | N/A | N/A | N/A | 32846750 | 588 | 156.9255 | 0% | 0% | 100% | 0% | 100% | 40% | 7243714 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 89 | 16179411 | 3748 | 89.952 | 3.748 | 9.5 | 9.5 | 2B | 0 | 0 | 865 | 0 | 1089 | N/A | N/A | N/A | N/A | 32847340 | 590 | 157.4173 | 0% | 0% | 100% | 0% | 100% | 40% | 7244925 | 1211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 16183252 | 3841 | 92.184 | 3.841 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 1038 | N/A | N/A | N/A | N/A | 32847864 | 524 | 136.4228 | 0% | 0% | 100% | 0% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 116 | 16187773 | 4521 | 108.504 | 4.521 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1109 | N/A | N/A | N/A | N/A | 32848588 | 724 | 160.1416 | 0% | 0% | 100% | 0% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 16193775 | 6002 | 144.048 | 6.002 | 9.2 | 9.2 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32849922 | 1334 | 222.2592 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 16199863 | 6088 | 146.112 | 6.088 | 8.5 | 8.5 | 3B+1S | 0 | 1067 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32851291 | 1369 | 224.8686 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 16206078 | 6215 | 149.16 | 6.215 | 7.8 | 7.8 | 3B+1S | 0 | 1099 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32852690 | 1399 | 225.1006 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 16212280 | 6202 | 148.848 | 6.202 | 7.1 | 7.1 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32854100 | 1410 | 227.346 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 16218370 | 6090 | 146.16 | 6.09 | 6.5 | 6.5 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32855476 | 1376 | 225.9442 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 16224425 | 6055 | 145.32 | 6.055 | 5.8 | 5.8 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32856858 | 1382 | 228.2411 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 16230363 | 5938 | 142.512 | 5.938 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32858212 | 1354 | 228.0229 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 16236012 | 5649 | 135.576 | 5.649 | 5.3 | 5.3 | 3B+1S | 0 | 1000 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32859516 | 1304 | 230.8373 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 129 | 16241646 | 5634 | 135.216 | 5.634 | 5.2 | 5.2 | 3B+1S | 0 | 1002 | 1164 | 1185 | 1181 | N/A | N/A | N/A | N/A | 32860818 | 1302 | 231.0969 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 131 | 16247073 | 5427 | 130.248 | 5.427 | 5.1 | 5.1 | 3B+1S | 0 | 1013 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32862066 | 1248 | 229.9613 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 16252641 | 5568 | 133.632 | 5.568 | 4.8 | 4.8 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 32863370 | 1304 | 234.1954 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 16258118 | 5477 | 131.448 | 5.477 | 4.6 | 4.6 | 3B+1S | 0 | 997 | 1175 | 1185 | 1181 | N/A | N/A | N/A | N/A | 32864654 | 1284 | 234.4349 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 16263683 | 5565 | 133.56 | 5.565 | 4.5 | 4.5 | 3B+1S | 0 | 988 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32865906 | 1252 | 224.9775 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 123 | 16269031 | 5348 | 128.352 | 5.348 | 4.4 | 4.4 | 3B+1S | 0 | 980 | 1115 | 1185 | 1128 | N/A | N/A | N/A | N/A | 32867110 | 1204 | 225.1309 | 0% | 100% | 100% | 100% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 123 | 16274280 | 5249 | 125.976 | 5.249 | 3.7 | 3.7 | 2B+1S | 0 | 1027 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32868161 | 1051 | 200.2286 | 0% | 100% | 100% | 0% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 131 | 16279255 | 4975 | 119.4 | 4.975 | 3.4 | 3.4 | 2B+1S | 0 | 1006 | 1196 | 0 | 1139 | N/A | N/A | N/A | N/A | 32869158 | 997 | 200.402 | 0% | 100% | 100% | 0% | 100% | 0% | 7244925 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 94 | 16283474 | 4219 | 101.256 | 4.219 | 4.2 | 4.2 | 2B | 0 | 0 | 1076 | 0 | 1109 | N/A | N/A | N/A | N/A | 32869904 | 746 | 176.8192 | 0% | 0% | 100% | 0% | 100% | 35% | 7245522 | 597 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 87 | 16287303 | 3829 | 91.896 | 3.829 | 5.1 | 5.1 | 2B | 0 | 0 | 986 | 0 | 1109 | N/A | N/A | N/A | N/A | 32870562 | 658 | 171.8464 | 0% | 0% | 100% | 0% | 100% | 35% | 7246446 | 924 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.6667 | 123074 | 123074 | 123.074 | 123.074 | [12 empty] | 25650 | 25650 | 208.4112 | [6 empty] | 6403 | 6403 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 3) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25750 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16287303 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32870562 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7246446 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 89 | 16290899 | 3596 | 86.304 | 3.596 | 6.5 | 6.5 | 2B | 0 | 0 | 967 | 0 | 1109 | N/A | N/A | N/A | N/A | 32871186 | 624 | 173.5261 | 0% | 0% | 100% | 0% | 100% | 40% | 7247682 | 1236 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 82 | 16294440 | 3541 | 84.984 | 3.541 | 7.7 | 7.7 | 2B | 0 | 0 | 934 | 0 | 1110 | N/A | N/A | N/A | N/A | 32871758 | 572 | 161.5363 | 0% | 0% | 100% | 0% | 100% | 40% | 7248910 | 1228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 84 | 16297898 | 3458 | 82.992 | 3.458 | 9 | 9 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 32872330 | 572 | 165.4135 | 0% | 0% | 100% | 0% | 100% | 40% | 7250311 | 1401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 89 | 16301615 | 3717 | 89.208 | 3.717 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 0 | 1109 | N/A | N/A | N/A | N/A | 32872890 | 560 | 150.6591 | 0% | 0% | 100% | 0% | 100% | 40% | 7250697 | 386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 96 | 16305333 | 3718 | 89.232 | 3.718 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 0 | 1110 | N/A | N/A | N/A | N/A | 32873450 | 560 | 150.6186 | 0% | 0% | 100% | 0% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 123 | 16310020 | 4687 | 112.488 | 4.687 | 9.5 | 9.5 | 2B | 0 | 0 | 1172 | 0 | 1160 | N/A | N/A | N/A | N/A | 32874200 | 750 | 160.0171 | 0% | 0% | 100% | 0% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 16316121 | 6101 | 146.424 | 6.101 | 9 | 9 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32875562 | 1362 | 223.2421 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 16322259 | 6138 | 147.312 | 6.138 | 8.4 | 8.4 | 3B+1S | 0 | 1097 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32876950 | 1388 | 226.1323 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 16328341 | 6082 | 145.968 | 6.082 | 7.6 | 7.6 | 3B+1S | 0 | 1112 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32878332 | 1382 | 227.2279 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 146 | 16334562 | 6221 | 149.304 | 6.221 | 6.6 | 6.6 | 3B+1S | 0 | 1135 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32879760 | 1428 | 229.5451 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 144 | 16340640 | 6078 | 145.872 | 6.078 | 5.9 | 5.9 | 3B+1S | 0 | 1161 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32881162 | 1402 | 230.668 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 146 | 16346653 | 6013 | 144.312 | 6.013 | 5.1 | 5.1 | 3B+1S | 0 | 1117 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32882556 | 1394 | 231.831 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 144 | 16352434 | 5781 | 138.744 | 5.781 | 4.9 | 4.9 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32883874 | 1318 | 227.9882 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 143 | 16358348 | 5914 | 141.936 | 5.914 | 4.7 | 4.7 | 3B+1S | 0 | 903 | 1176 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32885220 | 1346 | 227.5955 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 132 | 16363788 | 5440 | 130.56 | 5.44 | 4.6 | 4.6 | 3B+1S | 0 | 994 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32886484 | 1264 | 232.3529 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 124 | 16369359 | 5571 | 133.704 | 5.571 | 4.6 | 4.6 | 3B+1S | 0 | 999 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32887758 | 1274 | 228.6843 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 16374907 | 5548 | 133.152 | 5.548 | 4.5 | 4.5 | 3B+1S | 0 | 1014 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32889074 | 1316 | 237.2026 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 128 | 16380369 | 5462 | 131.088 | 5.462 | 4.3 | 4.3 | 3B+1S | 0 | 980 | 1174 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32890328 | 1254 | 229.5862 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 128 | 16385802 | 5433 | 130.392 | 5.433 | 4.2 | 4.2 | 3B+1S | 0 | 983 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 32891580 | 1252 | 230.4436 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 125 | 16391163 | 5361 | 128.664 | 5.361 | 4.1 | 4.1 | 3B+1S | 0 | 884 | 1136 | 1185 | 1139 | N/A | N/A | N/A | N/A | 32892782 | 1202 | 224.2119 | 0% | 100% | 100% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 122 | 16396329 | 5166 | 123.984 | 5.166 | 3.5 | 3.5 | 2B+1S | 0 | 1035 | 0 | 0 | 1151 | N/A | N/A | N/A | N/A | 32893834 | 1052 | 203.6392 | 0% | 100% | 0% | 100% | 100% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 119 | 16401495 | 5166 | 123.984 | 5.166 | 2.7 | 2.7 | 2B+1S | 0 | 1057 | 1126 | 0 | 0 | N/A | N/A | N/A | N/A | 32894838 | 1004 | 194.3477 | 0% | 100% | 100% | 100% | 0% | 0% | 7250697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 100 | 16405838 | 4343 | 104.232 | 4.343 | 3.1 | 3.1 | 2B | 0 | 0 | 1096 | 0 | 1109 | N/A | N/A | N/A | N/A | 32895620 | 782 | 180.0599 | 0% | 0% | 100% | 0% | 100% | 30% | 7251163 | 466 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 91 | 16409884 | 4046 | 97.104 | 4.046 | 4.1 | 4.1 | 2B | 0 | 0 | 1025 | 0 | 1110 | N/A | N/A | N/A | N/A | 32896312 | 692 | 171.0331 | 0% | 0% | 100% | 0% | 100% | 30% | 7252087 | 924 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.0833 | 122581 | 122581 | 122.581 | 122.581 | [12 empty] | 25750 | 25750 | 210.0652 | [6 empty] | 5641 | 5641 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 4) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Engr. Arthuro Trinidad and Maintenance team conducted the Monthly preventive maintenance of all units @ 8:00 pm
BP2 - STOPPED @ 8:01 PM
BP1 - STOPPED @ 8:36 PM
BP2 - STARTED @ 8:36 PM
BP1 - STARTED @ 9:12 PM
BP3 - STOPPED @ 9:12 PM
BP2 - STOPPED @ 10:01 PM
BP3 - STARTED @ 10:01 PM
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26090 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16409884 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32896312 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7252087 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 85 | 16413463 | 3579 | 85.896 | 3.579 | 5.4 | 5.4 | 2B | 0 | 0 | 1004 | 0 | 1073 | N/A | N/A | N/A | N/A | 32896918 | 606 | 169.321 | 0% | 0% | 100% | 0% | 100% | 40% | 7253258 | 1171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 87 | 16417107 | 3644 | 87.456 | 3.644 | 7.5 | 7.5 | 2B | 0 | 0 | 936 | 0 | 1078 | N/A | N/A | N/A | N/A | 32897475 | 557 | 152.854 | 0% | 0% | 100% | 0% | 100% | 40% | 7254537 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 83 | 16420751 | 3644 | 87.456 | 3.644 | 8.9 | 8.9 | 2B | 0 | 0 | 932 | 0 | 1079 | N/A | N/A | N/A | N/A | 32898032 | 557 | 152.854 | 0% | 0% | 100% | 0% | 100% | 40% | 7255816 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 90 | 16424395 | 3644 | 87.456 | 3.644 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 0 | 1079 | N/A | N/A | N/A | N/A | 32898589 | 557 | 152.854 | 0% | 0% | 100% | 0% | 100% | 40% | 7257149 | 1333 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 99 | 16428041 | 3646 | 87.504 | 3.646 | 9.5 | 9.5 | 2B | 0 | 0 | 983 | 0 | 1080 | N/A | N/A | N/A | N/A | 32899146 | 557 | 152.7702 | 0% | 0% | 100% | 0% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 120 | 16432545 | 4504 | 108.096 | 4.504 | 9.5 | 9.5 | 2B | 0 | 0 | 1155 | 0 | 1140 | N/A | N/A | N/A | N/A | 32899854 | 708 | 157.1936 | 0% | 0% | 100% | 0% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 144 | 16438552 | 6007 | 144.168 | 6.007 | 9.1 | 9.1 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32901202 | 1348 | 224.4049 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 133 | 16444839 | 6287 | 150.888 | 6.287 | 8.3 | 8.3 | 3B+1S | 0 | 1118 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32902626 | 1424 | 226.4991 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 150 | 16451061 | 6222 | 149.328 | 6.222 | 7.6 | 7.6 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32904042 | 1416 | 227.5796 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 152 | 16457206 | 6145 | 147.48 | 6.145 | 6.5 | 6.5 | 3B+1S | 0 | 1157 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32905464 | 1422 | 231.4076 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 147 | 16463268 | 6062 | 145.488 | 6.062 | 5.6 | 5.6 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32906879 | 1415 | 233.4213 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 140 | 16469330 | 6062 | 145.488 | 6.062 | 4.8 | 4.8 | 3B+1S | 0 | 1107 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32908294 | 1415 | 233.4213 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 16475184 | 5854 | 140.496 | 5.854 | 4.4 | 4.4 | 3B+1S | 0 | 1033 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32909646 | 1352 | 230.9532 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 134 | 16482021 | 6837 | 164.088 | 6.837 | 4.2 | 4.2 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32911242 | 1596 | 233.4357 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 131 | 16486493 | 4472 | 107.328 | 4.472 | 4.1 | 4.1 | 3B+1S | 0 | 977 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32912286 | 1044 | 233.4526 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 16491949 | 5456 | 130.944 | 5.456 | 4 | 4 | 3B+1S | 0 | 1001 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32913574 | 1288 | 236.0704 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 16497646 | 5697 | 136.728 | 5.697 | 3.7 | 3.7 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32914902 | 1328 | 233.1051 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 16503260 | 5614 | 134.736 | 5.614 | 3.5 | 3.5 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32916208 | 1306 | 232.6327 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 131 | 16508815 | 5555 | 133.32 | 5.555 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 32917516 | 1308 | 235.4635 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 125 | 16514321 | 5506 | 132.144 | 5.506 | 3.2 | 3.2 | 3B+1S | 0 | 990 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 32918790 | 1274 | 231.3839 | 0% | 100% | 100% | 100% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 | 98 | 16519587 | 5266 | 126.384 | 5.266 | 2.6 | 2.6 | 2B+1S | 0 | 1066 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 32919862 | 1072 | 203.5701 | 0% | 100% | 100% | 0% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 108 | 16524633 | 5046 | 121.104 | 5.046 | 2.1 | 2.1 | 2B+1S | 0 | 996 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32920882 | 1020 | 202.1403 | 0% | 100% | 100% | 0% | 100% | 0% | 7257149 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 106 | 16529118 | 4485 | 107.64 | 4.485 | 2.7 | 2.7 | 2B | 0 | 0 | 1135 | 0 | 1130 | N/A | N/A | N/A | N/A | 32921694 | 812 | 181.0479 | 0% | 0% | 100% | 0% | 100% | 35% | 7257762 | 613 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 16533258 | 4140 | 99.36 | 4.14 | 3.8 | 3.8 | 2B | 0 | 0 | 1114 | 0 | 1110 | N/A | N/A | N/A | N/A | 32922402 | 708 | 171.0145 | 0% | 0% | 100% | 0% | 100% | 35% | 7258690 | 928 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.2917 | 123374 | 123374 | 123.374 | 123.374 | [12 empty] | 26090 | 26090 | 211.4708 | [6 empty] | 6603 | 6603 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 5) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Magallanes In-line Booster over current due to low suction pressure. RESTARTED @ 8:14 PM
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26020 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16533258 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32922402 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7258690 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 16537398 | 4140 | 99.36 | 4.14 | 5 | 5 | 2B | 0 | 0 | 1043 | 0 | 1110 | N/A | N/A | N/A | N/A | 32923110 | 708 | 171.0145 | 0% | 0% | 100% | 0% | 100% | 40% | 7259619 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 16541295 | 3897 | 93.528 | 3.897 | 6.9 | 6.9 | 2B | 0 | 0 | 1005 | 0 | 1109 | N/A | N/A | N/A | N/A | 32923765 | 655 | 168.078 | 0% | 0% | 100% | 0% | 100% | 40% | 7260970 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 16545193 | 3898 | 93.552 | 3.898 | 7.7 | 7.7 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 32924420 | 655 | 168.0349 | 0% | 0% | 100% | 0% | 100% | 40% | 7262321 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 90 | 16548929 | 3736 | 89.664 | 3.736 | 8.9 | 8.9 | 2B | 0 | 0 | 972 | 0 | 1109 | N/A | N/A | N/A | N/A | 32925038 | 618 | 165.4176 | 0% | 0% | 100% | 0% | 100% | 40% | 7263580 | 1259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 95 | 16553081 | 4152 | 99.648 | 4.152 | 9.5 | 9.5 | 2B | 0 | 0 | 989 | 0 | 1080 | N/A | N/A | N/A | N/A | 32925666 | 628 | 151.2524 | 0% | 0% | 100% | 0% | 100% | 40% | 7264139 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 115 | 16557493 | 4412 | 105.888 | 4.412 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1109 | 0 | 1198 | N/A | N/A | N/A | N/A | 32926366 | 700 | 158.6582 | 0% | 0% | 100% | 0% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 16563459 | 5966 | 143.184 | 5.966 | 9.1 | 9.1 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32927700 | 1334 | 223.6004 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 16569651 | 6192 | 148.608 | 6.192 | 8.2 | 8.2 | 3B+1S | 0 | 1105 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32929096 | 1396 | 225.4522 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 16575857 | 6206 | 148.944 | 6.206 | 7.7 | 7.7 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32930498 | 1402 | 225.9104 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 16582025 | 6168 | 148.032 | 6.168 | 6.9 | 6.9 | 3B+1S | 0 | 1104 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32931894 | 1396 | 226.3294 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 144 | 16588130 | 6105 | 146.52 | 6.105 | 6.3 | 6.3 | 3B+1S | 0 | 1137 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32933280 | 1386 | 227.027 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 146 | 16594199 | 6069 | 145.656 | 6.069 | 5.4 | 5.4 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32934690 | 1410 | 232.3282 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 16600084 | 5885 | 141.24 | 5.885 | 5.1 | 5.1 | 3B+1S | 0 | 1004 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32936026 | 1336 | 227.0178 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 136 | 16605699 | 5615 | 134.76 | 5.615 | 5 | 5 | 3B+1S | 0 | 994 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32937334 | 1308 | 232.9475 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 131 | 16611310 | 5611 | 134.664 | 5.611 | 5 | 5 | 3B+1S | 0 | 994 | 1186 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32938638 | 1304 | 232.4006 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 16616740 | 5430 | 130.32 | 5.43 | 4.9 | 4.9 | 3B+1S | 0 | 994 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32939902 | 1264 | 232.7808 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 16622358 | 5618 | 134.832 | 5.618 | 4.7 | 4.7 | 3B+1S | 0 | 1012 | 1180 | 1185 | 1190 | N/A | N/A | N/A | N/A | 32941222 | 1320 | 234.9591 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 16627976 | 5618 | 134.832 | 5.618 | 4.4 | 4.4 | 3B+1S | 0 | 1012 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32942524 | 1302 | 231.7551 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 133 | 16633470 | 5494 | 131.856 | 5.494 | 4 | 4 | 3B+1S | 0 | 1005 | 1170 | 1185 | 1173 | N/A | N/A | N/A | N/A | 32943782 | 1258 | 228.9771 | 0% | 100% | 100% | 100% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 129 | 16638790 | 5320 | 127.68 | 5.32 | 3.4 | 3.4 | 2B+1S | 0 | 1081 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 32944864 | 1082 | 203.3835 | 0% | 100% | 100% | 0% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 121 | 16644077 | 5287 | 126.888 | 5.287 | 2.8 | 2.8 | 2B+1S | 0 | 1030 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32945926 | 1062 | 200.8701 | 0% | 100% | 100% | 0% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 113 | 16648934 | 4857 | 116.568 | 4.857 | 2.5 | 2.5 | 2B+1S | 0 | 1012 | 1196 | 0 | 1140 | N/A | N/A | N/A | N/A | 32946898 | 972 | 200.1235 | 0% | 100% | 100% | 0% | 100% | 0% | 7264139 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 105 | 16653344 | 4410 | 105.84 | 4.41 | 3.1 | 3.1 | 2B | 0 | 0 | 1141 | 0 | 1110 | N/A | N/A | N/A | N/A | 32947694 | 796 | 180.4989 | 0% | 0% | 100% | 0% | 100% | 35% | 7264747 | 608 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 97 | 16657599 | 4255 | 102.12 | 4.255 | 4.2 | 4.2 | 2B | 0 | 0 | 1077 | 0 | 1110 | N/A | N/A | N/A | N/A | 32948422 | 728 | 171.0928 | 0% | 0% | 100% | 0% | 100% | 35% | 7265659 | 912 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.3333 | 124341 | 124341 | 124.341 | 124.341 | [12 empty] | 26020 | 26020 | 209.2632 | [6 empty] | 6969 | 6969 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 6) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25856 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16657599 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32948422 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7265659 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 90 | 16661482 | 3883 | 93.192 | 3.883 | 5.8 | 5.8 | 2B | 0 | 0 | 1026 | 0 | 1110 | N/A | N/A | N/A | N/A | 32949063 | 641 | 165.0785 | 0% | 0% | 100% | 0% | 100% | 40% | 7266864 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 89 | 16665365 | 3883 | 93.192 | 3.883 | 6.6 | 6.6 | 2B | 0 | 0 | 984 | 0 | 1109 | N/A | N/A | N/A | N/A | 32949704 | 641 | 165.0785 | 0% | 0% | 100% | 0% | 100% | 40% | 7268069 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 91 | 16669250 | 3885 | 93.24 | 3.885 | 8 | 8 | 2B | 0 | 0 | 954 | 0 | 1110 | N/A | N/A | N/A | N/A | 32950346 | 642 | 165.251 | 0% | 0% | 100% | 0% | 100% | 40% | 7269276 | 1207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 85 | 16673382 | 4132 | 99.168 | 4.132 | 9.5 | 9.5 | 2B | 0 | 0 | 931 | 0 | 1078 | N/A | N/A | N/A | N/A | 32951002 | 656 | 158.7609 | 0% | 0% | 100% | 0% | 100% | 40% | 7270724 | 1448 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 90 | 16676724 | 3342 | 80.208 | 3.342 | 9.5 | 9.5 | 2B | 0 | 0 | 878 | 0 | 1059 | N/A | N/A | N/A | N/A | 32951470 | 468 | 140.0359 | 0% | 0% | 100% | 0% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 109 | 16680846 | 4122 | 98.928 | 4.122 | 9.5 | 9.5 | 2B | 0 | 0 | 1034 | 0 | 1109 | N/A | N/A | N/A | N/A | 32952040 | 570 | 138.2824 | 0% | 0% | 100% | 0% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 144 | 16686533 | 5687 | 136.488 | 5.687 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32953246 | 1206 | 212.0626 | 0% | 0% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 16692721 | 6188 | 148.512 | 6.188 | 9.3 | 9.3 | 3B+1S | 0 | 1077 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32954596 | 1350 | 218.1642 | 0% | 0% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 145 | 16698994 | 6273 | 150.552 | 6.273 | 8.3 | 8.3 | 3B+1S | 0 | 1179 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32956008 | 1412 | 225.0917 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 16705271 | 6277 | 150.648 | 6.277 | 7.4 | 7.4 | 3B+1S | 0 | 1170 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32957440 | 1432 | 228.1345 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 16711543 | 6272 | 150.528 | 6.272 | 6.5 | 6.5 | 3B+1S | 0 | 1106 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32958858 | 1418 | 226.0842 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 148 | 16717795 | 6252 | 150.048 | 6.252 | 5.9 | 5.9 | 3B+1S | 0 | 1156 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32960270 | 1412 | 225.8477 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 145 | 16723886 | 6091 | 146.184 | 6.091 | 5.1 | 5.1 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32961670 | 1400 | 229.8473 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 16729786 | 5900 | 141.6 | 5.9 | 4.6 | 4.6 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32963026 | 1356 | 229.8305 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 142 | 16735578 | 5792 | 139.008 | 5.792 | 4.2 | 4.2 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32964366 | 1340 | 231.3536 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 16741304 | 5726 | 137.424 | 5.726 | 3.8 | 3.8 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32965690 | 1324 | 231.226 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 141 | 16746889 | 5585 | 134.04 | 5.585 | 3.4 | 3.4 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32966990 | 1300 | 232.7663 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 16752583 | 5694 | 136.656 | 5.694 | 3.1 | 3.1 | 3B+1S | 0 | 1021 | 1176 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32968294 | 1304 | 229.013 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 135 | 16758128 | 5545 | 133.08 | 5.545 | 3 | 3 | 3B+1S | 0 | 995 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 32969570 | 1276 | 230.1172 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 132 | 16763500 | 5372 | 128.928 | 5.372 | 2.9 | 2.9 | 3B+1S | 0 | 999 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 32970782 | 1212 | 225.6143 | 0% | 100% | 100% | 100% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 121 | 16768758 | 5258 | 126.192 | 5.258 | 5.2 | 5.2 | 2B+1S | 0 | 1018 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32971848 | 1066 | 202.7387 | 0% | 100% | 100% | 0% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 100 | 106 | 16773515 | 4757 | 114.168 | 4.757 | 2.4 | 2.4 | 2B+1S | 0 | 989 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 32972790 | 942 | 198.024 | 0% | 100% | 100% | 0% | 100% | 0% | 7270724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 105 | 16777950 | 4435 | 106.44 | 4.435 | 3.1 | 3.1 | 2B | 0 | 0 | 1145 | 0 | 1100 | N/A | N/A | N/A | N/A | 32973566 | 776 | 174.9718 | 0% | 0% | 100% | 0% | 100% | 35% | 7271578 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 100 | 16782101 | 4151 | 99.624 | 4.151 | 4.2 | 4.2 | 2B | 0 | 0 | 1063 | 0 | 1100 | N/A | N/A | N/A | N/A | 32974278 | 712 | 171.5249 | 0% | 0% | 100% | 0% | 100% | 35% | 7272432 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.3333 | 124502 | 124502 | 124.502 | 124.502 | [12 empty] | 25856 | 25856 | 207.6754 | [6 empty] | 6773 | 6773 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:09 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6.15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 7) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
MAGALLANES- ONLINE BOOSTER TRIP OVER LOAD, RESET @ 11:11 PM NORMAL OPERATION @ 11:13 PM
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / C. DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24794 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16782101 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32974278 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7272432 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 89 | 16785989 | 3888 | 93.312 | 3.888 | 5.8 | 5.8 | 2B | 0 | 0 | 1033 | 0 | 1110 | N/A | N/A | N/A | N/A | 32974917 | 639 | 164.3519 | 0% | 0% | 100% | 0% | 100% | 40% | 7273537 | 1105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 91 | 16789879 | 3890 | 93.36 | 3.89 | 6.3 | 6.3 | 2B | 0 | 0 | 998 | 0 | 1110 | N/A | N/A | N/A | N/A | 32975560 | 643 | 165.2956 | 0% | 0% | 100% | 0% | 100% | 40% | 7274642 | 1105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 16793783 | 3904 | 93.696 | 3.904 | 7.7 | 7.7 | 2B | 0 | 0 | 975 | 0 | 1109 | N/A | N/A | N/A | N/A | 32976216 | 656 | 168.0328 | 0% | 0% | 100% | 0% | 100% | 40% | 7275748 | 1106 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 88 | 16797552 | 3769 | 90.456 | 3.769 | 9 | 9 | 2B | 0 | 0 | 949 | 0 | 1109 | N/A | N/A | N/A | N/A | 32976822 | 606 | 160.7854 | 0% | 0% | 100% | 0% | 100% | 40% | 7276960 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 85 | 16801126 | 3574 | 85.776 | 3.574 | 9.5 | 9.5 | 2B | 0 | 0 | 910 | 0 | 1049 | N/A | N/A | N/A | N/A | 32977350 | 528 | 147.7336 | 0% | 0% | 100% | 0% | 100% | 40% | 7277488 | 528 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 97 | 98 | 16805093 | 3967 | 95.208 | 3.967 | 9.5 | 9.5 | 2B | 0 | 0 | 944 | 0 | 1008 | N/A | N/A | N/A | N/A | 32977862 | 512 | 129.0648 | 0% | 0% | 100% | 0% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 139 | 16810279 | 5186 | 124.464 | 5.186 | 9.5 | 9.5 | 3B | 0 | 0 | 1029 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32978900 | 1038 | 200.1543 | 0% | 0% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 149 | 16816082 | 5803 | 139.272 | 5.803 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32980126 | 1226 | 211.27 | 0% | 0% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 143 | 16822208 | 6126 | 147.024 | 6.126 | 9.1 | 9.1 | 3B+1S | 0 | 1034 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32981492 | 1366 | 222.984 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 140 | 16828311 | 6103 | 146.472 | 6.103 | 8.6 | 8.6 | 3B+1S | 0 | 1054 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32982858 | 1366 | 223.8243 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 16834465 | 6154 | 147.696 | 6.154 | 8.1 | 8.1 | 3B+1S | 0 | 1059 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32984234 | 1376 | 223.5944 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 16840539 | 6074 | 145.776 | 6.074 | 7.3 | 7.3 | 3B+1S | 0 | 1071 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32985622 | 1388 | 228.515 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 16846446 | 5907 | 141.768 | 5.907 | 6.9 | 6.9 | 3B+1S | 0 | 1043 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32986970 | 1348 | 228.2038 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 134 | 16852211 | 5765 | 138.36 | 5.765 | 6.6 | 6.6 | 3B+1S | 0 | 998 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32988282 | 1312 | 227.5802 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 141 | 16857925 | 5714 | 137.136 | 5.714 | 6.4 | 6.4 | 3B+1S | 0 | 990 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 32989614 | 1332 | 233.1117 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 16863522 | 5597 | 134.328 | 5.597 | 6.4 | 6.4 | 3B+1S | 0 | 983 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 32990926 | 1312 | 234.4113 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 16868999 | 5477 | 131.448 | 5.477 | 6.2 | 6.2 | 3B+1S | 0 | 1013 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 32992218 | 1292 | 235.8956 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 129 | 16874446 | 5447 | 130.728 | 5.447 | 6.1 | 6.1 | 3B+1S | 0 | 983 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 32993478 | 1260 | 231.32 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 134 | 16879969 | 5523 | 132.552 | 5.523 | 5.3 | 5.3 | 2B+1S | 0 | 1123 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 32994610 | 1132 | 204.9611 | 0% | 100% | 100% | 100% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 123 | 128 | 16885279 | 5310 | 127.44 | 5.31 | 4.6 | 4.6 | 2B+1S | 0 | 1034 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32995660 | 1050 | 197.7401 | 0% | 100% | 100% | 0% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 120 | 16890388 | 5109 | 122.616 | 5.109 | 4.3 | 4.3 | 2B+1S | 0 | 985 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 32996670 | 1010 | 197.6904 | 0% | 100% | 100% | 0% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 115 | 16895269 | 4881 | 117.144 | 4.881 | 4.2 | 4.2 | 2B | 0 | 0 | 1144 | 0 | 1140 | N/A | N/A | N/A | N/A | 32997588 | 918 | 188.0762 | 0% | 0% | 100% | 0% | 100% | 0% | 7277488 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 99 | 16899669 | 4400 | 105.6 | 4.4 | 5 | 5 | 2B | 0 | 0 | 1046 | 0 | 1109 | N/A | N/A | N/A | N/A | 32998330 | 742 | 168.6364 | 0% | 0% | 100% | 0% | 100% | 30% | 7278166 | 678 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 97 | 16904070 | 4401 | 105.624 | 4.401 | 5.7 | 5.7 | 2B | 0 | 0 | 1032 | 0 | 1109 | N/A | N/A | N/A | N/A | 32999072 | 742 | 168.598 | 0% | 0% | 100% | 0% | 100% | 30% | 7278810 | 644 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.9167 | 121969 | 121969 | 121.969 | 121.969 | [12 empty] | 24794 | 24794 | 203.2812 | [6 empty] | 6378 | 6378 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:22 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 8) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:38 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / C. DIO
[13 empty] | 10pm - 6am | R. MALLARI / A. CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23270 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16904070 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 32999072 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7278810 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 95 | 16907749 | 3679 | 88.296 | 3.679 | 6.1 | 6.1 | 2B | 0 | 0 | 960 | 0 | 1110 | N/A | N/A | N/A | N/A | 32999666 | 594 | 161.4569 | 0% | 0% | 100% | 0% | 100% | 40% | 7279843 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 16911430 | 3681 | 88.344 | 3.681 | 7.5 | 7.5 | 2B | 0 | 0 | 949 | 0 | 1110 | N/A | N/A | N/A | N/A | 33000257 | 591 | 160.5542 | 0% | 0% | 100% | 0% | 100% | 40% | 7280876 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 89 | 16915114 | 3684 | 88.416 | 3.684 | 8.8 | 8.8 | 2B | 0 | 0 | 940 | 0 | 1109 | N/A | N/A | N/A | N/A | 33000858 | 601 | 163.1379 | 0% | 0% | 100% | 0% | 100% | 40% | 7281909 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | R. MALLARI / A. CABREROS
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 87 | 16918743 | 3629 | 87.096 | 3.629 | 9.5 | 9.5 | 2B | 0 | 0 | 962 | 0 | 1078 | N/A | N/A | N/A | N/A | 33001394 | 536 | 147.6991 | 0% | 0% | 100% | 0% | 100% | 40% | 7282541 | 632 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 91 | 16922658 | 3915 | 93.96 | 3.915 | 9.5 | 9.5 | 2B | 0 | 0 | 902 | 0 | 1010 | N/A | N/A | N/A | N/A | 33001901 | 507 | 129.5019 | 0% | 0% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 24 | 16.9014 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 | 106 | 16926573 | 3915 | 93.96 | 3.915 | 9.5 | 9.5 | 2B | 0 | 0 | 1028 | 0 | 1009 | N/A | N/A | N/A | N/A | 33002408 | 507 | 129.5019 | 0% | 0% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 145 | 16932057 | 5484 | 131.616 | 5.484 | 9.5 | 9.5 | 3B | 0 | 0 | 1160 | 1185 | 1139 | N/A | N/A | N/A | N/A | 33003514 | 1106 | 201.6776 | 0% | 0% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 16938031 | 5974 | 143.376 | 5.974 | 9.5 | 9.5 | 3B | 0 | 0 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33004780 | 1266 | 211.9183 | 0% | 0% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 147 | 16943700 | 5669 | 136.056 | 5.669 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33005998 | 1218 | 214.8527 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 141 | 16949292 | 5592 | 134.208 | 5.592 | 9.2 | 9.2 | 3B+1S | 0 | 1018 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33007314 | 1316 | 235.3362 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 16955601 | 6309 | 151.416 | 6.309 | 8.9 | 8.9 | 3B+1S | 0 | 1023 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33008574 | 1260 | 199.7147 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 139 | 16961446 | 5845 | 140.28 | 5.845 | 8.7 | 8.7 | 3B+1S | 0 | 984 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33009872 | 1298 | 222.0701 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 136 | 16967079 | 5633 | 135.192 | 5.633 | 8.2 | 8.2 | 3B+1S | 0 | 1039 | 1146 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33011102 | 1230 | 218.3561 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 134 | 16973127 | 6048 | 145.152 | 6.048 | 7.7 | 7.7 | 3B+1S | 0 | 1018 | 1146 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33012438 | 1336 | 220.8995 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 130 | 16978200 | 5073 | 121.752 | 5.073 | 7.5 | 7.5 | 3B+1S | 0 | 988 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33013566 | 1128 | 222.3536 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 127 | 16983600 | 5400 | 129.6 | 5.4 | 7.5 | 7.5 | 3B+1S | 0 | 964 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33014774 | 1208 | 223.7037 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 116 | 137 | 16989013 | 5413 | 129.912 | 5.413 | 7.2 | 7.2 | 3B+1S | 0 | 1104 | 1104 | 1185 | 1108 | N/A | N/A | N/A | N/A | 33015970 | 1196 | 220.9496 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 130 | 16994585 | 5572 | 133.728 | 5.572 | 6.7 | 6.7 | 3B+1S | 0 | 1005 | 1126 | 1185 | 1128 | N/A | N/A | N/A | N/A | 33017176 | 1206 | 216.4393 | 0% | 100% | 100% | 100% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 130 | 16999971 | 5386 | 129.264 | 5.386 | 6 | 6 | 2B+1S | 0 | 1082 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33018262 | 1086 | 201.6339 | 0% | 100% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 124 | 17005223 | 5252 | 126.048 | 5.252 | 5.4 | 5.4 | 2B+1S | 0 | 1016 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33019302 | 1040 | 198.0198 | 0% | 100% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 119 | 17010251 | 5028 | 120.672 | 5.028 | 5 | 5 | 2B+1S | 0 | 995 | 1145 | 0 | 1150 | N/A | N/A | N/A | N/A | 33020278 | 976 | 194.113 | 0% | 100% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 109 | 17015000 | 4749 | 113.976 | 4.749 | 4.8 | 4.8 | 2B+1S | 0 | 906 | 1115 | 0 | 1110 | N/A | N/A | N/A | N/A | 33021126 | 848 | 178.5639 | 0% | 100% | 100% | 0% | 100% | 0% | 7282541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 110 | 93 | 17018838 | 3838 | 92.112 | 3.838 | 5.5 | 5.5 | 2B | 0 | 0 | 949 | 0 | 1110 | N/A | N/A | N/A | N/A | 33021734 | 608 | 158.4158 | 0% | 0% | 100% | 0% | 100% | 25% | 7283207 | 666 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 107 | 88 | 17022676 | 3838 | 92.112 | 3.838 | 6.1 | 6.1 | 2B | 0 | 0 | 910 | 0 | 1109 | N/A | N/A | N/A | N/A | 33022342 | 608 | 158.4158 | 0% | 0% | 100% | 0% | 100% | 25% | 7283874 | 667 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.9167 | 118606 | 118606 | 118.606 | 118.606 | [12 empty] | 23270 | 23270 | 196.1958 | [6 empty] | 5064 | 5064 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 9:30 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 9) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / C. DIO
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22980 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17022676 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33022342 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7283874 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 90 | 17026168 | 3492 | 83.808 | 3.492 | 6.9 | 6.9 | 2B | 0 | 0 | 928 | 0 | 1109 | N/A | N/A | N/A | N/A | 33022872 | 530 | 151.7755 | 0% | 0% | 100% | 0% | 100% | 30% | 7284945 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 85 | 17029660 | 3492 | 83.808 | 3.492 | 8.9 | 8.9 | 2B | 0 | 0 | 910 | 0 | 1040 | N/A | N/A | N/A | N/A | 33023401 | 529 | 151.4891 | 0% | 0% | 100% | 0% | 100% | 30% | 7286016 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 111 | 78 | 17033153 | 3493 | 83.832 | 3.493 | 9.5 | 9.5 | 2B | 0 | 0 | 899 | 0 | 1020 | N/A | N/A | N/A | N/A | 33023946 | 545 | 156.0263 | 0% | 0% | 100% | 0% | 100% | 30% | 7287088 | 1072 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 80 | 17036775 | 3622 | 86.928 | 3.622 | 9.5 | 9.5 | 2B | 0 | 0 | 823 | 0 | 978 | N/A | N/A | N/A | N/A | 33024399 | 453 | 125.069 | 0% | 0% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 85 | 17040391 | 3616 | 86.784 | 3.616 | 9.5 | 9.5 | 2B | 0 | 0 | 840 | 0 | 978 | N/A | N/A | N/A | N/A | 33024858 | 459 | 126.9358 | 0% | 0% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 105 | 105 | 17044195 | 3804 | 91.296 | 3.804 | 9.5 | 9.5 | 2B | 0 | 0 | 907 | 0 | 1001 | N/A | N/A | N/A | N/A | 33025316 | 458 | 120.3996 | 0% | 0% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 21 | 14.7887 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 127 | 17049379 | 5184 | 124.416 | 5.184 | 9.5 | 9.5 | 3B | 0 | 0 | 964 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33026384 | 1068 | 206.0185 | 0% | 0% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 137 | 17054975 | 5596 | 134.304 | 5.596 | 9.5 | 9.5 | 3B | 0 | 0 | 1181 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33027546 | 1162 | 207.6483 | 0% | 0% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 143 | 17060770 | 5795 | 139.08 | 5.795 | 9.5 | 9.5 | 3B | 0 | 0 | 1185 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33028780 | 1234 | 212.9422 | 0% | 0% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 17066747 | 5977 | 143.448 | 5.977 | 9.5 | 9 | 3B | 0 | 1049 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33030042 | 1262 | 211.1427 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 17072682 | 5935 | 142.44 | 5.935 | 9 | 8.5 | 3B+1S | 0 | 1025 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33031318 | 1276 | 214.9958 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule
59:00 | 12:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 134 | 17078407 | 5725 | 137.4 | 5.725 | 8.2 | 8.2 | 3B+1S | 0 | 985 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33032570 | 1252 | 218.69 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 117 | 138 | 17084111 | 5704 | 136.896 | 5.704 | 7.4 | 7.4 | 2B+1S | 0 | 1146 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33033690 | 1120 | 196.3534 | 0% | 100% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 113 | 141 | 17089708 | 5597 | 134.328 | 5.597 | 6.6 | 6.6 | 2B+1S | 0 | 1163 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33034810 | 1120 | 200.1072 | 0% | 100% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 113 | 133 | 17095181 | 5473 | 131.352 | 5.473 | 5.6 | 5.6 | 2B+1S | 0 | 1128 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33035916 | 1106 | 202.083 | 0% | 100% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 130 | 17100865 | 5684 | 136.416 | 5.684 | 4.9 | 4.9 | 2B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33037112 | 1196 | 210.4152 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 130 | 17106058 | 5193 | 124.632 | 5.193 | 4.7 | 4.7 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33038330 | 1218 | 234.5465 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 123 | 132 | 17111543 | 5485 | 131.64 | 5.485 | 4.3 | 4.3 | 3B+1S | 0 | 1035 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33039590 | 1260 | 229.7174 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 131 | 17116948 | 5405 | 129.72 | 5.405 | 3.9 | 3.9 | 3B+1S | 0 | 991 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33040842 | 1252 | 231.6374 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 123 | 123 | 17122205 | 5257 | 126.168 | 5.257 | 3.8 | 3.8 | 3B+1S | 0 | 991 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 33042024 | 1182 | 224.8431 | 0% | 100% | 100% | 100% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 121 | 17127217 | 5012 | 120.288 | 5.012 | 3.5 | 3.5 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33043060 | 1036 | 206.7039 | 0% | 100% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 110 | 17132086 | 4869 | 116.856 | 4.869 | 3.4 | 3.4 | 2B+1S | 0 | 990 | 1146 | 0 | 1150 | N/A | N/A | N/A | N/A | 33044022 | 962 | 197.5765 | 0% | 100% | 100% | 0% | 100% | 0% | 7287088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 109 | 96 | 17136191 | 4105 | 98.52 | 4.105 | 3.9 | 3.9 | 2B | 0 | 0 | 1066 | 0 | 1068 | N/A | N/A | N/A | N/A | 33044724 | 702 | 171.011 | 0% | 0% | 100% | 0% | 100% | 25% | 7287631 | 543 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 107 | 89 | 17139923 | 3732 | 89.568 | 3.732 | 4.7 | 4.7 | 2B | 0 | 0 | 1017 | 0 | 1019 | N/A | N/A | N/A | N/A | 33045322 | 598 | 160.2358 | 0% | 0% | 100% | 0% | 100% | 25% | 7288267 | 636 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.7083 | 117247 | 117247 | 117.247 | 117.247 | [12 empty] | 22980 | 22980 | 195.9965 | [6 empty] | 4393 | 4393 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 30% @ 12:01 AM
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:24 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 9:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 10) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 12:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM, NORMAL OPERATION
BP2 - STARTED @ 3:40 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25716 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17139923 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33045322 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7288267 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 104 | 85 | 17143557 | 3634 | 87.216 | 3.634 | 5.9 | 5.9 | 2B | 0 | 0 | 1006 | 0 | 1018 | N/A | N/A | N/A | N/A | 33045863 | 541 | 148.8718 | 0% | 0% | 100% | 0% | 100% | 35% | 7289311 | 1044 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 83 | 17147165 | 3608 | 86.592 | 3.608 | 7.2 | 7.2 | 2B | 0 | 0 | 949 | 0 | 1018 | N/A | N/A | N/A | N/A | 33046391 | 528 | 146.3415 | 0% | 0% | 100% | 0% | 100% | 35% | 7290458 | 1147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 86 | 17150767 | 3602 | 86.448 | 3.602 | 8.5 | 8.5 | 2B | 0 | 0 | 923 | 0 | 998 | N/A | N/A | N/A | N/A | 33046896 | 505 | 140.1999 | 0% | 0% | 100% | 0% | 100% | 35% | 7291713 | 1255 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 85 | 17154314 | 3547 | 85.128 | 3.547 | 9.5 | 9.5 | 2B | 0 | 0 | 865 | 0 | 998 | N/A | N/A | N/A | N/A | 33047389 | 493 | 138.9907 | 0% | 0% | 100% | 0% | 100% | 35% | 7292864 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 109 | 17158129 | 3815 | 91.56 | 3.815 | 9.5 | 9.5 | 2B | 0 | 0 | 1072 | 0 | 1099 | N/A | N/A | N/A | N/A | 33047948 | 559 | 146.5269 | 0% | 0% | 100% | 0% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 116 | 17162240 | 4111 | 98.664 | 4.111 | 9.5 | 9.5 | 2B | 0 | 0 | 1124 | 0 | 1149 | N/A | N/A | N/A | N/A | 33048578 | 630 | 153.2474 | 0% | 0% | 100% | 0% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 17168200 | 5960 | 143.04 | 5.96 | 9.1 | 9.1 | 3B+1S | 0 | 1046 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33049908 | 1330 | 223.1544 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 149 | 17174520 | 6320 | 151.68 | 6.32 | 8.2 | 8.2 | 3B+1S | 0 | 1180 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33051338 | 1430 | 226.2658 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 152 | 17180856 | 6336 | 152.064 | 6.336 | 7.23 | 7.23 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33052794 | 1456 | 229.798 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 145 | 17187162 | 6306 | 151.344 | 6.306 | 6.1 | 9 | 3B+1S | 0 | 1180 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33054226 | 1432 | 227.0853 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 17193410 | 6248 | 149.952 | 6.248 | 5.3 | 8.5 | 3B+1S | 0 | 1140 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33055672 | 1446 | 231.4341 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 144 | 17199627 | 6217 | 149.208 | 6.217 | 4.2 | 4.2 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33057106 | 1434 | 230.6579 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 143 | 17205801 | 6174 | 148.176 | 6.174 | 3.5 | 3.5 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33058520 | 1414 | 229.0249 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 137 | 17211563 | 5762 | 138.288 | 5.762 | 3.5 | 3.5 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33059840 | 1320 | 229.0871 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 139 | 17217287 | 5724 | 137.376 | 5.724 | 3.1 | 3.1 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33061144 | 1304 | 227.8127 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 135 | 17222900 | 5613 | 134.712 | 5.613 | 2.9 | 2.9 | 3B+1S | 0 | 1007 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33062430 | 1286 | 229.111 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 153 | 17228577 | 5677 | 136.248 | 5.677 | 2.7 | 2.7 | 3B+1S | 0 | 1034 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33063730 | 1300 | 228.9942 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 130 | 17234126 | 5549 | 133.176 | 5.549 | 2.4 | 2.4 | 3B+1S | 0 | 998 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33064988 | 1258 | 226.7075 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 124 | 17239575 | 5449 | 130.776 | 5.449 | 2.3 | 2.3 | 3B+1S | 0 | 983 | 1155 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33066226 | 1238 | 227.1977 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 126 | 17244953 | 5378 | 129.072 | 5.378 | 2.2 | 2.2 | 3B+1S | 0 | 950 | 1154 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33067442 | 1216 | 226.1064 | 0% | 100% | 100% | 100% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 17250240 | 5287 | 126.888 | 5.287 | 1.7 | 1.7 | 2B+1S | 0 | 1067 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33068518 | 1076 | 203.5181 | 0% | 100% | 100% | 0% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 117 | 17254951 | 4711 | 113.064 | 4.711 | 1.4 | 1.4 | 2B+1S | 0 | 929 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33069434 | 916 | 194.4385 | 0% | 100% | 100% | 0% | 100% | 0% | 7292864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 101 | 17259663 | 4712 | 113.088 | 4.712 | 1.8 | 1.8 | 2B | 0 | 0 | 1127 | 0 | 1109 | N/A | N/A | N/A | N/A | 33070350 | 916 | 194.3973 | 0% | 0% | 100% | 0% | 100% | 35% | 7293392 | 528 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 92 | 17263632 | 3969 | 95.256 | 3.969 | 3 | 3 | 2B | 0 | 0 | 1042 | 0 | 1109 | N/A | N/A | N/A | N/A | 33071038 | 688 | 173.3434 | 0% | 0% | 100% | 0% | 100% | 35% | 7294425 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5833 | 123709 | 123709 | 123.709 | 123.709 | [12 empty] | 25716 | 25716 | 207.8749 | [6 empty] | 6158 | 6158 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:02 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:18 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 11) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:53 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25558 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17263632 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33071038 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7294425 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 88 | 17267398 | 3766 | 90.384 | 3.766 | 4.5 | 4.5 | 2B | 0 | 0 | 1020 | 0 | 1109 | N/A | N/A | N/A | N/A | 33071690 | 652 | 173.128 | 0% | 0% | 100% | 0% | 100% | 40% | 7295669 | 1244 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 89 | 17271299 | 3901 | 93.624 | 3.901 | 5.9 | 5.9 | 2B | 0 | 0 | 1013 | 0 | 1079 | N/A | N/A | N/A | N/A | 33072320 | 630 | 161.4971 | 0% | 0% | 100% | 0% | 100% | 40% | 7296899 | 1230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 85 | 17275214 | 3915 | 93.96 | 3.915 | 8.3 | 8.3 | 2B | 0 | 0 | 981 | 0 | 1079 | N/A | N/A | N/A | N/A | 33072930 | 610 | 155.811 | 0% | 0% | 100% | 0% | 100% | 40% | 7298139 | 1240 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 84 | 17279145 | 3931 | 94.344 | 3.931 | 9.2 | 9.2 | 2B | 0 | 0 | 944 | 0 | 1080 | N/A | N/A | N/A | N/A | 33073558 | 628 | 159.7558 | 0% | 0% | 100% | 0% | 100% | 40% | 7299361 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 99 | 17283087 | 3942 | 94.608 | 3.942 | 9.5 | 9.5 | 2B | 0 | 0 | 1090 | 0 | 1080 | N/A | N/A | N/A | N/A | 33074192 | 634 | 160.8321 | 0% | 0% | 100% | 0% | 100% | 40% | 7300579 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / C. DIO
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 117 | 17286452 | 3365 | 80.76 | 3.365 | 9.5 | 9.5 | 2B | 0 | 0 | 1142 | 0 | 1170 | N/A | N/A | N/A | N/A | 33074746 | 554 | 164.636 | 0% | 0% | 100% | 0% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 145 | 17292279 | 5827 | 139.848 | 5.827 | 9.2 | 9.2 | 3B+1S | 0 | 1036 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33076044 | 1298 | 222.7561 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 17298427 | 6148 | 147.552 | 6.148 | 8.5 | 8.5 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33077453 | 1409 | 229.1802 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 151 | 17304579 | 6152 | 147.648 | 6.152 | 7.4 | 7.4 | 3B+1S | 0 | 1179 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33078874 | 1421 | 230.9818 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 17310755 | 6176 | 148.224 | 6.176 | 6.3 | 9 | 3B+1S | 0 | 1177 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33080303 | 1429 | 231.3795 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 148 | 17316962 | 6207 | 148.968 | 6.207 | 5.5 | 8.5 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33081752 | 1449 | 233.4461 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | UNITS
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 146 | 17323086 | 6124 | 146.976 | 6.124 | 4.6 | 4.6 | 3B+1S | 0 | 1167 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33083184 | 1432 | 233.8341 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Normal operation schedule | PRESSURE | Atmospheric Pressure
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 17328908 | 5822 | 139.728 | 5.822 | 4 | 4 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33084548 | 1364 | 234.2838 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 17334705 | 5797 | 139.128 | 5.797 | 3.7 | 3.7 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33085886 | 1338 | 230.809 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 17340478 | 5773 | 138.552 | 5.773 | 3.5 | 3.5 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33087198 | 1312 | 227.2649 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 130 | 17346057 | 5579 | 133.896 | 5.579 | 3.4 | 3.4 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33088502 | 1304 | 233.7336 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 17351658 | 5601 | 134.424 | 5.601 | 3.2 | 3.2 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33089832 | 1330 | 237.4576 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 131 | 17357196 | 5538 | 132.912 | 5.538 | 3 | 3 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33091149 | 1317 | 237.8115 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 128 | 17362711 | 5515 | 132.36 | 5.515 | 2.9 | 2.9 | 3B+1S | 0 | 1006 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33092442 | 1293 | 234.4515 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 129 | 17368020 | 5309 | 127.416 | 5.309 | 2.6 | 2.6 | 3B+1S | 0 | 1017 | 1094 | 1185 | 1099 | N/A | N/A | N/A | N/A | 33093586 | 1144 | 215.4831 | 0% | 100% | 100% | 100% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 121 | 17373144 | 5124 | 122.976 | 5.124 | 2.1 | 2.1 | 2B+1S | 0 | 1030 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33094620 | 1034 | 201.7955 | 0% | 100% | 100% | 0% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 121 | 17378216 | 5072 | 121.728 | 5.072 | 2 | 2 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33095636 | 1016 | 200.3155 | 0% | 100% | 100% | 0% | 100% | 0% | 7300579 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Manual Operation | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 105 | 17382549 | 4333 | 103.992 | 4.333 | 2.5 | 2.5 | 2B | 0 | 0 | 1154 | 0 | 1109 | N/A | N/A | N/A | N/A | 33096414 | 778 | 179.5523 | 0% | 0% | 100% | 0% | 100% | 30% | 7301118 | 539 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Manual Operation | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 101 | 17386263 | 3714 | 89.136 | 3.714 | 3.5 | 3.5 | 2B | 0 | 0 | 1089 | 0 | 1110 | N/A | N/A | N/A | N/A | 33096596 | 182 | 49.0038 | 0% | 0% | 100% | 0% | 100% | 30% | 7301892 | 774 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | MLD | 1
[10 empty] | TOTAL |  |  |  | 123.7083 | 122631 | 122631 | 122.631 | 122.631 | [12 empty] | 25558 | 25558 | 208.4139 | [6 empty] | 7467 | 7467 | #DIV/0! |  | m3/hr | 41.67
[44 empty] | Liter/sec | 11.575
NOTABLE REMARKS FOR THE DAY :
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:16 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 12) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
SOURCE EMISSION TEST - START @ 11:01 PM
GENSET 1 WARM-UP START @ 10:55 PM
MERALCO POWER OFF @11:01 PM / GENSET (1) POWER START @ 11:01 PM
BP1 - STOPPED @ 11:01 PM / BP1 - START NORMAL OPERATION @ 11:05 PM
BP3 - STOPPED @ 11:01 PM / BP3 - START NORMAL OPERATION @ 11:05 PM
GENSET 1 - STOPPED @ 11:23 PM ( SWITCH TO ) GENSET 2 - STARTED @ 11:23 PM
GENSET 2 - STOPPED @11:43 PM / MERALCO POWER RESUMED @ 11:45 PM
BP1 - STOPPED @ 11:46 PM / BP1 - START NORMAL OPERATION @ 11:47 PM
BP3 - STOPPED @ 11:46 PM / BP3 - START NORMAL OPERATION @ 11:47 PM
NORMAL OPERATION

## DEC 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | C. DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25998 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17386263 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33096596 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7301892 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 91 | 17390230 | 3967 | 95.208 | 3.967 | 4.7 | 4.7 | 2B | 0 | 0 | 1036 | 0 | 1110 | N/A | N/A | N/A | N/A | 33097284 | 688 | 173.4308 | 0% | 0% | 100% | 0% | 100% | 40% | 7303053 | 1161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 88 | 17394078 | 3848 | 92.352 | 3.848 | 6.2 | 6.2 | 2B | 0 | 0 | 1016 | 0 | 1109 | N/A | N/A | N/A | N/A | 33097940 | 656 | 170.4782 | 0% | 0% | 100% | 0% | 100% | 40% | 7304457 | 1404 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 17397832 | 3754 | 90.096 | 3.754 | 7.8 | 7.8 | 2B | 0 | 0 | 968 | 0 | 1109 | N/A | N/A | N/A | N/A | 33098562 | 622 | 165.6899 | 0% | 0% | 100% | 0% | 100% | 40% | 7305872 | 1415 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 89 | 17401692 | 3860 | 92.64 | 3.86 | 8.9 | 8.9 | 2B | 0 | 0 | 1002 | 0 | 1059 | N/A | N/A | N/A | N/A | 33099164 | 602 | 155.9585 | 0% | 0% | 100% | 0% | 100% | 40% | 7307298 | 1426 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 98 | 17405553 | 3861 | 92.664 | 3.861 | 9.5 | 9.5 | 2B | 0 | 0 | 925 | 0 | 1059 | N/A | N/A | N/A | N/A | 33099766 | 602 | 155.9182 | 0% | 0% | 100% | 0% | 100% | 40% | 7307701 | 403 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 116 | 17410109 | 4556 | 109.344 | 4.556 | 9.5 | 9.5 | 2B | 0 | 0 | 1173 | 0 | 1109 | N/A | N/A | N/A | N/A | 33100478 | 712 | 156.2774 | 0% | 0% | 100% | 0% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 17416109 | 6000 | 144 | 6 | 9.1 | 9.1 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33101814 | 1336 | 222.6667 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 17422220 | 6111 | 146.664 | 6.111 | 8.4 | 8.4 | 3B+1S | 0 | 1114 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33103212 | 1398 | 228.7678 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 17428375 | 6155 | 147.72 | 6.155 | 7.6 | 7.6 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33104602 | 1390 | 225.8327 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 17434560 | 6185 | 148.44 | 6.185 | 6.9 | 9 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33105998 | 1396 | 225.7074 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 17440660 | 6100 | 146.4 | 6.1 | 6.2 | 8.5 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33107393 | 1395 | 228.6885 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 17446671 | 6011 | 144.264 | 6.011 | 5.5 | 5.5 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33108778 | 1385 | 230.4109 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 17452472 | 5801 | 139.224 | 5.801 | 5.1 | 5.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33110116 | 1338 | 230.6499 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 137 | 17458160 | 5688 | 136.512 | 5.688 | 5 | 5 | 3B+1S | 0 | 992 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33111434 | 1318 | 231.7159 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 17463787 | 5627 | 135.048 | 5.627 | 4.9 | 4.9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33112744 | 1310 | 232.8061 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 131 | 17469280 | 5493 | 131.832 | 5.493 | 4.8 | 4.8 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33114052 | 1308 | 238.1212 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 17474955 | 5675 | 136.2 | 5.675 | 4.5 | 4.5 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33115382 | 1330 | 234.3612 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 129 | 17480410 | 5455 | 130.92 | 5.455 | 4.4 | 4.4 | 3B+1S | 0 | 999 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33116640 | 1258 | 230.6141 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 17485793 | 5383 | 129.192 | 5.383 | 4.2 | 4.2 | 3B+1S | 0 | 920 | 1164 | 1185 | 1170 | N/A | N/A | N/A | N/A | 33117882 | 1242 | 230.7264 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 127 | 17491113 | 5320 | 127.68 | 5.32 | 4.1 | 4.1 | 3B+1S | 0 | 974 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 33119074 | 1192 | 224.0602 | 0% | 100% | 100% | 100% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 17496290 | 5177 | 124.248 | 5.177 | 3.6 | 3.6 | 2B+1S | 0 | 1017 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33120134 | 1060 | 204.7518 | 0% | 100% | 100% | 0% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 117 | 17501285 | 4995 | 119.88 | 4.995 | 3.2 | 3.2 | 2B+1S | 0 | 1031 | 1145 | 0 | 1150 | N/A | N/A | N/A | N/A | 33121126 | 992 | 198.5986 | 0% | 100% | 100% | 0% | 100% | 0% | 7307701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 97 | 17505563 | 4278 | 102.672 | 4.278 | 3.7 | 3.7 | 2B | 0 | 0 | 1117 | 0 | 1109 | N/A | N/A | N/A | N/A | 33121882 | 756 | 176.7181 | 0% | 0% | 100% | 0% | 100% | 35% | 7308134 | 433 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 93 | 17509674 | 4111 | 98.664 | 4.111 | 4.7 | 4.7 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 33122594 | 712 | 173.1939 | 0% | 0% | 100% | 0% | 100% | 35% | 7309087 | 953 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.375 | 123411 | 123411 | 123.411 | 123.411 | [12 empty] | 25998 | 25998 | 210.6619 | [6 empty] | 7195 | 7195 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:16 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 13) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:05 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:47 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25420 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17509674 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33122594 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7309087 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 93 | 17513195 | 3521 | 84.504 | 3.521 | 5.7 | 5.7 | 2B | 0 | 0 | 1002 | 0 | 1109 | N/A | N/A | N/A | N/A | 33123193 | 599 | 170.1221 | 0% | 0% | 100% | 0% | 100% | 35% | 7310116 | 1029 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 83 | 17516716 | 3521 | 84.504 | 3.521 | 6.9 | 6.9 | 2B | 0 | 0 | 932 | 0 | 1089 | N/A | N/A | N/A | N/A | 33123792 | 599 | 170.1221 | 0% | 0% | 100% | 0% | 100% | 35% | 7311145 | 1029 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 82 | 17520186 | 3470 | 83.28 | 3.47 | 8.3 | 8.3 | 2B | 0 | 0 | 930 | 0 | 1089 | N/A | N/A | N/A | N/A | 33124301 | 509 | 146.6859 | 0% | 0% | 100% | 0% | 100% | 35% | 7312392 | 1247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 80 | 17523650 | 3464 | 83.136 | 3.464 | 9.5 | 9.5 | 2B | 0 | 0 | 925 | 0 | 1018 | N/A | N/A | N/A | N/A | 33124815 | 514 | 148.3834 | 0% | 0% | 100% | 0% | 100% | 35% | 7313640 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 90 | 17527119 | 3469 | 83.256 | 3.469 | 9.5 | 9.5 | 2B | 0 | 0 | 879 | 0 | 1019 | N/A | N/A | N/A | N/A | 33125330 | 515 | 148.4578 | 0% | 0% | 100% | 0% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 105 | 17531330 | 4211 | 101.064 | 4.211 | 9.5 | 9.5 | 2B | 0 | 0 | 1062 |  | 1018 | N/A | N/A | N/A | N/A | 33125904 | 574 | 136.3097 | 0% | 0% | 100% | 0% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 148 | 17536990 | 5660 | 135.84 | 5.66 | 9.5 | 9.5 | 3B | 0 | 0 | 1185 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33127100 | 1196 | 211.3074 | 0% | 0% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 17542955 | 5965 | 143.16 | 5.965 | 9.2 | 9.2 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33128426 | 1326 | 222.2967 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 17549228 | 6273 | 150.552 | 6.273 | 8.5 | 8.5 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33129830 | 1404 | 223.8164 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 17555563 | 6335 | 152.04 | 6.335 | 7.4 | 9 | 3B+1S | 0 | 1181 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33131266 | 1436 | 226.6772 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 17562029 | 6466 | 155.184 | 6.466 | 6.6 | 8.5 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33132692 | 1426 | 220.5382 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 140 | 17568189 | 6160 | 147.84 | 6.16 | 5.7 | 5.7 | 3B+1S | 0 | 1181 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33134122 | 1430 | 232.1429 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 144 | 17574263 | 6074 | 145.776 | 6.074 | 4.9 | 4.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33135526 | 1404 | 231.1492 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 17580106 | 5843 | 140.232 | 5.843 | 4.4 | 4.4 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33136868 | 1342 | 229.6765 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 17586119 | 6013 | 144.312 | 6.013 | 3.9 | 3.9 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33138242 | 1374 | 228.5049 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 17591735 | 5616 | 134.784 | 5.616 | 3.6 | 3.6 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33139538 | 1296 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 17597489 | 5754 | 138.096 | 5.754 | 3.2 | 3.2 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33140892 | 1354 | 235.3146 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 17603055 | 5566 | 133.584 | 5.566 | 3.1 | 3.1 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33142194 | 1302 | 233.9202 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 17608664 | 5609 | 134.616 | 5.609 | 2.9 | 2.9 | 3B+1S | 0 | 983 | 1163 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33143484 | 1290 | 229.9875 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 129 | 17613930 | 5266 | 126.384 | 5.266 | 2.6 | 2.6 | 3B+1S | 0 | 1017 | 1104 | 1185 | 1108 | N/A | N/A | N/A | N/A | 33144634 | 1150 | 218.3821 | 0% | 100% | 100% | 100% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 17618941 | 5011 | 120.264 | 5.011 | 2.3 | 2.3 | 2B+1S | 0 | 1035 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33145640 | 1006 | 200.7583 | 0% | 100% | 100% | 0% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 118 | 17623952 | 5011 | 120.264 | 5.011 | 2 | 2 | 2B+1S | 0 | 993 | 1195 | 0 | 1140 | N/A | N/A | N/A | N/A | 33146646 | 1006 | 200.7583 | 0% | 100% | 100% | 0% | 100% | 0% | 7313640 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 96 | 17627944 | 3992 | 95.808 | 3.992 | 2.9 | 2.9 | 2B | 0 | 0 | 1145 | 0 | 1110 | N/A | N/A | N/A | N/A | 33147330 | 684 | 171.3427 | 0% | 0% | 100% | 0% | 100% | 35% | 7314783 | 1143 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 90 | 17631930 | 3986 | 95.664 | 3.986 | 4.5 | 4.5 | 2B | 0 | 0 | 1126 | 0 | 1110 | N/A | N/A | N/A | N/A | 33148014 | 684 | 171.6006 | 0% | 0% | 100% | 0% | 100% | 35% | 7315922 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.4167 | 122256 | 122256 | 122.256 | 122.256 | [12 empty] | 25420 | 25420 | 207.9244 | [6 empty] | 6835 | 6835 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 14) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:47 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25010 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17631930 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33148014 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7315922 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 90 | 17635920 | 3990 | 95.76 | 3.99 | 5.1 | 5.1 | 2B | 0 | 0 | 1010 | 0 | 1109 | N/A | N/A | N/A | N/A | 33148704 | 690 | 172.9323 | 0% | 0% | 100% | 0% | 100% | 40% | 7317067 | 1145 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 83 | 17639919 | 3999 | 95.976 | 3.999 | 7.1 | 7.1 | 2B | 0 | 0 | 965 | 0 | 1068 | N/A | N/A | N/A | N/A | 33149382 | 678 | 169.5424 | 0% | 0% | 100% | 0% | 100% | 40% | 7318213 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 81 | 17643059 | 3140 | 75.36 | 3.14 | 8 | 8 | 2B | 0 | 0 | 920 | 0 | 1068 | N/A | N/A | N/A | N/A | 33149874 | 492 | 156.6879 | 0% | 0% | 100% | 0% | 100% | 40% | 7319451 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 83 | 80 | 17646200 | 3141 | 75.384 | 3.141 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 0 | 1009 | N/A | N/A | N/A | N/A | 33150366 | 492 | 156.638 | 0% | 0% | 100% | 0% | 100% | 40% | 7320689 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 90 | 17649752 | 3552 | 85.248 | 3.552 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 1008 | N/A | N/A | N/A | N/A | 33150840 | 474 | 133.4459 | 0% | 0% | 100% | 0% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 97 | 17653726 | 3974 | 95.376 | 3.974 | 9.5 | 9.5 | 2B | 0 | 0 | 959 | 0 | 1110 | N/A | N/A | N/A | N/A | 33151342 | 502 | 126.3211 | 0% | 0% | 100% | 0% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 135 | 17659009 | 5283 | 126.792 | 5.283 | 9.5 | 9.5 | 3B | 0 | 0 | 1125 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33152366 | 1024 | 193.8293 | 0% | 0% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 143 | 17664849 | 5840 | 140.16 | 5.84 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33153598 | 1232 | 210.9589 | 0% | 0% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 17671011 | 6162 | 147.888 | 6.162 | 9 | 9 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33154962 | 1364 | 221.3567 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 146 | 17677297 | 6286 | 150.864 | 6.286 | 8.1 | 9 | 3B+1S | 0 | 1157 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33156386 | 1424 | 226.5352 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 17683572 | 6275 | 150.6 | 6.275 | 7.2 | 8.5 | 3B+1S | 0 | 1150 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33157810 | 1424 | 226.9323 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 148 | 17689788 | 6216 | 149.184 | 6.216 | 6.4 | 6.4 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33159230 | 1420 | 228.4427 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 146 | 17695949 | 6161 | 147.864 | 6.161 | 5.5 | 5.5 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33160644 | 1414 | 229.5082 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 17701831 | 5882 | 141.168 | 5.882 | 5 | 5 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33162010 | 1366 | 232.2339 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 17707572 | 5741 | 137.784 | 5.741 | 4.7 | 4.7 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33163330 | 1320 | 229.9251 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 17713266 | 5694 | 136.656 | 5.694 | 4.5 | 4.5 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33164646 | 1316 | 231.1205 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 131 | 17718914 | 5648 | 135.552 | 5.648 | 4.2 | 4.2 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33165976 | 1330 | 235.4816 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 17724370 | 5456 | 130.944 | 5.456 | 4 | 4 | 3B+1S | 0 | 1007 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33167234 | 1258 | 230.5718 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 17729885 | 5515 | 132.36 | 5.515 | 3.9 | 3.9 | 3B+1S | 0 | 994 | 1146 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33168490 | 1256 | 227.7425 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 124 | 17735099 | 5214 | 125.136 | 5.214 | 3.9 | 3.9 | 3B+1S | 0 | 976 | 1105 | 1185 | 1109 | N/A | N/A | N/A | N/A | 33169620 | 1130 | 216.7242 | 0% | 100% | 100% | 100% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 122 | 17740277 | 5178 | 124.272 | 5.178 | 3.5 | 3.5 | 2B+1S | 0 | 999 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33170658 | 1038 | 200.4635 | 0% | 100% | 100% | 0% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 118 | 17745227 | 4950 | 118.8 | 4.95 | 3.4 | 3.4 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33171650 | 992 | 200.404 | 0% | 100% | 100% | 0% | 100% | 0% | 7320689 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 97 | 17749500 | 4273 | 102.552 | 4.273 | 4 | 4 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 33172374 | 724 | 169.436 | 0% | 0% | 100% | 0% | 100% | 25% | 7321192 | 503 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 104 | 90 | 17753431 | 3931 | 94.344 | 3.931 | 4.8 | 4.8 | 2B | 0 | 0 | 947 | 0 | 1110 | N/A | N/A | N/A | N/A | 33173024 | 650 | 165.3523 | 0% | 0% | 100% | 0% | 100% | 25% | 7321829 | 637 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.7917 | 121501 | 121501 | 121.501 | 121.501 | [12 empty] | 25010 | 25010 | 205.8419 | [6 empty] | 5907 | 5907 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 3:51 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:27 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:39 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:17 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25120 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17753431 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33173024 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7321829 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 90 | 17756962 | 3531 | 84.744 | 3.531 | 6.1 | 6.1 | 2B | 0 | 0 | 974 | 0 | 1048 | N/A | N/A | N/A | N/A | 33173648 | 624 | 176.7205 | 0% | 0% | 100% | 0% | 100% | 35% | 7322993 | 1164 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 86 | 17760454 | 3492 | 83.808 | 3.492 | 7.3 | 7.3 | 2B | 0 | 0 | 956 | 0 | 1008 | N/A | N/A | N/A | N/A | 33174194 | 546 | 156.3574 | 0% | 0% | 100% | 0% | 100% | 35% | 7324230 | 1237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 84 | 17763815 | 3361 | 80.664 | 3.361 | 8.4 | 8.4 | 2B | 0 | 0 | 927 | 0 | 1008 | N/A | N/A | N/A | N/A | 33174694 | 500 | 148.7652 | 0% | 0% | 100% | 0% | 100% | 35% | 7325512 | 1282 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 82 | 17767210 | 3395 | 81.48 | 3.395 | 9.5 | 9.5 | 2B | 0 | 0 | 859 | 0 | 988 | N/A | N/A | N/A | N/A | 33175180 | 486 | 143.1517 | 0% | 0% | 100% | 0% | 100% | 35% | 7326363 | 851 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 17771055 | 3845 | 92.28 | 3.845 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 988 | N/A | N/A | N/A | N/A | 33175674 | 494 | 128.4785 | 0% | 0% | 100% | 0% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 120 | 17775652 | 4597 | 110.328 | 4.597 | 9.5 | 9.5 | 2B | 0 | 0 | 1138 | 0 | 1130 | N/A | N/A | N/A | N/A | 33176394 | 720 | 156.6239 | 0% | 0% | 100% | 0% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 147 | 17781510 | 5858 | 140.592 | 5.858 | 9.3 | 9.3 | 3B+1S | 0 | 992 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33177690 | 1296 | 221.2359 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 17787612 | 6102 | 146.448 | 6.102 | 8.9 | 8.9 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33179044 | 1354 | 221.8945 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 17793745 | 6133 | 147.192 | 6.133 | 8.4 | 8.4 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33180404 | 1360 | 221.7512 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 17799809 | 6064 | 145.536 | 6.064 | 8 | 9 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33181760 | 1356 | 223.6148 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 17805865 | 6056 | 145.344 | 6.056 | 7.6 | 8.5 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33183120 | 1360 | 224.5707 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 17811837 | 5972 | 143.328 | 5.972 | 7.2 | 7.2 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33184464 | 1344 | 225.0502 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 17817743 | 5906 | 141.744 | 5.906 | 6.8 | 6.8 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33185804 | 1340 | 226.8879 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 138 | 17823503 | 5760 | 138.24 | 5.76 | 6.5 | 6.5 | 3B+1S | 0 | 992 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33187128 | 1324 | 229.8611 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 17829060 | 5557 | 133.368 | 5.557 | 6.4 | 6.4 | 3B+1S | 0 | 990 | 1185 | 1185 | 1190 | N/A | N/A | N/A | N/A | 33188426 | 1298 | 233.5793 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 128 | 17834447 | 5387 | 129.288 | 5.387 | 6.3 | 6.3 | 3B+1S | 0 | 988 | 1185 | 1185 | 1190 | N/A | N/A | N/A | N/A | 33189690 | 1264 | 234.6389 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 17840017 | 5570 | 133.68 | 5.57 | 6.1 | 6.1 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33191002 | 1312 | 235.5476 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 133 | 17845548 | 5531 | 132.744 | 5.531 | 5.8 | 5.8 | 3B+1S | 0 | 1000 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33192258 | 1256 | 227.0837 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 134 | 17850975 | 5427 | 130.248 | 5.427 | 5.6 | 5.6 | 3B+1S | 0 | 979 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33193504 | 1246 | 229.5928 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 126 | 17856331 | 5356 | 128.544 | 5.356 | 5.4 | 5.4 | 3B+1S | 0 | 970 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 33194686 | 1182 | 220.6871 | 0% | 100% | 100% | 100% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 17861564 | 5233 | 125.592 | 5.233 | 4.9 | 4.9 | 2B+1S | 0 | 1028 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33195738 | 1052 | 201.0319 | 0% | 100% | 100% | 0% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 110 | 17866252 | 4688 | 112.512 | 4.688 | 4.4 | 4.4 | 2B+1S | 0 | 1018 | 1130 | 0 | 1124 | N/A | N/A | N/A | N/A | 33196622 | 884 | 188.5666 | 0% | 100% | 100% | 0% | 100% | 0% | 7326363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 96 | 17870941 | 4689 | 112.536 | 4.689 | 4.8 | 4.8 | 2B | 0 | 0 | 1067 | 0 | 1110 | N/A | N/A | N/A | N/A | 33197506 | 884 | 188.5263 | 0% | 0% | 100% | 0% | 100% | 30% | 7326756 | 393 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 87 | 17874743 | 3802 | 91.248 | 3.802 | 5.5 | 5.5 | 2B | 0 | 0 | 984 | 0 | 1109 | N/A | N/A | N/A | N/A | 33198144 | 638 | 167.8064 | 0% | 0% | 100% | 0% | 100% | 30% | 7327432 | 676 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.2917 | 121312 | 121312 | 121.312 | 121.312 | [12 empty] | 25120 | 25120 | 207.0694 | [6 empty] | 5603 | 5603 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 15) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
GENSET # 2 EXERCISED WITHOUT LOAD @ 4:01PM TO 4:11 PM FOR 10 MINUTES RUN
GENSET # 1 EXERCISED WITHOUT LOAD @ 4:12 PM TO 4:22PM FOR 10 MINUTES RUN
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25532 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17874743 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33198144 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7327432 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 86 | 17878399 | 3656 | 87.744 | 3.656 | 6.6 | 6.6 | 2B | 0 | 0 | 990 | 0 | 1059 | N/A | N/A | N/A | N/A | 33198754 | 610 | 166.849 | 0% | 0% | 100% | 0% | 100% | 35% | 7328491 | 1059 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 90 | 17881841 | 3442 | 82.608 | 3.442 | 7.9 | 7.9 | 2B | 0 | 0 | 930 | 0 | 1059 | N/A | N/A | N/A | N/A | 33199314 | 560 | 162.6961 | 0% | 0% | 100% | 0% | 100% | 35% | 7329594 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 108 | 88 | 17885315 | 3474 | 83.376 | 3.474 | 8.8 | 8.8 | 2B | 0 | 0 | 910 | 0 | 1058 | N/A | N/A | N/A | N/A | 33199814 | 500 | 143.9263 | 0% | 0% | 100% | 0% | 100% | 35% | 7330751 | 1157 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 86 | 17888786 | 3471 | 83.304 | 3.471 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 1059 | N/A | N/A | N/A | N/A | 33200346 | 532 | 153.27 | 0% | 0% | 100% | 0% | 100% | 35% | 7331309 | 558 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 105 | 17892964 | 4178 | 100.272 | 4.178 | 9.5 | 9.5 | 2B | 0 | 0 | 892 | 0 | 1059 | N/A | N/A | N/A | N/A | 33200946 | 600 | 143.6094 | 0% | 0% | 100% | 0% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 115 | 17897143 | 4179 | 100.296 | 4.179 | 9.5 | 9.5 | 2B | 0 | 0 | 1059 | 0 | 1100 | N/A | N/A | N/A | N/A | 33201546 | 600 | 143.575 | 0% | 0% | 100% | 0% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 148 | 17903154 | 6011 | 144.264 | 6.011 | 9.3 | 9.3 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33202860 | 1314 | 218.5992 | 0% | 0% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 17909307 | 6153 | 147.672 | 6.153 | 8.8 | 8.8 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33204232 | 1372 | 222.9807 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 17915570 | 6263 | 150.312 | 6.263 | 8 | 8 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33205648 | 1416 | 226.0897 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 17921857 | 6287 | 150.888 | 6.287 | 7.2 | 9 | 3B+1S | 0 | 1128 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33207096 | 1448 | 230.3165 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 17927989 | 6132 | 147.168 | 6.132 | 6.5 | 8.5 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33208450 | 1354 | 220.8089 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 17934130 | 6141 | 147.384 | 6.141 | 5.9 | 5.9 | 3B+1S | 0 | 1158 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33209852 | 1402 | 228.3016 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 17940034 | 5904 | 141.696 | 5.904 | 5.3 | 5.3 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33211206 | 1354 | 229.336 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 17945087 | 5053 | 121.272 | 5.053 | 5 | 5 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33212546 | 1340 | 265.189 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 17951329 | 6242 | 149.808 | 6.242 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33213840 | 1294 | 207.3054 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 17956902 | 5573 | 133.752 | 5.573 | 4.6 | 4.6 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33215144 | 1304 | 233.9853 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 17962522 | 5620 | 134.88 | 5.62 | 4.2 | 4.2 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33216468 | 1324 | 235.5872 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 138 | 17968159 | 5637 | 135.288 | 5.637 | 3.8 | 3.8 | 3B+1S | 0 | 1038 | 1164 | 1185 | 1168 | N/A | N/A | N/A | N/A | 33217742 | 1274 | 226.0067 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 137 | 17973966 | 5807 | 139.368 | 5.807 | 3.5 | 3.5 | 3B+1S | 0 | 995 | 1164 | 1185 | 1168 | N/A | N/A | N/A | N/A | 33219062 | 1320 | 227.3119 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 126 | 17979032 | 5066 | 121.584 | 5.066 | 3.2 | 3.2 | 3B+1S | 0 | 1017 | 1105 | 1185 | 1108 | N/A | N/A | N/A | N/A | 33220164 | 1102 | 217.5286 | 0% | 100% | 100% | 100% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 122 | 17984283 | 5251 | 126.024 | 5.251 | 2.6 | 2.6 | 2B+1S | 0 | 1040 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33221230 | 1066 | 203.009 | 0% | 100% | 100% | 0% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 117 | 17989311 | 5028 | 120.672 | 5.028 | 2.2 | 2.2 | 2B+1S | 0 | 1059 | 1146 | 0 | 1150 | N/A | N/A | N/A | N/A | 33222212 | 982 | 195.3063 | 0% | 100% | 100% | 0% | 100% | 0% | 7331309 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 102 | 17993584 | 4273 | 102.552 | 4.273 | 2.7 | 2.7 | 2B | 0 | 0 | 1088 | 0 | 1110 | N/A | N/A | N/A | N/A | 33222966 | 754 | 176.4568 | 0% | 0% | 100% | 0% | 100% | 30% | 7331947 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 96 | 17997454 | 3870 | 92.88 | 3.87 | 3.7 | 3.7 | 2B | 0 | 0 | 1050 | 0 | 1110 | N/A | N/A | N/A | N/A | 33223676 | 710 | 183.4625 | 0% | 0% | 100% | 0% | 100% | 30% | 7332857 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.2083 | 122711 | 122711 | 122.711 | 122.711 | [12 empty] | 25532 | 25532 | 208.0661 | [6 empty] | 5425 | 5425 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:31 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 17) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:42 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17997454 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33223676 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7332857 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 96 | 18001124 | 3670 | 88.08 | 3.67 | 4.9 | 4.9 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 33224264 | 588 | 160.218 | 0% | 0% | 100% | 0% | 100% | 35% | 7334116 | 1259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 92 | 18004804 | 3680 | 88.32 | 3.68 | 6.3 | 6.3 | 2B | 0 | 0 | 934 | 0 | 1109 | N/A | N/A | N/A | N/A | 33224845 | 581 | 157.8804 | 0% | 0% | 100% | 0% | 100% | 35% | 7335377 | 1261 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 18008489 | 3685 | 88.44 | 3.685 | 7.9 | 7.9 | 2B | 0 | 0 | 950 | 0 | 1109 | N/A | N/A | N/A | N/A | 33225424 | 579 | 157.1235 | 0% | 0% | 100% | 0% | 100% | 35% | 7336643 | 1266 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 92 | 18012177 | 3688 | 88.512 | 3.688 | 9.1 | 9.1 | 2B | 0 | 0 | 979 | 0 | 1059 | N/A | N/A | N/A | N/A | 33226030 | 606 | 164.3167 | 0% | 0% | 100% | 0% | 100% | 35% | 7337922 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 96 | 18016404 | 4227 | 101.448 | 4.227 | 9.5 | 9.5 | 2B | 0 | 0 | 1010 | 0 | 1059 | N/A | N/A | N/A | N/A | 33226652 | 622 | 147.1493 | 0% | 0% | 100% | 0% | 100% | 35% | 7338278 | 356 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 115 | 18020632 | 4228 | 101.472 | 4.228 | 9.5 | 9.5 | 2B | 0 | 0 | 1180 | 0 | 1109 | N/A | N/A | N/A | N/A | 33227274 | 622 | 147.1145 | 0% | 0% | 100% | 0% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 149 | 18026302 | 5670 | 136.08 | 5.67 | 9.3 | 9.3 | 3B+1S | 0 | 988 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33228554 | 1280 | 225.7496 | 0% | 0% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 18032395 | 6093 | 146.232 | 6.093 | 8.9 | 8.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33229918 | 1364 | 223.8634 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 144 | 18038631 | 6236 | 149.664 | 6.236 | 8.1 | 8.1 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33231332 | 1414 | 226.7479 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 18044795 | 6164 | 147.936 | 6.164 | 7.4 | 9 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33232730 | 1398 | 226.8008 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 18050980 | 6185 | 148.44 | 6.185 | 6.7 | 8.5 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33234122 | 1392 | 225.0606 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 18057003 | 6023 | 144.552 | 6.023 | 6 | 6 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33235514 | 1392 | 231.1141 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 146 | 18062944 | 5941 | 142.584 | 5.941 | 5.5 | 5.5 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33236870 | 1356 | 228.2444 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 135 | 18068637 | 5693 | 136.632 | 5.693 | 5.3 | 5.3 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33238182 | 1312 | 230.4585 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 134 | 18074291 | 5654 | 135.696 | 5.654 | 5.2 | 5.2 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33239502 | 1320 | 233.463 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 18079776 | 5485 | 131.64 | 5.485 | 5.1 | 5.1 | 3B+1S | 0 | 998 | 1186 | 1185 | 1190 | N/A | N/A | N/A | N/A | 33240792 | 1290 | 235.1869 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 132 | 18085328 | 5552 | 133.248 | 5.552 | 4.6 | 4.6 | 3B+1S | 0 | 1072 | 1175 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33242098 | 1306 | 235.2305 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 138 | 18090906 | 5578 | 133.872 | 5.578 | 4.1 | 4.1 | 3B+1S | 0 | 1030 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 33243374 | 1276 | 228.7558 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 18096487 | 5581 | 133.944 | 5.581 | 3.7 | 3.7 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33244646 | 1272 | 227.9161 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 132 | 18101859 | 5372 | 128.928 | 5.372 | 3.5 | 3.5 | 3B+1S | 0 | 980 | 1125 | 1185 | 1150 | N/A | N/A | N/A | N/A | 33245834 | 1188 | 221.1467 | 0% | 100% | 100% | 100% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 18107108 | 5249 | 125.976 | 5.249 | 3 | 3 | 2B+1S | 0 | 1034 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33246890 | 1056 | 201.1812 | 0% | 100% | 100% | 0% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 120 | 18112106 | 4998 | 119.952 | 4.998 | 2.7 | 2.7 | 2B+1S | 0 | 995 | 1196 | 0 | 1170 | N/A | N/A | N/A | N/A | 33247878 | 988 | 197.6791 | 0% | 100% | 100% | 0% | 100% | 0% | 7338278 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 97 | 18116457 | 4351 | 104.424 | 4.351 | 3.6 | 3.6 | 2B | 0 | 0 | 1067 | 0 | 1110 | N/A | N/A | N/A | N/A | 33248626 | 748 | 171.9145 | 0% | 0% | 100% | 0% | 100% | 35% | 7339157 | 879 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 95 | 18120429 | 3972 | 95.328 | 3.972 | 4.9 | 4.9 | 2B | 0 | 0 | 1039 | 0 | 1110 | N/A | N/A | N/A | N/A | 33249316 | 690 | 173.716 | 0% | 0% | 100% | 0% | 100% | 35% | 7340148 | 991 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.3333 | 122975 | 122975 | 122.975 | 122.975 | [12 empty] | 25640 | 25640 | 208.4977 | [6 empty] | 7291 | 7291 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 18) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:09 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18120429 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33249316 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7340148 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 85 | 18124148 | 3719 | 89.256 | 3.719 | 5.8 | 5.8 | 2B | 0 | 0 | 900 | 0 | 1110 | N/A | N/A | N/A | N/A | 33249906 | 590 | 158.6448 | 0% | 0% | 100% | 0% | 100% | 38% | 7341270 | 1122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 80 | 18127873 | 3725 | 89.4 | 3.725 | 7.1 | 7.1 | 2B | 0 | 0 | 906 | 0 | 1109 | N/A | N/A | N/A | N/A | 33250488 | 582 | 156.2416 | 0% | 0% | 100% | 0% | 100% | 38% | 7342389 | 1119 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 83 | 18131613 | 3740 | 89.76 | 3.74 | 8 | 8 | 2B | 0 | 0 | 907 | 0 | 1110 | N/A | N/A | N/A | N/A | 33251081 | 593 | 158.5561 | 0% | 0% | 100% | 0% | 100% | 38% | 7343514 | 1125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 89 | 18135347 | 3734 | 89.616 | 3.734 | 9.5 | 9.5 | 2B | 0 | 0 | 862 | 0 | 1069 | N/A | N/A | N/A | N/A | 33251678 | 597 | 159.8822 | 0% | 0% | 100% | 0% | 100% | 38% | 7344636 | 1122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 96 | 18139314 | 3967 | 95.208 | 3.967 | 9.5 | 9.5 | 2B | 0 | 0 | 1010 | 0 | 1058 | N/A | N/A | N/A | N/A | 33252243 | 565 | 142.425 | 0% | 0% | 100% | 0% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 115 | 18143281 | 3967 | 95.208 | 3.967 | 9.5 | 9.5 | 2B | 0 | 0 | 1161 | 0 | 1058 | N/A | N/A | N/A | N/A | 33252808 | 565 | 142.425 | 0% | 0% | 100% | 0% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 139 | 18149045 | 5764 | 138.336 | 5.764 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33254054 | 1246 | 216.1693 | 0% | 0% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 18155241 | 6196 | 148.704 | 6.196 | 9.1 | 9.1 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33255443 | 1389 | 224.1769 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 18161438 | 6197 | 148.728 | 6.197 | 8.3 | 8.3 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33256832 | 1389 | 224.1407 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 18167497 | 6059 | 145.416 | 6.059 | 7.4 | 9 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33258212 | 1380 | 227.7604 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 18173562 | 6065 | 145.56 | 6.065 | 6.9 | 8.5 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33259602 | 1390 | 229.1838 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 18179584 | 6022 | 144.528 | 6.022 | 6.4 | 6.4 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33260970 | 1368 | 227.1671 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 146 | 18185584 | 6000 | 144 | 6 | 6.2 | 6.2 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33262324 | 1354 | 225.6667 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 18191260 | 5676 | 136.224 | 5.676 | 6 | 6 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33263658 | 1334 | 235.0247 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 132 | 18196711 | 5451 | 130.824 | 5.451 | 5.9 | 5.9 | 3B+1S | 0 | 979 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33264930 | 1272 | 233.3517 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 132 | 18202273 | 5562 | 133.488 | 5.562 | 5.9 | 5.9 | 3B+1S | 0 | 994 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33266190 | 1260 | 226.5372 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 18208092 | 5819 | 139.656 | 5.819 | 5.7 | 5.7 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33267534 | 1344 | 230.9675 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 130 | 18213530 | 5438 | 130.512 | 5.438 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33268770 | 1236 | 227.2894 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 18218988 | 5458 | 130.992 | 5.458 | 5.2 | 5.2 | 3B+1S | 0 | 955 | 1170 | 1185 | 1174 | N/A | N/A | N/A | N/A | 33270024 | 1254 | 229.7545 | 0% | 100% | 100% | 100% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 18224324 | 5336 | 128.064 | 5.336 | 4.6 | 4.6 | 2B+1S | 0 | 1046 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33271106 | 1082 | 202.7736 | 0% | 100% | 100% | 0% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 18229460 | 5136 | 123.264 | 5.136 | 4 | 4 | 2B+1S | 0 | 1011 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33272138 | 1032 | 200.9346 | 0% | 100% | 100% | 0% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 118 | 18234357 | 4897 | 117.528 | 4.897 | 3.6 | 3.6 | 2B+1S | 0 | 997 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 33273094 | 956 | 195.2216 | 0% | 100% | 100% | 0% | 100% | 0% | 7344636 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 99 | 18238664 | 4307 | 103.368 | 4.307 | 4.4 | 4.4 | 2B | 0 | 0 | 1127 | 0 | 1109 | N/A | N/A | N/A | N/A | 33273850 | 756 | 175.5282 | 0% | 0% | 100% | 0% | 100% | 35% | 7345208 | 572 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 18242637 | 3973 | 95.352 | 3.973 | 5.6 | 5.6 | 2B | 0 | 0 | 1087 | 0 | 1110 | N/A | N/A | N/A | N/A | 33274548 | 698 | 175.6859 | 0% | 0% | 100% | 0% | 100% | 35% | 7345990 | 782 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.125 | 122208 | 122208 | 122.208 | 122.208 | [12 empty] | 25232 | 25232 | 206.4677 | [6 empty] | 5842 | 5842 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 3:49 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 19) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25574 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18242637 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33274548 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7345990 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 18246252 | 3615 | 86.76 | 3.615 | 6.1 | 6.1 | 2B | 0 | 0 | 992 | 0 | 1110 | N/A | N/A | N/A | N/A | 33275097 | 549 | 151.8672 | 0% | 0% | 100% | 0% | 100% | 35% | 7347016 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 18249882 | 3630 | 87.12 | 3.63 | 7.3 | 7.3 | 2B | 0 | 0 | 946 | 0 | 1110 | N/A | N/A | N/A | N/A | 33275653 | 556 | 153.168 | 0% | 0% | 100% | 0% | 100% | 35% | 7348048 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 18253511 | 3629 | 87.096 | 3.629 | 8.6 | 8.6 | 2B | 0 | 0 | 901 | 0 | 1109 | N/A | N/A | N/A | N/A | 33276230 | 577 | 158.997 | 0% | 0% | 100% | 0% | 100% | 35% | 7349088 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 102 | 18257154 | 3643 | 87.432 | 3.643 | 9.5 | 9.5 | 2B | 0 | 0 | 869 | 0 | 1058 | N/A | N/A | N/A | N/A | 33276892 | 662 | 181.7184 | 0% | 0% | 100% | 0% | 100% | 35% | 7350183 | 1095 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 105 | 18261055 | 3901 | 93.624 | 3.901 | 9.5 | 9.5 | 2B | 0 | 0 | 850 | 0 | 1058 | N/A | N/A | N/A | N/A | 33277423 | 531 | 136.1189 | 0% | 0% | 100% | 0% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 113 | 18265155 | 4100 | 98.4 | 4.1 | 9.5 | 9.5 | 2B | 0 | 0 | 1046 | 0 | 1059 | N/A | N/A | N/A | N/A | 33278030 | 607 | 148.0488 | 0% | 0% | 100% | 0% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 145 | 18271005 | 5850 | 140.4 | 5.85 | 9.5 | 9.5 | 3B+1S | 0 | 985 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33279302 | 1272 | 217.4359 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 18277111 | 6106 | 146.544 | 6.106 | 9 | 9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33280666 | 1364 | 223.3868 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 18283276 | 6165 | 147.96 | 6.165 | 8.2 | 8.2 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33282062 | 1396 | 226.4396 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 18289447 | 6171 | 148.104 | 6.171 | 7.4 | 7.4 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33283482 | 1420 | 230.1086 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 18295604 | 6157 | 147.768 | 6.157 | 6.6 | 6.6 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33284894 | 1412 | 229.3325 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 146 | 18301669 | 6065 | 145.56 | 6.065 | 5.9 | 5.9 | 3B+1S | 0 | 1163 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33286278 | 1384 | 228.1946 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 18307686 | 6017 | 144.408 | 6.017 | 5.2 | 5.2 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33287660 | 1382 | 229.6826 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 18313546 | 5860 | 140.64 | 5.86 | 4.8 | 4.8 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33289010 | 1350 | 230.3754 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 18319245 | 5699 | 136.776 | 5.699 | 4.6 | 4.6 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33290324 | 1314 | 230.5668 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 18324960 | 5715 | 137.16 | 5.715 | 4.4 | 4.4 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33291652 | 1328 | 232.371 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 18330519 | 5559 | 133.416 | 5.559 | 4 | 4 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33292968 | 1316 | 236.7332 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 18336148 | 5629 | 135.096 | 5.629 | 3.7 | 3.7 | 3B+1S | 0 | 1005 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33294258 | 1290 | 229.1704 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 18341602 | 5454 | 130.896 | 5.454 | 3.6 | 3.6 | 3B+1S | 0 | 995 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33295514 | 1256 | 230.2897 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 128 | 18346895 | 5293 | 127.032 | 5.293 | 3.5 | 3.5 | 3B+1S | 0 | 935 | 1114 | 1185 | 1119 | N/A | N/A | N/A | N/A | 33296686 | 1172 | 221.4245 | 0% | 100% | 100% | 100% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 120 | 18352066 | 5171 | 124.104 | 5.171 | 3.1 | 3.1 | 2B+1S | 0 | 1016 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33297716 | 1030 | 199.1878 | 0% | 100% | 100% | 0% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 119 | 18357042 | 4976 | 119.424 | 4.976 | 2.8 | 2.8 | 2B+1S | 0 | 1031 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 33298694 | 978 | 196.5434 | 0% | 100% | 100% | 0% | 100% | 0% | 7350183 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 101 | 18361404 | 4362 | 104.688 | 4.362 | 3.5 | 3.5 | 2B | 0 | 0 | 1082 | 0 | 1109 | N/A | N/A | N/A | N/A | 33299450 | 756 | 173.315 | 0% | 0% | 100% | 0% | 100% | 35% | 7350985 | 802 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 88 | 18365300 | 3896 | 93.504 | 3.896 | 4.6 | 4.6 | 2B | 0 | 0 | 1006 | 0 | 1110 | N/A | N/A | N/A | N/A | 33300122 | 672 | 172.4846 | 0% | 0% | 100% | 0% | 100% | 35% | 7351838 | 853 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5 | 122663 | 122663 | 122.663 | 122.663 | [12 empty] | 25574 | 25574 | 208.4899 | [6 empty] | 5848 | 5848 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:28 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 20) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:32 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25362 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18365300 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33300122 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7351838 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 111 | 87 | 18368668 | 3368 | 80.832 | 3.368 | 5.6 | 5.6 | 2B | 0 | 0 | 1038 | 0 | 1110 | N/A | N/A | N/A | N/A | 33300710 | 588 | 174.5843 | 0% | 0% | 100% | 0% | 100% | 35% | 7352772 | 934 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 83 | 18372037 | 3369 | 80.856 | 3.369 | 6.6 | 6.6 | 2B | 0 | 0 | 1003 | 0 | 1018 | N/A | N/A | N/A | N/A | 33301298 | 588 | 174.5325 | 0% | 0% | 100% | 0% | 100% | 35% | 7353706 | 934 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 83 | 18375560 | 3523 | 84.552 | 3.523 | 7.4 | 7.4 | 2B | 0 | 0 | 996 | 0 | 1019 | N/A | N/A | N/A | N/A | 33301823 | 525 | 149.0207 | 0% | 0% | 100% | 0% | 100% | 35% | 7354893 | 1187 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 91 | 18379089 | 3529 | 84.696 | 3.529 | 8.9 | 8.9 | 2B | 0 | 0 | 980 | 0 | 1018 | N/A | N/A | N/A | N/A | 33302350 | 527 | 149.3341 | 0% | 0% | 100% | 0% | 100% | 35% | 7356081 | 1188 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 87 | 18382615 | 3526 | 84.624 | 3.526 | 9.5 | 9.5 | 2B | 0 | 0 | 879 | 0 | 1018 | N/A | N/A | N/A | N/A | 33302878 | 528 | 149.7448 | 0% | 0% | 100% | 0% | 100% | 35% | 7356432 | 351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 107 | 102 | 18386772 | 4157 | 99.768 | 4.157 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 1009 | N/A | N/A | N/A | N/A | 33303430 | 552 | 132.7881 | 0% | 0% | 100% | 0% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 147 | 18392327 | 5555 | 133.32 | 5.555 | 9.5 | 9.5 | 3B | 0 | 0 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33304598 | 1168 | 210.261 | 0% | 0% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 18398277 | 5950 | 142.8 | 5.95 | 9.4 | 9.4 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33305892 | 1294 | 217.479 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 144 | 18404603 | 6326 | 151.824 | 6.326 | 8.6 | 8.6 | 3B+1S | 0 | 1160 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33307314 | 1422 | 224.7866 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 147 | 18410959 | 6356 | 152.544 | 6.356 | 7.6 | 9 | 3B+1S | 0 | 1173 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33308770 | 1456 | 229.0749 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 145 | 18417240 | 6281 | 150.744 | 6.281 | 6.7 | 8.5 | 3B+1S | 0 | 113 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33310202 | 1432 | 227.9892 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 18423506 | 6266 | 150.384 | 6.266 | 5.8 | 5.8 | 3B+1S | 0 | 1148 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33311642 | 1440 | 229.8117 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 18429533 | 6027 | 144.648 | 6.027 | 5.2 | 5.2 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33313016 | 1374 | 227.9741 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 144 | 18435465 | 5932 | 142.368 | 5.932 | 4.8 | 4.8 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33314376 | 1360 | 229.265 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 146 | 18441321 | 5856 | 140.544 | 5.856 | 4.4 | 4.4 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33315710 | 1334 | 227.8005 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 145 | 18447135 | 5814 | 139.536 | 5.814 | 4.1 | 4.1 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33317040 | 1330 | 228.7582 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 141 | 18452942 | 5807 | 139.368 | 5.807 | 3.8 | 3.8 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33318394 | 1354 | 233.1669 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 139 | 18458512 | 5570 | 133.68 | 5.57 | 3.5 | 3.5 | 3B+1S | 0 | 1022 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33319654 | 1260 | 226.2118 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 138 | 18464039 | 5527 | 132.648 | 5.527 | 3.3 | 3.3 | 3B+1S | 0 | 1006 | 1135 | 1185 | 1150 | N/A | N/A | N/A | N/A | 33320918 | 1264 | 228.6955 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 132 | 18469310 | 5271 | 126.504 | 5.271 | 3.1 | 3.1 | 3B+1S | 0 | 997 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 33322090 | 1172 | 222.3487 | 0% | 100% | 100% | 100% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 125 | 18474452 | 5142 | 123.408 | 5.142 | 2.6 | 2.6 | 2B+1S | 0 | 1022 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33323126 | 1036 | 201.478 | 0% | 100% | 100% | 0% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 114 | 18479365 | 4913 | 117.912 | 4.913 | 2.4 | 2.4 | 2B+1S | 0 | 1000 | 1166 | 0 | 1170 | N/A | N/A | N/A | N/A | 33324088 | 962 | 195.807 | 0% | 100% | 100% | 0% | 100% | 0% | 7356432 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 98 | 18483571 | 4206 | 100.944 | 4.206 | 3.3 | 3.3 | 2B | 0 | 0 | 1122 | 0 | 1110 | N/A | N/A | N/A | N/A | 33324830 | 742 | 176.4146 | 0% | 0% | 100% | 0% | 100% | 38% | 7357349 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 92 | 18487373 | 3802 | 91.248 | 3.802 | 4.7 | 4.7 | 2B | 0 | 0 | 1012 | 0 | 1110 | N/A | N/A | N/A | N/A | 33325484 | 654 | 172.0147 | 0% | 0% | 100% | 0% | 100% | 38% | 7358498 | 1149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5417 | 122073 | 122073 | 122.073 | 122.073 | [12 empty] | 25362 | 25362 | 207.7609 | [6 empty] | 6660 | 6660 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:27 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:32 AM, NORMAL OPERATION
SP2 - STARTED @ 7:30AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:17 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 21) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:21 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:17 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / A. CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24562 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18487373 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33325484 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7358498 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 92 | 18490952 | 3579 | 85.896 | 3.579 | 5.9 | 5.9 | 2B | 0 | 0 | 999 | 0 | 1109 | N/A | N/A | N/A | N/A | 33326067 | 583 | 162.8947 | 0% | 0% | 100% | 0% | 100% | 38% | 7359648 | 1150 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 18494538 | 3586 | 86.064 | 3.586 | 7.3 | 7.3 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 33326653 | 586 | 163.4133 | 0% | 0% | 100% | 0% | 100% | 38% | 7360804 | 1156 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 18498127 | 3589 | 86.136 | 3.589 | 8.5 | 8.5 | 2B | 0 | 0 | 975 | 0 | 1110 | N/A | N/A | N/A | N/A | 33327248 | 595 | 165.7843 | 0% | 0% | 100% | 0% | 100% | 38% | 7361958 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 88 | 18501700 | 3573 | 85.752 | 3.573 | 9.4 | 9.4 | 2B | 0 | 0 | 912 | 0 | 1109 | N/A | N/A | N/A | N/A | 33327850 | 602 | 168.4859 | 0% | 0% | 100% | 0% | 100% | 38% | 7363111 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 89 | 18505301 | 3601 | 86.424 | 3.601 | 9.5 | 9.5 | 2B | 0 | 0 | 870 | 0 | 1059 | N/A | N/A | N/A | N/A | 33328358 | 508 | 141.0719 | 0% | 0% | 100% | 0% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 101 | 18509303 | 4002 | 96.048 | 4.002 | 9.5 | 9.5 | 2B | 0 | 0 | 929 | 0 | 1008 | N/A | N/A | N/A | N/A | 33328866 | 508 | 126.9365 | 0% | 0% | 100% | 0% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule | Error - General | E | R. REGENCIA / A. CABREROS
54:00 | 7:00 | 25 | 17.6056 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 138 | 18514654 | 5351 | 128.424 | 5.351 | 9.5 | 9.5 | 3B | 0 | 0 | 957 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33329868 | 1002 | 187.2547 | 0% | 0% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 149 | 18520495 | 5841 | 140.184 | 5.841 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33331086 | 1218 | 208.5259 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 18526686 | 6191 | 148.584 | 6.191 | 9.2 | 9.2 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33332452 | 1366 | 220.6429 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 18532886 | 6200 | 148.8 | 6.2 | 8.4 | 9 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33333850 | 1398 | 225.4839 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 18539163 | 6277 | 150.648 | 6.277 | 7.7 | 8.5 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33335258 | 1408 | 224.311 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 151 | 18545373 | 6210 | 149.04 | 6.21 | 7.1 | 7.1 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33336650 | 1392 | 224.1546 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 18551331 | 5958 | 142.992 | 5.958 | 6.8 | 6.8 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33337994 | 1344 | 225.5791 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 144 | 18557124 | 5793 | 139.032 | 5.793 | 6.5 | 6.5 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33339326 | 1332 | 229.9327 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 146 | 18562913 | 5789 | 138.936 | 5.789 | 6.3 | 6.3 | 3B+1S | 0 | 997 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33340652 | 1326 | 229.0551 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 145 | 18568616 | 5703 | 136.872 | 5.703 | 6.2 | 6.2 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33341996 | 1344 | 235.6654 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 18574300 | 5684 | 136.416 | 5.684 | 5.9 | 5.9 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33343300 | 1304 | 229.4159 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 18579842 | 5542 | 133.008 | 5.542 | 5.8 | 5.8 | 3B+1S | 0 | 999 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33344558 | 1258 | 226.9939 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 122 | 133 | 18585279 | 5437 | 130.488 | 5.437 | 5.5 | 5.5 | 3B+1S | 0 | 1022 | 1104 | 1185 | 1140 | N/A | N/A | N/A | N/A | 33345784 | 1226 | 225.492 | 0% | 100% | 100% | 100% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 18590567 | 5288 | 126.912 | 5.288 | 4.9 | 4.9 | 2B+1S | 0 | 1025 | 1197 | 0 | 1198 | N/A | N/A | N/A | N/A | 33346850 | 1066 | 201.5885 | 0% | 100% | 100% | 0% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 120 | 18595656 | 5089 | 122.136 | 5.089 | 4.5 | 4.5 | 2B+1S | 0 | 988 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33347854 | 1004 | 197.2883 | 0% | 100% | 100% | 0% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 114 | 18600583 | 4927 | 118.248 | 4.927 | 4.3 | 4.3 | 2B+1S | 0 | 972 | 1166 | 0 | 1170 | N/A | N/A | N/A | N/A | 33348802 | 948 | 192.4092 | 0% | 100% | 100% | 0% | 100% | 0% | 7363111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 99 | 18604807 | 4224 | 101.376 | 4.224 | 5.2 | 5.2 | 2B | 0 | 0 | 1101 | 0 | 1059 | N/A | N/A | N/A | N/A | 33349458 | 656 | 155.303 | 0% | 0% | 100% | 0% | 100% | 30% | 7364091 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 95 | 18608505 | 3698 | 88.752 | 3.698 | 5.9 | 5.9 | 2B | 0 | 0 | 1095 | 0 | 1059 | N/A | N/A | N/A | N/A | 33350046 | 588 | 159.0049 | 0% | 0% | 100% | 0% | 100% | 30% | 7364897 | 806 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.0833 | 121132 | 121132 | 121.132 | 121.132 | [12 empty] | 24562 | 24562 | 202.7705 | [6 empty] | 6399 | 6399 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 4:03 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:16 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:12 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 22) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:12 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | CHRISTIAN DIO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25728 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18608505 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33350046 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7364897 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 93 | 18612205 | 3700 | 88.8 | 3.7 | 6.5 | 6.5 | 2B | 0 | 0 | 1109 | 0 | 1059 | N/A | N/A | N/A | N/A | 33350604 | 558 | 150.8108 | 0% | 0% | 100% | 0% | 100% | 30% | 7365702 | 805 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 89 | 18615906 | 3701 | 88.824 | 3.701 | 7.4 | 7.4 | 2B | 0 | 0 | 1099 | 0 | 1058 | N/A | N/A | N/A | N/A | 33351200 | 596 | 161.0376 | 0% | 0% | 100% | 0% | 100% | 30% | 7366503 | 801 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 85 | 18619616 | 3710 | 89.04 | 3.71 | 8.3 | 8.3 | 2B | 0 | 0 | 940 | 0 | 1059 | N/A | N/A | N/A | N/A | 33351797 | 597 | 160.9164 | 0% | 0% | 100% | 0% | 100% | 35% | 7367312 | 809 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 88 | 18623322 | 3706 | 88.944 | 3.706 | 9.3 | 9.3 | 2B | 0 | 0 | 939 | 0 | 1059 | N/A | N/A | N/A | N/A | 33352400 | 603 | 162.7091 | 0% | 0% | 100% | 0% | 100% | 35% | 7368199 | 887 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 88 | 18626953 | 3631 | 87.144 | 3.631 | 9.5 | 9.5 | 2B | 0 | 0 | 854 | 0 | 1059 | N/A | N/A | N/A | N/A | 33352904 | 504 | 138.8047 | 0% | 0% | 100% | 0% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 | 104 | 18631073 | 4120 | 98.88 | 4.12 | 9.5 | 9.5 | 2B | 0 | 0 | 1004 | 0 | 1059 | N/A | N/A | N/A | N/A | 33353468 | 564 | 136.8932 | 0% | 0% | 100% | 0% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 150 | 18636736 | 5663 | 135.912 | 5.663 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33354654 | 1186 | 209.4296 | 0% | 0% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 148 | 18642774 | 6038 | 144.912 | 6.038 | 9.3 | 9.3 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33355952 | 1298 | 214.9718 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 18649056 | 6282 | 150.768 | 6.282 | 8.9 | 8.9 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33357348 | 1396 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 18655329 | 6273 | 150.552 | 6.273 | 8.1 | 9 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33358766 | 1418 | 226.0481 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 18661635 | 6306 | 151.344 | 6.306 | 7.2 | 8.5 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33360190 | 1424 | 225.8167 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 18667993 | 6358 | 152.592 | 6.358 | 6.3 | 6.3 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33361624 | 1434 | 225.5426 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 18674176 | 6183 | 148.392 | 6.183 | 5.5 | 5.5 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33363036 | 1412 | 228.3681 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 146 | 18680191 | 6015 | 144.36 | 6.015 | 4.9 | 4.9 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33364410 | 1374 | 228.4289 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 18686169 | 5978 | 143.472 | 5.978 | 4.4 | 4.4 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33365772 | 1362 | 227.8354 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 18692002 | 5833 | 139.992 | 5.833 | 4.1 | 4.1 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33367110 | 1338 | 229.3845 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 18697835 | 5833 | 139.992 | 5.833 | 3.5 | 3.5 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33368470 | 1360 | 233.1562 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 139 | 18703543 | 5708 | 136.992 | 5.708 | 3.2 | 3.2 | 3B+1S | 0 | 1046 | 1171 | 1185 | 1174 | N/A | N/A | N/A | N/A | 33369758 | 1288 | 225.6482 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 18709586 | 6043 | 145.032 | 6.043 | 2.8 | 2.8 | 3B+1S | 0 | 1036 | 1171 | 1185 | 1174 | N/A | N/A | N/A | N/A | 33371134 | 1376 | 227.7015 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 | 132 | 18714621 | 5035 | 120.84 | 5.035 | 2.8 | 2.8 | 3B+1S | 0 | 930 | 1154 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33372280 | 1146 | 227.6068 | 0% | 100% | 100% | 100% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 124 | 18719949 | 5328 | 127.872 | 5.328 | 2.3 | 2.3 | 2B+1S | 0 | 1049 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33373348 | 1068 | 200.4505 | 0% | 100% | 100% | 0% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 120 | 18725009 | 5060 | 121.44 | 5.06 | 1.9 | 1.9 | 2B+1S | 0 | 995 | 1177 | 0 | 1181 | N/A | N/A | N/A | N/A | 33374338 | 990 | 195.6522 | 0% | 100% | 100% | 0% | 100% | 0% | 7368199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 100 | 18729419 | 4410 | 105.84 | 4.41 | 2.4 | 2.4 | 2B | 0 | 0 | 1127 | 0 | 1109 | N/A | N/A | N/A | N/A | 33375012 | 674 | 152.8345 | 0% | 0% | 100% | 0% | 100% | 30% | 7368909 | 710 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 96 | 18733517 | 4098 | 98.352 | 4.098 | 3.1 | 3.1 | 2B | 0 | 0 | 1041 | 0 | 1109 | N/A | N/A | N/A | N/A | 33375774 | 762 | 185.9444 | 0% | 0% | 100% | 0% | 100% | 30% | 7369454 | 545 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.375 | 125012 | 125012 | 125.012 | 125.012 | [12 empty] | 25728 | 25728 | 205.8042 | [6 empty] | 4557 | 4557 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 3:01 AM
XCV1 CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
SP2 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:32 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 23) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:18 AM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25991 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18733517 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33375774 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7369454 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 90 | 18737460 | 3943 | 94.632 | 3.943 | 4.5 | 4.5 | 2B | 0 | 0 | 1031 | 0 | 1110 | N/A | N/A | N/A | N/A | 33376448 | 674 | 170.9358 | 0% | 0% | 100% | 0% | 100% | 40% | 7370935 | 1481 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 88 | 18741209 | 3749 | 89.976 | 3.749 | 6 | 6 | 2B | 0 | 0 | 973 | 0 | 1110 | N/A | N/A | N/A | N/A | 33377078 | 630 | 168.0448 | 0% | 0% | 100% | 0% | 100% | 40% | 7372416 | 1481 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 86 | 18744884 | 3675 | 88.2 | 3.675 | 7.3 | 7.3 | 2B | 0 | 0 | 939 | 0 | 1110 | N/A | N/A | N/A | N/A | 33377674 | 596 | 162.1769 | 0% | 0% | 100% | 0% | 100% | 40% | 7373897 | 1481 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 85 | 18748811 | 3927 | 94.248 | 3.927 | 8.8 | 8.8 | 2B | 0 | 0 | 934 | 0 | 1110 | N/A | N/A | N/A | N/A | 33378310 | 636 | 161.9557 | 0% | 0% | 100% | 0% | 100% | 40% | 7375381 | 1484 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 97 | 18752920 | 4109 | 98.616 | 4.109 | 9.5 | 9.5 | 2B | 0 | 0 | 912 | 0 | 1110 | N/A | N/A | N/A | N/A | 33378922 | 612 | 148.9413 | 0% | 0% | 100% | 0% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 108 | 18756632 | 3712 | 89.088 | 3.712 | 9.5 | 9.5 | 2B | 0 | 0 | 1041 | 0 | 1110 | N/A | N/A | N/A | N/A | 33379442 | 520 | 140.0862 | 0% | 0% | 100% | 0% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 146 | 18762350 | 5718 | 137.232 | 5.718 | 9.4 | 9.4 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33380652 | 1210 | 211.6125 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 18768451 | 6101 | 146.424 | 6.101 | 8.9 | 8.9 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33382014 | 1362 | 223.2421 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 18774670 | 6219 | 149.256 | 6.219 | 8.4 | 8.4 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33383386 | 1372 | 220.6142 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 18781002 | 6332 | 151.968 | 6.332 | 7.6 | 9 | 3B+1S | 0 | 1115 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33384806 | 1420 | 224.2577 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 18787265 | 6263 | 150.312 | 6.263 | 7 | 8.5 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33386202 | 1396 | 222.8964 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 18793516 | 6251 | 150.024 | 6.251 | 6 | 6 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33387632 | 1430 | 228.7634 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 144 | 18799539 | 6023 | 144.552 | 6.023 | 5.5 | 5.5 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33389002 | 1370 | 227.4614 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 18805347 | 5808 | 139.392 | 5.808 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33390326 | 1324 | 227.9614 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 18811155 | 5808 | 139.392 | 5.808 | 4.8 | 4.8 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33391650 | 1324 | 227.9614 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 18817040 | 5885 | 141.24 | 5.885 | 4.5 | 4.5 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33392996 | 1346 | 228.7171 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 18822877 | 5837 | 140.088 | 5.837 | 3.8 | 3.8 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33394356 | 1360 | 232.9964 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 136 | 18828677 | 5800 | 139.2 | 5.8 | 3.5 | 3.5 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33395690 | 1334 | 230 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 18834239 | 5562 | 133.488 | 5.562 | 3.2 | 3.2 | 3B+1S | 0 | 1012 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33396966 | 1276 | 229.4139 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 127 | 18839739 | 5500 | 132 | 5.5 | 3.1 | 3.1 | 3B+1S | 0 | 981 | 1135 | 1185 | 1140 | N/A | N/A | N/A | N/A | 33398186 | 1220 | 221.8182 | 0% | 100% | 100% | 100% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 124 | 18845073 | 5334 | 128.016 | 5.334 | 2.5 | 2.5 | 2B+1S | 0 | 1049 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33399246 | 1060 | 198.7252 | 0% | 100% | 100% | 0% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 126 | 18850163 | 5090 | 122.16 | 5.09 | 2.2 | 2.2 | 2B+1S | 0 | 1006 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33400250 | 1004 | 197.2495 | 0% | 100% | 100% | 0% | 100% | 0% | 7375381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 98 | 18854214 | 4051 | 97.224 | 4.051 | 3.9 | 3.9 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 33401055 | 805 | 198.7164 | 0% | 0% | 100% | 0% | 100% | 38% | 7376291 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 96 | 18858194 | 3980 | 95.52 | 3.98 | 5.2 | 5.2 | 2B | 0 | 0 | 1085 | 0 | 1110 | N/A | N/A | N/A | N/A | 33401765 | 710 | 178.392 | 0% | 0% | 100% | 0% | 100% | 38% | 7377306 | 1015 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.25 | 124677 | 124677 | 124.677 | 124.677 | [12 empty] | 25991 | 25991 | 208.4667 | [6 empty] | 7852 | 7852 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:32 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:16 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:19 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 24) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:12 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION | [10 empty] | CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM, NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23437 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18858194 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33401765 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7377306 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 89 | 18861974 | 3780 | 90.72 | 3.78 | 6.3 | 6.3 | 2B | 0 | 0 | 1010 | 0 | 1109 | N/A | N/A | N/A | N/A | 33402354 | 589 | 155.8201 | 0% | 0% | 100% | 0% | 100% | 38% | 7378544 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 87 | 18865759 | 3785 | 90.84 | 3.785 | 7.2 | 7.2 | 2B | 0 | 0 | 998 | 0 | 1110 | N/A | N/A | N/A | N/A | 33402949 | 595 | 157.1995 | 0% | 0% | 100% | 0% | 100% | 38% | 7379793 | 1249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 85 | 18869566 | 3807 | 91.368 | 3.807 | 8.2 | 8.2 | 2B | 0 | 0 | 906 | 0 | 1109 | N/A | N/A | N/A | N/A | 33403542 | 593 | 155.7657 | 0% | 0% | 100% | 0% | 100% | 38% | 7381053 | 1260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 86 | 18873190 | 3624 | 86.976 | 3.624 | 9.5 | 9.5 | 2B | 0 | 0 | 906 | 0 | 1008 | N/A | N/A | N/A | N/A | 33404118 | 576 | 158.9404 | 0% | 0% | 100% | 0% | 100% | 38% | 7382295 | 1242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 88 | 18876840 | 3650 | 87.6 | 3.65 | 9.5 | 9.5 | 2B | 0 | 0 | 833 | 0 | 1008 | N/A | N/A | N/A | N/A | 33404602 | 484 | 132.6027 | 0% | 0% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 30 | 21.1268 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 100 | 95 | 18880662 | 3822 | 91.728 | 3.822 | 9.5 | 9.5 | 2B | 0 | 0 | 933 | 0 | 957 | N/A | N/A | N/A | N/A | 33405046 | 444 | 116.1695 | 0% | 0% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 24 | 16.9014 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 135 | 18886041 | 5379 | 129.096 | 5.379 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33405966 | 920 | 171.0355 | 0% | 0% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 143 | 18891599 | 5558 | 133.392 | 5.558 | 9.5 | 9.5 | 3B | 0 | 0 | 1101 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33407080 | 1114 | 200.4318 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 144 | 18897469 | 5870 | 140.88 | 5.87 | 9.5 | 9.5 | 3B | 0 | 0 | 1180 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33408302 | 1222 | 208.1772 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 146 | 18903358 | 5889 | 141.336 | 5.889 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33409560 | 1258 | 213.6186 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 18909691 | 6333 | 151.992 | 6.333 | 9 | 9 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33410956 | 1396 | 220.4327 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule
59:00 | 12:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 18915564 | 5873 | 140.952 | 5.873 | 8.8 | 8.8 | 3B+1S | 0 | 1021 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33412240 | 1284 | 218.6276 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 18921507 | 5943 | 142.632 | 5.943 | 8.3 | 8.3 | 3B+1S | 0 | 1036 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33413522 | 1282 | 215.716 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 142 | 18927264 | 5757 | 138.168 | 5.757 | 7.8 | 7.8 | 3B+1S | 0 | 1020 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33414760 | 1238 | 215.0426 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 18933051 | 5787 | 138.888 | 5.787 | 7.5 | 7.5 | 3B+1S | 0 | 995 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33416018 | 1258 | 217.3838 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 18938872 | 5821 | 139.704 | 5.821 | 7.2 | 7.2 | 3B+1S | 0 | 1009 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 33417270 | 1252 | 215.0833 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 18944680 | 5808 | 139.392 | 5.808 | 6.7 | 6.7 | 3B+1S | 0 | 1035 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33418546 | 1276 | 219.697 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 131 | 18950270 | 5590 | 134.16 | 5.59 | 6.4 | 6.4 | 3B+1S | 0 | 999 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 33419742 | 1196 | 213.9535 | 0% | 100% | 100% | 100% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 115 | 132 | 18955785 | 5515 | 132.36 | 5.515 | 5.6 | 5.6 | 2B+1S | 0 | 1105 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33420846 | 1104 | 200.1813 | 0% | 100% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 120 | 128 | 18961320 | 5535 | 132.84 | 5.535 | 5.1 | 5.1 | 2B+1S | 0 | 1016 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33421922 | 1076 | 194.3993 | 0% | 100% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 122 | 18966395 | 5075 | 121.8 | 5.075 | 4.7 | 4.7 | 2B+1S | 0 | 1001 | 1176 | 0 | 1181 | N/A | N/A | N/A | N/A | 33422900 | 978 | 192.7094 | 0% | 100% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 19 | 13.3803 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 118 | 18971360 | 4965 | 119.16 | 4.965 | 3.9 | 3.9 | 2B+1S | 0 | 1021 | 1126 | 0 | 1129 | N/A | N/A | N/A | N/A | 33423802 | 902 | 181.6717 | 0% | 100% | 100% | 0% | 100% | 0% | 7382295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 109 | 18975296 | 3936 | 94.464 | 3.936 | 4.2 | 4.2 | 2B | 0 | 0 | 1100 | 0 | 1110 | N/A | N/A | N/A | N/A | 33424522 | 720 | 182.9268 | 0% | 0% | 100% | 0% | 100% | 35% | 7382933 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 101 | 18979223 | 3927 | 94.248 | 3.927 | 5.8 | 5.8 | 2B | 0 | 0 | 1053 | 0 | 1109 | N/A | N/A | N/A | N/A | 33425202 | 680 | 173.1602 | 0% | 0% | 100% | 0% | 100% | 35% | 7383848 | 915 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.7917 | 121029 | 121029 | 121.029 | 121.029 | [12 empty] | 23437 | 23437 | 193.6478 | [6 empty] | 6542 | 6542 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:24 AM, NORMAL OPERATION
BP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:31 AM, NORMAL OPERATION
SP2 - STARTED @ 10:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:25 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 25) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:25 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | CHRISTIAN DIO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 21822 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
H |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18979223 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33425202 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7383848 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 18983171 | 3948 | 94.752 | 3.948 | 6.8 | 6.8 | 2B | 0 | 0 | 1015 | 0 | 1110 | N/A | N/A | N/A | N/A | 33425791 | 589 | 149.1895 | 0% | 0% | 100% | 0% | 100% | 35% | 7384988 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 91 | 18987107 | 3936 | 94.464 | 3.936 | 7.7 | 7.7 | 2B | 0 | 0 | 971 | 0 | 1109 | N/A | N/A | N/A | N/A | 33426362 | 571 | 145.0711 | 0% | 0% | 100% | 0% | 100% | 35% | 7386134 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 90 | 18991040 | 3933 | 94.392 | 3.933 | 8.8 | 8.8 | 2B | 0 | 0 | 950 | 0 | 1059 | N/A | N/A | N/A | N/A | 33426942 | 580 | 147.4701 | 0% | 0% | 100% | 0% | 100% | 35% | 7387284 | 1150 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 82 | 18994726 | 3686 | 88.464 | 3.686 | 9.5 | 9.5 | 2B | 0 | 0 | 905 | 0 | 1059 | N/A | N/A | N/A | N/A | 33427439 | 497 | 134.8345 | 0% | 0% | 100% | 0% | 100% | 35% | 7387601 | 317 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 34 | 23.9437 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 86 | 84 | 18998413 | 3687 | 88.488 | 3.687 | 9.5 | 9.5 | 2B | 0 | 0 | 790 | 0 | 908 | N/A | N/A | N/A | N/A | 33427936 | 497 | 134.7979 | 0% | 0% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 31 | 21.831 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 95 | 94 | 19002079 | 3666 | 87.984 | 3.666 | 9.5 | 9.5 | 2B | 0 | 0 | 941 | 0 | 908 | N/A | N/A | N/A | N/A | 33428346 | 410 | 111.8385 | 0% | 0% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 24 | 16.9014 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 127 | 132 | 19007085 | 5006 | 120.144 | 5.006 | 9.5 | 9.5 | 2B | 0 | 0 | 1177 | 0 | 1199 | N/A | N/A | N/A | N/A | 33429202 | 856 | 170.9948 | 0% | 0% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 19012669 | 5584 | 134.016 | 5.584 | 9.5 | 9.5 | 3B | 0 | 0 | 1145 | 1185 | 1150 | N/A | N/A | N/A | N/A | 33430326 | 1124 | 201.2894 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 149 | 19018485 | 5816 | 139.584 | 5.816 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33431560 | 1234 | 212.1733 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 19024536 | 6051 | 145.224 | 6.051 | 9.4 | 9 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33432884 | 1324 | 218.8068 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 147 | 19030544 | 6008 | 144.192 | 6.008 | 9.2 | 8.5 | 3B+1S | 0 | 980 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33434218 | 1334 | 222.0373 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 19036662 | 6118 | 146.832 | 6.118 | 8.9 | 8.9 | 3B+1S | 0 | 1022 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33435548 | 1330 | 217.3913 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 134 | 19042204 | 5542 | 133.008 | 5.542 | 8.4 | 8.4 | 3B+1S | 0 | 996 | 1104 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33436714 | 1166 | 210.3934 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 135 | 19047648 | 5444 | 130.656 | 5.444 | 8.1 | 8.1 | 3B+1S | 0 | 987 | 1104 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33437868 | 1154 | 211.9765 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 129 | 19053086 | 5438 | 130.512 | 5.438 | 8 | 8 | 3B+1S | 0 | 969 | 1083 | 1185 | 1087 | N/A | N/A | N/A | N/A | 33438996 | 1128 | 207.4292 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 127 | 19058418 | 5332 | 127.968 | 5.332 | 7.9 | 7.9 | 3B+1S | 0 | 1005 | 1034 | 1185 | 1036 | N/A | N/A | N/A | N/A | 33440086 | 1090 | 204.4261 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 118 | 126 | 19063789 | 5371 | 128.904 | 5.371 | 7.5 | 7.5 | 3B+1S | 0 | 1046 | 1044 | 1185 | 1046 | N/A | N/A | N/A | N/A | 33441170 | 1084 | 201.8246 | 0% | 100% | 100% | 100% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 19 | 13.3803 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 113 | 125 | 19069036 | 5247 | 125.928 | 5.247 | 6.8 | 6.8 | 2B+1S | 0 | 1040 | 1146 | 0 | 1150 | N/A | N/A | N/A | N/A | 33442114 | 944 | 179.9123 | 0% | 100% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 18 | 12.6761 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 | 125 | 19074248 | 5212 | 125.088 | 5.212 | 6.2 | 6.2 | 2B+1S | 0 | 1045 | 1146 | 0 | 1150 | N/A | N/A | N/A | N/A | 33443062 | 948 | 181.888 | 0% | 100% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 108 | 119 | 19079375 | 5127 | 123.048 | 5.127 | 5.5 | 5.5 | 2B+1S | 0 | 1058 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 33443958 | 896 | 174.7611 | 0% | 100% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 120 | 19084432 | 5057 | 121.368 | 5.057 | 4.9 | 4.9 | 2B+1S | 0 | 1035 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 33444826 | 868 | 171.6433 | 0% | 100% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 22 | 15.493 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 115 | 19089288 | 4856 | 116.544 | 4.856 | 4.5 | 4.5 | 2B+1S | 0 | 992 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 33445666 | 840 | 172.9819 | 0% | 100% | 100% | 0% | 100% | 0% | 7387601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 108 | 97 | 19093502 | 4214 | 101.136 | 4.214 | 4.9 | 4.9 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 33446372 | 706 | 167.5368 | 0% | 0% | 100% | 0% | 100% | 35% | 7388109 | 508 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 93 | 19097477 | 3975 | 95.4 | 3.975 | 5.6 | 5.6 | 2B | 0 | 0 | 944 | 0 | 1110 | N/A | N/A | N/A | N/A | 33447024 | 652 | 164.0252 | 0% | 0% | 100% | 0% | 100% | 35% | 7388861 | 752 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.2083 | 118254 | 118254 | 118.254 | 118.254 | [12 empty] | 21822 | 21822 | 184.535 | [6 empty] | 5013 | 5013 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 AM, NORMAL OPERATION
BP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:16 AM, NORMAL OPERATION
SP2 - STARTED @ 9:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 26) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:09 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25315 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19097477 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33447024 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7388861 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 86 | 19101216 | 3739 | 89.736 | 3.739 | 6.9 | 6.9 | 2B | 0 | 0 | 910 | 0 | 1110 | N/A | N/A | N/A | N/A | 33447610 | 586 | 156.7264 | 0% | 0% | 100% | 0% | 100% | 35% | 7389998 | 1137 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 88 | 19104869 | 3653 | 87.672 | 3.653 | 8.2 | 8.2 | 2B | 0 | 0 | 884 | 0 | 1110 | N/A | N/A | N/A | N/A | 33448174 | 564 | 154.3936 | 0% | 0% | 100% | 0% | 100% | 35% | 7391280 | 1282 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 87 | 19108494 | 3625 | 87 | 3.625 | 8.7 | 8.7 | 2B | 0 | 0 | 844 | 0 | 1110 | N/A | N/A | N/A | N/A | 33448705 | 531 | 146.4828 | 0% | 0% | 100% | 0% | 100% | 35% | 7392105 | 825 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 85 | 19111912 | 3418 | 82.032 | 3.418 | 9.5 | 9.5 | 2B | 0 | 0 | 760 | 0 | 1110 | N/A | N/A | N/A | N/A | 33449210 | 505 | 147.7472 | 0% | 0% | 100% | 0% | 100% | 35% | 7392453 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 33 | 23.2394 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 86 | 90 | 19115332 | 3420 | 82.08 | 3.42 | 9.5 | 9.5 | 2B | 0 | 0 | 754 | 0 | 1110 | N/A | N/A | N/A | N/A | 33449718 | 508 | 148.538 | 0% | 0% | 100% | 0% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 102 | 99 | 19119247 | 3915 | 93.96 | 3.915 | 9.5 | 9.5 | 2B | 0 | 0 | 872 | 0 | 1110 | N/A | N/A | N/A | N/A | 33450222 | 504 | 128.7356 | 0% | 0% | 100% | 0% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 147 | 19124866 | 5619 | 134.856 | 5.619 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 33451346 | 1124 | 200.0356 | 0% | 0% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 149 | 19130538 | 5672 | 136.128 | 5.672 | 9.4 | 9.4 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33452552 | 1206 | 212.6234 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 19136786 | 6248 | 149.952 | 6.248 | 9 | 9 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33453912 | 1360 | 217.6697 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 19143200 | 6414 | 153.936 | 6.414 | 8.3 | 9 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33455334 | 1422 | 221.7025 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 19149629 | 6429 | 154.296 | 6.429 | 7.3 | 8.5 | 3B+1S | 0 | 1138 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33456772 | 1438 | 223.674 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 148 | 19156014 | 6385 | 153.24 | 6.385 | 6.5 | 6.5 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33458206 | 1434 | 224.5889 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 142 | 149 | 19162381 | 6367 | 152.808 | 6.367 | 6.1 | 6.1 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33459602 | 1396 | 219.2555 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 141 | 147 | 19168533 | 6152 | 147.648 | 6.152 | 5.5 | 5.5 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33460990 | 1388 | 225.6177 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 147 | 19174676 | 6143 | 147.432 | 6.143 | 5 | 5 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33462372 | 1382 | 224.9715 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 144 | 19180513 | 5837 | 140.088 | 5.837 | 4.6 | 4.6 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33463715 | 1343 | 230.0839 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 19186351 | 5838 | 140.112 | 5.838 | 4.2 | 4.2 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33465058 | 1343 | 230.0445 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 137 | 19191990 | 5639 | 135.336 | 5.639 | 4.1 | 4.1 | 3B+1S | 0 | 988 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33466360 | 1302 | 230.892 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 131 | 19197629 | 5639 | 135.336 | 5.639 | 4 | 4 | 3B+1S | 0 | 1030 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 33467662 | 1302 | 230.892 | 0% | 100% | 100% | 100% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 127 | 19202919 | 5290 | 126.96 | 5.29 | 3.4 | 3.4 | 2B+1S | 0 | 1097 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33468717 | 1055 | 199.4329 | 0% | 100% | 100% | 0% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 122 | 125 | 19208205 | 5286 | 126.864 | 5.286 | 2.8 | 2.8 | 2B+1S | 0 | 1029 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33469767 | 1050 | 198.6379 | 0% | 100% | 100% | 0% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 123 | 19213493 | 5288 | 126.912 | 5.288 | 2.4 | 2.4 | 2B+1S | 0 | 992 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33470820 | 1053 | 199.1301 | 0% | 100% | 100% | 0% | 100% | 0% | 7392453 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 109 | 19218479 | 4986 | 119.664 | 4.986 | 3.9 | 3.9 | 2B | 0 | 0 | 1098 | 0 | 1110 | N/A | N/A | N/A | N/A | 33471629 | 809 | 162.2543 | 0% | 0% | 100% | 0% | 100% | 38% | 7393328 | 875 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 99 | 19222389 | 3910 | 93.84 | 3.91 | 5.1 | 5.1 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 33472339 | 710 | 181.5857 | 0% | 0% | 100% | 0% | 100% | 38% | 7394251 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.875 | 124912 | 124912 | 124.912 | 124.912 | [12 empty] | 25315 | 25315 | 202.6627 | [6 empty] | 5390 | 5390 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:35 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:17 AM, NORMAL OPERATION
SP2 - STARTED @ 7:35 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 27) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:09 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24595 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19222389 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33472339 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7394251 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 19225798 | 3409 | 81.816 | 3.409 | 6.3 | 6.3 | 2B | 0 | 0 | 968 | 0 | 1109 | N/A | N/A | N/A | N/A | 33472888 | 549 | 161.0443 | 0% | 0% | 100% | 0% | 100% | 38% | 7395704 | 1453 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 19229197 | 3399 | 81.576 | 3.399 | 7.5 | 7.5 | 2B | 0 | 0 | 931 | 0 | 1110 | N/A | N/A | N/A | N/A | 33473426 | 538 | 158.2818 | 0% | 0% | 100% | 0% | 100% | 38% | 7397153 | 1449 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 87 | 19232586 | 3389 | 81.336 | 3.389 | 8.7 | 8.7 | 2B | 0 | 0 | 909 | 0 | 1109 | N/A | N/A | N/A | N/A | 33473976 | 550 | 162.2898 | 0% | 0% | 100% | 0% | 100% | 38% | 7398603 | 1450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 84 | 19235985 | 3399 | 81.576 | 3.399 | 9.5 | 9.5 | 2B | 0 | 0 | 842 | 0 | 1008 | N/A | N/A | N/A | N/A | 33474528 | 552 | 162.4007 | 0% | 0% | 100% | 0% | 100% | 38% | 7399107 | 504 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 89 | 19239576 | 3591 | 86.184 | 3.591 | 9.5 | 9.5 | 2B | 0 | 0 | 848 | 0 | 1009 | N/A | N/A | N/A | N/A | 33475002 | 474 | 131.9967 | 0% | 0% | 100% | 0% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 99 | 19243611 | 4035 | 96.84 | 4.035 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1009 | N/A | N/A | N/A | N/A | 33475448 | 446 | 110.5328 | 0% | 0% | 100% | 0% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 19248889 | 5278 | 126.672 | 5.278 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33476478 | 1030 | 195.1497 | 0% | 0% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 149 | 19254834 | 5945 | 142.68 | 5.945 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33477718 | 1240 | 208.5786 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 147 | 19261045 | 6211 | 149.064 | 6.211 | 9.3 | 9.3 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33479078 | 1360 | 218.9664 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 19267290 | 6245 | 149.88 | 6.245 | 8.8 | 9 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33480414 | 1336 | 213.9311 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 19273664 | 6374 | 152.976 | 6.374 | 8.2 | 8.5 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33481810 | 1396 | 219.0147 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 145 | 19279970 | 6306 | 151.344 | 6.306 | 7.8 | 7.8 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33483186 | 1376 | 218.2049 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 142 | 19286032 | 6062 | 145.488 | 6.062 | 7.1 | 7.1 | 3B+1S | 0 | 167 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33484530 | 1344 | 221.709 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 145 | 19292017 | 5985 | 143.64 | 5.985 | 6.5 | 6.5 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33485894 | 1364 | 227.9031 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 144 | 19297932 | 5915 | 141.96 | 5.915 | 6.1 | 6.1 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33487242 | 1348 | 227.8952 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 19303770 | 5838 | 140.112 | 5.838 | 5.8 | 5.8 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33488566 | 1324 | 226.79 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 142 | 19309537 | 5767 | 138.408 | 5.767 | 5.4 | 5.4 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33489906 | 1340 | 232.3565 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 141 | 19315190 | 5653 | 135.672 | 5.653 | 5.2 | 5.2 | 3B+1S | 0 | 1012 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33491178 | 1272 | 225.0133 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 143 | 19320733 | 5543 | 133.032 | 5.543 | 4.8 | 4.8 | 3B+1S | 0 | 993 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33492426 | 1248 | 225.1488 | 0% | 100% | 100% | 100% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 129 | 19326127 | 5394 | 129.456 | 5.394 | 4 | 4 | 2B+1S | 0 | 1063 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33493508 | 1082 | 200.5933 | 0% | 100% | 100% | 0% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 19331387 | 5260 | 126.24 | 5.26 | 3.5 | 3.5 | 2B+1S | 0 | 1025 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33494538 | 1030 | 195.8175 | 0% | 100% | 100% | 0% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 118 | 19336462 | 5075 | 121.8 | 5.075 | 3.2 | 3.2 | 2B+1S | 0 | 988 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33495550 | 1012 | 199.4089 | 0% | 100% | 100% | 0% | 100% | 0% | 7399107 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 100 | 19340699 | 4237 | 101.688 | 4.237 | 4 | 4 | 2B | 0 | 0 | 1100 | 0 | 1109 | N/A | N/A | N/A | N/A | 33496284 | 734 | 173.2358 | 0% | 0% | 100% | 0% | 100% | 35% | 7399846 | 739 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 95 | 19344472 | 3773 | 90.552 | 3.773 | 5.6 | 5.6 | 2B | 0 | 0 | 1087 | 0 | 1110 | N/A | N/A | N/A | N/A | 33496934 | 650 | 172.2767 | 0% | 0% | 100% | 0% | 100% | 35% | 7400855 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4583 | 122083 | 122083 | 122.083 | 122.083 | [12 empty] | 24595 | 24595 | 201.4613 | [6 empty] | 6604 | 6604 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 3:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM, NORMAL OPERATION
SP2 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:21 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:17 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 28) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:35 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:21 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24126 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19344472 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33496934 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7400855 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 90 | 19348309 | 3837 | 92.088 | 3.837 | 6.7 | 6.7 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 33497545 | 611 | 159.239 | 0% | 0% | 100% | 0% | 100% | 35% | 7401925 | 1070 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 87 | 19352030 | 3721 | 89.304 | 3.721 | 7.5 | 7.5 | 2B | 0 | 0 | 998 | 0 | 1109 | N/A | N/A | N/A | N/A | 33498140 | 595 | 159.9033 | 0% | 0% | 100% | 0% | 100% | 35% | 7402981 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 85 | 19355829 | 3799 | 91.176 | 3.799 | 8.9 | 8.9 | 2B | 0 | 0 | 950 | 0 | 1109 | N/A | N/A | N/A | N/A | 33498730 | 590 | 155.304 | 0% | 0% | 100% | 0% | 100% | 35% | 7404024 | 1043 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 86 | 19359666 | 3837 | 92.088 | 3.837 | 9.5 | 9.5 | 2B | 0 | 0 | 888 | 0 | 1008 | N/A | N/A | N/A | N/A | 33499328 | 598 | 155.8509 | 0% | 0% | 100% | 0% | 100% | 35% | 7405028 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 88 | 19363168 | 3502 | 84.048 | 3.502 | 9.5 | 9.5 | 2B | 0 | 0 | 840 | 0 | 1008 | N/A | N/A | N/A | N/A | 33499790 | 462 | 131.9246 | 0% | 0% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 99 | 19367199 | 4031 | 96.744 | 4.031 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 0 | 1109 | N/A | N/A | N/A | N/A | 33500290 | 500 | 124.0387 | 0% | 0% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 137 | 19372676 | 5477 | 131.448 | 5.477 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1129 | N/A | N/A | N/A | N/A | 33501334 | 1044 | 190.6153 | 0% | 0% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 140 | 19378236 | 5560 | 133.44 | 5.56 | 9.5 | 9.5 | 3B | 0 | 0 | 1176 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33502478 | 1144 | 205.7554 | 0% | 0% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 147 | 19384308 | 6072 | 145.728 | 6.072 | 9.4 | 9.4 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33503784 | 1306 | 215.0856 | 0% | 0% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 19390452 | 6144 | 147.456 | 6.144 | 8.9 | 9 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33505148 | 1364 | 222.0052 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 19396712 | 6260 | 150.24 | 6.26 | 8.4 | 8.5 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33506530 | 1382 | 220.7668 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 19402908 | 6196 | 148.704 | 6.196 | 7.9 | 7.9 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33507900 | 1370 | 221.1104 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 19408861 | 5953 | 142.872 | 5.953 | 7.4 | 7.4 | 3B+1S | 0 | 1060 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33509204 | 1304 | 219.0492 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 19414728 | 5867 | 140.808 | 5.867 | 6.9 | 6.9 | 3B+1S | 0 | 1014 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33510494 | 1290 | 219.8739 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 141 | 19420546 | 5818 | 139.632 | 5.818 | 6.5 | 6.5 | 3B+1S | 0 | 1049 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33511782 | 1288 | 221.3819 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 19426290 | 5744 | 137.856 | 5.744 | 6 | 6 | 3B+1S | 0 | 1029 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33513068 | 1286 | 223.8858 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 134 | 19432037 | 5747 | 137.928 | 5.747 | 5.5 | 5.5 | 3B+1S | 0 | 1013 | 1177 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33514386 | 1318 | 229.337 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 131 | 19437566 | 5529 | 132.696 | 5.529 | 5.1 | 5.1 | 3B+1S | 0 | 1042 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 33515610 | 1224 | 221.3782 | 0% | 100% | 100% | 100% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 115 | 130 | 19443059 | 5493 | 131.832 | 5.493 | 4.1 | 4.1 | 2B+1S | 0 | 1107 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33516730 | 1120 | 203.8959 | 0% | 100% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 129 | 19448332 | 5273 | 126.552 | 5.273 | 3.5 | 3.5 | 2B+1S | 0 | 1040 | 1176 | 0 | 1181 | N/A | N/A | N/A | N/A | 33517746 | 1016 | 192.6797 | 0% | 100% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 121 | 19453490 | 5158 | 123.792 | 5.158 | 3 | 3 | 2B+1S | 0 | 1017 | 1176 | 0 | 1181 | N/A | N/A | N/A | N/A | 33518736 | 990 | 191.9349 | 0% | 100% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 120 | 19458461 | 4971 | 119.304 | 4.971 | 2.7 | 2.7 | 2B+1S | 0 | 1004 | 1160 | 0 | 1160 | N/A | N/A | N/A | N/A | 33519670 | 934 | 187.8898 | 0% | 100% | 100% | 0% | 100% | 0% | 7405028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 107 | 19462711 | 4250 | 102 | 4.25 | 3.7 | 3.7 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 33520380 | 710 | 167.0588 | 0% | 0% | 100% | 0% | 100% | 35% | 7405958 | 930 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 94 | 19466701 | 3990 | 95.76 | 3.99 | 4.8 | 4.8 | 2B | 0 | 0 | 1005 | 0 | 1109 | N/A | N/A | N/A | N/A | 33521060 | 680 | 170.4261 | 0% | 0% | 100% | 0% | 100% | 35% | 7406929 | 971 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.0833 | 122229 | 122229 | 122.229 | 122.229 | [12 empty] | 24126 | 24126 | 197.3836 | [6 empty] | 6074 | 6074 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:39 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:1 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 29) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | CHRISTIAN DIO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24850 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19466701 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33521060 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7406929 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 89 | 19470592 | 3891 | 93.384 | 3.891 | 6.1 | 6.1 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 33521662 | 602 | 154.716 | 0% | 0% | 100% | 0% | 100% | 38% | 7408062 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 85 | 19474317 | 3725 | 89.4 | 3.725 | 7.4 | 7.4 | 2B | 0 | 0 | 941 | 0 | 1108 | N/A | N/A | N/A | N/A | 33522240 | 578 | 155.1678 | 0% | 0% | 100% | 0% | 100% | 38% | 7409202 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 83 | 19477913 | 3596 | 86.304 | 3.596 | 8.8 | 8.8 | 2B | 0 | 0 | 920 | 0 | 1109 | N/A | N/A | N/A | N/A | 33522798 | 558 | 155.1724 | 0% | 0% | 100% | 0% | 100% | 38% | 7410341 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 82 | 83 | 19481211 | 3298 | 79.152 | 3.298 | 9.5 | 9.5 | 2B | 0 | 0 | 805 | 0 | 968 | N/A | N/A | N/A | N/A | 33523366 | 568 | 172.2256 | 0% | 0% | 100% | 0% | 100% | 38% | 7411461 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 90 | 19485002 | 3791 | 90.984 | 3.791 | 9.5 | 9.5 | 2B | 0 | 0 | 901 | 0 | 968 | N/A | N/A | N/A | N/A | 33523796 | 430 | 113.4265 | 0% | 0% | 100% | 0% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 101 | 19488794 | 3792 | 91.008 | 3.792 | 9.5 | 9.5 | 2B | 0 | 0 | 985 | 0 | 1009 | N/A | N/A | N/A | N/A | 33524286 | 490 | 129.2194 | 0% | 0% | 100% | 0% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 144 | 19494355 | 5561 | 133.464 | 5.561 | 9.5 | 9.5 | 3B | 0 | 0 | 1142 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33525374 | 1088 | 195.6483 | 0% | 0% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 149 | 19500323 | 5968 | 143.232 | 5.968 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33526620 | 1246 | 208.7802 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 19506582 | 6259 | 150.216 | 6.259 | 9 | 9 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33528000 | 1380 | 220.4825 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 46 | 19512877 | 6295 | 151.08 | 6.295 | 8.3 | 9 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33529406 | 1406 | 223.3519 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 19519155 | 6278 | 150.672 | 6.278 | 7.7 | 8.5 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33530808 | 1402 | 223.3195 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 19525295 | 6140 | 147.36 | 6.14 | 7.1 | 7.1 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33532190 | 1382 | 225.0814 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 19531478 | 6183 | 148.392 | 6.183 | 6.8 | 6.8 | 3B+1S | 0 | 1039 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33533538 | 1348 | 218.0171 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 19537325 | 5847 | 140.328 | 5.847 | 6.1 | 6.1 | 3B+1S | 0 | 1072 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33534867 | 1329 | 227.296 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 19543140 | 5815 | 139.56 | 5.815 | 5.6 | 5.6 | 3B+1S | 0 | 1037 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33536178 | 1311 | 225.4514 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 19548920 | 5780 | 138.72 | 5.78 | 5.2 | 5.2 | 3B+1S | 0 | 1022 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33537482 | 1304 | 225.6055 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 19554643 | 5723 | 137.352 | 5.723 | 4.7 | 4.7 | 3B+1S | 0 | 1017 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33538814 | 1332 | 232.7451 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 130 | 19560258 | 5615 | 134.76 | 5.615 | 4.2 | 4.2 | 3B+1S | 0 | 1030 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 33540082 | 1268 | 225.8237 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 129 | 19565774 | 5516 | 132.384 | 5.516 | 3.8 | 3.8 | 3B+1S | 0 | 1009 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 33541310 | 1228 | 222.6251 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 125 | 19571093 | 5319 | 127.656 | 5.319 | 3.5 | 3.5 | 3B+1S | 0 | 1012 | 1103 | 1185 | 1109 | N/A | N/A | N/A | N/A | 33542474 | 1164 | 218.8381 | 0% | 100% | 100% | 100% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 124 | 19576290 | 5197 | 124.728 | 5.197 | 3 | 3 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33543516 | 1042 | 200.5003 | 0% | 100% | 100% | 0% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 117 | 19581288 | 4998 | 119.952 | 4.998 | 2.9 | 2.9 | 2B+1S | 0 | 938 | 1176 | 0 | 1179 | N/A | N/A | N/A | N/A | 33544490 | 974 | 194.878 | 0% | 100% | 100% | 0% | 100% | 0% | 7411461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 101 | 19585590 | 4302 | 103.248 | 4.302 | 3.7 | 3.7 | 2B | 0 | 0 | 1080 | 0 | 1110 | N/A | N/A | N/A | N/A | 33545236 | 746 | 173.4077 | 0% | 0% | 100% | 0% | 100% | 0% | 7412293 | 832 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 85 | 19589562 | 3972 | 95.328 | 3.972 | 4.8 | 4.8 | 2B | 0 | 0 | 976 | 0 | 1110 | N/A | N/A | N/A | N/A | 33545910 | 674 | 169.6878 | 0% | 0% | 100% | 0% | 100% | 0% | 7413368 | 1075 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.7917 | 122861 | 122861 | 122.861 | 122.861 | [12 empty] | 24850 | 24850 | 202.2611 | [6 empty] | 6439 | 6439 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:21 AM, NORMAL OPERATION
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 30) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:17 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24410 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19589562 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33545910 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7413368 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 85 | 19593244 | 3682 | 88.368 | 3.682 | 6.2 | 6.2 | 2B | 0 | 0 | 968 | 0 | 1110 | N/A | N/A | N/A | N/A | 33546538 | 628 | 170.5595 | 0% | 0% | 100% | 0% | 100% | 40% | 7414511 | 1143 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 84 | 19596838 | 3594 | 86.256 | 3.594 | 7.5 | 7.5 | 2B | 0 | 0 | 935 | 0 | 1110 | N/A | N/A | N/A | N/A | 33547136 | 598 | 166.3884 | 0% | 0% | 100% | 0% | 100% | 40% | 7415840 | 1329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 84 | 19600344 | 3506 | 84.144 | 3.506 | 8.8 | 8.8 | 2B | 0 | 0 | 893 | 0 | 1110 | N/A | N/A | N/A | N/A | 33547706 | 570 | 162.5784 | 0% | 0% | 100% | 0% | 100% | 40% | 7417222 | 1382 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 84 | 19603877 | 3533 | 84.792 | 3.533 | 9.5 | 9.5 | 2B | 0 | 0 | 778 | 0 | 1110 | N/A | N/A | N/A | N/A | 33548244 | 538 | 152.2785 | 0% | 0% | 100% | 0% | 100% | 40% | 7417714 | 492 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 91 | 19607522 | 3645 | 87.48 | 3.645 | 9.5 | 9.5 | 2B | 0 | 0 | 771 | 0 | 1109 | N/A | N/A | N/A | N/A | 33548766 | 522 | 143.2099 | 0% | 0% | 100% | 0% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 29 | 20.4225 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 100 | 19611573 | 4051 | 97.224 | 4.051 | 9.5 | 9.5 | 2B | 0 | 0 | 853 | 0 | 1110 | N/A | N/A | N/A | N/A | 33549306 | 540 | 133.3004 | 0% | 0% | 100% | 0% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 132 | 19616936 | 5363 | 128.712 | 5.363 | 9.5 | 9.5 | 3B | 0 | 0 | 1105 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33550390 | 1084 | 202.1257 | 0% | 0% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 19622657 | 5721 | 137.304 | 5.721 | 9.3 | 9.3 | 3B+1S | 0 | 1032 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33551580 | 1190 | 208.0056 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 148 | 19628868 | 6211 | 149.064 | 6.211 | 9 | 9 | 3B+1S | 0 | 1017 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33552870 | 1290 | 207.696 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 19635080 | 6212 | 149.088 | 6.212 | 8.5 | 8.5 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33554242 | 1372 | 220.8628 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 149 | 19641273 | 6193 | 148.632 | 6.193 | 7.9 | 7.9 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33555616 | 1374 | 221.8634 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 19647536 | 6263 | 150.312 | 6.263 | 7.6 | 7.6 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33557000 | 1384 | 220.9804 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 19653488 | 5952 | 142.848 | 5.952 | 7.2 | 7.2 | 3B+1S | 0 | 993 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33558304 | 1304 | 219.086 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 19659178 | 5690 | 136.56 | 5.69 | 6.9 | 6.9 | 3B+1S | 0 | 1051 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33559564 | 1260 | 221.4411 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 139 | 19664993 | 5815 | 139.56 | 5.815 | 6.4 | 6.4 | 3B+1S | 0 | 1031 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33560856 | 1292 | 222.184 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 142 | 19670780 | 5787 | 138.888 | 5.787 | 5.9 | 5.9 | 3B+1S | 0 | 1057 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33562156 | 1300 | 224.6414 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 137 | 19676564 | 5784 | 138.816 | 5.784 | 5.4 | 5.4 | 3B+1S | 0 | 1063 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33563468 | 1312 | 226.8326 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 132 | 19682042 | 5478 | 131.472 | 5.478 | 5 | 5 | 3B+1S | 0 | 1027 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 33564696 | 1228 | 224.1694 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 130 | 19687832 | 5790 | 138.96 | 5.79 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 33565896 | 1200 | 207.2539 | 0% | 100% | 100% | 100% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 19692807 | 4975 | 119.4 | 4.975 | 4.2 | 4.2 | 2B+1S | 0 | 1012 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33566940 | 1044 | 209.8492 | 0% | 100% | 100% | 0% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 120 | 19697988 | 5181 | 124.344 | 5.181 | 3.7 | 3.7 | 2B+1S | 0 | 1035 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 33567948 | 1008 | 194.557 | 0% | 100% | 100% | 0% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 120 | 19703159 | 5171 | 124.104 | 5.171 | 3.1 | 3.1 | 2B+1S | 0 | 999 | 1165 | 0 | 1170 | N/A | N/A | N/A | N/A | 33568924 | 976 | 188.7449 | 0% | 100% | 100% | 0% | 100% | 0% | 7417714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 101 | 19707645 | 4486 | 107.664 | 4.486 | 4.3 | 4.3 | 2B | 0 | 0 | 1129 | 0 | 1110 | N/A | N/A | N/A | N/A | 33569657 | 733 | 163.3972 | 0% | 0% | 100% | 0% | 100% | 35% | 7418524 | 810 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 89 | 19711419 | 3774 | 90.576 | 3.774 | 5.4 | 5.4 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 33570320 | 663 | 175.6757 | 0% | 0% | 100% | 0% | 100% | 35% | 7419504 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.5417 | 121857 | 121857 | 121.857 | 121.857 | [13 empty] | 24410 | 200.3168 | [6 empty] | 6136 | 6136 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 3:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:32 AM, NORMAL OPERATION
SP2 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET PRESSURE
Engr. Diloy arrived @ 8:14am and assist Mr. W. De Jesus of ABB to dismantel and pulled-out some parts of SP1 (VFD 4)
Engr. W. De Jesus of ABB arrived @ 8:49am to dismantel Overvoltage Protection Board (OVVP Board) w/ SVA subprint Board and Analog/Digital Converter Protection Board (ADCVI Board)
Additional 3 psi to target discharge pressure from 12:01pm to 5am (DEC 30) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:32 AM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## DEC 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | CHRISTIAN DIO
[13 empty] | 10pm - 6am | CHRISTIAN DIO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2014-12-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23988 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19711419 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33570320 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7419504 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 85 | 19715118 | 3699 | 88.776 | 3.699 | 6.7 | 6.7 | 2B | 0 | 0 | 1019 | 0 | 1059 | N/A | N/A | N/A | N/A | 33570930 | 610 | 164.9094 | 0% | 0% | 100% | 0% | 100% | 35% | 7420602 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 84 | 19718648 | 3530 | 84.72 | 3.53 | 7.5 | 7.5 | 2B | 0 | 0 | 1002 | 0 | 1060 | N/A | N/A | N/A | N/A | 33571489 | 559 | 158.3569 | 0% | 0% | 100% | 0% | 100% | 35% | 7421705 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 83 | 19722240 | 3592 | 86.208 | 3.592 | 8.6 | 8.6 | 2B | 0 | 0 | 950 | 0 | 1059 | N/A | N/A | N/A | N/A | 33572034 | 545 | 151.7261 | 0% | 0% | 100% | 0% | 100% | 35% | 7422805 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 84 | 19725734 | 3494 | 83.856 | 3.494 | 9.5 | 9.5 | 2B | 0 | 0 | 820 | 0 | 1059 | N/A | N/A | N/A | N/A | 33572500 | 466 | 133.3715 | 0% | 0% | 100% | 0% | 100% | 35% | 7423491 | 686 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 90 | 19729487 | 3753 | 90.072 | 3.753 | 9.5 | 9.5 | 2B | 0 | 0 | 851 | 0 | 1009 | N/A | N/A | N/A | N/A | 33572952 | 452 | 120.437 | 0% | 0% | 100% | 0% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | C. DIO
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 100 | 98 | 19733300 | 3813 | 91.512 | 3.813 | 9.5 | 9.5 | 2B | 0 | 0 | 892 | 0 | 1009 | N/A | N/A | N/A | N/A | 33573444 | 492 | 129.0323 | 0% | 0% | 100% | 0% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 139 | 19738505 | 5205 | 124.92 | 5.205 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33574420 | 976 | 187.512 | 0% | 0% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 149 | 19744253 | 5748 | 137.952 | 5.748 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33575596 | 1176 | 204.5929 | 0% | 0% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 148 | 19750393 | 6140 | 147.36 | 6.14 | 9.4 | 9.4 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33576908 | 1312 | 213.6808 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 19756523 | 6130 | 147.12 | 6.13 | 9 | 9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33578260 | 1352 | 220.5546 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 19762684 | 6161 | 147.864 | 6.161 | 8.7 | 8.5 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33579620 | 1360 | 220.7434 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 19768646 | 5962 | 143.088 | 5.962 | 8.4 | 8.4 | 3B+1S | 0 | 1016 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33580908 | 1288 | 216.0349 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 123 | 135 | 19774454 | 5808 | 139.392 | 5.808 | 7.6 | 7.6 | 3B+1S | 0 | 1128 | 1115 | 1185 | 1118 | N/A | N/A | N/A | N/A | 33582156 | 1248 | 214.876 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 19780222 | 5768 | 138.432 | 5.768 | 7.2 | 7.2 | 3B+1S | 0 | 1015 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33583412 | 1256 | 217.7531 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 138 | 19785992 | 5770 | 138.48 | 5.77 | 6.8 | 6.8 | 3B+1S | 0 | 1057 | 1154 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33584676 | 1264 | 219.0641 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 19791802 | 5810 | 139.44 | 5.81 | 6.2 | 6.2 | 3B+1S | 0 | 1050 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33585964 | 1288 | 221.6867 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 19797642 | 5840 | 140.16 | 5.84 | 5.5 | 5.5 | 3B+1S | 0 | 1043 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33587264 | 1300 | 222.6027 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 139 | 19803245 | 5603 | 134.472 | 5.603 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33588532 | 1268 | 226.3073 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 19808871 | 5626 | 135.024 | 5.626 | 4.8 | 4.8 | 3B+1S | 0 | 1013 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33589784 | 1252 | 222.5382 | 0% | 100% | 100% | 100% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 19814357 | 5486 | 131.664 | 5.486 | 3.9 | 3.9 | 2B+1S | 0 | 1073 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33590876 | 1092 | 199.0521 | 0% | 100% | 100% | 0% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 125 | 19819679 | 5322 | 127.728 | 5.322 | 3.3 | 3.3 | 2B+1S | 0 | 1020 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33591916 | 1040 | 195.4153 | 0% | 100% | 100% | 0% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 119 | 19824727 | 5048 | 121.152 | 5.048 | 2.8 | 2.8 | 2B+1S | 0 | 1036 | 1145 | 0 | 1150 | N/A | N/A | N/A | N/A | 33592876 | 960 | 190.1743 | 0% | 100% | 100% | 0% | 100% | 0% | 7423491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 106 | 19829221 | 4494 | 107.856 | 4.494 | 3.3 | 3.3 | 2B | 0 | 0 | 1103 | 0 | 1109 | N/A | N/A | N/A | N/A | 33593620 | 744 | 165.5541 | 0% | 0% | 100% | 0% | 100% | 30% | 7424129 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 99 | 19833452 | 4231 | 101.544 | 4.231 | 4.4 | 4.4 | 2B | 0 | 0 | 1014 | 0 | 1109 | N/A | N/A | N/A | N/A | 33594308 | 688 | 162.6093 | 0% | 0% | 100% | 0% | 100% | 30% | 7424963 | 834 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.125 | 122033 | 122033 | 122.033 | 122.033 | [12 empty] | 23988 | 23988 | 196.5698 | [6 empty] | 5459 | 5459 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:17 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION