## JAN 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 20812 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19833452 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33594308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7424963 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 100 | 19837523 | 4071 | 97.704 | 4.071 | 5.5 | 5.5 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 33594984 | 676 | 166.0526 | 0% | 0% | 100% | 0% | 100% | 35% | 7425968 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 99 | 19841676 | 4153 | 99.672 | 4.153 | 6.5 | 6.5 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 33595658 | 674 | 162.2923 | 0% | 0% | 100% | 0% | 100% | 35% | 7426954 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 87 | 19845546 | 3870 | 92.88 | 3.87 | 7.5 | 7.5 | 2B | 0 | 0 | 932 | 0 | 1109 | N/A | N/A | N/A | N/A | 33596300 | 642 | 165.8915 | 0% | 0% | 100% | 0% | 100% | 35% | 7428004 | 1050 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 80 | 19849222 | 3676 | 88.224 | 3.676 | 8.8 | 8.8 | 2B | 0 | 0 | 889 | 0 | 1110 | N/A | N/A | N/A | N/A | 33596872 | 572 | 155.6039 | 0% | 0% | 100% | 0% | 100% | 35% | 7429378 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 85 | 87 | 19852648 | 3426 | 82.224 | 3.426 | 9.5 | 9.5 | 2B | 0 | 0 | 715 | 0 | 1110 | N/A | N/A | N/A | N/A | 33597388 | 516 | 150.613 | 0% | 0% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 36 | 25.3521 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 90 | 88 | 19856310 | 3662 | 87.888 | 3.662 | 9.5 | 9.5 | 2B | 0 | 0 | 713 | 0 | 1100 | N/A | N/A | N/A | N/A | 33597860 | 472 | 128.8913 | 0% | 0% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 23 | 16.1972 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 128 | 19861321 | 5011 | 120.264 | 5.011 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1169 | N/A | N/A | N/A | N/A | 33598692 | 832 | 166.0347 | 0% | 0% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 22 | 15.493 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 126 | 19866333 | 5012 | 120.288 | 5.012 | 9.5 | 9.5 | 2B | 0 | 0 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33599524 | 832 | 166.0016 | 0% | 0% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 135 | 19871987 | 5654 | 135.696 | 5.654 | 9.5 | 9.5 | 3B | 0 | 0 | 1150 | 1185 | 1110 | N/A | N/A | N/A | N/A | 33600636 | 1112 | 196.6749 | 0% | 0% | 100% | 100% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 120 | 144 | 19877838 | 5851 | 140.424 | 5.851 | 8.6 | 9 | 2B+1S | 0 | 1188 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33601764 | 1128 | 192.7876 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule
58:00 | 11:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 139 | 19883781 | 5943 | 142.632 | 5.943 | 8.3 | 8.5 | 3B+1S | 0 | 1005 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 33602996 | 1232 | 207.3027 | 0% | 100% | 100% | 100% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule
59:00 | 12:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 134 | 19889550 | 5769 | 138.456 | 5.769 | 8.2 | 8.2 | 3B+1S | 0 | 989 | 1105 | 1185 | 1108 | N/A | N/A | N/A | N/A | 33604204 | 1208 | 209.395 | 0% | 100% | 100% | 100% | 100% | 0% | 7429378 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 118 | 130 | 19895123 | 5573 | 133.752 | 5.573 | 7.5 | 7.5 | 2B+1S | 0 | 1094 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33605240 | 1036 | 185.8963 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 20 | 14.0845 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 130 | 19900608 | 5485 | 131.64 | 5.485 | 7.1 | 7.1 | 2B+1S | 0 | 1014 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 33606284 | 1044 | 190.3373 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 21 | 14.7887 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 120 | 127 | 19905993 | 5385 | 129.24 | 5.385 | 6.5 | 6.5 | 2B+1S | 0 | 1007 | 1177 | 0 | 1182 | N/A | N/A | N/A | N/A | 33607292 | 1008 | 187.1866 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 19 | 13.3803 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 127 | 19911378 | 5385 | 129.24 | 5.385 | 6.1 | 6.1 | 2B+1S | 0 | 1058 | 1177 | 0 | 1181 | N/A | N/A | N/A | N/A | 33608286 | 994 | 184.5868 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 18 | 12.6761 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 120 | 127 | 19916648 | 5270 | 126.48 | 5.27 | 5.8 | 5.8 | 2B+1S | 0 | 1047 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33609270 | 984 | 186.7173 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 16 | 11.2676 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 122 | 132 | 19922124 | 5476 | 131.424 | 5.476 | 5.5 | 5.5 | 2B+1S | 0 | 1033 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33610308 | 1038 | 189.5544 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 15 | 10.5634 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 122 | 19927316 | 5192 | 124.608 | 5.192 | 5.1 | 5.1 | 2B+1S | 0 | 998 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33611312 | 1004 | 193.3744 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 116 | 19932297 | 4981 | 119.544 | 4.981 | 4.9 | 4.9 | 2B+1S | 0 | 989 | 1150 | 0 | 1161 | N/A | N/A | N/A | N/A | 33612228 | 916 | 183.8988 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 118 | 19937302 | 5005 | 120.12 | 5.005 | 4.8 | 4.8 | 2B+1S | 0 | 990 | 1125 | 0 | 1130 | N/A | N/A | N/A | N/A | 33613128 | 900 | 179.8202 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 24 | 16.9014 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 114 | 19942206 | 4904 | 117.696 | 4.904 | 4.7 | 4.7 | 2B+1S | 0 | 989 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 33613972 | 844 | 172.1044 | 0% | 100% | 100% | 0% | 100% | 0% | 7429378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 96 | 19946392 | 4186 | 100.464 | 4.186 | 5.3 | 5.3 | 2B | 0 | 0 | 1035 | 0 | 1028 | N/A | N/A | N/A | N/A | 33614604 | 632 | 150.9795 | 0% | 0% | 100% | 0% | 100% | 25% | 7430563 | 1185 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 92 | 19950086 | 3694 | 88.656 | 3.694 | 6.1 | 6.1 | 2B | 0 | 0 | 946 | 0 | 987 | N/A | N/A | N/A | N/A | 33615120 | 516 | 139.686 | 0% | 0% | 100% | 0% | 100% | 25% | 7431330 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 115.75 | 116634 | 116634 | 116.634 | 116.634 | [12 empty] | 20812 | 20812 | 178.4385 | [6 empty] | 6367 | 6367 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 38% @ 12:01 AM
XCV1 CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:10 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
BP2 - STOPPED @ 9:01 PM DUE TO HIGH SUCTION PRESSURE AND LOW WATER USED
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 AM, NORMAL OPERATION
SP2 - STARTED @ 9:01 AM TO MEET 83 PSI TARGET PRESSURE
BP2 - RESTARTED @ 10:01
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
BP2 - STOPPED @ 12:01 PM DUE TO HIGH SUCTION PRESSURE AND LOW WATER USED
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24004 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19950086 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33615120 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7431330 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 90 | 89 | 19953836 | 3750 | 90 | 3.75 | 7.1 | 7.1 | 2B | 0 | 0 | 1010 | 0 | 1008 | N/A | N/A | N/A | N/A | 33615648 | 528 | 140.8 | 0% | 0% | 100% | 0% | 100% | 35% | 7432338 | 1008 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 87 | 86 | 19957398 | 3562 | 85.488 | 3.562 | 8.2 | 8.2 | 2B | 0 | 0 | 950 | 0 | 1008 | N/A | N/A | N/A | N/A | 33616153 | 505 | 141.7743 | 0% | 0% | 100% | 0% | 100% | 35% | 7433480 | 1142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 83 | 82 | 19960858 | 3460 | 83.04 | 3.46 | 9.5 | 9.5 | 2B | 0 | 0 | 886 | 0 | 886 | N/A | N/A | N/A | N/A | 33616644 | 491 | 141.9075 | 0% | 0% | 100% | 0% | 100% | 35% | 7434529 | 1049 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 33 | 23.2394 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 82 | 19964088 | 3230 | 77.52 | 3.23 | 9.5 | 9.5 | 2B | 0 | 0 | 839 | 0 | 867 | N/A | N/A | N/A | N/A | 33617020 | 376 | 116.4087 | 0% | 0% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 34 | 23.9437 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 86 | 19967631 | 3543 | 85.032 | 3.543 | 9.5 | 9.5 | 2B | 0 | 0 | 847 | 0 | 867 | N/A | N/A | N/A | N/A | 33617631 | 611 | 172.4527 | 0% | 0% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 32 | 22.5352 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 97 | 94 | 19971417 | 3786 | 90.864 | 3.786 | 9.5 | 9.5 | 2B | 0 | 0 | 941 | 0 | 907 | N/A | N/A | N/A | N/A | 33617800 | 169 | 44.6381 | 0% | 0% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 120 | 19976774 | 5357 | 128.568 | 5.357 | 9.5 | 9.5 | 3B | 0 | 0 | 1110 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33618838 | 1038 | 193.7652 | 0% | 0% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 141 | 19982131 | 5357 | 128.568 | 5.357 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33619876 | 1038 | 193.7652 | 0% | 0% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 19988200 | 6069 | 145.656 | 6.069 | 9 | 9 | 3B+1S | 0 | 1056 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33621156 | 1280 | 210.9079 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 153 | 19994397 | 6197 | 148.728 | 6.197 | 8.4 | 8.4 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33622524 | 1368 | 220.752 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 20000789 | 6392 | 153.408 | 6.392 | 7.8 | 8.5 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33623932 | 1408 | 220.2753 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 152 | 20007039 | 6250 | 150 | 6.25 | 7.2 | 7.2 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33625316 | 1384 | 221.44 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 150 | 20013197 | 6158 | 147.792 | 6.158 | 6.6 | 6.6 | 3B+1S | 0 | 1074 | 1154 | 1185 | 1160 | N/A | N/A | N/A | N/A | 33626632 | 1316 | 213.7057 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 143 | 20019308 | 6111 | 146.664 | 6.111 | 6 | 6 | 3B+1S | 0 | 1052 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33627996 | 1364 | 223.2041 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 20025501 | 6193 | 148.632 | 6.193 | 5.5 | 5.5 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33629396 | 1400 | 226.0617 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 144 | 20031221 | 5720 | 137.28 | 5.72 | 5.2 | 5.2 | 3B+1S | 0 | 1033 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33630684 | 1288 | 225.1748 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 20037115 | 5894 | 141.456 | 5.894 | 4.7 | 4.7 | 3B+1S | 0 | 1077 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33632036 | 1352 | 229.3858 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 20042876 | 5761 | 138.264 | 5.761 | 4.5 | 4.5 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33633364 | 1328 | 230.5155 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 133 | 20048513 | 5637 | 135.288 | 5.637 | 4.4 | 4.4 | 3B+1S | 0 | 989 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33634652 | 1288 | 228.4903 | 0% | 100% | 100% | 100% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 131 | 20054011 | 5498 | 131.952 | 5.498 | 3.7 | 3.7 | 2B+1S | 0 | 1040 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33635748 | 1096 | 199.3452 | 0% | 100% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 126 | 20059197 | 5186 | 124.464 | 5.186 | 3.2 | 3.2 | 2B+1S | 0 | 1012 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33636764 | 1016 | 195.9121 | 0% | 100% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 119 | 20064248 | 5051 | 121.224 | 5.051 | 3.1 | 3.1 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33637748 | 984 | 194.8129 | 0% | 100% | 100% | 0% | 100% | 0% | 7434529 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 103 | 20068601 | 4353 | 104.472 | 4.353 | 3.7 | 3.7 | 2B | 0 | 0 | 1065 | 0 | 1088 | N/A | N/A | N/A | N/A | 33638476 | 728 | 167.241 | 0% | 0% | 100% | 0% | 100% | 25% | 7435108 | 579 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 94 | 20072724 | 4123 | 98.952 | 4.123 | 4.5 | 4.5 | 2B | 0 | 0 | 1043 | 0 | 1028 | N/A | N/A | N/A | N/A | 33639124 | 648 | 157.1671 | 0% | 0% | 100% | 0% | 100% | 25% | 7435764 | 656 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.375 | 122638 | 122638 | 122.638 | 122.638 | [12 empty] | 24004 | 24004 | 195.7305 | [6 empty] | 4434 | 4434 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 2:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:00 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 2, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25092 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20072724 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33639124 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7435764 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 91 | 20076529 | 3805 | 91.32 | 3.805 | 5.7 | 5.7 | 2B | 0 | 0 | 1042 | 0 | 1027 | N/A | N/A | N/A | N/A | 33639740 | 616 | 161.8922 | 0% | 0% | 100% | 0% | 100% | 35% | 7436854 | 1090 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 88 | 20080244 | 3715 | 89.16 | 3.715 | 6.4 | 6.4 | 2B | 0 | 0 | 1042 | 0 | 1028 | N/A | N/A | N/A | N/A | 33640318 | 578 | 155.5855 | 0% | 0% | 100% | 0% | 100% | 35% | 7437968 | 1114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 86 | 20083902 | 3658 | 87.792 | 3.658 | 7.8 | 7.8 | 2B | 0 | 0 | 945 | 0 | 1029 | N/A | N/A | N/A | N/A | 33640856 | 538 | 147.0749 | 0% | 0% | 100% | 0% | 100% | 35% | 7439117 | 1149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 88 | 20087437 | 3535 | 84.84 | 3.535 | 9.2 | 9.2 | 2B | 0 | 0 | 959 | 0 | 1008 | N/A | N/A | N/A | N/A | 33641372 | 516 | 145.9689 | 0% | 0% | 100% | 0% | 100% | 35% | 7440316 | 1199 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 87 | 20091037 | 3600 | 86.4 | 3.6 | 9.5 | 9.5 | 2B | 0 | 0 | 915 | 0 | 908 | N/A | N/A | N/A | N/A | 33641812 | 440 | 122.2222 | 0% | 0% | 100% | 0% | 100% | 35% | 7440558 | 242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 102 | 98 | 20095079 | 4042 | 97.008 | 4.042 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 987 | N/A | N/A | N/A | N/A | 33642308 | 496 | 122.7115 | 0% | 0% | 100% | 0% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 132 | 20100334 | 5255 | 126.12 | 5.255 | 9.5 | 9.5 | 3B | 0 | 0 | 1059 | 1185 | 1108 | N/A | N/A | N/A | N/A | 33643308 | 1000 | 190.295 | 0% | 0% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 141 | 20106110 | 5776 | 138.624 | 5.776 | 9.5 | 9.5 | 3B | 0 | 0 | 1191 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33644492 | 1184 | 204.9861 | 0% | 0% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 20112229 | 6119 | 146.856 | 6.119 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33645836 | 1344 | 219.6437 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 155 | 20118663 | 6434 | 154.416 | 6.434 | 8.6 | 8.6 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33647260 | 1424 | 221.3242 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 20124717 | 6054 | 145.296 | 6.054 | 8.1 | 8.1 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33648596 | 1336 | 220.6805 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 149 | 20130980 | 6263 | 150.312 | 6.263 | 7.6 | 7.6 | 3B+1S | 0 | 1137 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33649980 | 1384 | 220.9804 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 146 | 20137197 | 6217 | 149.208 | 6.217 | 7 | 7 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33651380 | 1400 | 225.189 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 146 | 20143135 | 5938 | 142.512 | 5.938 | 6.6 | 6.6 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33652716 | 1336 | 224.9916 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 20149025 | 5890 | 141.36 | 5.89 | 6.3 | 6.3 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33654060 | 1344 | 228.1834 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 142 | 20154996 | 5971 | 143.304 | 5.971 | 6 | 6 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33655404 | 1344 | 225.0879 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 20160851 | 5855 | 140.52 | 5.855 | 5.5 | 5.5 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33656752 | 1348 | 230.2306 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 142 | 20166720 | 5869 | 140.856 | 5.869 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33658092 | 1340 | 228.3183 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 20172284 | 5564 | 133.536 | 5.564 | 5.1 | 5.1 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33659376 | 1284 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 125 | 20177674 | 5390 | 129.36 | 5.39 | 4.5 | 4.5 | 2B+1S | 0 | 1044 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33660452 | 1076 | 199.6289 | 0% | 100% | 100% | 0% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 123 | 20183033 | 5359 | 128.616 | 5.359 | 3.9 | 3.9 | 2B+1S | 0 | 1039 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33661500 | 1048 | 195.5589 | 0% | 100% | 100% | 0% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 130 | 20188177 | 5144 | 123.456 | 5.144 | 3.6 | 3.6 | 2B+1S | 0 | 1068 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33662508 | 1008 | 195.9565 | 0% | 100% | 100% | 0% | 100% | 0% | 7440558 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 106 | 20193193 | 5016 | 120.384 | 5.016 | 4.3 | 4.3 | 2B | 0 | 0 | 1109 | 0 | 1100 | N/A | N/A | N/A | N/A | 33663458 | 950 | 189.3939 | 0% | 0% | 100% | 0% | 100% | 30% | 7441170 | 612 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 98 | 20198038 | 4845 | 116.28 | 4.845 | 5.2 | 5.2 | 2B | 0 | 0 | 999 | 0 | 1100 | N/A | N/A | N/A | N/A | 33664216 | 758 | 156.4499 | 0% | 0% | 100% | 0% | 100% | 30% | 7441920 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.5833 | 125314 | 125314 | 125.314 | 125.314 | [12 empty] | 25092 | 25092 | 200.233 | [6 empty] | 6156 | 6156 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:12 AM WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM, NORMAL OPERATION
BP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 4, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:00 PM, NORMAL OPERATION
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24087 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20198038 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33664216 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7441920 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 20201697 | 3659 | 87.816 | 3.659 | 6.2 | 6.2 | 2B | 0 | 0 | 1010 | 0 | 1059 | N/A | N/A | N/A | N/A | 33664754 | 538 | 147.0347 | 0% | 0% | 100% | 0% | 100% | 35% | 7442868 | 948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 89 | 20205151 | 3454 | 82.896 | 3.454 | 7.2 | 7.2 | 2B | 0 | 0 | 999 | 0 | 1059 | N/A | N/A | N/A | N/A | 33665276 | 522 | 151.1291 | 0% | 0% | 100% | 0% | 100% | 35% | 7443878 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 89 | 20208508 | 3357 | 80.568 | 3.357 | 8.3 | 8.3 | 2B | 0 | 0 | 968 | 0 | 1059 | N/A | N/A | N/A | N/A | 33665788 | 512 | 152.5171 | 0% | 0% | 100% | 0% | 100% | 35% | 7445017 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 88 | 20211710 | 3202 | 76.848 | 3.202 | 9.4 | 9.4 | 2B | 0 | 0 | 944 | 0 | 1059 | N/A | N/A | N/A | N/A | 33666267 | 479 | 149.594 | 0% | 0% | 100% | 0% | 100% | 35% | 7446054 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 89 | 20215203 | 3493 | 83.832 | 3.493 | 9.5 | 9.5 | 2B | 0 | 0 | 932 | 0 | 918 | N/A | N/A | N/A | N/A | 33666732 | 465 | 133.1234 | 0% | 0% | 100% | 0% | 100% | 35% | 7446160 | 106 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 30 | 21.1268 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 99 | 97 | 20219186 | 3983 | 95.592 | 3.983 | 9.5 | 9.5 | 2B | 0 | 0 | 938 | 0 | 937 | N/A | N/A | N/A | N/A | 33667212 | 480 | 120.5122 | 0% | 0% | 100% | 0% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 21 | 14.7887 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 128 | 20224294 | 5108 | 122.592 | 5.108 | 9.5 | 9.5 | 3B | 0 | 0 | 1028 | 1185 | 1103 | N/A | N/A | N/A | N/A | 33668124 | 912 | 178.5435 | 0% | 0% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 142 | 20230041 | 5747 | 137.928 | 5.747 | 9.5 | 9.5 | 3B | 0 | 0 | 1166 | 1185 | 1159 | N/A | N/A | N/A | N/A | 33669260 | 1136 | 197.6683 | 0% | 0% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 149 | 20236128 | 6087 | 146.088 | 6.087 | 9.4 | 9.4 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33670572 | 1312 | 215.5413 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 20242303 | 6175 | 148.2 | 6.175 | 9 | 9 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33671932 | 1360 | 220.2429 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 20248541 | 6238 | 149.712 | 6.238 | 8.4 | 8.4 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33673316 | 1384 | 221.866 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 20254678 | 6137 | 147.288 | 6.137 | 8 | 8 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33674684 | 1368 | 222.9102 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 144 | 20260613 | 5935 | 142.44 | 5.935 | 7.7 | 7.7 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33676028 | 1344 | 226.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 20266588 | 5975 | 143.4 | 5.975 | 7.3 | 7.3 | 3B+1S | 0 | 1041 | 1185 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33677376 | 1348 | 225.6067 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 138 | 20272445 | 5857 | 140.568 | 5.857 | 6.9 | 6.9 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33678720 | 1344 | 229.469 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 130 | 20278151 | 5706 | 136.944 | 5.706 | 6.6 | 6.6 | 3B+1S | 0 | 993 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33680036 | 1316 | 230.6344 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 20283906 | 5755 | 138.12 | 5.755 | 6.2 | 6.2 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33681364 | 1328 | 230.7559 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 134 | 20289654 | 5748 | 137.952 | 5.748 | 5.8 | 5.8 | 3B+1S | 0 | 1013 | 1135 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33682660 | 1296 | 225.4697 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 20295127 | 5473 | 131.352 | 5.473 | 5.4 | 5.4 | 3B+1S | 0 | 988 | 1135 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33683900 | 1240 | 226.5668 | 0% | 100% | 100% | 100% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 125 | 20300597 | 5470 | 131.28 | 5.47 | 4.7 | 4.7 | 2B+1S | 0 | 1091 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33685020 | 1120 | 204.7532 | 0% | 100% | 100% | 0% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 119 | 20305741 | 5144 | 123.456 | 5.144 | 4.3 | 4.3 | 2B+1S | 0 | 998 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33686012 | 992 | 192.846 | 0% | 100% | 100% | 0% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 112 | 20310886 | 5145 | 123.48 | 5.145 | 4 | 4 | 2B+1S | 0 | 976 | 1166 | 0 | 1170 | N/A | N/A | N/A | N/A | 33687004 | 992 | 192.8086 | 0% | 100% | 100% | 0% | 100% | 0% | 7446160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 103 | 20315881 | 4995 | 119.88 | 4.995 | 4.8 | 4.8 | 2B | 0 | 0 | 1059 | 0 | 1109 | N/A | N/A | N/A | N/A | 33687702 | 698 | 139.7397 | 0% | 0% | 100% | 0% | 100% | 35% | 7446970 | 810 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 90 | 20320691 | 4810 | 115.44 | 4.81 | 5.7 | 5.7 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 33688303 | 601 | 124.948 | 0% | 0% | 100% | 0% | 100% | 35% | 7447920 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.625 | 122653 | 122653 | 122.653 | 122.653 | [12 empty] | 24087 | 24087 | 196.3833 | [6 empty] | 6000 | 6000 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:09 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:52 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:300 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 5, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25546 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20320691 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33688303 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7447920 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 84 | 20323886 | 3195 | 76.68 | 3.195 | 6.9 | 6.9 | 2B | 0 | 0 | 972 | 0 | 1059 | N/A | N/A | N/A | N/A | 33688875 | 572 | 179.0297 | 0% | 0% | 100% | 0% | 100% | 35% | 7449100 | 1180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 80 | 20327076 | 3190 | 76.56 | 3.19 | 7.8 | 7.8 | 2B | 0 | 0 | 950 | 0 | 1059 | N/A | N/A | N/A | N/A | 33689443 | 568 | 178.0564 | 0% | 0% | 100% | 0% | 100% | 35% | 7450265 | 1165 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 83 | 20330262 | 3186 | 76.464 | 3.186 | 8.9 | 8.9 | 2B | 0 | 0 | 909 | 0 | 1059 | N/A | N/A | N/A | N/A | 33690005 | 562 | 176.3967 | 0% | 0% | 100% | 0% | 100% | 35% | 7451408 | 1143 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 85 | 20333420 | 3158 | 75.792 | 3.158 | 9.5 | 9.5 | 2B | 0 | 0 | 860 | 0 | 1059 | N/A | N/A | N/A | N/A | 33690552 | 547 | 173.2109 | 0% | 0% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 96 | 20337234 | 3814 | 91.536 | 3.814 | 9.5 | 9.5 | 2B | 0 | 0 | 906 | 0 | 1058 | N/A | N/A | N/A | N/A | 33691068 | 516 | 135.291 | 0% | 0% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 116 | 20341695 | 4461 | 107.064 | 4.461 | 9.5 | 9.5 | 2B | 0 | 0 | 1092 | 0 | 1139 | N/A | N/A | N/A | N/A | 33691732 | 664 | 148.8456 | 0% | 0% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 122 | 20347702 | 6007 | 144.168 | 6.007 | 9.2 | 9.2 | 3B+1S | 0 | 1024 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33693055 | 1323 | 220.243 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 20353710 | 6008 | 144.192 | 6.008 | 8.9 | 8.9 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33694378 | 1323 | 220.2064 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 20359810 | 6100 | 146.4 | 6.1 | 8.3 | 8.3 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33695724 | 1346 | 220.6557 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 20366003 | 6193 | 148.632 | 6.193 | 7.6 | 7.6 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33697112 | 1388 | 224.124 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 154 | 20372301 | 6298 | 151.152 | 6.298 | 6.9 | 6.9 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33698516 | 1404 | 222.9279 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 20378600 | 6299 | 151.176 | 6.299 | 6.4 | 6.4 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33699920 | 1404 | 222.8925 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 20384507 | 5907 | 141.768 | 5.907 | 6.1 | 6.1 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33701252 | 1332 | 225.4952 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 20390367 | 5860 | 140.64 | 5.86 | 5.7 | 5.7 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33702580 | 1328 | 226.6212 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 20396071 | 5704 | 136.896 | 5.704 | 5.5 | 5.5 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33703900 | 1320 | 231.4165 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 20401686 | 5615 | 134.76 | 5.615 | 5.2 | 5.2 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33705224 | 1324 | 235.797 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 137 | 20407461 | 5775 | 138.6 | 5.775 | 4.9 | 4.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33706548 | 1324 | 229.2641 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 20413191 | 5730 | 137.52 | 5.73 | 4.6 | 4.6 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33707872 | 1324 | 231.0646 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 133 | 20418847 | 5656 | 135.744 | 5.656 | 4.4 | 4.4 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33709180 | 1308 | 231.2588 | 0% | 100% | 100% | 100% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 20424354 | 5507 | 132.168 | 5.507 | 3.5 | 3.5 | 2B+1S | 0 | 1130 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33710288 | 1108 | 201.1985 | 0% | 100% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 20429789 | 5435 | 130.44 | 5.435 | 2.7 | 2.7 | 2B+1S | 0 | 1081 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33711372 | 1084 | 199.448 | 0% | 100% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 118 | 20434943 | 5154 | 123.696 | 5.154 | 2.3 | 2.3 | 2B+1S | 0 | 1004 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33712396 | 1024 | 198.6806 | 0% | 100% | 100% | 0% | 100% | 0% | 7451408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 102 | 20439296 | 4353 | 104.472 | 4.353 | 2.9 | 2.9 | 2B | 0 | 0 | 1096 | 0 | 1109 | N/A | N/A | N/A | N/A | 33713164 | 768 | 176.43 | 0% | 0% | 100% | 0% | 100% | 30% | 7452068 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 94 | 20443383 | 4087 | 98.088 | 4.087 | 3.7 | 3.7 | 2B | 0 | 0 | 1049 | 0 | 1059 | N/A | N/A | N/A | N/A | 33713849 | 685 | 167.6046 | 0% | 0% | 100% | 0% | 100% | 30% | 7452885 | 817 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.4583 | 122692 | 122692 | 122.692 | 122.692 | [12 empty] | 25546 | 25546 | 208.2124 | [6 empty] | 4965 | 4965 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 6, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25759 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20443383 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33713849 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7452885 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 94 | 20447297 | 3914 | 93.936 | 3.914 | 4.7 | 4.7 | 2B | 0 | 0 | 1077 | 0 | 1059 | N/A | N/A | N/A | N/A | 33714477 | 628 | 160.4497 | 0% | 0% | 100% | 0% | 100% | 35% | 7453892 | 1007 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 20451032 | 3735 | 89.64 | 3.735 | 5.9 | 5.9 | 2B | 0 | 0 | 1077 | 0 | 1059 | N/A | N/A | N/A | N/A | 33715066 | 589 | 157.6975 | 0% | 0% | 100% | 0% | 100% | 35% | 7454991 | 1099 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 20454601 | 3569 | 85.656 | 3.569 | 7.3 | 7.3 | 2B | 0 | 0 | 1048 | 0 | 1059 | N/A | N/A | N/A | N/A | 33715628 | 562 | 157.4671 | 0% | 0% | 100% | 0% | 100% | 35% | 7456219 | 1228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 88 | 20458068 | 3467 | 83.208 | 3.467 | 8.6 | 8.6 | 2B | 0 | 0 | 988 | 0 | 988 | N/A | N/A | N/A | N/A | 33716160 | 532 | 153.4468 | 0% | 0% | 100% | 0% | 100% | 35% | 7457348 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 95 | 20461954 | 3886 | 93.264 | 3.886 | 9.5 | 9.5 | 2B | 0 | 0 | 1091 | 0 | 987 | N/A | N/A | N/A | N/A | 33716732 | 572 | 147.1951 | 0% | 0% | 100% | 0% | 100% | 35% | 7458306 | 958 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 115 | 20466673 | 4719 | 113.256 | 4.719 | 9.5 | 9.5 | 2B | 0 | 0 | 1133 | 0 | 1129 | N/A | N/A | N/A | N/A | 33717476 | 744 | 157.6605 | 0% | 0% | 100% | 0% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 144 | 20472378 | 5705 | 136.92 | 5.705 | 9.4 | 9.4 | 3B+1S | 0 | 992 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33718732 | 1256 | 220.1578 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 20478532 | 6154 | 147.696 | 6.154 | 9 | 9 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33720100 | 1368 | 222.2944 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 20484803 | 6271 | 150.504 | 6.271 | 8.3 | 8.3 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33721500 | 1400 | 223.2499 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 20490919 | 6116 | 146.784 | 6.116 | 7.6 | 7.6 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33722880 | 1380 | 225.6377 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 20497179 | 6260 | 150.24 | 6.26 | 7 | 7 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33724276 | 1396 | 223.0032 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 139 | 20503097 | 5918 | 142.032 | 5.918 | 6.4 | 6.4 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33725640 | 1364 | 230.4833 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 20508924 | 5827 | 139.848 | 5.827 | 6.1 | 6.1 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33726972 | 1332 | 228.591 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 20514911 | 5987 | 143.688 | 5.987 | 5.6 | 5.6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33728348 | 1376 | 229.8313 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 134 | 20520583 | 5672 | 136.128 | 5.672 | 5.4 | 5.4 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33729671 | 1323 | 233.2511 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 20526233 | 5650 | 135.6 | 5.65 | 5.3 | 5.3 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33730988 | 1317 | 233.0973 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 139 | 20531899 | 5666 | 135.984 | 5.666 | 4.9 | 4.9 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33732308 | 1320 | 232.9686 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 20537752 | 5853 | 140.472 | 5.853 | 4.3 | 4.3 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33733676 | 1368 | 233.7263 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 20543293 | 5541 | 132.984 | 5.541 | 3.9 | 3.9 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33734852 | 1176 | 212.2361 | 0% | 100% | 100% | 100% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 130 | 20548835 | 5542 | 133.008 | 5.542 | 3.2 | 3.2 | 2B+1S | 0 | 1113 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33736028 | 1176 | 212.1978 | 0% | 100% | 100% | 0% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 20554168 | 5333 | 127.992 | 5.333 | 2.3 | 2.3 | 2B+1S | 0 | 1029 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33737088 | 1060 | 198.7624 | 0% | 100% | 100% | 0% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 120 | 20559501 | 5333 | 127.992 | 5.333 | 2 | 2 | 2B+1S | 0 | 1010 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33738148 | 1060 | 198.7624 | 0% | 100% | 100% | 0% | 100% | 0% | 7458306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 109 | 90 | 20563724 | 4223 | 101.352 | 4.223 | 2.9 | 2.9 | 2B | 0 | 0 | 1039 | 0 | 1110 | N/A | N/A | N/A | N/A | 33738938 | 790 | 187.0708 | 0% | 0% | 100% | 0% | 100% | 35% | 7459206 | 900 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 103 | 91 | 20567907 | 4183 | 100.392 | 4.183 | 3.9 | 3.9 | 2B | 0 | 0 | 1010 | 0 | 1110 | N/A | N/A | N/A | N/A | 33739608 | 670 | 160.1721 | 0% | 0% | 100% | 0% | 100% | 35% | 7460146 | 940 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.25 | 124524 | 124524 | 124.524 | 124.524 | [12 empty] | 25759 | 25759 | 206.8597 | [6 empty] | 7261 | 7261 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 6, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | R. REGENCIA / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25676 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20567907 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33739608 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7460146 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 89 | 20571880 | 3973 | 95.352 | 3.973 | 5.8 | 5.8 | 2B | 0 | 0 | 998 | 0 | 1109 | N/A | N/A | N/A | N/A | 33740248 | 640 | 161.0873 | 0% | 0% | 100% | 0% | 100% | 35% | 7461280 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 20575755 | 3875 | 93 | 3.875 | 6.9 | 6.9 | 2B | 0 | 0 | 971 | 0 | 1109 | N/A | N/A | N/A | N/A | 33740868 | 620 | 160 | 0% | 0% | 100% | 0% | 100% | 35% | 7462393 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 20579575 | 3820 | 91.68 | 3.82 | 8.7 | 8.7 | 2B | 0 | 0 | 969 | 0 | 1110 | N/A | N/A | N/A | N/A | 33741479 | 611 | 159.9476 | 0% | 0% | 100% | 0% | 100% | 35% | 7463517 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 93 | 20583434 | 3859 | 92.616 | 3.859 | 9.5 | 9.5 | 2B | 0 | 0 | 952 | 0 | 1109 | N/A | N/A | N/A | N/A | 33742077 | 598 | 154.9624 | 0% | 0% | 100% | 0% | 100% | 35% | 7464637 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 101 | 20587272 | 3838 | 92.112 | 3.838 | 9.5 | 9.5 | 2B | 0 | 0 | 939 | 0 | 1110 | N/A | N/A | N/A | N/A | 33742712 | 635 | 165.4508 | 0% | 0% | 100% | 0% | 100% | 35% | 7465404 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | R. REGENCIA / G. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 115 | 20591938 | 4666 | 111.984 | 4.666 | 9.5 | 9.5 | 2B | 0 | 0 | 1152 | 0 | 1110 | N/A | N/A | N/A | N/A | 33743452 | 740 | 158.5941 | 0% | 0% | 100% | 0% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 118 | 147 | 20597958 | 6020 | 144.48 | 6.02 | 9.1 | 9.1 | 3B+1S | 0 | 1068 | 1178 | 1185 | 1189 | N/A | N/A | N/A | N/A | 33744781 | 1329 | 220.7641 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 20603996 | 6038 | 144.912 | 6.038 | 8.6 | 8.6 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33746120 | 1339 | 221.7622 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 152 | 20610001 | 6005 | 144.12 | 6.005 | 8 | 8 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33747468 | 1348 | 224.4796 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 20616152 | 6151 | 147.624 | 6.151 | 7.3 | 7.3 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33748856 | 1388 | 225.6544 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 20622305 | 6153 | 147.672 | 6.153 | 6.8 | 6.8 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33750236 | 1380 | 224.2808 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 20628442 | 6137 | 147.288 | 6.137 | 6.2 | 6.2 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33751636 | 1400 | 228.1245 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 139 | 20634080 | 5638 | 135.312 | 5.638 | 6.1 | 6.1 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33752932 | 1296 | 229.8687 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 130 | 20639712 | 5632 | 135.168 | 5.632 | 5.9 | 5.9 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33754244 | 1312 | 232.9545 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 20645603 | 5891 | 141.384 | 5.891 | 5.8 | 5.8 | 3B+1S | 0 | 991 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33755604 | 1360 | 230.8606 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 20650976 | 5373 | 128.952 | 5.373 | 5.8 | 5.8 | 3B+1S | 0 | 991 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 33756852 | 1248 | 232.2725 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 129 | 20656559 | 5583 | 133.992 | 5.583 | 5.4 | 5.4 | 3B+1S | 0 | 1048 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33758148 | 1296 | 232.1333 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 20662132 | 5573 | 133.752 | 5.573 | 5.2 | 5.2 | 3B+1S | 0 | 978 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33759428 | 1280 | 229.6788 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 20667626 | 5494 | 131.856 | 5.494 | 5.2 | 5.2 | 3B+1S | 0 | 950 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33760692 | 1264 | 230.0692 | 0% | 100% | 100% | 100% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 120 | 20672955 | 5329 | 127.896 | 5.329 | 4.6 | 4.6 | 2B+1S | 0 | 1070 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33761764 | 1072 | 201.1634 | 0% | 100% | 100% | 0% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 121 | 20678339 | 5384 | 129.216 | 5.384 | 3.7 | 3.7 | 2B+1S | 0 | 1001 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33762844 | 1080 | 200.5944 | 0% | 100% | 100% | 0% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 117 | 20683376 | 5037 | 120.888 | 5.037 | 3.6 | 3.6 | 2B+1S | 0 | 980 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 33763840 | 996 | 197.7367 | 0% | 100% | 100% | 0% | 100% | 0% | 7465404 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 97 | 20687639 | 4263 | 102.312 | 4.263 | 4.1 | 4.1 | 2B | 0 | 0 | 1050 | 0 | 1100 | N/A | N/A | N/A | N/A | 33764596 | 756 | 177.3399 | 0% | 0% | 100% | 0% | 100% | 25% | 7465848 | 444 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 85 | 20691749 | 4110 | 98.64 | 4.11 | 4.9 | 4.9 | 2B | 0 | 0 | 999 | 0 | 1100 | N/A | N/A | N/A | N/A | 33765284 | 688 | 167.3966 | 0% | 0% | 100% | 0% | 100% | 25% | 7466507 | 659 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.6667 | 123842 | 123842 | 123.842 | 123.842 | [12 empty] | 25676 | 25676 | 207.3287 | [6 empty] | 6361 | 6361 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 PM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 8, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 PM, NORMAL OPERATION
NORMAL OPERATION

## JAN 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25312 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20691749 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33765284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7466507 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 91 | 20695206 | 3457 | 82.968 | 3.457 | 5.7 | 5.7 | 2B | 0 | 0 | 1004 | 0 | 1047 | N/A | N/A | N/A | N/A | 33765852 | 568 | 164.3043 | 0% | 0% | 100% | 0% | 100% | 35% | 7467386 | 879 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 85 | 20698646 | 3440 | 82.56 | 3.44 | 6.8 | 6.8 | 2B | 0 | 0 | 957 | 0 | 1047 | N/A | N/A | N/A | N/A | 33766396 | 544 | 158.1395 | 0% | 0% | 100% | 0% | 100% | 35% | 7468403 | 1017 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 89 | 20702332 | 3686 | 88.464 | 3.686 | 8 | 8 | 2B | 0 | 0 | 953 | 0 | 1027 | N/A | N/A | N/A | N/A | 33766956 | 560 | 151.9262 | 0% | 0% | 100% | 0% | 100% | 35% | 7469515 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 87 | 20705993 | 3661 | 87.864 | 3.661 | 8.9 | 8.9 | 2B | 0 | 0 | 963 | 0 | 1027 | N/A | N/A | N/A | N/A | 33767500 | 544 | 148.5933 | 0% | 0% | 100% | 0% | 100% | 35% | 7470509 | 994 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 98 | 20709539 | 3546 | 85.104 | 3.546 | 9.5 | 9.5 | 2B | 0 | 0 | 961 | 0 | 1027 | N/A | N/A | N/A | N/A | 33768008 | 508 | 143.26 | 0% | 0% | 100% | 0% | 100% | 35% | 7471026 | 517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 112 | 20714029 | 4490 | 107.76 | 4.49 | 9.5 | 9.5 | 2B | 0 | 0 | 1183 | 0 | 1079 | N/A | N/A | N/A | N/A | 33768724 | 716 | 159.4655 | 0% | 0% | 100% | 0% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 149 | 20719971 | 5942 | 142.608 | 5.942 | 9.4 | 9.4 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33770040 | 1316 | 221.4743 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 20726125 | 6154 | 147.696 | 6.154 | 8.8 | 8.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33771416 | 1376 | 223.5944 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 20732125 | 6000 | 144 | 6 | 8.3 | 8.3 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33772772 | 1356 | 226 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 20738232 | 6107 | 146.568 | 6.107 | 7.6 | 7.6 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33774148 | 1376 | 225.3152 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 20744371 | 6139 | 147.336 | 6.139 | 7.2 | 7.2 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33775524 | 1376 | 224.1407 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 138 | 20750272 | 5901 | 141.624 | 5.901 | 6.6 | 6.6 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33776876 | 1352 | 229.1137 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 138 | 20756271 | 5999 | 143.976 | 5.999 | 6.4 | 6.4 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33778242 | 1366 | 227.7046 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 134 | 20762260 | 5989 | 143.736 | 5.989 | 6.2 | 6.2 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33779608 | 1366 | 228.0848 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 132 | 20767615 | 5355 | 128.52 | 5.355 | 6.1 | 6.1 | 3B+1S | 0 | 986 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33780840 | 1232 | 230.0654 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 20773124 | 5509 | 132.216 | 5.509 | 6 | 6 | 3B+1S | 0 | 995 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33782072 | 1232 | 223.6341 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 135 | 20778795 | 5671 | 136.104 | 5.671 | 5.7 | 5.7 | 3B+1S | 0 | 1062 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33783368 | 1296 | 228.5311 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 20784598 | 5803 | 139.272 | 5.803 | 5.5 | 5.5 | 3B+1S | 0 | 1000 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33784676 | 1308 | 225.4007 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 20790036 | 5438 | 130.512 | 5.438 | 5.3 | 5.3 | 3B+1S | 0 | 984 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33785924 | 1248 | 229.4961 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 111 | 128 | 20795967 | 5931 | 142.344 | 5.931 | 4.7 | 4.7 | 2B+1S | 0 | 1078 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33787024 | 1100 | 185.4662 | 0% | 100% | 100% | 0% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 20800800 | 4833 | 115.992 | 4.833 | 3.9 | 3.9 | 2B+1S | 0 | 1003 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33788108 | 1084 | 224.2913 | 0% | 100% | 100% | 0% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 119 | 20805805 | 5005 | 120.12 | 5.005 | 3.6 | 3.6 | 2B+1S | 0 | 1003 | 0 | 1185 | 1199 | N/A | N/A | N/A | N/A | 33789112 | 1004 | 200.5994 | 0% | 100% | 0% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 104 | 20810226 | 4421 | 106.104 | 4.421 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 982 | N/A | N/A | N/A | N/A | 33789892 | 780 | 176.4307 | 0% | 0% | 0% | 100% | 100% | 25% | 7471486 | 460 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 102 | 20814272 | 4046 | 97.104 | 4.046 | 4.8 | 4.8 | 2B | 0 | 0 | 962 | 1185 | 0 | N/A | N/A | N/A | N/A | 33790596 | 704 | 173.999 | 0% | 0% | 100% | 100% | 0% | 25% | 7472012 | 526 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0417 | 122523 | 122523 | 122.523 | 122.523 | [12 empty] | 25312 | 25312 | 206.5898 | [6 empty] | 5505 | 5505 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 33% @ 12:01 AM
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
BP1 - STOPPED @ 9:01 PM
BP2 - RESTRATED @ 9:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
BP1 - RESTARTED @ 11:01 PM
BP3 - STOPPED @ 11:01 PM
NORMAL OPERATION

## JAN 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24660 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20814272 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33790596 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7472012 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 85 | 20818147 | 3875 | 93 | 3.875 | 5.7 | 5.7 | 2B | 0 | 0 | 998 | 0 | 1059 | N/A | N/A | N/A | N/A | 33791288 | 692 | 178.5806 | 0% | 0% | 100% | 0% | 100% | 35% | 7473044 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 85 | 20821936 | 3789 | 90.936 | 3.789 | 7 | 7 | 2B | 0 | 0 | 1008 | 0 | 1008 | N/A | N/A | N/A | N/A | 33791892 | 604 | 159.4088 | 0% | 0% | 100% | 0% | 100% | 35% | 7474180 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 81 | 20825275 | 3339 | 80.136 | 3.339 | 8 | 8 | 2B | 0 | 0 | 972 | 0 | 1008 | N/A | N/A | N/A | N/A | 33792396 | 504 | 150.9434 | 0% | 0% | 100% | 0% | 100% | 35% | 7475240 | 1060 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 87 | 20828731 | 3456 | 82.944 | 3.456 | 9.1 | 9.1 | 2B | 0 | 0 | 1012 | 0 | 998 | N/A | N/A | N/A | N/A | 33792908 | 512 | 148.1481 | 0% | 0% | 100% | 0% | 100% | 35% | 7476248 | 1008 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 94 | 20832530 | 3799 | 91.176 | 3.799 | 9.5 | 9.5 | 2B | 0 | 0 | 999 | 0 | 998 | N/A | N/A | N/A | N/A | 33793440 | 532 | 140.0369 | 0% | 0% | 100% | 0% | 100% | 35% | 7476580 | 332 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 108 | 20836924 | 4394 | 105.456 | 4.394 | 9.5 | 9.5 | 2B | 0 | 0 | 1089 | 0 | 1110 | N/A | N/A | N/A | N/A | 33794116 | 676 | 153.8462 | 0% | 0% | 100% | 0% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 140 | 20842849 | 5925 | 142.2 | 5.925 | 9.1 | 9.1 | 3B+1S | 0 | 996 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33795390 | 1274 | 215.0211 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 150 | 20848774 | 5925 | 142.2 | 5.925 | 8.8 | 8.8 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33796664 | 1274 | 215.0211 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 20854936 | 6162 | 147.888 | 6.162 | 8 | 8 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33798020 | 1356 | 220.0584 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 20861041 | 6105 | 146.52 | 6.105 | 7.5 | 7.5 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33799384 | 1364 | 223.4234 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 144 | 20867117 | 6076 | 145.824 | 6.076 | 7.1 | 7.1 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33800740 | 1356 | 223.1731 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 20873171 | 6054 | 145.296 | 6.054 | 6.7 | 6.7 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33802116 | 1376 | 227.2877 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 20878841 | 5670 | 136.08 | 5.67 | 6.6 | 6.6 | 3B+1S | 0 | 913 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33803420 | 1304 | 229.9824 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 129 | 20884477 | 5636 | 135.264 | 5.636 | 6.4 | 6.4 | 3B+1S | 0 | 988 | 1135 | 1185 | 1135 | N/A | N/A | N/A | N/A | 33804668 | 1248 | 221.4336 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 131 | 20889875 | 5398 | 129.552 | 5.398 | 6.2 | 6.2 | 3B+1S | 0 | 1016 | 1135 | 1185 | 1135 | N/A | N/A | N/A | N/A | 33805844 | 1176 | 217.8585 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 132 | 20895355 | 5480 | 131.52 | 5.48 | 5.9 | 5.9 | 3B+1S | 0 | 1026 | 1135 | 1185 | 1135 | N/A | N/A | N/A | N/A | 33807048 | 1204 | 219.708 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 20900941 | 5586 | 134.064 | 5.586 | 5.3 | 5.3 | 3B+1S | 0 | 1019 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33808308 | 1260 | 225.5639 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 131 | 20906423 | 5482 | 131.568 | 5.482 | 5.1 | 5.1 | 3B+1S | 0 | 1001 | 1145 | 1185 | 1158 | N/A | N/A | N/A | N/A | 33809548 | 1240 | 226.1948 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 129 | 20911864 | 5441 | 130.584 | 5.441 | 4.9 | 4.9 | 3B+1S | 0 | 982 | 1145 | 1185 | 1158 | N/A | N/A | N/A | N/A | 33810772 | 1224 | 224.9586 | 0% | 100% | 100% | 100% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 126 | 20917131 | 5267 | 126.408 | 5.267 | 4.4 | 4.4 | 2B+1S | 0 | 1054 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33811840 | 1068 | 202.772 | 0% | 100% | 100% | 0% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 126 | 20922367 | 5236 | 125.664 | 5.236 | 3.7 | 3.7 | 2B+1S | 0 | 1019 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33812888 | 1048 | 200.1528 | 0% | 100% | 100% | 0% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 131 | 20927400 | 5033 | 120.792 | 5.033 | 3.5 | 3.5 | 2B+1S | 0 | 1000 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 33813892 | 1004 | 199.4834 | 0% | 100% | 100% | 0% | 100% | 0% | 7476580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 101 | 114 | 20931660 | 4260 | 102.24 | 4.26 | 4.1 | 4.1 | 2B | 0 | 0 | 1085 | 0 | 1050 | N/A | N/A | N/A | N/A | 33814620 | 728 | 170.892 | 0% | 0% | 100% | 0% | 100% | 25% | 7477109 | 529 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 97 | 110 | 20935615 | 3955 | 94.92 | 3.955 | 4.8 | 4.8 | 2B | 0 | 0 | 1017 | 0 | 1058 | N/A | N/A | N/A | N/A | 33815256 | 636 | 160.8091 | 0% | 0% | 100% | 0% | 100% | 25% | 7477697 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.875 | 121343 | 121343 | 121.343 | 121.343 | [12 empty] | 24660 | 24660 | 203.2256 | [6 empty] | 5685 | 5685 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
BP3 - STARTED @ 1:01 AM
BP2 - STOPPED @ 1:01 AM
XCV1 CLOSED @ 4:21 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 10, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25404 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20935615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33815256 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7477697 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 97 | 20939364 | 3749 | 89.976 | 3.749 | 5.7 | 5.7 | 2B | 0 | 0 | 1003 | 0 | 1058 | N/A | N/A | N/A | N/A | 33815860 | 604 | 161.1096 | 0% | 0% | 100% | 0% | 100% | 35% | 7478559 | 862 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 20943001 | 3637 | 87.288 | 3.637 | 6.8 | 6.8 | 2B | 0 | 0 | 981 | 0 | 1038 | N/A | N/A | N/A | N/A | 33816424 | 564 | 155.0729 | 0% | 0% | 100% | 0% | 100% | 35% | 7479700 | 1141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 85 | 20946416 | 3415 | 81.96 | 3.415 | 7.9 | 7.9 | 2B | 0 | 0 | 965 | 0 | 1009 | N/A | N/A | N/A | N/A | 33816940 | 516 | 151.0981 | 0% | 0% | 100% | 0% | 100% | 35% | 7480853 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 88 | 20949981 | 3565 | 85.56 | 3.565 | 9.2 | 9.2 | 2B | 0 | 0 | 998 | 0 | 987 | N/A | N/A | N/A | N/A | 33817472 | 532 | 149.2286 | 0% | 0% | 100% | 0% | 100% | 35% | 7481953 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 91 | 20953740 | 3759 | 90.216 | 3.759 | 9.5 | 9.5 | 2B | 0 | 0 | 982 | 0 | 907 | N/A | N/A | N/A | N/A | 33817972 | 500 | 133.0141 | 0% | 0% | 100% | 0% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 | 104 | 20957963 | 4223 | 101.352 | 4.223 | 9.5 | 9.5 | 2B | 0 | 0 | 1055 | 0 | 1008 | N/A | N/A | N/A | N/A | 33818532 | 560 | 132.6072 | 0% | 0% | 100% | 0% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 136 | 20963532 | 5569 | 133.656 | 5.569 | 9.5 | 9.5 | 3B | 0 | 0 | 1173 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33819692 | 1160 | 208.2959 | 0% | 0% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 146 | 20969651 | 6119 | 146.856 | 6.119 | 9.3 | 9.3 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33821044 | 1352 | 220.9511 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 20975887 | 6236 | 149.664 | 6.236 | 8.7 | 8.7 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33822428 | 1384 | 221.9371 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 152 | 20982270 | 6383 | 153.192 | 6.383 | 7.8 | 7.8 | 3B+1S | 0 | 1170 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33823868 | 1440 | 225.5992 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 20988610 | 6340 | 152.16 | 6.34 | 6.8 | 6.8 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33825304 | 1436 | 226.4984 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 149 | 20994946 | 6336 | 152.064 | 6.336 | 5.8 | 5.8 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33826756 | 1452 | 229.1667 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 144 | 21001022 | 6076 | 145.824 | 6.076 | 5.2 | 5.2 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33828148 | 1392 | 229.0981 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 21006799 | 5777 | 138.648 | 5.777 | 4 | 4 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33829488 | 1340 | 231.9543 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 21012465 | 5666 | 135.984 | 5.666 | 4.2 | 4.2 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33830816 | 1328 | 234.3805 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 21018255 | 5790 | 138.96 | 5.79 | 3.8 | 3.8 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33832152 | 1336 | 230.7427 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 136 | 21023971 | 5716 | 137.184 | 5.716 | 3.3 | 3.3 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33833492 | 1340 | 234.4297 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 21029597 | 5626 | 135.024 | 5.626 | 3.1 | 3.1 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33834812 | 1320 | 234.625 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 132 | 21035289 | 5692 | 136.608 | 5.692 | 2.9 | 2.9 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33836136 | 1324 | 232.6072 | 0% | 100% | 100% | 100% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 125 | 21040572 | 5283 | 126.792 | 5.283 | 2.4 | 2.4 | 2B+1S | 0 | 1080 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33837224 | 1088 | 205.9436 | 0% | 100% | 100% | 0% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 21045700 | 5128 | 123.072 | 5.128 | 1.9 | 1.9 | 2B+1S | 0 | 1030 | 1195 | 0 | 1195 | N/A | N/A | N/A | N/A | 33838244 | 1020 | 198.908 | 0% | 100% | 100% | 0% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 137 | 117 | 21050650 | 4950 | 118.8 | 4.95 | 1.7 | 1.7 | 2B+1S | 0 | 999 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33839236 | 992 | 200.404 | 0% | 100% | 100% | 0% | 100% | 0% | 7481953 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 98 | 21054909 | 4259 | 102.216 | 4.259 | 2.4 | 2.4 | 2B | 0 | 0 | 1094 | 0 | 1090 | N/A | N/A | N/A | N/A | 33839988 | 752 | 176.5673 | 0% | 0% | 100% | 0% | 100% | 25% | 7482999 | 1046 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 93 | 21058918 | 4009 | 96.216 | 4.009 | 3.2 | 3.2 | 2B | 0 | 0 | 1084 | 0 | 1059 | N/A | N/A | N/A | N/A | 33840660 | 672 | 167.6228 | 0% | 0% | 100% | 0% | 100% | 25% | 7483834 | 835 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.2083 | 123303 | 123303 | 123.303 | 123.303 | [12 empty] | 25404 | 25404 | 206.0291 | [6 empty] | 6137 | 6137 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:40 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 11, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24688 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21058918 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33840660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7483834 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 88 | 21062822 | 3904 | 93.696 | 3.904 | 4.4 | 4.4 | 2B | 0 | 0 | 1054 | 0 | 1059 | N/A | N/A | N/A | N/A | 33841316 | 656 | 168.0328 | 0% | 0% | 100% | 0% | 100% | 35% | 7484840 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 86 | 21066452 | 3630 | 87.12 | 3.63 | 5.4 | 5.4 | 2B | 0 | 0 | 1010 | 0 | 1059 | N/A | N/A | N/A | N/A | 33841908 | 592 | 163.0854 | 0% | 0% | 100% | 0% | 100% | 35% | 7485871 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 81 | 21069981 | 3529 | 84.696 | 3.529 | 6.6 | 6.6 | 2B | 0 | 0 | 1005 | 0 | 1008 | N/A | N/A | N/A | N/A | 33842468 | 560 | 158.6852 | 0% | 0% | 100% | 0% | 100% | 35% | 7486952 | 1081 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 85 | 21073592 | 3611 | 86.664 | 3.611 | 7.1 | 7.1 | 2B | 0 | 0 | 964 | 0 | 1008 | N/A | N/A | N/A | N/A | 33843020 | 552 | 152.8662 | 0% | 0% | 100% | 0% | 100% | 35% | 7488133 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 127 | 90 | 21077085 | 3493 | 83.832 | 3.493 | 9.2 | 9.2 | 2B | 0 | 0 | 951 | 0 | 988 | N/A | N/A | N/A | N/A | 33843564 | 544 | 155.7401 | 0% | 0% | 100% | 0% | 100% | 35% | 7489248 | 1115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 31 | 21.831 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 99 | 21081083 | 3998 | 95.952 | 3.998 | 9.5 | 9.5 | 2B | 0 | 0 | 984 | 0 | 908 | N/A | N/A | N/A | N/A | 33844036 | 472 | 118.059 | 0% | 0% | 100% | 0% | 100% | 35% | 7489400 | 152 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 134 | 21086254 | 5171 | 124.104 | 5.171 | 9.5 | 9.5 | 3B | 0 | 0 | 1073 | 1185 | 1109 | N/A | N/A | N/A | N/A | 33844980 | 944 | 182.5566 | 0% | 0% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 141 | 21091944 | 5690 | 136.56 | 5.69 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33846148 | 1168 | 205.2724 | 0% | 0% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 150 | 21098129 | 6185 | 148.44 | 6.185 | 9 | 9 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33847542 | 1394 | 225.384 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 151 | 21104315 | 6186 | 148.464 | 6.186 | 8.2 | 8.2 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33848936 | 1394 | 225.3476 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 21110484 | 6169 | 148.056 | 6.169 | 7.3 | 7.3 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33850344 | 1408 | 228.238 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 21116770 | 6286 | 150.864 | 6.286 | 6.5 | 6.5 | 3B+1S | 0 | 1147 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33851772 | 1428 | 227.1715 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 21122711 | 5941 | 142.584 | 5.941 | 6 | 6 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33853132 | 1360 | 228.9177 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 21128472 | 5761 | 138.264 | 5.761 | 5.7 | 5.7 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33854452 | 1320 | 229.1269 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 21134187 | 5715 | 137.16 | 5.715 | 5.3 | 5.3 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33855742 | 1290 | 225.7218 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 21139816 | 5629 | 135.096 | 5.629 | 5.1 | 5.1 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33857002 | 1260 | 223.8408 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 21145322 | 5506 | 132.144 | 5.506 | 4.9 | 4.9 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33858360 | 1358 | 246.64 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 148 | 21151111 | 5789 | 138.936 | 5.789 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33859658 | 1298 | 224.2183 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 131 | 21156625 | 5514 | 132.336 | 5.514 | 4.5 | 4.5 | 3B+1S | 0 | 992 | 1144 | 1185 | 1149 | N/A | N/A | N/A | N/A | 33860956 | 1298 | 235.4008 | 0% | 100% | 100% | 100% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 129 | 21161875 | 5250 | 126 | 5.25 | 4 | 4 | 2B+1S | 0 | 1044 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33862012 | 1056 | 201.1429 | 0% | 100% | 100% | 0% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 117 | 21167206 | 5331 | 127.944 | 5.331 | 3.4 | 3.4 | 2B+1S | 0 | 1015 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33863068 | 1056 | 198.0867 | 0% | 100% | 100% | 0% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 113 | 21172111 | 4905 | 117.72 | 4.905 | 3.3 | 3.3 | 2B+1S | 0 | 799 | 1196 | 0 | 1109 | N/A | N/A | N/A | N/A | 33864012 | 944 | 192.4567 | 0% | 100% | 100% | 0% | 100% | 0% | 7489400 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 100 | 21176265 | 4154 | 99.696 | 4.154 | 3.9 | 3.9 | 2B | 0 | 0 | 1037 | 0 | 1110 | N/A | N/A | N/A | N/A | 33864708 | 696 | 167.5494 | 0% | 0% | 100% | 0% | 100% | 25% | 7489955 | 555 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 92 | 21180119 | 3854 | 92.496 | 3.854 | 4.6 | 4.6 | 2B | 0 | 0 | 979 | 0 | 1110 | N/A | N/A | N/A | N/A | 33865348 | 640 | 166.0612 | 0% | 0% | 100% | 0% | 100% | 25% | 7490530 | 575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.3333 | 121201 | 121201 | 121.201 | 121.201 | [12 empty] | 24688 | 24688 | 203.6947 | [6 empty] | 6696 | 6696 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @5:06 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:44 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:35 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 12, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25040 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21180119 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33865348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7490530 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 87 | 21183864 | 3745 | 89.88 | 3.745 | 5.6 | 5.6 | 2B | 0 | 0 | 1027 | 0 | 1038 | N/A | N/A | N/A | N/A | 33865972 | 624 | 166.6222 | 0% | 0% | 100% | 0% | 100% | 35% | 7491545 | 1015 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 84 | 21187490 | 3626 | 87.024 | 3.626 | 6.6 | 6.6 | 2B | 0 | 0 | 984 | 0 | 1038 | N/A | N/A | N/A | N/A | 33866540 | 568 | 156.6464 | 0% | 0% | 100% | 0% | 100% | 35% | 7492658 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 85 | 21191028 | 3538 | 84.912 | 3.538 | 7.9 | 7.9 | 2B | 0 | 0 | 957 | 0 | 1038 | N/A | N/A | N/A | N/A | 33867084 | 544 | 153.7592 | 0% | 0% | 100% | 0% | 100% | 35% | 7493800 | 1142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 88 | 21194626 | 3598 | 86.352 | 3.598 | 9 | 9 | 2B | 0 | 0 | 1010 | 0 | 987 | N/A | N/A | N/A | N/A | 33867620 | 536 | 148.9717 | 0% | 0% | 100% | 0% | 100% | 35% | 7494885 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 100 | 21198490 | 3864 | 92.736 | 3.864 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 0 | 997 | N/A | N/A | N/A | N/A | 33868148 | 528 | 136.646 | 0% | 0% | 100% | 0% | 100% | 35% | 7495243 | 358 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 110 | 21203115 | 4625 | 111 | 4.625 | 9.5 | 9.5 | 2B | 0 | 0 | 1120 | 0 | 1095 | N/A | N/A | N/A | N/A | 33868876 | 728 | 157.4054 | 0% | 0% | 100% | 0% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 21209016 | 5901 | 141.624 | 5.901 | 9.3 | 9.3 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33870200 | 1324 | 224.3688 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 148 | 21214917 | 5901 | 141.624 | 5.901 | 8.9 | 8.9 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33871524 | 1324 | 224.3688 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 147 | 21221114 | 6197 | 148.728 | 6.197 | 8.3 | 8.3 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33872916 | 1392 | 224.6248 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 146 | 21227299 | 6185 | 148.44 | 6.185 | 7.6 | 7.6 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33874312 | 1396 | 225.7074 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 21233457 | 6158 | 147.792 | 6.158 | 7 | 7 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33875700 | 1388 | 225.3979 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 134 | 21239386 | 5929 | 142.296 | 5.929 | 6.7 | 6.7 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33877048 | 1348 | 227.3571 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 132 | 21244951 | 5565 | 133.56 | 5.565 | 6.4 | 6.4 | 3B+1S | 0 | 1010 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33878308 | 1260 | 226.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 132 | 21250550 | 5599 | 134.376 | 5.599 | 6.1 | 6.1 | 3B+1S | 0 | 1039 | 1134 | 1185 | 1139 | N/A | N/A | N/A | N/A | 33879546 | 1238 | 221.1109 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 135 | 21256137 | 5587 | 134.088 | 5.587 | 5.7 | 5.7 | 3B+1S | 0 | 1068 | 1134 | 1185 | 1139 | N/A | N/A | N/A | N/A | 33880784 | 1238 | 221.5858 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 21261696 | 5559 | 133.416 | 5.559 | 5.6 | 5.6 | 3B+1S | 0 | 997 | 1175 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33882060 | 1276 | 229.5377 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 115 | 137 | 21267344 | 5648 | 135.552 | 5.648 | 5.3 | 5.3 | 3B+1S | 0 | 1043 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33883356 | 1296 | 229.4618 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 110 | 132 | 21272943 | 5599 | 134.376 | 5.599 | 5.1 | 5.1 | 3B+1S | 0 | 1006 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33884668 | 1312 | 234.3276 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 127 | 21278427 | 5484 | 131.616 | 5.484 | 4.2 | 4.2 | 2B+1S | 0 | 1176 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33885804 | 1136 | 207.1481 | 0% | 100% | 100% | 100% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 127 | 21283805 | 5378 | 129.072 | 5.378 | 3.3 | 3.3 | 2B+1S | 0 | 1104 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33886888 | 1084 | 201.5619 | 0% | 100% | 100% | 0% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 126 | 21289127 | 5322 | 127.728 | 5.322 | 2.6 | 2.6 | 2B+1S | 0 | 1061 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33887956 | 1068 | 200.6764 | 0% | 100% | 100% | 0% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 113 | 21294198 | 5071 | 121.704 | 5.071 | 2.3 | 2.3 | 2B+1S | 0 | 996 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33888980 | 1024 | 201.9326 | 0% | 100% | 100% | 0% | 100% | 0% | 7495243 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 100 | 21298449 | 4251 | 102.024 | 4.251 | 2.9 | 2.9 | 2B | 0 | 0 | 1083 | 0 | 1109 | N/A | N/A | N/A | N/A | 33889724 | 744 | 175.0176 | 0% | 0% | 100% | 0% | 100% | 25% | 7495949 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 90 | 21302379 | 3930 | 94.32 | 3.93 | 3.7 | 3.7 | 2B | 0 | 0 | 1005 | 0 | 1109 | N/A | N/A | N/A | N/A | 33890388 | 664 | 168.9567 | 0% | 0% | 100% | 0% | 100% | 25% | 7496750 | 801 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.75 | 122260 | 122260 | 122.26 | 122.26 | [12 empty] | 25040 | 25040 | 204.8094 | [6 empty] | 6220 | 6220 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21302379 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33890388 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7496750 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 86 | 21306068 | 3689 | 88.536 | 3.689 | 4.9 | 4.9 | 2B | 0 | 0 | 980 | 0 | 1109 | N/A | N/A | N/A | N/A | 33891012 | 624 | 169.1515 | 0% | 0% | 100% | 0% | 100% | 33% | 7497805 | 1055 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 85 | 21309705 | 3637 | 87.288 | 3.637 | 6.1 | 6.1 | 2B | 0 | 0 | 998 | 0 | 1028 | N/A | N/A | N/A | N/A | 33891600 | 588 | 161.6717 | 0% | 0% | 100% | 0% | 100% | 33% | 7498939 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 87 | 21313253 | 3548 | 85.152 | 3.548 | 7.3 | 7.3 | 2B | 0 | 0 | 963 | 0 | 973 | N/A | N/A | N/A | N/A | 33892144 | 544 | 153.3258 | 0% | 0% | 100% | 0% | 100% | 33% | 7500106 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 87 | 21316863 | 3610 | 86.64 | 3.61 | 8.5 | 8.5 | 2B | 0 | 0 | 996 | 0 | 997 | N/A | N/A | N/A | N/A | 33892676 | 532 | 147.3684 | 0% | 0% | 100% | 0% | 100% | 33% | 7501222 | 1116 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 21320703 | 3840 | 92.16 | 3.84 | 9.5 | 9.5 | 2B | 0 | 0 | 1019 | 0 | 1001 | N/A | N/A | N/A | N/A | 33893244 | 568 | 147.9167 | 0% | 0% | 100% | 0% | 100% | 33% | 7502118 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 113 | 21325300 | 4597 | 110.328 | 4.597 | 9.5 | 9.5 | 2B | 0 | 0 | 1142 | 0 | 1124 | N/A | N/A | N/A | N/A | 33893968 | 724 | 157.494 | 0% | 0% | 100% | 0% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 148 | 21331126 | 5826 | 139.824 | 5.826 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33895252 | 1284 | 220.3913 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 21337296 | 6170 | 148.08 | 6.17 | 8.7 | 8.7 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33896628 | 1376 | 223.0146 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 48 | 21343395 | 6099 | 146.376 | 6.099 | 8.1 | 8.1 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33897992 | 1364 | 223.6432 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 21349551 | 6156 | 147.744 | 6.156 | 7.4 | 7.4 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33899376 | 1384 | 224.8213 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 143 | 21355688 | 6137 | 147.288 | 6.137 | 6.9 | 6.9 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33900756 | 1380 | 224.8656 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 21361508 | 5820 | 139.68 | 5.82 | 6.6 | 6.6 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33902084 | 1328 | 228.1787 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 131 | 21367198 | 5690 | 136.56 | 5.69 | 6.3 | 6.3 | 3B+1S | 0 | 1010 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33903360 | 1276 | 224.2531 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 132 | 21372888 | 5690 | 136.56 | 5.69 | 6.1 | 6.1 | 3B+1S | 0 | 1006 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33904636 | 1276 | 224.2531 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 130 | 21378271 | 5383 | 129.192 | 5.383 | 5.9 | 5.9 | 3B+1S | 0 | 1006 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33905860 | 1224 | 227.3825 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 129 | 21383688 | 5417 | 130.008 | 5.417 | 5.7 | 5.7 | 3B+1S | 0 | 1002 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33907092 | 1232 | 227.4322 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 21389269 | 5581 | 133.944 | 5.581 | 5.4 | 5.4 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33908388 | 1296 | 232.2164 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 133 | 21394840 | 5571 | 133.704 | 5.571 | 5.3 | 5.3 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33909700 | 1312 | 235.5053 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 127 | 21400317 | 5477 | 131.448 | 5.477 | 5.1 | 5.1 | 3B+1S | 0 | 994 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33910992 | 1292 | 235.8956 | 0% | 100% | 100% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 127 | 21405586 | 5269 | 126.456 | 5.269 | 4.3 | 4.3 | 2B+1S | 0 | 1054 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33912064 | 1072 | 203.4542 | 0% | 100% | 100% | 0% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 127 | 21410781 | 5195 | 124.68 | 5.195 | 3.8 | 3.8 | 2B+1S | 0 | 1017 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33913100 | 1036 | 199.4225 | 0% | 100% | 100% | 0% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 116 | 21415809 | 5028 | 120.672 | 5.028 | 3.6 | 3.6 | 2B+1S | 0 | 982 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33914108 | 1008 | 200.4773 | 0% | 100% | 0% | 100% | 100% | 0% | 7502118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 97 | 21420063 | 4254 | 102.096 | 4.254 | 4.1 | 4.1 | 2B | 0 | 0 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 33914836 | 728 | 171.1331 | 0% | 0% | 0% | 100% | 100% | 25% | 7502612 | 494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 96 | 21424242 | 4179 | 100.296 | 4.179 | 4.7 | 4.7 | 2B | 0 | 0 | 1024 | 0 | 1110 | N/A | N/A | N/A | N/A | 33915524 | 688 | 164.6327 | 0% | 0% | 100% | 100% | 0% | 25% | 7503144 | 532 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.5833 | 121863 | 121863 | 121.863 | 121.863 | [12 empty] | 25136 | 25136 | 206.2644 | [6 empty] | 6394 | 6394 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 14, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25408 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21424242 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33915524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7503144 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 103 | 21428183 | 3941 | 94.584 | 3.941 | 5.6 | 5.6 | 2B | 0 | 0 | 1009 | 0 | 1110 | N/A | N/A | N/A | N/A | 33916180 | 656 | 166.4552 | 0% | 0% | 100% | 0% | 100% | 33% | 7504093 | 949 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 92 | 21432033 | 3850 | 92.4 | 3.85 | 6.7 | 6.7 | 2B | 0 | 0 | 1015 | 0 | 1108 | N/A | N/A | N/A | N/A | 33916792 | 612 | 158.961 | 0% | 0% | 100% | 0% | 100% | 33% | 7505118 | 1025 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 90 | 21435813 | 3780 | 90.72 | 3.78 | 7.9 | 7.9 | 2B | 0 | 0 | 992 | 0 | 1029 | N/A | N/A | N/A | N/A | 33917364 | 572 | 151.3228 | 0% | 0% | 100% | 0% | 100% | 33% | 7506223 | 1105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 88 | 21439616 | 3803 | 91.272 | 3.803 | 8.9 | 8.9 | 2B | 0 | 0 | 1006 | 0 | 1018 | N/A | N/A | N/A | N/A | 33917928 | 564 | 148.304 | 0% | 0% | 100% | 0% | 100% | 33% | 7507249 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 96 | 21443486 | 3870 | 92.88 | 3.87 | 9.5 | 9.5 | 2B | 0 | 0 | 985 | 0 | 1008 | N/A | N/A | N/A | N/A | 33918468 | 540 | 139.5349 | 0% | 0% | 100% | 0% | 100% | 33% | 7507699 | 450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 113 | 21448035 | 4549 | 109.176 | 4.549 | 9.5 | 9.5 | 2B | 0 | 0 | 1106 | 0 | 1129 | N/A | N/A | N/A | N/A | 33919164 | 696 | 153.0007 | 0% | 0% | 100% | 0% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 139 | 21453911 | 5876 | 141.024 | 5.876 | 9.4 | 9.4 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33920476 | 1312 | 223.2811 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 21459917 | 6006 | 144.144 | 6.006 | 9 | 9 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33921820 | 1344 | 223.7762 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 21466096 | 6179 | 148.296 | 6.179 | 8.4 | 8.4 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33923204 | 1384 | 223.9845 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 144 | 21472200 | 6104 | 146.496 | 6.104 | 7.8 | 7.8 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33924580 | 1376 | 225.426 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 21478223 | 6023 | 144.552 | 6.023 | 7.1 | 7.1 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33925932 | 1352 | 224.4729 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 21484246 | 6023 | 144.552 | 6.023 | 6.8 | 6.8 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33927284 | 1352 | 224.4729 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 21490082 | 5836 | 140.064 | 5.836 | 6.5 | 6.5 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33928624 | 1340 | 229.6093 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 135 | 21495831 | 5749 | 137.976 | 5.749 | 6.2 | 6.2 | 3B+1S | 0 | 991 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33929948 | 1324 | 230.3009 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 21501374 | 5543 | 133.032 | 5.543 | 6.1 | 6.1 | 3B+1S | 0 | 998 | 1175 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33931196 | 1248 | 225.1488 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 21506915 | 5541 | 132.984 | 5.541 | 5.9 | 5.9 | 3B+1S | 0 | 1007 | 1175 | 1185 | 1181 | N/A | N/A | N/A | N/A | 33932468 | 1272 | 229.5615 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 136 | 21512473 | 5558 | 133.392 | 5.558 | 5.6 | 5.6 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33933764 | 1296 | 233.1774 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 133 | 21518035 | 5562 | 133.488 | 5.562 | 5.5 | 5.5 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33935064 | 1300 | 233.7289 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 129 | 21523524 | 5489 | 131.736 | 5.489 | 5.3 | 5.3 | 3B+1S | 0 | 996 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33936324 | 1260 | 229.55 | 0% | 100% | 100% | 100% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 115 | 127 | 21528852 | 5328 | 127.872 | 5.328 | 4.8 | 4.8 | 2B+1S | 0 | 1054 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33937400 | 1076 | 201.952 | 0% | 100% | 100% | 0% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 123 | 21534079 | 5227 | 125.448 | 5.227 | 4.1 | 4.1 | 2B+1S | 0 | 1029 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33938437 | 1037 | 198.393 | 0% | 100% | 100% | 0% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 120 | 21539027 | 4948 | 118.752 | 4.948 | 3.8 | 3.8 | 2B+1S | 0 | 983 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 33939436 | 999 | 201.8998 | 0% | 100% | 100% | 0% | 100% | 0% | 7507699 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 104 | 21543529 | 4502 | 108.048 | 4.502 | 4.3 | 4.3 | 2B | 0 | 0 | 1086 | 0 | 1110 | N/A | N/A | N/A | N/A | 33940228 | 792 | 175.9218 | 0% | 0% | 100% | 0% | 100% | 25% | 7508139 | 440 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 100 | 21547734 | 4205 | 100.92 | 4.205 | 4.9 | 4.9 | 2B | 0 | 0 | 1032 | 0 | 1109 | N/A | N/A | N/A | N/A | 33940932 | 704 | 167.4197 | 0% | 0% | 100% | 0% | 100% | 25% | 7508653 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0833 | 123492 | 123492 | 123.492 | 123.492 | [12 empty] | 25408 | 25408 | 205.7461 | [6 empty] | 5509 | 5509 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25416 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21547734 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33940932 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7508653 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 93 | 21551744 | 4010 | 96.24 | 4.01 | 5.7 | 5.7 | 2B | 0 | 0 | 1048 | 0 | 1078 | N/A | N/A | N/A | N/A | 33941596 | 664 | 165.586 | 0% | 0% | 100% | 0% | 100% | 35% | 7509555 | 902 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 81 | 21555608 | 3864 | 92.736 | 3.864 | 6.7 | 6.7 | 2B | 0 | 0 | 1031 | 0 | 1035 | N/A | N/A | N/A | N/A | 33942212 | 616 | 159.4203 | 0% | 0% | 100% | 0% | 100% | 35% | 7510559 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 98 | 21559449 | 3841 | 92.184 | 3.841 | 7.9 | 7.9 | 2B | 0 | 0 | 1004 | 0 | 1038 | N/A | N/A | N/A | N/A | 33942796 | 584 | 152.0437 | 0% | 0% | 100% | 0% | 100% | 35% | 7511640 | 1081 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 87 | 21563298 | 3849 | 92.376 | 3.849 | 8.9 | 8.9 | 2B | 0 | 0 | 981 | 0 | 990 | N/A | N/A | N/A | N/A | 33943372 | 576 | 149.6493 | 0% | 0% | 100% | 0% | 100% | 35% | 7512641 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 90 | 21566955 | 3657 | 87.768 | 3.657 | 9.5 | 9.5 | 2B | 0 | 0 | 935 | 0 | 948 | N/A | N/A | N/A | N/A | 33943876 | 504 | 137.8179 | 0% | 0% | 100% | 0% | 100% | 35% | 7513079 | 438 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 105 | 100 | 21571118 | 4163 | 99.912 | 4.163 | 9.5 | 9.5 | 2B | 0 | 0 | 1022 | 0 | 1018 | N/A | N/A | N/A | N/A | 33944436 | 560 | 134.5184 | 0% | 0% | 100% | 0% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 21576389 | 5271 | 126.504 | 5.271 | 9.5 | 9.5 | 2B+1S | 0 | 0 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33945524 | 1088 | 206.4124 | 0% | 0% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 145 | 21582317 | 5928 | 142.272 | 5.928 | 9.5 | 9.5 | 3B+1S | 0 | 982 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33946788 | 1264 | 213.2254 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 21588508 | 6191 | 148.584 | 6.191 | 8.9 | 8.9 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33948164 | 1376 | 222.2581 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 21594751 | 6243 | 149.832 | 6.243 | 8.2 | 8.2 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33949564 | 1400 | 224.2512 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 21600990 | 6239 | 149.736 | 6.239 | 7.3 | 7.3 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33950976 | 1412 | 226.3183 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 148 | 21607255 | 6265 | 150.36 | 6.265 | 6.6 | 6.6 | 3B+1S | 0 | 1178 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33952412 | 1436 | 229.2099 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 150 | 149 | 21613300 | 6045 | 145.08 | 6.045 | 5.9 | 5.9 | 3B+1S | 0 | 1175 | 1195 | 1185 | 119+8 | N/A | N/A | N/A | N/A | 33953784 | 1372 | 226.9644 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 141 | 21619265 | 5965 | 143.16 | 5.965 | 5.3 | 5.3 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33955164 | 1380 | 231.3495 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 138 | 21625109 | 5844 | 140.256 | 5.844 | 4.7 | 4.7 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33956508 | 1344 | 229.9795 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 21630810 | 5701 | 136.824 | 5.701 | 4.3 | 4.3 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33957836 | 1328 | 232.9416 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 138 | 21636569 | 5759 | 138.216 | 5.759 | 3.6 | 3.6 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33959188 | 1352 | 234.763 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 129 | 21642137 | 5568 | 133.632 | 5.568 | 3.4 | 3.4 | 3B+1S | 0 | 998 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 33960476 | 1288 | 231.3218 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 128 | 21647528 | 5391 | 129.384 | 5.391 | 3.2 | 3.2 | 3B+1S | 0 | 1000 | 1164 | 1185 | 1164 | N/A | N/A | N/A | N/A | 33961676 | 1200 | 222.5932 | 0% | 100% | 100% | 100% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 128 | 21652860 | 5332 | 127.968 | 5.332 | 2.5 | 2.5 | 2B+1S | 0 | 1107 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33962729 | 1053 | 197.4869 | 0% | 100% | 100% | 0% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 21658148 | 5288 | 126.912 | 5.288 | 1.9 | 1.9 | 2B+1S | 0 | 1054 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33963824 | 1095 | 207.0726 | 0% | 100% | 100% | 0% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 123 | 21663280 | 5132 | 123.168 | 5.132 | 1.6 | 1.6 | 2B+1S | 0 | 1012 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33964852 | 1028 | 200.3118 | 0% | 100% | 100% | 0% | 100% | 0% | 7513079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 101 | 21667631 | 4351 | 104.424 | 4.351 | 2.3 | 2.3 | 2B | 0 | 0 | 1103 | 0 | 1119 | N/A | N/A | N/A | N/A | 33965656 | 804 | 184.7851 | 0% | 0% | 100% | 0% | 100% | 25% | 7513972 | 893 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 93 | 21671640 | 4009 | 96.216 | 4.009 | 3.4 | 3.4 | 2B | 0 | 0 | 1065 | 0 | 1079 | N/A | N/A | N/A | N/A | 33966348 | 692 | 172.6116 | 0% | 0% | 100% | 0% | 100% | 25% | 7514997 | 1025 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.1667 | 123906 | 123906 | 123.906 | 123.906 | [12 empty] | 25416 | 25416 | 205.1232 | [6 empty] | 6344 | 6344 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 33% @ 12:01 AM
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:37 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 16, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21671640 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33966348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7514997 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 88 | 21675432 | 3792 | 91.008 | 3.792 | 4.9 | 4.9 | 2B | 0 | 0 | 1049 | 0 | 1059 | N/A | N/A | N/A | N/A | 33966996 | 648 | 170.8861 | 0% | 0% | 100% | 0% | 100% | 33% | 7516484 | 1487 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 83 | 21679064 | 3632 | 87.168 | 3.632 | 6.6 | 6.6 | 2B | 0 | 0 | 1009 | 0 | 1020 | N/A | N/A | N/A | N/A | 33967588 | 592 | 162.9956 | 0% | 0% | 100% | 0% | 100% | 33% | 7518060 | 1576 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 84 | 21682559 | 3495 | 83.88 | 3.495 | 8.2 | 8.2 | 2B | 0 | 0 | 993 | 0 | 1012 | N/A | N/A | N/A | N/A | 33968140 | 552 | 157.9399 | 0% | 0% | 100% | 0% | 100% | 33% | 7519640 | 1580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 83 | 21686077 | 3518 | 84.432 | 3.518 | 9.5 | 9.5 | 2B | 0 | 0 | 919 | 0 | 977 | N/A | N/A | N/A | N/A | 33968656 | 516 | 146.6742 | 0% | 0% | 100% | 0% | 100% | 33% | 7520633 | 993 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 88 | 21689630 | 3553 | 85.272 | 3.553 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 0 | 932 | N/A | N/A | N/A | N/A | 33969124 | 468 | 131.7197 | 0% | 0% | 100% | 0% | 100% | 33% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 100 | 21693690 | 4060 | 97.44 | 4.06 | 9.5 | 9.5 | 2B | 0 | 0 | 1020 | 0 | 977 | N/A | N/A | N/A | N/A | 33969644 | 520 | 128.0788 | 0% | 0% | 100% | 0% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 130 | 21698998 | 5308 | 127.392 | 5.308 | 9.5 | 9.5 | 3B | 0 | 0 | 1103 | 1185 | 1139 | N/A | N/A | N/A | N/A | 33970696 | 1052 | 198.1914 | 0% | 0% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 146 | 21704746 | 5748 | 137.952 | 5.748 | 9.4 | 9.4 | 3B | 0 | 0 | 1145 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33971900 | 1204 | 209.4642 | 0% | 0% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 21710900 | 6154 | 147.696 | 6.154 | 9.1 | 9.1 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33973265 | 1365 | 221.807 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 21717095 | 6195 | 148.68 | 6.195 | 8.4 | 8.4 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33974654 | 1389 | 224.2131 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 21723290 | 6195 | 148.68 | 6.195 | 7.9 | 7.9 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33976044 | 1390 | 224.3745 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 147 | 21729392 | 6102 | 146.448 | 6.102 | 7.2 | 7.2 | 3B+1S | 0 | 1141 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33977428 | 1384 | 226.8109 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 21735343 | 5951 | 142.824 | 5.951 | 6.8 | 6.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33978780 | 1352 | 227.1887 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 21741233 | 5890 | 141.36 | 5.89 | 6.3 | 6.3 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33980116 | 1336 | 226.8251 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 21747043 | 5810 | 139.44 | 5.81 | 5.9 | 5.9 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33981452 | 1336 | 229.9484 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 21752671 | 5628 | 135.072 | 5.628 | 5.1 | 5.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33982760 | 1308 | 232.4094 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 21758394 | 5723 | 137.352 | 5.723 | 5.2 | 5.2 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33984092 | 1332 | 232.7451 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 21763964 | 5570 | 133.68 | 5.57 | 5.1 | 5.1 | 3B+1S | 0 | 1020 | 1177 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33985376 | 1284 | 230.5206 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 132 | 21769498 | 5534 | 132.816 | 5.534 | 4.9 | 4.9 | 3B+1S | 0 | 993 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 33986652 | 1276 | 230.5746 | 0% | 100% | 100% | 100% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 112 | 131 | 21774801 | 5303 | 127.272 | 5.303 | 4.3 | 4.3 | 2B+1S | 0 | 1086 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33987732 | 1080 | 203.6583 | 0% | 100% | 100% | 0% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 21780084 | 5283 | 126.792 | 5.283 | 3.5 | 3.5 | 2B+1S | 0 | 1051 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33988788 | 1056 | 199.8864 | 0% | 100% | 100% | 0% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 120 | 21785150 | 5066 | 121.584 | 5.066 | 3.1 | 3.1 | 2B+1S | 0 | 998 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 33989804 | 1016 | 200.5527 | 0% | 100% | 100% | 0% | 100% | 0% | 7520633 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 102 | 21789470 | 4320 | 103.68 | 4.32 | 3.5 | 3.5 | 2B | 0 | 0 | 1089 | 0 | 1109 | N/A | N/A | N/A | N/A | 33990560 | 756 | 175 | 0% | 0% | 100% | 0% | 100% | 25% | 7521099 | 466 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 94 | 21793465 | 3995 | 95.88 | 3.995 | 4.2 | 4.2 | 2B | 0 | 0 | 1030 | 0 | 1053 | N/A | N/A | N/A | N/A | 33991228 | 668 | 167.209 | 0% | 0% | 100% | 0% | 100% | 25% | 7521656 | 557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.6667 | 121825 | 121825 | 121.825 | 121.825 | [12 empty] | 24880 | 24880 | 204.2274 | [6 empty] | 6659 | 6659 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 16, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24740 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21793465 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33991228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7521656 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 91 | 21797267 | 3802 | 91.248 | 3.802 | 5.2 | 5.2 | 2B | 0 | 0 | 1032 | 0 | 1059 | N/A | N/A | N/A | N/A | 33991860 | 632 | 166.2283 | 0% | 0% | 100% | 0% | 100% | 33% | 7522627 | 971 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 84 | 21800932 | 3665 | 87.96 | 3.665 | 6.3 | 6.3 | 2B | 0 | 0 | 1012 | 0 | 1028 | N/A | N/A | N/A | N/A | 33992452 | 592 | 161.528 | 0% | 0% | 100% | 0% | 100% | 33% | 7523699 | 1072 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 80 | 21804474 | 3542 | 85.008 | 3.542 | 7.5 | 7.5 | 2B | 0 | 0 | 986 | 0 | 998 | N/A | N/A | N/A | N/A | 33992996 | 544 | 153.5855 | 0% | 0% | 100% | 0% | 100% | 33% | 7524837 | 1138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 87 | 21808032 | 3558 | 85.392 | 3.558 | 8.6 | 8.6 | 2B | 0 | 0 | 980 | 0 | 998 | N/A | N/A | N/A | N/A | 33993528 | 532 | 149.5222 | 0% | 0% | 100% | 0% | 100% | 33% | 7525953 | 1116 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 87 | 21811754 | 3722 | 89.328 | 3.722 | 9.5 | 9.5 | 2B | 0 | 0 | 891 | 0 | 927 | N/A | N/A | N/A | N/A | 33994044 | 516 | 138.6351 | 0% | 0% | 100% | 0% | 100% | 33% | 7526659 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 95 | 21815630 | 3876 | 93.024 | 3.876 | 9.5 | 9.5 | 2B | 0 | 0 | 1010 | 0 | 968 | N/A | N/A | N/A | N/A | 33994540 | 496 | 127.967 | 0% | 0% | 100% | 0% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 129 | 21820774 | 5144 | 123.456 | 5.144 | 9.5 | 9.5 | 3B | 0 | 0 | 1121 | 1185 | 1087 | N/A | N/A | N/A | N/A | 33995548 | 1008 | 195.9565 | 0% | 0% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 143 | 21826680 | 5906 | 141.744 | 5.906 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33996788 | 1240 | 209.956 | 0% | 0% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 151 | 21832776 | 6096 | 146.304 | 6.096 | 9.5 | 9.5 | 3B+1S | 0 | 1019 | 1195 | 1185 | 198 | N/A | N/A | N/A | N/A | 33998128 | 1340 | 219.8163 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 21838903 | 6127 | 147.048 | 6.127 | 8.7 | 8.7 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 33999500 | 1372 | 223.9269 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 21845116 | 6213 | 149.112 | 6.213 | 8 | 8 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34000892 | 1392 | 224.0464 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 150 | 21851144 | 6028 | 144.672 | 6.028 | 7.4 | 7.4 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34002268 | 1376 | 228.2681 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 147 | 21857195 | 6051 | 145.224 | 6.051 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34003644 | 1376 | 227.4004 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 146 | 21863213 | 6018 | 144.432 | 6.018 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34005020 | 1376 | 228.6474 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 21868950 | 5737 | 137.688 | 5.737 | 5.8 | 5.8 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34006332 | 1312 | 228.691 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 21874687 | 5737 | 137.688 | 5.737 | 5.5 | 5.5 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34007652 | 1320 | 230.0854 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 21880351 | 5664 | 135.936 | 5.664 | 5.1 | 5.1 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34008988 | 1336 | 235.8757 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 21885874 | 5523 | 132.552 | 5.523 | 4.9 | 4.9 | 3B+1S | 0 | 1002 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34010260 | 1272 | 230.3096 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 128 | 21891351 | 5477 | 131.448 | 5.477 | 4.8 | 4.8 | 3B+1S | 0 | 999 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34011528 | 1268 | 231.5136 | 0% | 100% | 100% | 100% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 125 | 21896539 | 5188 | 124.512 | 5.188 | 4.3 | 4.3 | 2B+1S | 0 | 1039 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34012572 | 1044 | 201.2336 | 0% | 100% | 100% | 0% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 124 | 21901699 | 5160 | 123.84 | 5.16 | 3.7 | 3.7 | 2B+1S | 0 | 1010 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34013604 | 1032 | 200 | 0% | 100% | 100% | 0% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 116 | 21906674 | 4975 | 119.4 | 4.975 | 3.6 | 3.6 | 2B+1S | 0 | 1010 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34014596 | 992 | 199.397 | 0% | 100% | 100% | 0% | 100% | 0% | 7526659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 102 | 21910884 | 4210 | 101.04 | 4.21 | 4.2 | 4.2 | 2B | 0 | 0 | 1077 | 0 | 1109 | N/A | N/A | N/A | N/A | 34015316 | 720 | 171.0214 | 0% | 0% | 100% | 0% | 100% | 25% | 7527134 | 475 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 95 | 21914867 | 3983 | 95.592 | 3.983 | 4.8 | 4.8 | 2B | 0 | 0 | 1043 | 0 | 1058 | N/A | N/A | N/A | N/A | 34015968 | 652 | 163.6957 | 0% | 0% | 100% | 0% | 100% | 25% | 7527709 | 575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.625 | 121402 | 121402 | 121.402 | 121.402 | [12 empty] | 24740 | 24740 | 203.7858 | [6 empty] | 6053 | 6053 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 21577 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21914867 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34015968 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7527709 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 95 | 21918625 | 3758 | 90.192 | 3.758 | 5.6 | 5.6 | 2B | 0 | 0 | 1068 | 0 | 1058 | N/A | N/A | N/A | N/A | 34016598 | 630 | 167.6424 | 0% | 0% | 100% | 0% | 100% | 33% | 7528389 | 680 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 90 | 21922246 | 3621 | 86.904 | 3.621 | 6.6 | 6.6 | 2B | 0 | 0 | 1040 | 0 | 1028 | N/A | N/A | N/A | N/A | 34017187 | 589 | 162.6622 | 0% | 0% | 100% | 0% | 100% | 33% | 7529334 | 945 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 84 | 21925846 | 3600 | 86.4 | 3.6 | 7.7 | 7.7 | 2B | 0 | 0 | 986 | 0 | 1010 | N/A | N/A | N/A | N/A | 34017752 | 565 | 156.9444 | 0% | 0% | 100% | 0% | 100% | 33% | 7530374 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 87 | 21929420 | 3574 | 85.776 | 3.574 | 8.9 | 8.9 | 2B | 0 | 0 | 994 | 0 | 1009 | N/A | N/A | N/A | N/A | 34018292 | 540 | 151.0912 | 0% | 0% | 100% | 0% | 100% | 33% | 7531680 | 1306 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 86 | 21932978 | 3558 | 85.392 | 3.558 | 9.5 | 9.5 | 2B | 0 | 0 | 913 | 0 | 957 | N/A | N/A | N/A | N/A | 34018796 | 504 | 141.6526 | 0% | 0% | 100% | 0% | 100% | 33% | 7532252 | 572 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 31 | 21.831 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 97 | 86 | 21936881 | 3903 | 93.672 | 3.903 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 0 | 948 | N/A | N/A | N/A | N/A | 34019264 | 468 | 119.9078 | 0% | 0% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 26 | 18.3099 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 126 | 123 | 21941721 | 4840 | 116.16 | 4.84 | 9.5 | 9.5 | 2B | 0 | 0 | 1180 | 0 | 1150 | N/A | N/A | N/A | N/A | 34020092 | 828 | 171.0744 | 0% | 0% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 133 | 21947111 | 5390 | 129.36 | 5.39 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1138 | N/A | N/A | N/A | N/A | 34021140 | 1048 | 194.4341 | 0% | 0% | 100% | 100% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 140 | 21952915 | 5804 | 139.296 | 5.804 | 9.5 | 9.5 | 3B+1S | 0 | 988 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 34022332 | 1192 | 205.3756 | 0% | 100% | 100% | 100% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 138 | 21958841 | 5926 | 142.224 | 5.926 | 9.1 | 9.1 | 3B+1S | 0 | 1008 | 1155 | 1185 | 1160 | N/A | N/A | N/A | N/A | 34023604 | 1272 | 214.6473 | 0% | 100% | 100% | 100% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 140 | 21964670 | 5829 | 139.896 | 5.829 | 8.8 | 8.8 | 3B+1S | 0 | 991 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34024864 | 1260 | 216.1606 | 0% | 100% | 100% | 100% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 111 | 123 | 21970500 | 5830 | 139.92 | 5.83 | 8.7 | 8.7 | 2B+1S | 0 | 1188 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34026124 | 1260 | 216.1235 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 115 | 133 | 21975495 | 4995 | 119.88 | 4.995 | 7.7 | 7.7 | 2B+1S | 0 | 1089 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34027200 | 1076 | 215.4154 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 113 | 132 | 21981393 | 5898 | 141.552 | 5.898 | 6.9 | 6.9 | 2B+1S | 0 | 1111 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34028752 | 1552 | 263.14 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 130 | 21986660 | 5267 | 126.408 | 5.267 | 6.3 | 6.3 | 2B+1S | 0 | 1031 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34029288 | 536 | 101.7657 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 123 | 21991927 | 5267 | 126.408 | 5.267 | 6 | 6 | 2B+1S | 0 | 1014 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34030342 | 1054 | 200.1139 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 115 | 122 | 21997077 | 5150 | 123.6 | 5.15 | 5.6 | 5.6 | 2B+1S | 0 | 1034 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34031348 | 1006 | 195.3398 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 110 | 132 | 22002255 | 5178 | 124.272 | 5.178 | 5.1 | 5.1 | 2B+1S | 0 | 1098 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34032340 | 992 | 191.5798 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 114 | 125 | 22007559 | 5304 | 127.296 | 5.304 | 4.2 | 4.2 | 2B+1S | 0 | 1065 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34033404 | 1064 | 200.6033 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 117 | 122 | 22012663 | 5104 | 122.496 | 5.104 | 3.7 | 3.7 | 2B+1S | 0 | 1010 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34034420 | 1016 | 199.0596 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 114 | 22017719 | 5056 | 121.344 | 5.056 | 3.6 | 3.6 | 2B+1S | 0 | 956 | 1176 | 0 | 1181 | N/A | N/A | N/A | N/A | 34035428 | 1008 | 199.3671 | 0% | 100% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 93 | 111 | 22022534 | 4815 | 115.56 | 4.815 | 3.4 | 3.4 | 2B | 0 | 0 | 1138 | 0 | 1100 | N/A | N/A | N/A | N/A | 34036304 | 876 | 181.9315 | 0% | 0% | 100% | 0% | 100% | 0% | 7532252 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 103 | 22026457 | 3923 | 94.152 | 3.923 | 4.2 | 4.2 | 2B | 0 | 0 | 1096 | 0 | 1080 | N/A | N/A | N/A | N/A | 34036956 | 652 | 166.1993 | 0% | 0% | 100% | 0% | 100% | 25% | 7533001 | 749 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 99 | 22030329 | 3872 | 92.928 | 3.872 | 5.4 | 5.4 | 2B | 0 | 0 | 1069 | 0 | 1081 | N/A | N/A | N/A | N/A | 34037545 | 589 | 152.1178 | 0% | 0% | 100% | 0% | 100% | 25% | 7533205 | 204 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 115.4583 | 115462 | 115462 | 115.462 | 115.462 | [12 empty] | 21577 | 21577 | 186.8753 | [6 empty] | 5496 | 5496 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 32% @ 12:01 AM
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 7:17 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:31 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 11:53 AM DUE TO EXCESS CAPACITY
BP1 - STOPPED @ 9:01 PM
BP2 - RESTRATED @ 9:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 9:49 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (32%) @ 10:01 PM FOR REFILLING
BP1 - RESTARTED @ 11:01 PM
BP3 - STOPPED @ 11:01 PM
NORMAL OPERATION

## JAN 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25615 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22030329 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34037545 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7533205 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 22034201 | 3872 | 92.928 | 3.872 | 6.6 | 6.6 | 2B | 0 | 0 | 1021 | 0 | 1050 | N/A | N/A | N/A | N/A | 34038144 | 599 | 154.7004 | 0% | 0% | 100% | 0% | 100% | 33% | 7534377 | 1172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 22038069 | 3868 | 92.832 | 3.868 | 7.5 | 7.5 | 2B | 0 | 0 | 1010 | 0 | 1051 | N/A | N/A | N/A | N/A | 34038737 | 593 | 153.3092 | 0% | 0% | 100% | 0% | 100% | 33% | 7535545 | 1168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 87 | 22041957 | 3888 | 93.312 | 3.888 | 8.6 | 8.6 | 2B | 0 | 0 | 989 | 0 | 1051 | N/A | N/A | N/A | N/A | 34039326 | 589 | 151.4918 | 0% | 0% | 100% | 0% | 100% | 33% | 7536707 | 1162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 90 | 22045808 | 3851 | 92.424 | 3.851 | 9.2 | 9.2 | 2B | 0 | 0 | 939 | 0 | 1009 | N/A | N/A | N/A | N/A | 34039916 | 590 | 153.207 | 0% | 0% | 100% | 0% | 100% | 33% | 7537853 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 119 | 90 | 22050393 | 4585 | 110.04 | 4.585 | 9.5 | 9.5 | 2B | 0 | 0 | 844 | 0 | 937 | N/A | N/A | N/A | N/A | 34040488 | 572 | 124.7546 | 0% | 0% | 100% | 0% | 100% | 33% | 7538013 | 160 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 93 | 93 | 22053411 | 3018 | 72.432 | 3.018 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 0 | 958 | N/A | N/A | N/A | N/A | 34040864 | 376 | 124.5858 | 0% | 0% | 100% | 0% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 99 | 133 | 22059010 | 5599 | 134.376 | 5.599 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1109 | N/A | N/A | N/A | N/A | 34041974 | 1110 | 198.2497 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 142 | 22064630 | 5620 | 134.88 | 5.62 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34043133 | 1159 | 206.2278 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 143 | 22070344 | 5714 | 137.136 | 5.714 | 9.2 | 9.2 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34044412 | 1279 | 223.8362 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 22076549 | 6205 | 148.92 | 6.205 | 8.8 | 8.8 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34045792 | 1380 | 222.4013 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 22082674 | 6125 | 147 | 6.125 | 7.9 | 7.9 | 3B+1S | 0 | 1119 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34047182 | 1390 | 226.9388 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 22088799 | 6125 | 147 | 6.125 | 7.3 | 7.3 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34048572 | 1390 | 226.9388 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 22094857 | 6058 | 145.392 | 6.058 | 6.7 | 6.7 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34049968 | 1396 | 230.4391 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 145 | 22100872 | 6015 | 144.36 | 6.015 | 6.1 | 6.1 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34051318 | 1350 | 224.4389 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 22106659 | 5787 | 138.888 | 5.787 | 5.6 | 5.6 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34052668 | 1350 | 233.2815 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 22112430 | 5771 | 138.504 | 5.771 | 5.1 | 5.1 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34054012 | 1344 | 232.8886 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 22118301 | 5871 | 140.904 | 5.871 | 4.5 | 4.5 | 3B+1S | 0 | 1107 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34055388 | 1376 | 234.3723 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 141 | 22124076 | 5775 | 138.6 | 5.775 | 3.8 | 3.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34056744 | 1356 | 234.8052 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 22129707 | 5631 | 135.144 | 5.631 | 3.3 | 3.3 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34058076 | 1332 | 236.5477 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 130 | 22135251 | 5544 | 133.056 | 5.544 | 2.8 | 2.8 | 3B+1S | 0 | 1012 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34059322 | 1246 | 224.7475 | 0% | 100% | 100% | 100% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 | 129 | 22140811 | 5560 | 133.44 | 5.56 | 2.6 | 2.6 | 3B+1S | 0 | 975 | 1155 | 0 | 1159 | N/A | N/A | N/A | N/A | 34060568 | 1246 | 224.1007 | 0% | 100% | 100% | 0% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 132 | 120 | 22145917 | 5106 | 122.544 | 5.106 | 2.2 | 2.2 | 3B+1S | 0 | 1012 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34061602 | 1034 | 202.5069 | 0% | 100% | 100% | 0% | 100% | 0% | 7538013 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 98 | 22150273 | 4356 | 104.544 | 4.356 | 2.8 | 2.8 | 2B | 0 | 0 | 1098 | 0 | 1109 | N/A | N/A | N/A | N/A | 34062372 | 770 | 176.7677 | 0% | 0% | 100% | 0% | 100% | 25% | 7538691 | 678 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 97 | 22155058 | 4785 | 114.84 | 4.785 | 3.8 | 3.8 | 2B | 0 | 0 | 1053 | 0 | 1099 | N/A | N/A | N/A | N/A | 34063160 | 788 | 164.6813 | 0% | 0% | 100% | 0% | 100% | 25% | 7539604 | 913 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  | 121 | 123.25 | 124729 | 124729 | 124.729 | 124.729 | [12 empty] | 25615 | 25615 | 205.3652 | [6 empty] | 6399 | 6399 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 4:31 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:07 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | D. GUANZON / G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26192 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22155058 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34063160 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7539604 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 93 | 22158344 | 3286 | 78.864 | 3.286 | 4.8 | 4.8 | 2B | 0 | 0 | 1045 | 0 | 1059 | N/A | N/A | N/A | N/A | 34063724 | 564 | 171.6372 | 0% | 0% | 100% | 0% | 100% | 33% | 7540451 | 847 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 92 | 22162275 | 3931 | 94.344 | 3.931 | 5.9 | 5.9 | 2B | 0 | 0 | 1014 | 0 | 1059 | N/A | N/A | N/A | N/A | 34064322 | 598 | 152.1241 | 0% | 0% | 100% | 0% | 100% | 33% | 7541545 | 1094 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 95 | 22166099 | 3824 | 91.776 | 3.824 | 7.2 | 7.2 | 2B | 0 | 0 | 998 | 0 | 1059 | N/A | N/A | N/A | N/A | 34064413 | 91 | 23.7971 | 0% | 0% | 100% | 0% | 100% | 33% | 7542643 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 93 | 22169817 | 3718 | 89.232 | 3.718 | 8.3 | 8.3 | 2B | 0 | 0 | 995 | 0 | 1008 | N/A | N/A | N/A | N/A | 34065502 | 1089 | 292.8994 | 0% | 0% | 100% | 0% | 100% | 33% | 7543841 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 120 | 100 | 22173722 | 3905 | 93.72 | 3.905 | 9.2 | 9.2 | 2B | 0 | 0 | 1025 | 0 | 1049 | N/A | N/A | N/A | N/A | 34066089 | 587 | 150.3201 | 0% | 0% | 100% | 0% | 100% | 33% | 7544793 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | D. GUANZON / G. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 115 | 22178293 | 4571 | 109.704 | 4.571 | 9.5 | 9.5 | 2B | 0 | 0 | 1120 | 0 | 1140 | N/A | N/A | N/A | N/A | 34066820 | 731 | 159.9212 | 0% | 0% | 100% | 0% | 100% | 0% | 7545040 | 247 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 143 | 22184204 | 5911 | 141.864 | 5.911 | 9.2 | 9.2 | 3B+1S | 0 | 1048 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34068092 | 1272 | 215.192 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 22190214 | 6010 | 144.24 | 6.01 | 8.5 | 8.5 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34069444 | 1352 | 224.9584 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 147 | 22196300 | 6086 | 146.064 | 6.086 | 7.9 | 7.9 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34070828 | 1384 | 227.4072 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 22202614 | 6314 | 151.536 | 6.314 | 7.2 | 7.2 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34072244 | 1416 | 224.2635 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 22208712 | 6098 | 146.352 | 6.098 | 6.5 | 6.5 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34073620 | 1376 | 225.6478 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 22214684 | 5972 | 143.328 | 5.972 | 6.1 | 6.1 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34074992 | 1372 | 229.7388 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 124 | 140 | 22220576 | 5892 | 141.408 | 5.892 | 5.2 | 5.2 | 3B+1S | 0 | 1124 | 1144 | 1185 | 1149 | N/A | N/A | N/A | N/A | 34076316 | 1324 | 224.7115 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 22226323 | 5747 | 137.928 | 5.747 | 4.5 | 4.5 | 3B+1S | 0 | 1103 | 1145 | 1185 | 1049 | N/A | N/A | N/A | N/A | 34077596 | 1280 | 222.7249 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 22231900 | 5577 | 133.848 | 5.577 | 4.2 | 4.2 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34078912 | 1316 | 235.9692 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 134 | 22237389 | 5489 | 131.736 | 5.489 | 4.1 | 4.1 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34080212 | 1300 | 236.8373 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 22243104 | 5715 | 137.16 | 5.715 | 3.7 | 3.7 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34081552 | 1340 | 234.4707 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 133 | 22248747 | 5643 | 135.432 | 5.643 | 3.4 | 3.4 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34082864 | 1312 | 232.5004 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 22254338 | 5591 | 134.184 | 5.591 | 3.3 | 3.3 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34084180 | 1316 | 235.3783 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 22259800 | 5462 | 131.088 | 5.462 | 3.2 | 3.2 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34085428 | 1248 | 228.4877 | 0% | 100% | 100% | 100% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 151 | 22265157 | 5357 | 128.568 | 5.357 | 2.5 | 2.5 | 2B+1S | 0 | 1101 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34086520 | 1092 | 203.8454 | 0% | 100% | 100% | 0% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 117 | 22270239 | 5082 | 121.968 | 5.082 | 2 | 2 | 2B+1S | 0 | 1016 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34087540 | 1020 | 200.7084 | 0% | 100% | 100% | 0% | 100% | 0% | 7545040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 102 | 22274733 | 4494 | 107.856 | 4.494 | 2.5 | 2.5 | 2B | 0 | 0 | 1128 | 0 | 1110 | N/A | N/A | N/A | N/A | 34088356 | 816 | 181.5754 | 0% | 0% | 100% | 0% | 100% | 25% | 7545654 | 614 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 102 | 22278720 | 3987 | 95.688 | 3.987 | 3.2 | 3.2 | 2B | 0 | 0 | 1008 | 0 | 1110 | N/A | N/A | N/A | N/A | 34089352 | 996 | 249.8119 | 0% | 0% | 100% | 0% | 100% | 25% | 7546763 | 1109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.1667 | 123662 | 123662 | 123.662 | 123.662 | [12 empty] | 26192 | 26192 | 211.8031 | [6 empty] | 7159 | 7159 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01AM TO 35%
XCV1 CLOSED @ 5:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 324796 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22278720 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 33790596 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7546763 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 87 | 22382654 | 103934 | 2494.416 | 103.934 | 4.3 | 4.3 | 2B | 0 | 0 | 1002 | 0 | 1110 | N/A | N/A | N/A | N/A | 34088708 | 298112 | 2868.2818 | 0% | 0% | 100% | 0% | 100% | 33% | 7467386 | -79377 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 22386237 | 3583 | 85.992 | 3.583 | 5.5 | 5.5 | 2B | 0 | 0 | 1002 | 0 | 1059 | N/A | N/A | N/A | N/A | 34090292 | 1584 | 442.0876 | 0% | 0% | 100% | 0% | 100% | 33% | 7468403 | 1017 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 83 | 22389844 | 3607 | 86.568 | 3.607 | 6.9 | 6.9 | 2B | 0 | 0 | 972 | 0 | 1059 | N/A | N/A | N/A | N/A | 34090868 | 576 | 159.6895 | 0% | 0% | 100% | 0% | 100% | 33% | 7469515 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 101 | 22393439 | 3595 | 86.28 | 3.595 | 8.1 | 8.1 | 2B | 0 | 0 | 1004 | 0 | 1038 | N/A | N/A | N/A | N/A | 34091420 | 552 | 153.5466 | 0% | 0% | 100% | 0% | 100% | 33% | 7470509 | 994 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 123 | 103 | 22397446 | 4007 | 96.168 | 4.007 | 9.1 | 9.1 | 2B | 0 | 0 | 1026 | 0 | 1110 | N/A | N/A | N/A | N/A | 34092036 | 616 | 153.731 | 0% | 0% | 100% | 0% | 100% | 33% | 7471026 | 517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G. SY
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 114 | 110 | 22402190 | 4744 | 113.856 | 4.744 | 9.5 | 9.5 | 2B | 0 | 0 | 1142 | 0 | 1160 | N/A | N/A | N/A | N/A | 34092836 | 800 | 168.6341 | 0% | 0% | 100% | 0% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 147 | 22407893 | 5703 | 136.872 | 5.703 | 9.2 | 9.2 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34094076 | 1240 | 217.4294 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 148 | 22414200 | 6307 | 151.368 | 6.307 | 8.3 | 8.3 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34095496 | 1420 | 225.1467 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 149 | 22420534 | 6334 | 152.016 | 6.334 | 7.5 | 7.5 | 3B+1S | 0 | 1139 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34096926 | 1430 | 225.7657 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 22426610 | 6076 | 145.824 | 6.076 | 6.7 | 6.7 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34098304 | 1378 | 226.7939 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 22432127 | 5517 | 132.408 | 5.517 | 6 | 6 | 3B+1S | 0 | 1175 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34099764 | 1460 | 264.6366 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 22438708 | 6581 | 157.944 | 6.581 | 5.1 | 5.1 | 3B+1S | 0 | 1165 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34101176 | 1412 | 214.5571 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 22445110 | 6402 | 153.648 | 6.402 | 4.3 | 4.3 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34102588 | 1412 | 220.5561 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 22450950 | 5840 | 140.16 | 5.84 | 3.6 | 3.6 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34103916 | 1328 | 227.3973 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 22456590 | 5640 | 135.36 | 5.64 | 3.3 | 3.3 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34105244 | 1328 | 235.461 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 22462104 | 5514 | 132.336 | 5.514 | 3.2 | 3.2 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34106512 | 1268 | 229.9601 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 135 | 22467715 | 5611 | 134.664 | 5.611 | 2.9 | 2.9 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34107832 | 1320 | 235.2522 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 135 | 22473340 | 5625 | 135 | 5.625 | 2.5 | 2.5 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34109124 | 1292 | 229.6889 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 135 | 22478944 | 5604 | 134.496 | 5.604 | 2 | 2 | 3B+1S | 0 | 1082 | 1176 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34110412 | 1288 | 229.8358 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 124 | 130 | 22484463 | 5519 | 132.456 | 5.519 | 1.6 | 1.6 | 3B+1S | 0 | 1045 | 1134 | 1185 | 1160 | N/A | N/A | N/A | N/A | 34111660 | 1248 | 226.1279 | 0% | 100% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 | 124 | 22489770 | 5307 | 127.368 | 5.307 | 1.3 | 1.3 | 3B | 0 | 0 | 1134 | 1185 | 1160 | N/A | N/A | N/A | N/A | 34112852 | 1192 | 224.609 | 0% | 0% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 116 | 22494937 | 5167 | 124.008 | 5.167 | 1.3 | 1.3 | 3B | 0 | 0 | 954 | 1185 | 1140 | N/A | N/A | N/A | N/A | 34113924 | 1072 | 207.4705 | 0% | 0% | 100% | 100% | 100% | 0% | 7471026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 141 | 105 | 22499060 | 4123 | 98.952 | 4.123 | 2.5 | 2.5 | 2B | 0 | 0 | 1059 | 0 | 1130 | N/A | N/A | N/A | N/A | 34114664 | 740 | 179.481 | 0% | 0% | 100% | 0% | 100% | 25% | 7553251 | 82225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 143 | 101 | 22503671 | 4611 | 110.664 | 4.611 | 4 | 4 | 2B | 0 | 0 | 1024 | 0 | 1110 | N/A | N/A | N/A | N/A | 34115392 | 728 | 157.8833 | 0% | 0% | 100% | 0% | 100% | 25% | 7554768 | 1517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.9583 | 224951 | 224951 | 224.951 | 224.951 | [12 empty] | 324796 | 324796 | 1443.8522 | [6 empty] | 8005 | 8005 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 33% @ 12:01 AM
XCV1 CLOSED @ 5:15AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 8:43 PM DUE TO LOW LEVEL (1.3 M)
BP2 - STOPPED @ 10.01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25620 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22503671 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34115392 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7554768 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 97 | 22507598 | 3927 | 94.248 | 3.927 | 5.6 | 5.6 | 2B | 0 | 0 | 1054 | 0 | 199 | N/A | N/A | N/A | N/A | 34116036 | 644 | 163.9929 | 0% | 0% | 100% | 0% | 100% | 33% | 7556160 | 1392 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 22511630 | 4032 | 96.768 | 4.032 | 6.8 | 6.8 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 34116716 | 680 | 168.6508 | 0% | 0% | 100% | 0% | 100% | 33% | 7557253 | 1093 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 22515568 | 3938 | 94.512 | 3.938 | 8 | 8 | 2B | 0 | 0 | 1031 | 0 | 1059 | N/A | N/A | N/A | N/A | 34117364 | 648 | 164.5505 | 0% | 0% | 100% | 0% | 100% | 33% | 7558392 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 94 | 22519689 | 4121 | 98.904 | 4.121 | 9 | 9 | 2B | 0 | 0 | 1045 | 0 | 1059 | N/A | N/A | N/A | N/A | 34118016 | 652 | 158.214 | 0% | 0% | 100% | 0% | 100% | 33% | 7559380 | 988 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 99 | 22523812 | 4123 | 98.952 | 4.123 | 9.5 | 9.5 | 2B | 0 | 0 | 962 | 0 | 1059 | N/A | N/A | N/A | N/A | 34118644 | 628 | 152.3163 | 0% | 0% | 100% | 0% | 100% | 33% | 7559821 | 441 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 115 | 22528473 | 4661 | 111.864 | 4.661 | 9.5 | 9.5 | 2B | 0 | 0 | 1044 | 0 | 1140 | N/A | N/A | N/A | N/A | 34119316 | 672 | 144.1751 | 0% | 0% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 140 | 22534400 | 5927 | 142.248 | 5.927 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34120548 | 1232 | 207.8623 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 146 | 22540442 | 6042 | 145.008 | 6.042 | 9.2 | 9.2 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34121884 | 1336 | 221.1188 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 150 | 22546726 | 6284 | 150.816 | 6.284 | 8.6 | 8.6 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34123276 | 1392 | 221.515 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 146 | 22552918 | 6192 | 148.608 | 6.192 | 8.1 | 8.1 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34124626 | 1350 | 218.0233 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 145 | 22559110 | 6192 | 148.608 | 6.192 | 7.9 | 7.9 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34125976 | 1350 | 218.0233 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 147 | 22565255 | 6145 | 147.48 | 6.145 | 7.7 | 7.7 | 3B+1S | 0 | 1000 | 1176 | 1185 | 1181 | N/A | N/A | N/A | N/A | 34127308 | 1332 | 216.7616 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 143 | 22571168 | 5913 | 141.912 | 5.913 | 7.4 | 7.4 | 3B+1S | 0 | 1002 | 1104 | 1185 | 1139 | N/A | N/A | N/A | N/A | 34128540 | 1232 | 208.3545 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 22577094 | 5926 | 142.224 | 5.926 | 7.1 | 7.1 | 3B+1S | 0 | 1012 | 1105 | 1185 | 1140 | N/A | N/A | N/A | N/A | 34129756 | 1216 | 205.1974 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 135 | 22582866 | 5772 | 138.528 | 5.772 | 6.8 | 6.8 | 3B+1S | 0 | 994 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34131004 | 1248 | 216.2162 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 22588626 | 5760 | 138.24 | 5.76 | 6.7 | 6.7 | 3B+1S | 0 | 997 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34132304 | 1300 | 225.6944 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 22594342 | 5716 | 137.184 | 5.716 | 6.3 | 6.3 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34133608 | 1304 | 228.1316 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 22600059 | 5717 | 137.208 | 5.717 | 6 | 6 | 3B+1S | 0 | 1027 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34134908 | 1300 | 227.392 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 135 | 22605747 | 5688 | 136.512 | 5.688 | 5.5 | 5.5 | 3B+1S | 0 | 1043 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34136204 | 1296 | 227.8481 | 0% | 100% | 100% | 100% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 130 | 22611229 | 5482 | 131.568 | 5.482 | 4.5 | 4.5 | 2B+1S | 0 | 1189 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34137344 | 1140 | 207.9533 | 0% | 100% | 100% | 0% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 128 | 22616670 | 5441 | 130.584 | 5.441 | 3.3 | 3.3 | 2B+1S | 0 | 1168 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34138464 | 1120 | 205.8445 | 0% | 100% | 100% | 0% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 22621881 | 5211 | 125.064 | 5.211 | 2.7 | 2.7 | 2B+1S | 0 | 1021 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34139500 | 1036 | 198.8102 | 0% | 100% | 100% | 0% | 100% | 0% | 7559821 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 100 | 22626360 | 4479 | 107.496 | 4.479 | 3.2 | 3.2 | 2B | 0 |  | 1085 | 0 | 1129 | N/A | N/A | N/A | N/A | 34140308 | 808 | 180.3974 | 0% | 0% | 100% | 0% | 100% | 25% | 7560395 | 574 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 96 | 22630476 | 4116 | 98.784 | 4.116 | 3.9 | 3.9 | 2B | 0 | 0 | 1058 | 0 | 1080 | N/A | N/A | N/A | N/A | 34141012 | 704 | 171.0398 | 0% | 0% | 100% | 0% | 0% | 25% | 7561093 | 698 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125 | 126805 | 126805 | 126.805 | 126.805 | [12 empty] | 25620 | 25620 | 202.0425 | [6 empty] | 6325 | 6325 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 41% @ 12:01 AM
XCV1 CLOSED @ 5:15AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 23, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
GENSET 1 WARMUP EXERCISED @ 4:01 PM
GENSET 2 WARMUP EXERCISED @ 4:11 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
BP1 - RESTARTED @ 11:01 PM
BP3 - STOPPED @ 11:01 PM
NORMAL OPERATION

## JAN 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | D GUANZON / F RAMOS
[13 empty] | 10pm - 6am | G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22630476 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34141012 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7561093 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 91 | 22633800 | 3324 | 79.776 | 3.324 | 5.2 | 5.2 | 2B | 0 | 0 | 1050 | 0 | 1067 | N/A | N/A | N/A | N/A | 34141656 | 644 | 193.7425 | 0% | 0% | 100% | 0% | 100% | 33% | 7562301 | 1208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 88 | 22638017 | 4217 | 101.208 | 4.217 | 6.6 | 6.6 | 2B | 0 | 0 | 1028 | 0 | 1038 | N/A | N/A | N/A | N/A | 34142268 | 612 | 145.1269 | 0% | 0% | 100% | 0% | 100% | 33% | 7563657 | 1356 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | D GUANZON / F RAMOS
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 89 | 22641698 | 3681 | 88.344 | 3.681 | 8.1 | 8.1 | 2B | 0 | 0 | 1028 | 0 | 1030 | N/A | N/A | N/A | N/A | 34142848 | 580 | 157.5659 | 0% | 0% | 100% | 0% | 100% | 33% | 7565046 | 1389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 87 | 22645315 | 3617 | 86.808 | 3.617 | 9.3 | 9.3 | 2B | 0 | 0 | 999 | 0 | 1037 | N/A | N/A | N/A | N/A | 34143404 | 556 | 153.7186 | 0% | 0% | 100% | 0% | 100% | 33% | 7566260 | 1214 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 97 | 22649492 | 4177 | 100.248 | 4.177 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 1018 | N/A | N/A | N/A | N/A | 34143992 | 588 | 140.7709 | 0% | 0% | 100% | 0% | 100% | 33% | 7566318 | 58 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G. SY
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 111 | 22654060 | 4568 | 109.632 | 4.568 | 9.5 | 9.5 | 2B | 0 | 0 | 1130 | 0 | 1149 | N/A | N/A | N/A | N/A | 34144740 | 748 | 163.7478 | 0% | 0% | 100% | 0% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 145 | 22660010 | 5950 | 142.8 | 5.95 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34146068 | 1328 | 223.1933 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 22665961 | 5951 | 142.824 | 5.951 | 8.6 | 8.6 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34147396 | 1328 | 223.1558 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 22672347 | 6386 | 153.264 | 6.386 | 7.9 | 7.9 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34148832 | 1436 | 224.8669 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 22678357 | 6010 | 144.24 | 6.01 | 6.9 | 6.9 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34150204 | 1372 | 228.2862 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 22684450 | 6093 | 146.232 | 6.093 | 6.2 | 6.2 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34151586 | 1382 | 226.8177 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 22690544 | 6094 | 146.256 | 6.094 | 5.5 | 5.5 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34152968 | 1382 | 226.7804 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 134 | 22696385 | 5841 | 140.184 | 5.841 | 5.1 | 5.1 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34154316 | 1348 | 230.7824 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 22702199 | 5814 | 139.536 | 5.814 | 4.5 | 4.5 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34155660 | 1344 | 231.1662 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 133 | 22707927 | 5728 | 137.472 | 5.728 | 4.2 | 4.2 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34156984 | 1324 | 231.1453 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 22713425 | 5498 | 131.952 | 5.498 | 4.1 | 4.1 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34158294 | 1310 | 238.2685 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 22719035 | 5610 | 134.64 | 5.61 | 3.8 | 3.8 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34159604 | 1310 | 233.5116 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 131 | 22724617 | 5582 | 133.968 | 5.582 | 3.5 | 3.5 | 3B+1S | 0 | 1010 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34160888 | 1284 | 230.0251 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 128 | 22730100 | 5483 | 131.592 | 5.483 | 3.3 | 3.3 | 3B+1S | 0 | 1008 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34162156 | 1268 | 231.2603 | 0% | 100% | 100% | 100% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 130 | 22735453 | 5353 | 128.472 | 5.353 | 2.7 | 2.7 | 2B+1S | 0 | 1100 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34163244 | 1088 | 203.2505 | 0% | 100% | 100% | 0% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 22740679 | 5226 | 125.424 | 5.226 | 2 | 2 | 2B+1S | 0 | 1057 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34164292 | 1048 | 200.5358 | 0% | 100% | 100% | 0% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 120 | 22745725 | 5046 | 121.104 | 5.046 | 1.7 | 1.7 | 2B | 0 | 1006 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34165300 | 1008 | 199.7622 | 0% | 100% | 100% | 0% | 100% | 0% | 7566318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 100 | 22750020 | 4295 | 103.08 | 4.295 | 2.5 | 2.5 | 2B | 0 | 0 | 1100 | 0 | 1139 | N/A | N/A | N/A | N/A | 34166076 | 776 | 180.6752 | 0% | 0% | 100% | 0% | 100% | 25% | 7567145 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 98 | 22754085 | 4065 | 97.56 | 4.065 | 3.5 | 3.5 | 2B | 0 | 0 | 1032 | 0 | 1139 | N/A | N/A | N/A | N/A | 34166780 | 704 | 173.1857 | 0% | 0% | 100% | 0% | 100% | 25% | 7568118 | 973 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5833 | 123609 | 123609 | 123.609 | 123.609 | [12 empty] | 25768 | 25768 | 208.4638 | [6 empty] | 7025 | 7025 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 43% @ 12:01 AM
XCV1 CLOSED @ 4:08AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 24, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
BP1 - RESTARTED @ 11:01 PM
BP3 - STOPPED @ 11:01 PM
NORMAL OPERATION

## JAN 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25736 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22754085 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34166780 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7568118 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 88 | 22757895 | 3810 | 91.44 | 3.81 | 5.1 | 5.1 | 2B | 0 | 0 | 1032 | 0 | 1109 | N/A | N/A | N/A | N/A | 34167436 | 656 | 172.1785 | 0% | 0% | 100% | 0% | 100% | 33% | 7569450 | 1332 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 85 | 22761614 | 3719 | 89.256 | 3.719 | 6.5 | 6.5 | 2B | 0 | 0 | 1005 | 0 | 1059 | N/A | N/A | N/A | N/A | 34168052 | 616 | 165.6359 | 0% | 0% | 100% | 0% | 100% | 33% | 7570909 | 1459 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 86 | 22765116 | 3502 | 84.048 | 3.502 | 8 | 8 | 2B | 0 | 0 | 1001 | 0 | 1028 | N/A | N/A | N/A | N/A | 34168608 | 556 | 158.7664 | 0% | 0% | 100% | 0% | 100% | 33% | 7572378 | 1469 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 83 | 22768803 | 3687 | 88.488 | 3.687 | 9.5 | 9.5 | 2B | 0 | 0 | 147 | 0 | 1008 | N/A | N/A | N/A | N/A | 34169164 | 556 | 150.8001 | 0% | 0% | 100% | 0% | 100% | 33% | 7573671 | 1293 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 94 | 22773011 | 4208 | 100.992 | 4.208 | 9.5 | 9.5 | 2B | 0 | 0 | 952 | 0 | 980 | N/A | N/A | N/A | N/A | 34169716 | 552 | 131.1787 | 0% | 0% | 100% | 0% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 110 | 108 | 22776630 | 3619 | 86.856 | 3.619 | 9.5 | 9.5 | 2B | 0 | 0 | 1050 | 0 | 1050 | N/A | N/A | N/A | N/A | 34170220 | 504 | 139.265 | 0% | 0% | 100% | 0% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 22782163 | 5533 | 132.792 | 5.533 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34171380 | 1160 | 209.6512 | 0% | 0% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 22788172 | 6009 | 144.216 | 6.009 | 9.3 | 9.3 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34172720 | 1340 | 222.9988 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 22794267 | 6095 | 146.28 | 6.095 | 8.7 | 8.7 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34174092 | 1372 | 225.1025 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 151 | 22800511 | 6244 | 149.856 | 6.244 | 8 | 8 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34175492 | 1400 | 224.2152 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 22806736 | 6225 | 149.4 | 6.225 | 7.2 | 7.2 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34176900 | 1408 | 226.1847 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 148 | 22812869 | 6133 | 147.192 | 6.133 | 6.4 | 6.4 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34178292 | 1392 | 226.9689 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 22818878 | 6009 | 144.216 | 6.009 | 5.6 | 5.6 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34179674 | 1382 | 229.9884 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 146 | 22824888 | 6010 | 144.24 | 6.01 | 5 | 5 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34181056 | 1382 | 229.9501 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 22830816 | 5928 | 142.272 | 5.928 | 4.4 | 4.4 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34182420 | 1364 | 230.0945 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 22836631 | 5815 | 139.56 | 5.815 | 3.8 | 3.8 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34183760 | 1340 | 230.4385 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 22842491 | 5860 | 140.64 | 5.86 | 3.1 | 3.1 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34185136 | 1376 | 234.8123 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 22848190 | 5699 | 136.776 | 5.699 | 2.7 | 2.7 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34186468 | 1332 | 233.7252 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 22853768 | 5578 | 133.872 | 5.578 | 2.3 | 2.3 | 3B+1S | 0 | 1024 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34187740 | 1272 | 228.0387 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 126 | 22859265 | 5497 | 131.928 | 5.497 | 2.2 | 2.2 | 3B+1S | 0 | 1000 | 1135 | 1185 | 1151 | N/A | N/A | N/A | N/A | 34188976 | 1236 | 224.8499 | 0% | 100% | 100% | 100% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 22864469 | 5204 | 124.896 | 5.204 | 1.6 | 1.6 | 2B+1S | 0 | 1078 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34190024 | 1048 | 201.3836 | 0% | 100% | 100% | 0% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 116 | 22869404 | 4935 | 118.44 | 4.935 | 1.4 | 1.4 | 2B+1S | 0 | 1003 | 1197 | 0 | 1171 | N/A | N/A | N/A | N/A | 34191020 | 996 | 201.8237 | 0% | 100% | 100% | 0% | 100% | 0% | 7573671 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 115 | 22873548 | 4144 | 99.456 | 4.144 | 2.5 | 2.5 | 2B | 0 | 0 | 1093 | 0 | 1110 | N/A | N/A | N/A | N/A | 34191771 | 751 | 181.2259 | 0% | 0% | 100% | 0% | 100% | 38% | 7574571 | 900 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 113 | 22877692 | 4144 | 99.456 | 4.144 | 3.4 | 3.4 | 2B | 0 | 0 | 1073 | 0 | 1110 | N/A | N/A | N/A | N/A | 34192516 | 745 | 179.778 | 0% | 0% | 100% | 0% | 100% | 38% | 7575661 | 1090 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.5 | 123607 | 123607 | 123.607 | 123.607 | [12 empty] | 25736 | 25736 | 208.2083 | [6 empty] | 7543 | 7543 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ 3:56AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 25, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:42PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | G. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25108 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22877692 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34192516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7575661 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 98 | 22881492 | 3800 | 91.2 | 3.8 | 5.7 | 5.7 | 2B | 0 | 0 | 1069 | 0 | 1088 | N/A | N/A | N/A | N/A | 34193151 | 635 | 167.1053 | 0% | 0% | 100% | 0% | 100% | 45% | 7577021 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 22885263 | 3771 | 90.504 | 3.771 | 6.6 | 6.6 | 2B | 0 | 0 | 1035 | 0 | 1088 | N/A | N/A | N/A | N/A | 34193766 | 615 | 163.0867 | 0% | 0% | 100% | 0% | 100% | 45% | 7578373 | 1352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 83 | 22889049 | 3786 | 90.864 | 3.786 | 7.9 | 7.9 | 2B | 0 | 0 | 966 | 0 | 1088 | N/A | N/A | N/A | N/A | 34194392 | 626 | 165.346 | 0% | 0% | 100% | 0% | 100% | 45% | 7579734 | 1361 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 85 | 22892742 | 3693 | 88.632 | 3.693 | 8.9 | 8.9 | 2B | 0 | 0 | 910 | 0 | 1059 | N/A | N/A | N/A | N/A | 34194927 | 535 | 144.8687 | 0% | 0% | 100% | 0% | 100% | 45% | 7581050 | 1316 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 89 | 22896416 | 3674 | 88.176 | 3.674 | 9.5 | 9.5 | 2B | 0 | 0 | 836 | 0 | 1059 | N/A | N/A | N/A | N/A | 34195455 | 528 | 143.7126 | 0% | 0% | 100% | 0% | 100% | 45% | 7581402 | 352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 99 | 22900071 | 3655 | 87.72 | 3.655 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 0 | 1018 | N/A | N/A | N/A | N/A | 34195956 | 501 | 137.0725 | 0% | 0% | 100% | 0% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 21 | 14.7887 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 129 | 22905285 | 5214 | 125.136 | 5.214 | 9.5 | 9.5 | 3B | 0 | 0 | 1095 | 1185 | 1057 | N/A | N/A | N/A | N/A | 34196900 | 944 | 181.051 | 0% | 0% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 140 | 22911178 | 5893 | 141.432 | 5.893 | 9.5 | 9.5 | 3B | 0 | 0 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34198112 | 1212 | 205.6677 | 0% | 0% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 22917171 | 5993 | 143.832 | 5.993 | 9.2 | 9.2 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34199420 | 1308 | 218.2546 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 22923400 | 6229 | 149.496 | 6.229 | 8.1 | 8.1 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34200820 | 1400 | 224.7552 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 152 | 22929630 | 6230 | 149.52 | 6.23 | 7.7 | 7.7 | 3B+1S | 0 | 1088 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34202220 | 1400 | 224.7191 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 147 | 22935691 | 6061 | 145.464 | 6.061 | 6.9 | 6.9 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34203612 | 1392 | 229.6651 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 144 | 22941657 | 5966 | 143.184 | 5.966 | 6.1 | 6.1 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34204940 | 1328 | 222.5947 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 22947687 | 6030 | 144.72 | 6.03 | 5.4 | 5.4 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34206376 | 1436 | 238.1426 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 142 | 22953604 | 5917 | 142.008 | 5.917 | 4.8 | 4.8 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34207740 | 1364 | 230.5222 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 22959421 | 5817 | 139.608 | 5.817 | 4.2 | 4.2 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34209092 | 1352 | 232.4222 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 22965080 | 5659 | 135.816 | 5.659 | 3.7 | 3.7 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34210416 | 1324 | 233.9636 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 137 | 22970728 | 5648 | 135.552 | 5.648 | 3.3 | 3.3 | 3B+1S | 0 | 1060 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34211700 | 1284 | 227.3371 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 22976370 | 5642 | 135.408 | 5.642 | 2.9 | 2.9 | 3B+1S | 0 | 1035 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34212972 | 1272 | 225.452 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 22981743 | 5373 | 128.952 | 5.373 | 2.2 | 2.2 | 2B+1S | 0 | 1106 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34214068 | 1096 | 203.9829 | 0% | 100% | 100% | 100% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 127 | 22987087 | 5344 | 128.256 | 5.344 | 1.6 | 1.6 | 2B+15 | 0 | 1052 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34215132 | 1064 | 199.1018 | 0% | 100% | 100% | 0% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 119 | 22991934 | 4847 | 116.328 | 4.847 | 1.4 | 1.4 | 2B+1S | 0 | 979 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34216100 | 968 | 199.7112 | 0% | 100% | 100% | 0% | 100% | 0% | 7581402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 120 | 22995834 | 3900 | 93.6 | 3.9 | 2.8 | 2.8 | 2B | 0 | 0 | 995 | 0 | 1150 | N/A | N/A | N/A | N/A | 34217024 | 924 | 236.9231 | 0% | 0% | 100% | 0% | 100% | 38% | 7580300 | -1102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 88 | 23000619 | 4785 | 114.84 | 4.785 | 3.5 | 3.5 | 2B | 0 | 0 | 991 | 0 | 1150 | N/A | N/A | N/A | N/A | 34217624 | 600 | 125.3918 | 0% | 0% | 100% | 0% | 100% | 38% | 7583500 | 3200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.875 | 122927 | 122927 | 122.927 | 122.927 | [12 empty] | 25108 | 25108 | 204.2513 | [6 empty] | 7839 | 7839 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ 4:10AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:23 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 25, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25500 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23000619 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34217624 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7583500 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 86 | 23004085 | 3466 | 83.184 | 3.466 | 4.9 | 4.9 | 2B | 0 | 0 | 1007 | 0 | 1111 | N/A | N/A | N/A | N/A | 34218236 | 612 | 176.5724 | 0% | 0% | 100% | 0% | 100% | 45% | 7584808 | 1308 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 86 | 23007622 | 3537 | 84.888 | 3.537 | 6.4 | 6.4 | 2B | 0 | 0 | 993 | 0 | 1059 | N/A | N/A | N/A | N/A | 34218828 | 592 | 167.3735 | 0% | 0% | 100% | 0% | 100% | 45% | 7586283 | 1475 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 23011203 | 3581 | 85.944 | 3.581 | 8 | 8 | 2B | 0 | 0 | 993 | 0 | 1059 | N/A | N/A | N/A | N/A | 34219459 | 631 | 176.2078 | 0% | 0% | 100% | 0% | 100% | 45% | 7587880 | 1597 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 88 | 23014849 | 3646 | 87.504 | 3.646 | 9.5 | 9.5 | 2B | 0 | 0 | 911 | 0 | 1009 | N/A | N/A | N/A | N/A | 34219944 | 485 | 133.0225 | 0% | 0% | 100% | 0% | 100% | 45% | 7589065 | 1185 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 95 | 23018655 | 3806 | 91.344 | 3.806 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 997 | N/A | N/A | N/A | N/A | 34220460 | 516 | 135.5754 | 0% | 0% | 100% | 0% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 110 | 23023318 | 4663 | 111.912 | 4.663 | 9.5 | 9.5 | 2B | 0 | 0 | 1112 | 0 | 1129 | N/A | N/A | N/A | N/A | 34221184 | 724 | 155.2649 | 0% | 0% | 100% | 0% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 23029159 | 5841 | 140.184 | 5.841 | 9.3 | 9.3 | 3B+1S | 0 | 1033 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34222460 | 1276 | 218.4557 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 23035162 | 6003 | 144.072 | 6.003 | 8.9 | 8.9 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34223780 | 1320 | 219.8901 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 23041318 | 6156 | 147.744 | 6.156 | 8.2 | 8.2 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34225168 | 1388 | 225.4711 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 124 | 145 | 23047446 | 6128 | 147.072 | 6.128 | 7.5 | 7.5 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34226540 | 1372 | 223.8903 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 23053597 | 6151 | 147.624 | 6.151 | 7.2 | 7.2 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34227916 | 1376 | 223.7035 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 142 | 23059671 | 6074 | 145.776 | 6.074 | 6.2 | 6.2 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34229300 | 1384 | 227.8564 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 23065599 | 5928 | 142.272 | 5.928 | 5.7 | 5.7 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34230660 | 1360 | 229.4197 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 23071423 | 5824 | 139.776 | 5.824 | 5.4 | 5.4 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34231996 | 1336 | 229.3956 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 23077031 | 5608 | 134.592 | 5.608 | 5.1 | 5.1 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34233284 | 1288 | 229.6719 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 23082695 | 5664 | 135.936 | 5.664 | 4.9 | 4.9 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34234596 | 1312 | 231.6384 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 23088377 | 5682 | 136.368 | 5.682 | 4.6 | 4.6 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34235946 | 1350 | 237.5924 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 122 | 23093987 | 5610 | 134.64 | 5.61 | 4.1 | 4.1 | 3B+1S | 0 | 1027 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34237212 | 1266 | 225.6684 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 23099583 | 5596 | 134.304 | 5.596 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34238492 | 1280 | 228.7348 | 0% | 100% | 100% | 100% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 120 | 130 | 23105008 | 5425 | 130.2 | 5.425 | 3 | 3 | 2B+1S | 0 | 1152 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34239588 | 1096 | 202.0276 | 0% | 100% | 100% | 0% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 23110382 | 5374 | 128.976 | 5.374 | 1.9 | 1.9 | 2B+1S | 0 | 1100 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34240664 | 1076 | 200.2233 | 0% | 100% | 100% | 0% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 120 | 23115557 | 5175 | 124.2 | 5.175 | 2.2 | 2.2 | 2B+1S | 0 | 1015 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34241692 | 1028 | 198.6473 | 0% | 100% | 100% | 0% | 100% | 0% | 7589065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 102 | 23119974 | 4417 | 106.008 | 4.417 | 2.4 | 2.4 | 2B | 0 | 0 | 1098 | 0 | 1110 | N/A | N/A | N/A | N/A | 34242464 | 772 | 174.7793 | 0% | 0% | 100% | 0% | 100% | 25% | 7589592 | 527 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 93 | 23123910 | 3936 | 94.464 | 3.936 | 2.9 | 2.9 | 2B | 0 | 0 | 1033 | 0 | 1058 | N/A | N/A | N/A | N/A | 34243124 | 660 | 167.6829 | 0% | 0% | 100% | 0% | 100% | 25% | 7590204 | 612 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.7917 | 123291 | 123291 | 123.291 | 123.291 | [12 empty] | 25500 | 25500 | 206.8277 | [6 empty] | 6704 | 6704 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:23 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 27, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25536 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23123910 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34243124 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7590204 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 89 | 23127895 | 3985 | 95.64 | 3.985 | 4.1 | 4.1 | 2B | 0 | 0 | 1190 | 0 | 1010 | N/A | N/A | N/A | N/A | 34243780 | 656 | 164.6173 | 0% | 0% | 100% | 0% | 100% | 35% | 7591493 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 87 | 23131581 | 3686 | 88.464 | 3.686 | 5.3 | 5.3 | 2B | 0 | 0 | 1190 | 0 | 1010 | N/A | N/A | N/A | N/A | 34244356 | 576 | 156.267 | 0% | 0% | 100% | 0% | 100% | 35% | 7592991 | 1498 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 81 | 23134832 | 3251 | 78.024 | 3.251 | 6.5 | 6.5 | 2B | 0 | 0 | 981 | 0 | 1010 | N/A | N/A | N/A | N/A | 34244860 | 504 | 155.0292 | 0% | 0% | 100% | 0% | 100% | 35% | 7594806 | 1815 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 83 | 23138254 | 3422 | 82.128 | 3.422 | 7.8 | 7.8 | 2B | 0 | 0 | 1000 | 0 | 1018 | N/A | N/A | N/A | N/A | 34245372 | 512 | 149.6201 | 0% | 0% | 100% | 0% | 100% | 50% | 7596237 | 1431 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 131 | 95 | 23142389 | 4135 | 99.24 | 4.135 | 9.2 | 9.2 | 2B | 0 | 0 | 1148 | 0 | 1018 | N/A | N/A | N/A | N/A | 34246020 | 648 | 156.711 | 0% | 0% | 100% | 0% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 119 | 23147207 | 4818 | 115.632 | 4.818 | 9.5 | 9.5 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 34246788 | 768 | 159.4022 | 0% | 0% | 100% | 0% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 146 | 23152987 | 5780 | 138.72 | 5.78 | 9.4 | 9.4 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34248068 | 1280 | 221.4533 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 23159252 | 6265 | 150.36 | 6.265 | 8.9 | 8.9 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34249460 | 1392 | 222.1868 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 23165288 | 6036 | 144.864 | 6.036 | 8.3 | 8.3 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34250812 | 1352 | 223.9894 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 23171471 | 6183 | 148.392 | 6.183 | 7.5 | 7.5 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34252212 | 1400 | 226.4273 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 146 | 23177655 | 6184 | 148.416 | 6.184 | 6.8 | 6.8 | 3B+1S | 0 | 1164 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34253628 | 1416 | 228.978 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 146 | 23183839 | 6184 | 148.416 | 6.184 | 5.9 | 5.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34255044 | 1416 | 228.978 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 145 | 23189807 | 5968 | 143.232 | 5.968 | 5.1 | 5.1 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34256420 | 1376 | 230.563 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 23195659 | 5852 | 140.448 | 5.852 | 4.6 | 4.6 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34257772 | 1352 | 231.0321 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 23201364 | 5705 | 136.92 | 5.705 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34259072 | 1300 | 227.8703 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 23206866 | 5502 | 132.048 | 5.502 | 4.3 | 4.3 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34260372 | 1300 | 236.2777 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 23211552 | 4686 | 112.464 | 4.686 | 4 | 4 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34261428 | 1056 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 23217090 | 5538 | 132.912 | 5.538 | 3.7 | 3.7 | 3B+1S | 0 | 1010 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34262708 | 1280 | 231.1304 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 23222558 | 5468 | 131.232 | 5.468 | 3.6 | 3.6 | 3B+1S | 0 | 995 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34263972 | 1264 | 231.1631 | 0% | 100% | 100% | 100% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 126 | 23227902 | 5344 | 128.256 | 5.344 | 2.9 | 2.9 | 2B+1S | 0 | 1107 | 1176 | 0 | 1198 | N/A | N/A | N/A | N/A | 34265068 | 1096 | 205.0898 | 0% | 100% | 100% | 0% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 23233138 | 5236 | 125.664 | 5.236 | 2.2 | 2.2 | 2B+1S | 0 | 1077 | 1176 | 0 | 1198 | N/A | N/A | N/A | N/A | 34266124 | 1056 | 201.6807 | 0% | 100% | 100% | 0% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 117 | 23238158 | 5020 | 120.48 | 5.02 | 1.9 | 1.9 | 2B+1S | 0 | 1005 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34267132 | 1008 | 200.7968 | 0% | 100% | 100% | 0% | 100% | 0% | 7596237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 103 | 23242545 | 4387 | 105.288 | 4.387 | 2.5 | 2.5 | 2B | 0 | 0 | 1109 | 0 | 1120 | N/A | N/A | N/A | N/A | 34267932 | 800 | 182.357 | 0% | 0% | 100% | 0% | 100% | 38% | 7597218 | 981 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 96 | 23246676 | 4131 | 99.144 | 4.131 | 3.4 | 3.4 | 2B | 0 | 0 | 1073 | 0 | 1099 | N/A | N/A | N/A | N/A | 34268660 | 728 | 176.2285 | 0% | 0% | 100% | 0% | 100% | 38% | 7598138 | 920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5833 | 122766 | 122766 | 122.766 | 122.766 | [12 empty] | 25536 | 25536 | 208.0055 | [6 empty] | 7934 | 7934 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 - INCREASE OPENING TO 50% @ 4:01 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 5:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 28, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
POWER FLUCTUATION @ 4:21 PM
RESUME MERALCO POWER @ 4:23 PM
RESUME NORMAL OPERATION @ 4:39 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25784 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23246676 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34268660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7598138 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 95 | 23250662 | 3986 | 95.664 | 3.986 | 4.9 | 4.9 | 2B | 0 | 0 | 1061 | 0 | 1099 | N/A | N/A | N/A | N/A | 34269348 | 688 | 172.6041 | 0% | 0% | 100% | 0% | 100% | 35% | 7599419 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 23254543 | 3881 | 93.144 | 3.881 | 6.2 | 6.2 | 2B | 0 | 0 | 1038 | 0 | 1068 | N/A | N/A | N/A | N/A | 34269996 | 648 | 166.9673 | 0% | 0% | 100% | 0% | 100% | 35% | 7600766 | 1347 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 23258373 | 3830 | 91.92 | 3.83 | 7.7 | 7.7 | 2B | 0 | 0 | 1017 | 0 | 1047 | N/A | N/A | N/A | N/A | 34270620 | 624 | 162.9243 | 0% | 0% | 100% | 0% | 100% | 35% | 7602140 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 89 | 23262173 | 3800 | 91.2 | 3.8 | 9.1 | 9.1 | 2B | 0 | 0 | 1014 | 0 | 1014 | N/A | N/A | N/A | N/A | 34271204 | 584 | 153.6842 | 0% | 0% | 100% | 0% | 100% | 50% | 7603529 | 1389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 100 | 23266094 | 3921 | 94.104 | 3.921 | 9.5 | 9.5 | 2B | 0 | 0 | 984 | 0 | 997 | N/A | N/A | N/A | N/A | 34271768 | 564 | 143.8409 | 0% | 0% | 100% | 0% | 100% | 0% | 7603701 | 172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 114 | 113 | 23270604 | 4510 | 108.24 | 4.51 | 9.5 | 9.5 | 2B | 0 | 0 | 1130 | 0 | 1110 | N/A | N/A | N/A | N/A | 34272484 | 716 | 158.7583 | 0% | 0% | 100% | 0% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 139 | 23276474 | 5870 | 140.88 | 5.87 | 9.4 | 9.4 | 3B+1S | 0 | 980 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34273816 | 1332 | 226.9165 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 23282251 | 5777 | 138.648 | 5.777 | 9 | 9 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34275120 | 1304 | 225.7227 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 139 | 23288352 | 6101 | 146.424 | 6.101 | 8.4 | 8.4 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34276492 | 1372 | 224.8812 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 151 | 23294501 | 6149 | 147.576 | 6.149 | 7.8 | 7.8 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34277872 | 1380 | 224.4267 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 144 | 23300595 | 6094 | 146.256 | 6.094 | 7.1 | 7.1 | 3B+1S | 0 | 1116 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34279252 | 1380 | 226.4522 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 144 | 23306554 | 5959 | 143.016 | 5.959 | 6.4 | 6.4 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34280624 | 1372 | 230.24 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 23312475 | 5921 | 142.104 | 5.921 | 6 | 6 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34281996 | 1372 | 231.7176 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 23318146 | 5671 | 136.104 | 5.671 | 5.6 | 5.6 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34283308 | 1312 | 231.3525 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 134 | 23323665 | 5519 | 132.456 | 5.519 | 5.4 | 5.4 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34284600 | 1292 | 234.1004 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 132 | 23329150 | 5485 | 131.64 | 5.485 | 5.3 | 5.3 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34285910 | 1310 | 238.8332 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 23334799 | 5649 | 135.576 | 5.649 | 5.1 | 5.1 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34287220 | 1310 | 231.8995 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 23340335 | 5536 | 132.864 | 5.536 | 4.8 | 4.8 | 3B+1S | 0 | 1011 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34288492 | 1272 | 229.7688 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 131 | 23345967 | 5632 | 135.168 | 5.632 | 4.5 | 4.5 | 3B+1S | 0 | 1011 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34289788 | 1296 | 230.1136 | 0% | 100% | 100% | 100% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 125 | 23351319 | 5352 | 128.448 | 5.352 | 3.5 | 3.5 | 2B+1S | 0 | 1123 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34290892 | 1104 | 206.278 | 0% | 100% | 100% | 0% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 23356493 | 5174 | 124.176 | 5.174 | 2.8 | 2.8 | 2B+1S | 0 | 1066 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34291940 | 1048 | 202.5512 | 0% | 100% | 100% | 0% | 100% | 0% | 7603701 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 117 | 23361645 | 5152 | 123.648 | 5.152 | 2.3 | 2.3 | 2B+1S | 0 | 1019 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34292972 | 1032 | 200.3106 | 0% | 100% | 100% | 0% | 100% | 0% | 7603701 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 105 | 23365822 | 4177 | 100.248 | 4.177 | 3.1 | 3.1 | 2B | 0 | 0 | 1031 | 0 | 1149 | N/A | N/A | N/A | N/A | 34293700 | 728 | 174.2878 | 0% | 0% | 100% | 0% | 100% | 38% | 7604596 | 895 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 96 | 23370049 | 4227 | 101.448 | 4.227 | 4 | 4 | 2B | 0 | 0 | 1049 | 0 | 1110 | N/A | N/A | N/A | N/A | 34294444 | 744 | 176.0114 | 0% | 0% | 100% | 0% | 100% | 38% | 7605363 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123 | 123373 | 123373 | 123.373 | 123.373 | [12 empty] | 25784 | 25784 | 208.9922 | [6 empty] | 7225 | 7225 | 0.99 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 - CLOSED @ 4:09 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:28 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 29, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (%) @ 10:01 AM FOR REFILLING
NORMAL OPERATION

## JAN 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS / FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25816 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23370049 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34294444 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7605363 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 89 | 23373848 | 3799 | 91.176 | 3.799 | 5.2 | 5.2 | 2B | 0 | 0 | 1024 | 0 | 1110 | N/A | N/A | N/A | N/A | 34295100 | 656 | 172.677 | 0% | 0% | 100% | 0% | 100% | 35% | 7606500 | 1137 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 23377666 | 3818 | 91.632 | 3.818 | 6.5 | 6.5 | 2B | 0 | 0 | 1029 | 0 | 1053 | N/A | N/A | N/A | N/A | 34295744 | 644 | 168.6747 | 0% | 0% | 100% | 0% | 100% | 35% | 7607809 | 1309 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 23381921 | 4255 | 102.12 | 4.255 | 8.2 | 8.2 | 2B | 0 | 0 | 976 | 0 | 1059 | N/A | N/A | N/A | N/A | 34296428 | 684 | 160.7521 | 0% | 0% | 100% | 0% | 100% | 35% | 7609384 | 1575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 88 | 23384979 | 3058 | 73.392 | 3.058 | 9.2 | 9.2 | 2B | 0 | 0 | 1002 | 0 | 1037 | N/A | N/A | N/A | N/A | 34296908 | 480 | 156.9653 | 0% | 0% | 100% | 0% | 100% | 50% | 7610396 | 1012 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 96 | 23388888 | 3909 | 93.816 | 3.909 | 9.5 | 9.5 | 2B | 0 | 0 | 1011 | 0 | 1018 | N/A | N/A | N/A | N/A | 34297476 | 568 | 145.3057 | 0% | 0% | 100% | 0% | 100% | 0% | 7610545 | 149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 112 | 23393355 | 4467 | 107.208 | 4.467 | 9.5 | 9.5 | 2B | 0 | 0 | 1140 | 0 | 1110 | N/A | N/A | N/A | N/A | 34298188 | 712 | 159.3911 | 0% | 0% | 100% | 0% | 100% | 0% | 7610545 | 0 | 1.15 | Normal operation schedule | Error - General | E | FIDEL RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 142 | 23399247 | 5892 | 141.408 | 5.892 | 9.3 | 9.3 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34299508 | 1320 | 224.0326 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Normal operation schedule | Power Interruption | PI | ALEXANDER CABREROS / FIDEL RAMOS
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 23405247 | 6000 | 144 | 6 | 8.8 | 8.8 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34300860 | 1352 | 225.3333 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 23411764 | 6517 | 156.408 | 6.517 | 8 | 8 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34302324 | 1464 | 224.6432 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 148 | 23417563 | 5799 | 139.176 | 5.799 | 7.4 | 7.4 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34303640 | 1316 | 226.9357 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 23424005 | 6442 | 154.608 | 6.442 | 6.7 | 6.7 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34305084 | 1444 | 224.154 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 148 | 23429810 | 5805 | 139.32 | 5.805 | 6.1 | 6.1 | 3B+1S | 0 | 1126 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34306420 | 1336 | 230.1464 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 138 | 23435866 | 6056 | 145.344 | 6.056 | 5.7 | 5.7 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34307812 | 1392 | 229.8547 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 23441490 | 5624 | 134.976 | 5.624 | 5.2 | 5.2 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34309120 | 1308 | 232.5747 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 23446946 | 5456 | 130.944 | 5.456 | 5 | 5 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34310404 | 1284 | 235.3372 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 131 | 23452443 | 5497 | 131.928 | 5.497 | 4.9 | 4.9 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34311700 | 1296 | 235.765 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 129 | 23457988 | 5545 | 133.08 | 5.545 | 4.7 | 4.7 | 3B+1S | 0 | 1038 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34313012 | 1312 | 236.6096 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 131 | 23463479 | 5491 | 131.784 | 5.491 | 4.4 | 4.4 | 3B+1S | 0 | 1012 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34314288 | 1276 | 232.3803 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 130 | 23469018 | 5539 | 132.936 | 5.539 | 4 | 4 | 3B+1S | 0 | 1014 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34315568 | 1280 | 231.0886 | 0% | 100% | 100% | 100% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 126 | 23474347 | 5329 | 127.896 | 5.329 | 3.1 | 3.1 | 2B+1S | 0 | 1150 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34316668 | 1100 | 206.4177 | 0% | 100% | 100% | 0% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 23479609 | 5262 | 126.288 | 5.262 | 2.4 | 2.4 | 2B+1S | 0 | 1061 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34317748 | 1080 | 205.2452 | 0% | 100% | 100% | 0% | 100% | 0% | 7610545 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 120 | 23484683 | 5074 | 121.776 | 5.074 | 2 | 2 | 2B+1S | 0 | 1008 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34318764 | 1016 | 200.2365 | 0% | 100% | 100% | 0% | 100% | 0% | 7610545 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 100 | 23489014 | 4331 | 103.944 | 4.331 | 2.7 | 2.7 | 2B | 0 | 0 | 1084 | 0 | 1140 | N/A | N/A | N/A | N/A | 34319556 | 792 | 182.8677 | 0% | 0% | 100% | 0% | 100% | 38% | 7611311 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 95 | 23493062 | 4048 | 97.152 | 4.048 | 3.6 | 3.6 | 2B | 0 | 0 | 1041 | 0 | 1120 | N/A | N/A | N/A | N/A | 34320260 | 704 | 173.913 | 0% | 0% | 100% | 0% | 100% | 38% | 7612256 | 945 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5 | 123013 | 123013 | 123.013 | 123.013 | [12 empty] | 25816 | 25816 | 209.864 | [6 empty] | 6893 | 6893 | 0.975 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 43% @ 12:01 AM
XCV1 CLOSED @ 4:11 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 28, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | D GUANZON/F RAMOS
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25624 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23493062 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34320260 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7612256 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 90 | 23496854 | 3792 | 91.008 | 3.792 | 5.1 | 5.1 | 2B | 0 | 0 | 1042 | 0 | 1079 | N/A | N/A | N/A | N/A | 34320908 | 648 | 170.8861 | 0% | 0% | 100% | 0% | 100% | 35% | 7613665 | 1409 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 87 | 23500522 | 3668 | 88.032 | 3.668 | 6.6 | 6.6 | 2B | 0 | 0 | 1011 | 0 | 1059 | N/A | N/A | N/A | N/A | 34321520 | 612 | 166.8484 | 0% | 0% | 100% | 0% | 100% | 35% | 7615121 | 1456 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 23504445 | 3923 | 94.152 | 3.923 | 8.5 | 8.5 | 2B | 0 | 0 | 1011 | 0 | 1059 | N/A | N/A | N/A | N/A | 34322170 | 650 | 165.6895 | 0% | 0% | 100% | 0% | 100% | 35% | 7616550 | 1429 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 87 | 23507644 | 3199 | 76.776 | 3.199 | 9.5 | 9.5 | 2B | 0 | 0 | 945 | 0 | 977 | N/A | N/A | N/A | N/A | 34322636 | 466 | 145.6705 | 0% | 0% | 100% | 0% | 100% | 50% | 7617660 | 1110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 94 | 23511120 | 3476 | 83.424 | 3.476 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 994 | N/A | N/A | N/A | N/A | 34323112 | 476 | 136.939 | 0% | 0% | 100% | 0% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 115 | 23516059 | 4939 | 118.536 | 4.939 | 9.5 | 9.5 | 2B | 0 | 0 | 1104 | 0 | 1160 | N/A | N/A | N/A | N/A | 34323884 | 772 | 156.3069 | 0% | 0% | 100% | 0% | 100% | 0% | 7617660 | 0 | 1.24 | Normal operation schedule | Error - General | E | D GUANZON/F RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 135 | 23521700 | 5641 | 135.384 | 5.641 | 9.4 | 9.4 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34325136 | 1252 | 221.9465 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 23527698 | 5998 | 143.952 | 5.998 | 9 | 9 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34326492 | 1356 | 226.0754 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 151 | 23533895 | 6197 | 148.728 | 6.197 | 8.4 | 8.4 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34327384 | 892 | 143.9406 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 23539983 | 6088 | 146.112 | 6.088 | 7.5 | 7.5 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34329272 | 1888 | 310.1183 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 23546046 | 6063 | 145.512 | 6.063 | 6.9 | 6.9 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34330660 | 1388 | 228.9296 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 23552043 | 5997 | 143.928 | 5.997 | 6.1 | 6.1 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34332044 | 1384 | 230.7821 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 23557955 | 5912 | 141.888 | 5.912 | 5.7 | 5.7 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34333396 | 1352 | 228.6874 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 112 | 138 | 23563665 | 5710 | 137.04 | 5.71 | 5.3 | 5.3 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 34334740 | 1344 | 235.3765 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 23569482 | 5817 | 139.608 | 5.817 | 4.9 | 4.9 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 34336072 | 1332 | 228.984 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 23575182 | 5700 | 136.8 | 5.7 | 4.8 | 4.8 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34337396 | 1324 | 232.2807 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 23580956 | 5774 | 138.576 | 5.774 | 4.3 | 4.3 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34338752 | 1356 | 234.8459 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 23586493 | 5537 | 132.888 | 5.537 | 3.9 | 3.9 | 3B+1S | 0 | 997 | 1170 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34340018 | 1266 | 228.6437 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 127 | 23591821 | 5328 | 127.872 | 5.328 | 3.8 | 3.8 | 3B+1S | 0 | 999 | 1174 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34341284 | 1266 | 237.6126 | 0% | 100% | 100% | 100% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 127 | 23597075 | 5254 | 126.096 | 5.254 | 3.1 | 3.1 | 2B+1S | 0 | 1170 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34342364 | 1080 | 205.5577 | 0% | 100% | 100% | 0% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 23602110 | 5035 | 120.84 | 5.035 | 2.5 | 2.5 | 2B+1S | 0 | 1053 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34343368 | 1004 | 199.4042 | 0% | 100% | 100% | 0% | 100% | 0% | 7617660 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 119 | 23607287 | 5177 | 124.248 | 5.177 | 2 | 2 | 2B+1S | 0 | 1002 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34344424 | 1056 | 203.9791 | 0% | 100% | 100% | 0% | 100% | 0% | 7617660 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 102 | 23611529 | 4242 | 101.808 | 4.242 | 2.8 | 2.8 | 2B | 0 | 0 | 1081 | 0 | 1141 | N/A | N/A | N/A | N/A | 34345184 | 760 | 179.1608 | 0% | 0% | 100% | 0% | 100% | 38% | 7618356 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 94 | 23615615 | 4086 | 98.064 | 4.086 | 3.6 | 3.6 | 2B | 0 | 0 | 1088 | 0 | 1032 | N/A | N/A | N/A | N/A | 34345884 | 700 | 171.3167 | 0% | 0% | 100% | 0% | 100% | 38% | 7619207 | 851 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0833 | 122553 | 122553 | 122.553 | 122.553 | [12 empty] | 25624 | 25624 | 209.085 | [6 empty] | 6951 | 6951 | 1.0483 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 28, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (32%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## JAN 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25884 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23615615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34345884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7619207 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 23619458 | 3843 | 92.232 | 3.843 | 5 | 5 | 2B | 0 | 0 | 1028 | 0 | 1088 | N/A | N/A | N/A | N/A | 34346540 | 656 | 170.7 | 0% | 0% | 100% | 0% | 100% | 35% | 7620499 | 1292 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 87 | 23623022 | 3564 | 85.536 | 3.564 | 6.1 | 6.1 | 2B | 0 | 0 | 1028 | 0 | 1088 | N/A | N/A | N/A | N/A | 34347120 | 580 | 162.7385 | 0% | 0% | 100% | 0% | 100% | 35% | 7621806 | 1307 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 83 | 23626645 | 3623 | 86.952 | 3.623 | 7.9 | 7.9 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 34347732 | 612 | 168.9208 | 0% | 0% | 100% | 0% | 100% | 35% | 7623155 | 1349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 82 | 23630215 | 3570 | 85.68 | 3.57 | 9.1 | 9.1 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 34348276 | 544 | 152.381 | 0% | 0% | 100% | 0% | 100% | 0% | 7624390 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 90 | 23633841 | 3626 | 87.024 | 3.626 | 9.5 | 9.5 | 2B | 0 | 0 | 921 | 0 | 937 | N/A | N/A | N/A | N/A | 34348792 | 516 | 142.3056 | 0% | 0% | 100% | 0% | 100% | 0% | 7624641 | 251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL RAMOS
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 107 | 105 | 23638046 | 4205 | 100.92 | 4.205 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 1059 | N/A | N/A | N/A | N/A | 34349356 | 564 | 134.126 | 0% | 0% | 100% | 0% | 100% | 0% | 7624641 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 135 | 23643869 | 5823 | 139.752 | 5.823 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1148 | N/A | N/A | N/A | N/A | 34350540 | 1184 | 203.3316 | 0% | 0% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 23649433 | 5564 | 133.536 | 5.564 | 9 | 9 | 3B+1S | 0 | 1130 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34351784 | 1244 | 223.5802 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 128 | 150 | 23655697 | 6264 | 150.336 | 6.264 | 8.2 | 8.2 | 3B+1S | 0 | 1150 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34353212 | 1428 | 227.9693 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 146 | 23661855 | 6158 | 147.792 | 6.158 | 7.2 | 7.2 | 3B+1S | 0 | 1187 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34354652 | 1440 | 233.8422 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 149 | 23668019 | 6164 | 147.936 | 6.164 | 6.3 | 6.3 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34356106 | 1454 | 235.8858 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 143 | 23674390 | 6371 | 152.904 | 6.371 | 5.2 | 5.2 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34357580 | 1474 | 231.3609 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 144 | 23680226 | 5836 | 140.064 | 5.836 | 4.4 | 4.4 | 3B+1S | 0 | 1116 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34358956 | 1376 | 235.7779 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 23686214 | 5988 | 143.712 | 5.988 | 3.5 | 3.5 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34360336 | 1380 | 230.4609 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 23692116 | 5902 | 141.648 | 5.902 | 2.9 | 2.9 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34361716 | 1380 | 233.819 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 23698013 | 5897 | 141.528 | 5.897 | 2.5 | 2.5 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34363084 | 1368 | 231.9824 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 142 | 23703865 | 5852 | 140.448 | 5.852 | 1.9 | 1.9 | 3B+1S | 0 | 1149 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34364460 | 1376 | 235.1333 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 23709610 | 5745 | 137.88 | 5.745 | 1.4 | 1.4 | 3B+1S | 0 | 1060 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34365780 | 1320 | 229.765 | 0% | 100% | 100% | 100% | 100% | 0% | 7624641 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 130 | 123 | 23714809 | 5199 | 124.776 | 5.199 | 1.3 | 1.3 | 3B | 0 | 0 | 1155 | 1185 | 1099 | N/A | N/A | N/A | N/A | 34366860 | 1080 | 207.7323 | 0% | 0% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 | 127 | 23720101 | 5292 | 127.008 | 5.292 | 1.3 | 1.3 | 3B | 0 | 0 | 1155 | 1185 | 1099 | N/A | N/A | N/A | N/A | 34367996 | 1136 | 214.6636 | 0% | 0% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 128 | 23725332 | 5231 | 125.544 | 5.231 | 1.3 | 1.3 | 3B | 0 | 0 | 1116 | 1185 | 1148 | N/A | N/A | N/A | N/A | 34369124 | 1128 | 215.6375 | 0% | 0% | 100% | 100% | 100% | 0% | 7624641 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 118 | 23730550 | 5218 | 125.232 | 5.218 | 1.3 | 1.3 | 3B | 0 | 0 | 1004 | 1185 | 1148 | N/A | N/A | N/A | N/A | 34370220 | 1096 | 210.0422 | 0% | 0% | 100% | 100% | 100% | 0% | 7624641 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 103 | 23734911 | 4361 | 104.664 | 4.361 | 2.2 | 2.2 | 2B | 0 | 0 | 1116 | 0 | 1139 | N/A | N/A | N/A | N/A | 34371036 | 816 | 187.113 | 0% | 0% | 100% | 0% | 100% | 38% | 7625540 | 899 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 99 | 23739060 | 4149 | 99.576 | 4.149 | 3.2 | 3.2 | 2B | 0 | 0 | 1083 | 0 | 1100 | N/A | N/A | N/A | N/A | 34371768 | 732 | 176.4281 | 0% | 0% | 100% | 0% | 100% | 38% | 7626574 | 1034 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.6667 | 123445 | 123445 | 123.445 | 123.445 | [12 empty] | 25884 | 25884 | 209.6804 | [6 empty] | 7367 | 7367 | 1.0717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 42% @ 12:01 AM
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
GENSET 1 WARMUP EXERCISED @ 4:01 PM
GENSET 2 WARMUP EXERCISED @ 4:11 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
SP2 - STOPPED @ 6:01 PM DUE TO LOW WATER LEVEL AND LOW SUCTION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @6:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 1 (hidden)
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-01-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | -34268660 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23246676 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34268660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7598138 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 |  |  |  | -23246676 | -557920.224 | -23246.676 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 35% |  | -7598138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 |  |  |  | 0 | 0 | 0 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 35% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 |  |  |  | 0 | 0 | 0 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 35% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 |  |  |  | 0 | 0 | 0 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 50% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 |  |  |  | 0 | 0 | 0 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 |  | 0 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 |  |  |  | 0 | 0 | 0 |  | 0 | 2B | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule
58:00 | 11:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule
59:00 | 12:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 |  | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 |  | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 |  |  |  | 0 | 0 | 0 |  | 0 |  | Motor Speed (RPM) SP1: 0; Motor Speed (RPM) BP4: N/A; Motor Speed (RPM) BP5: N/A; Motor Speed (RPM) BP6: N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 |  |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 |  |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 |  |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 38% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 0% | 100% | 38% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | #DIV/0! | -23246676 | -23246676 | -23246.676 | -23246.676 | [12 empty] | -34268660 | 0 | 0 | [6 empty] | -7598138 | -7598138 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: NO CHLORINE RESIDUAL DUE TO CALIBRATION OF COLORIMETER
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 35% @ 12:01 AM
XCV1 - INCREASE OPENING TO 50% @ 4:01 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 5:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (JAN 28, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM, NORMAL OPERATION
POWER FLUCTUATION @ 4:21 PM
RESUME MERALCO POWER @ 4:23 PM
RESUME NORMAL OPERATION @ 4:39 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION