## FEB 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | R. MALLARI / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25250 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23739060 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34371768 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7626574 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 92 | 23743015 | 3955 | 94.92 | 3.955 | 4.6 | 4.6 | 2B | 0 | 0 | 1067 | 0 | 1088 | N/A | N/A | N/A | N/A | 34372460 | 692 | 174.9684 | 0% | 0% | 100% | 0% | 100% | 42% | 7627797 | 1223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 87 | 23746820 | 3805 | 91.32 | 3.805 | 6.1 | 6.1 | 2B | 0 | 0 | 1008 | 0 | 1030 | N/A | N/A | N/A | N/A | 34373058 | 598 | 157.1616 | 0% | 0% | 100% | 0% | 100% | 42% | 7629122 | 1325 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 23750500 | 3680 | 88.32 | 3.68 | 7.5 | 7.5 | 2B | 0 | 0 | 1008 | 0 | 1030 | N/A | N/A | N/A | N/A | 34373710 | 652 | 177.1739 | 0% | 0% | 100% | 0% | 100% | 42% | 7630444 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 88 | 23753914 | 3414 | 81.936 | 3.414 | 8.8 | 8.8 | 2B | 0 | 0 | 1010 | 0 | 1028 | N/A | N/A | N/A | N/A | 34374256 | 546 | 159.9297 | 0% | 0% | 100% | 0% | 100% | 42% | 7631774 | 1330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 87 | 23757564 | 3650 | 87.6 | 3.65 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 957 | N/A | N/A | N/A | N/A | 34374788 | 532 | 145.7534 | 0% | 0% | 100% | 0% | 100% | 42% | 7632373 | 599 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 101 | 101 | 23761499 | 3935 | 94.44 | 3.935 | 9.5 | 9.5 | 2B | 0 | 0 | 969 | 0 | 968 | N/A | N/A | N/A | N/A | 34375292 | 504 | 128.0813 | 0% | 0% | 100% | 0% | 100% | 0% | 7632373 | 0 | 0.75 | Normal operation schedule | Error - General | E | R. MALLARI / F. RAMOS
54:00 | 7:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 130 | 23766741 | 5242 | 125.808 | 5.242 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1078 | N/A | N/A | N/A | N/A | 34376292 | 1000 | 190.7669 | 0% | 0% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 23772503 | 5762 | 138.288 | 5.762 | 9.5 | 9.5 | 3B+1S | 0 | 969 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34377516 | 1224 | 212.4262 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 23778596 | 6093 | 146.232 | 6.093 | 9.1 | 9.1 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34378864 | 1348 | 221.2375 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 23784804 | 6208 | 148.992 | 6.208 | 8.4 | 8.4 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34380272 | 1408 | 226.8041 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 | 0.87 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 23790873 | 6069 | 145.656 | 6.069 | 7.7 | 7.7 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34381644 | 1372 | 226.0669 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 148 | 23796967 | 6094 | 146.256 | 6.094 | 7 | 7 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34383036 | 1392 | 228.4214 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 149 | 23803025 | 6058 | 145.392 | 6.058 | 6.3 | 6.3 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34384424 | 1388 | 229.1185 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 142 | 23808976 | 5951 | 142.824 | 5.951 | 5.6 | 5.6 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34385820 | 1396 | 234.5824 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 23814790 | 5814 | 139.536 | 5.814 | 5 | 5 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34387184 | 1364 | 234.6061 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 139 | 23820572 | 5782 | 138.768 | 5.782 | 4.6 | 4.6 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34388532 | 1348 | 233.1373 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 141 | 23826324 | 5752 | 138.048 | 5.752 | 3.9 | 3.9 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34389864 | 1332 | 231.5716 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 133 | 23831862 | 5538 | 132.912 | 5.538 | 3.7 | 3.7 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34391168 | 1304 | 235.4641 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 23837364 | 5502 | 132.048 | 5.502 | 3.6 | 3.6 | 3B+1S | 0 | 995 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34392444 | 1276 | 231.9157 | 0% | 100% | 100% | 100% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 124 | 23842672 | 5308 | 127.392 | 5.308 | 3.1 | 3.1 | 2B+1S | 0 | 1049 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34393535 | 1091 | 205.5388 | 0% | 100% | 100% | 0% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 23847942 | 5270 | 126.48 | 5.27 | 2.4 | 2.4 | 2B+1S | 0 | 1048 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34394568 | 1033 | 196.0152 | 0% | 100% | 100% | 0% | 100% | 0% | 7632373 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 121 | 23853051 | 5109 | 122.616 | 5.109 | 2.2 | 2.2 | 2B+1S | 0 | 615 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34395580 | 1012 | 198.0818 | 0% | 100% | 100% | 0% | 100% | 0% | 7632373 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 99 | 23857492 | 4441 | 106.584 | 4.441 | 2.8 | 2.8 | 2B | 0 | 0 | 1098 | 0 | 1109 | N/A | N/A | N/A | N/A | 34396368 | 788 | 177.4375 | 0% | 0% | 100% | 0% | 100% | 30% | 7633004 | 631 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 94 | 23861314 | 3822 | 91.728 | 3.822 | 3.6 | 3.6 | 2B | 0 | 0 | 1009 | 0 | 1109 | N/A | N/A | N/A | N/A | 34397018 | 650 | 170.068 | 0% | 0% | 100% | 0% | 100% | 30% | 7633792 | 788 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5417 | 122254 | 122254 | 122.254 | 122.254 | [12 empty] | 25250 | 25250 | 206.5372 | [6 empty] | 7218 | 7218 | 0.89167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ 4:27 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:41 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:45 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25738 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23861314 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34397018 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7633792 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 87 | 23865182 | 3868 | 92.832 | 3.868 | 5.1 | 5.1 | 2B | 0 | 0 | 1043 | 0 | 1049 | N/A | N/A | N/A | N/A | 34397668 | 650 | 168.0455 | 0% | 0% | 100% | 0% | 100% | 40% | 7635125 | 1333 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 86 | 23868722 | 3540 | 84.96 | 3.54 | 6.3 | 6.3 | 2B | 0 | 0 | 1190 | 0 | 1040 | N/A | N/A | N/A | N/A | 34398236 | 568 | 160.452 | 0% | 0% | 100% | 0% | 100% | 40% | 7636425 | 1300 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 23872358 | 3636 | 87.264 | 3.636 | 7.9 | 7.9 | 2B | 0 | 0 | 965 | 0 | 1048 | N/A | N/A | N/A | N/A | 34398820 | 584 | 160.6161 | 0% | 0% | 100% | 0% | 100% | 40% | 7637814 | 1389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 90 | 23875869 | 3511 | 84.264 | 3.511 | 9.1 | 9.1 | 2B | 0 | 0 | 962 | 0 | 1049 | N/A | N/A | N/A | N/A | 34399360 | 540 | 153.8023 | 0% | 0% | 100% | 0% | 100% | 40% | 7639057 | 1243 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 101 | 23879747 | 3878 | 93.072 | 3.878 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 1048 | N/A | N/A | N/A | N/A | 34399920 | 560 | 144.4043 | 0% | 0% | 100% | 0% | 100% | 40% | 7639332 | 275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 114 | 23884210 | 4463 | 107.112 | 4.463 | 9.5 | 9.5 | 2B | 0 | 0 | 1100 | 0 | 1160 | N/A | N/A | N/A | N/A | 34400640 | 720 | 161.3265 | 0% | 0% | 100% | 0% | 100% | 0% | 7639332 | 0 | 0.88 | Normal operation schedule | Error - General | E | R. MALLARI / F. RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 145 | 23890920 | 6710 | 161.04 | 6.71 | 9.4 | 9.4 | 3B+1S | 0 | 994 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34401948 | 1308 | 194.9329 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 23896090 | 5170 | 124.08 | 5.17 | 8.9 | 8.9 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34403300 | 1352 | 261.5087 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 23902274 | 6184 | 148.416 | 6.184 | 8.3 | 8.3 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34404641 | 1341 | 216.8499 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 23908388 | 6114 | 146.736 | 6.114 | 7.6 | 7.6 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34406051 | 1410 | 230.6183 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 23914504 | 6116 | 146.784 | 6.116 | 7 | 7 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34407460 | 1409 | 230.3793 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 144 | 23920616 | 6112 | 146.688 | 6.112 | 6.2 | 6.2 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34408976 | 1516 | 248.0366 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 23926427 | 5811 | 139.464 | 5.811 | 5.7 | 5.7 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34410357 | 1381 | 237.6527 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 23932173 | 5746 | 137.904 | 5.746 | 5.4 | 5.4 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34411682 | 1325 | 230.5952 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 | 0.923 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 23937866 | 5693 | 136.632 | 5.693 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34412983 | 1301 | 228.5263 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 23943575 | 5709 | 137.016 | 5.709 | 4.9 | 4.9 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34414287 | 1304 | 228.4113 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 23949161 | 5586 | 134.064 | 5.586 | 4.5 | 4.5 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34415498 | 1211 | 216.792 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 23954785 | 5624 | 134.976 | 5.624 | 4.4 | 4.4 | 3B+1S | 0 | 993 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34416787 | 1289 | 229.1963 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 131 | 23960381 | 5596 | 134.304 | 5.596 | 4.2 | 4.2 | 3B+1S | 0 | 995 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34418092 | 1305 | 233.2023 | 0% | 100% | 100% | 100% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 134 | 23965833 | 5452 | 130.848 | 5.452 | 3.3 | 3.3 | 2B+1S | 0 | 1121 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34419209 | 1117 | 204.8789 | 0% | 100% | 100% | 0% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 125 | 23971195 | 5362 | 128.688 | 5.362 | 2.5 | 2.5 | 2B+1S | 0 | 1095 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34420286 | 1077 | 200.8579 | 0% | 100% | 100% | 0% | 100% | 0% | 7639332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 118 | 23976628 | 5433 | 130.392 | 5.433 | 2.1 | 2.1 | 2B+1S | 0 | 1005 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34421308 | 1022 | 188.1097 | 0% | 100% | 100% | 0% | 100% | 0% | 7639332 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 100 | 23980654 | 4026 | 96.624 | 4.026 | 5.6 | 5.6 | 2B | 0 | 0 | 1100 | 0 | 1110 | N/A | N/A | N/A | N/A | 34422084 | 776 | 192.7471 | 0% | 0% | 100% | 0% | 100% | 25% | 7639823 | 491 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 112 | 23984705 | 4051 | 97.224 | 4.051 | 3.2 | 3.2 | 2B | 0 | 0 | 1047 | 0 | 1067 | N/A | N/A | N/A | N/A | 34422756 | 672 | 165.885 | 0% | 0% | 100% | 0% | 100% | 25% | 7640412 | 589 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.625 | 123391 | 123391 | 123.391 | 123.391 | [12 empty] | 25738 | 25738 | 208.589 | [6 empty] | 6620 | 6620 | 0.8955 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 2, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A.CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26160 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23984705 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34422756 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7640412 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 | 92 | 23988520 | 3815 | 91.56 | 3.815 | 4.3 | 4.3 | 2B | 0 | 0 | 1082 | 0 | 1068 | N/A | N/A | N/A | N/A | 34423406 | 650 | 170.3801 | 0% | 0% | 100% | 0% | 100% | 40% | 7641527 | 1115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 90 | 23992244 | 3724 | 89.376 | 3.724 | 5.5 | 5.5 | 2B | 0 | 0 | 1082 | 0 | 1068 | N/A | N/A | N/A | N/A | 34424026 | 620 | 166.4876 | 0% | 0% | 100% | 0% | 100% | 40% | 7642816 | 1289 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 23995862 | 3618 | 86.832 | 3.618 | 7 | 7 | 2B | 0 | 0 | 952 | 0 | 1068 | N/A | N/A | N/A | N/A | 34424594 | 568 | 156.9928 | 0% | 0% | 100% | 0% | 100% | 40% | 7644329 | 1513 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 86 | 23999369 | 3507 | 84.168 | 3.507 | 8.7 | 8.7 | 2B | 0 | 0 | 952 | 0 | 1068 | N/A | N/A | N/A | N/A | 34425124 | 530 | 151.1263 | 0% | 0% | 100% | 0% | 100% | 40% | 7645700 | 1371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 99 | 24003196 | 3827 | 91.848 | 3.827 | 9.5 | 9.5 | 2B | 0 | 0 | 1020 | 0 | 987 | N/A | N/A | N/A | N/A | 34425708 | 584 | 152.5999 | 0% | 0% | 100% | 0% | 100% | 40% | 7646375 | 675 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 113 | 24007822 | 4626 | 111.024 | 4.626 | 9.5 | 9.5 | 2B | 0 | 0 | 1174 | 0 | 1109 | N/A | N/A | N/A | N/A | 34426460 | 752 | 162.5594 | 0% | 0% | 100% | 0% | 100% | 0% | 7646375 | 0 | 0.91 | Normal operation schedule | Error - General | E | A.CABREROS / F. RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 24013689 | 5867 | 140.808 | 5.867 | 9.2 | 9.2 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34427776 | 1316 | 224.3054 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 24019812 | 6123 | 146.952 | 6.123 | 8.5 | 8.5 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34429164 | 1388 | 226.6863 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 150 | 24025966 | 6154 | 147.696 | 6.154 | 7.7 | 7.7 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34430572 | 1408 | 228.7943 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 150 | 24032088 | 6122 | 146.928 | 6.122 | 6.8 | 6.8 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34431944 | 1372 | 224.1098 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 125 | 141 | 24038137 | 6049 | 145.176 | 6.049 | 6.1 | 6.1 | 3B+1S | 0 | 1158 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34433344 | 1400 | 231.4432 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 146 | 24044122 | 5985 | 143.64 | 5.985 | 5.2 | 5.2 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34434792 | 1448 | 241.9382 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 137 | 24049925 | 5803 | 139.272 | 5.803 | 4.8 | 4.8 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34436124 | 1332 | 229.5364 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 24055657 | 5732 | 137.568 | 5.732 | 4.5 | 4.5 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34437456 | 1332 | 232.3796 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 24061347 | 5690 | 136.56 | 5.69 | 4.1 | 4.1 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34438783 | 1327 | 233.2162 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 24067066 | 5719 | 137.256 | 5.719 | 3.8 | 3.8 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34440131 | 1348 | 235.7055 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 139 | 24072814 | 5748 | 137.952 | 5.748 | 3.3 | 3.3 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34441502 | 1371 | 238.5177 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 136 | 24078485 | 5671 | 136.104 | 5.671 | 3 | 3 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34442838 | 1336 | 235.5846 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 133 | 24084043 | 5558 | 133.392 | 5.558 | 2.9 | 2.9 | 3B+1S | 0 | 945 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34444118 | 1280 | 230.2987 | 0% | 100% | 100% | 100% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 120 | 128 | 24089448 | 5405 | 129.72 | 5.405 | 2.3 | 2.3 | 3B+1S | 0 | 1140 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 34445222 | 1104 | 204.2553 | 0% | 100% | 100% | 0% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 129 | 24094854 | 5406 | 129.744 | 5.406 | 1.4 | 1.4 | 3B+1S | 0 | 1118 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 34446326 | 1104 | 204.2175 | 0% | 100% | 100% | 0% | 100% | 0% | 7646375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 120 | 24099959 | 5105 | 122.52 | 5.105 | 1.3 | 1.3 | 2B+1S | 0 | 901 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 34447396 | 1070 | 209.5984 | 0% | 100% | 100% | 0% | 100% | 0% | 7646375 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 110 | 24104375 | 4416 | 105.984 | 4.416 | 2.2 | 2.2 | 2B | 0 | 0 | 1134 | 0 | 1110 | N/A | N/A | N/A | N/A | 34448184 | 788 | 178.442 | 0% | 0% | 100% | 0% | 100% | 38% | 7647324 | 949 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 93 | 24108500 | 4125 | 99 | 4.125 | 3.4 | 3.4 | 2B | 0 | 0 | 1051 | 0 | 1110 | N/A | N/A | N/A | N/A | 34448916 | 732 | 177.4545 | 0% | 0% | 100% | 0% | 100% | 38% | 7648411 | 1087 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4583 | 123795 | 123795 | 123.795 | 123.795 | [12 empty] | 26160 | 26160 | 211.3171 | [6 empty] | 7999 | 7999 | 0.945 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 40% @ 12:01 AM
XCV1 CLOSED @ : 4:36AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 3, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26380 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24108500 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34448916 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7648411 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 89 | 24112350 | 3850 | 92.4 | 3.85 | 4.7 | 4.7 | 2B | 0 | 0 | 1001 | 0 | 1109 | N/A | N/A | N/A | N/A | 34449584 | 668 | 173.5065 | 0% | 0% | 100% | 0% | 100% | 40% | 7649722 | 1311 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 88 | 24116133 | 3783 | 90.792 | 3.783 | 6.3 | 6.3 | 2B | 0 | 0 | 988 | 0 | 1110 | N/A | N/A | N/A | N/A | 34450228 | 644 | 170.2353 | 0% | 0% | 100% | 0% | 100% | 40% | 7651131 | 1409 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 86 | 24119533 | 3400 | 81.6 | 3.4 | 7.6 | 7.6 | 2B | 0 | 0 | 961 | 0 | 1110 | N/A | N/A | N/A | N/A | 34450804 | 576 | 169.4118 | 0% | 0% | 100% | 0% | 100% | 40% | 7652444 | 1313 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 108 | 88 | 24123112 | 3579 | 85.896 | 3.579 | 8.9 | 8.9 | 2B | 0 | 0 | 951 | 0 | 1110 | N/A | N/A | N/A | N/A | 34451404 | 600 | 167.6446 | 0% | 0% | 100% | 0% | 100% | 40% | 7653781 | 1337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 24127064 | 3952 | 94.848 | 3.952 | 9.5 | 9.5 | 2B | 0 | 0 | 1051 | 0 | 1109 | N/A | N/A | N/A | N/A | 34452024 | 620 | 156.8826 | 0% | 0% | 100% | 0% | 100% | 40% | 7654198 | 417 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 114 | 24131644 | 4580 | 109.92 | 4.58 | 9.5 | 9.5 | 2B | 0 | 0 | 1169 | 0 | 1109 | N/A | N/A | N/A | N/A | 34452780 | 756 | 165.0655 | 0% | 0% | 100% | 0% | 100% | 0% | 7654198 | 0 | 0.8 | Normal operation schedule | Error - General | E | A. CABREROS / F. RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 138 | 24137729 | 6085 | 146.04 | 6.085 | 9.3 | 9.3 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34454156 | 1376 | 226.1298 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 148 | 24143539 | 5810 | 139.44 | 5.81 | 8.7 | 8.7 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34455476 | 1320 | 227.1945 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 153 | 24149775 | 6236 | 149.664 | 6.236 | 7.8 | 7.8 | 3B+1S | 0 | 1143 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34456904 | 1428 | 228.9929 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 149 | 24155909 | 6134 | 147.216 | 6.134 | 6.9 | 6.9 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34458332 | 1428 | 232.8008 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 145 | 24161999 | 6090 | 146.16 | 6.09 | 6.1 | 6.1 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34459149 | 817 | 134.1544 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 149 | 24167960 | 5961 | 143.064 | 5.961 | 5.3 | 5.3 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34461140 | 1991 | 334.0044 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 138 | 24173814 | 5854 | 140.496 | 5.854 | 4.8 | 4.8 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34462492 | 1352 | 230.9532 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 24179441 | 5627 | 135.048 | 5.627 | 4.5 | 4.5 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34463830 | 1338 | 237.7821 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 130 | 24185011 | 5570 | 133.68 | 5.57 | 4.3 | 4.3 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34465116 | 1286 | 230.8797 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 24190706 | 5695 | 136.68 | 5.695 | 4.1 | 4.1 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34466464 | 1348 | 236.6989 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 24196451 | 5745 | 137.88 | 5.745 | 3.5 | 3.5 | 3B+1S | 0 | 1118 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34467820 | 1356 | 236.0313 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 24202090 | 5639 | 135.336 | 5.639 | 3.3 | 3.3 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34469141 | 1321 | 234.2614 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 133 | 24207662 | 5572 | 133.728 | 5.572 | 3.2 | 3.2 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34470436 | 1295 | 232.4121 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 128 | 24213211 | 5549 | 133.176 | 5.549 | 3.1 | 3.1 | 3B+1S | 0 | 990 | 1154 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34471688 | 1252 | 225.6262 | 0% | 100% | 100% | 100% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 129 | 24218559 | 5348 | 128.352 | 5.348 | 2.2 | 2.2 | 2B+1S | 0 | 1087 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34472782 | 1094 | 204.5625 | 0% | 100% | 100% | 0% | 100% | 0% | 7654198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 115 | 24223685 | 5126 | 123.024 | 5.126 | 2 | 2 | 2B+1S | 0 | 999 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34473808 | 1026 | 200.1561 | 0% | 100% | 100% | 0% | 100% | 0% | 7654198 | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 101 | 24227881 | 4196 | 100.704 | 4.196 | 2.9 | 2.9 | 2B | 0 | 0 | 1050 | 0 | 1109 | N/A | N/A | N/A | N/A | 34474562 | 754 | 179.6949 | 0% | 0% | 100% | 0% | 100% | 38% | 7655038 | 840 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 94 | 24232057 | 4176 | 100.224 | 4.176 | 3.9 | 3.9 | 2B | 0 | 0 | 1025 | 0 | 1100 | N/A | N/A | N/A | N/A | 34475296 | 734 | 175.7663 | 0% | 0% | 100% | 0% | 100% | 38% | 7656078 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.25 | 123557 | 123557 | 123.557 | 123.557 | [12 empty] | 26380 | 26380 | 213.5047 | [6 empty] | 7667 | 7667 | 0.89333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO 45% @ 12:01 AM
XCV1 CLOSED @ : 4:20AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 5, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26164 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24232057 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34475296 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7656078 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 90 | 24235727 | 3670 | 88.08 | 3.67 | 5.2 | 5.2 | 2B | 0 | 0 | 1011 | 0 | 1100 | N/A | N/A | N/A | N/A | 34475906 | 610 | 166.2125 | 0% | 0% | 100% | 0% | 100% | 40% | 7657328 | 1250 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 86 | 24239277 | 3550 | 85.2 | 3.55 | 6.9 | 6.9 | 2B | 0 | 0 | 957 | 0 | 1109 | N/A | N/A | N/A | N/A | 34476494 | 588 | 165.6338 | 0% | 0% | 100% | 0% | 100% | 40% | 7658548 | 1220 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 88 | 24242887 | 3610 | 86.64 | 3.61 | 8.1 | 8.1 | 2B | 0 | 0 | 936 | 0 | 1100 | N/A | N/A | N/A | N/A | 34477093 | 599 | 165.928 | 0% | 0% | 100% | 0% | 100% | 40% | 7659783 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 87 | 24246497 | 3610 | 86.64 | 3.61 | 9.1 | 9.1 | 2B | 0 | 0 | 1003 | 0 | 1059 | N/A | N/A | N/A | N/A | 34477692 | 599 | 165.928 | 0% | 0% | 100% | 0% | 100% | 40% | 7661021 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 98 | 24250397 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 1019 | 0 | 1009 | N/A | N/A | N/A | N/A | 34478276 | 584 | 149.7436 | 0% | 0% | 100% | 0% | 100% | 40% | 7661403 | 382 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 119 | 24255194 | 4797 | 115.128 | 4.797 | 9.5 | 9.5 | 2B | 0 | 0 | 1189 | 0 | 1099 | N/A | N/A | N/A | N/A | 34479060 | 784 | 163.4355 | 0% | 0% | 100% | 0% | 100% | 0% | 7661403 | 0 | 0.88 | Normal operation schedule | Error - General | E | A. CABREROS / F. RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 24261014 | 5820 | 139.68 | 5.82 | 9.3 | 9.3 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34480356 | 1296 | 222.6804 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 24267091 | 6077 | 145.848 | 6.077 | 8.6 | 8.6 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34481752 | 1396 | 229.7186 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 144 | 24273183 | 6092 | 146.208 | 6.092 | 7.8 | 7.8 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34483148 | 1396 | 229.153 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 147 | 24279245 | 6062 | 145.488 | 6.062 | 7 | 7 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34484544 | 1396 | 230.287 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 145 | 24285314 | 6069 | 145.656 | 6.069 | 6.3 | 6.3 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34485948 | 1404 | 231.3396 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 24291238 | 5924 | 142.176 | 5.924 | 5.6 | 5.6 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34487324 | 1376 | 232.2755 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 24296992 | 5754 | 138.096 | 5.754 | 5.2 | 5.2 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34488656 | 1332 | 231.4911 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 24302775 | 5783 | 138.792 | 5.783 | 4.9 | 4.9 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34489986 | 1330 | 229.9844 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 131 | 24308315 | 5540 | 132.96 | 5.54 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34491304 | 1318 | 237.9061 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 24313976 | 5661 | 135.864 | 5.661 | 4.5 | 4.5 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34492638 | 1334 | 235.6474 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 24319603 | 5627 | 135.048 | 5.627 | 4.1 | 4.1 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34493958 | 1320 | 234.5833 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 24325237 | 5634 | 135.216 | 5.634 | 3.7 | 3.7 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34495289 | 1331 | 236.2442 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 135 | 24330877 | 5640 | 135.36 | 5.64 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34496608 | 1319 | 233.8652 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 24336281 | 5404 | 129.696 | 5.404 | 3.2 | 3.2 | 3B+1S | 0 | 991 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 34497826 | 1218 | 225.3886 | 0% | 100% | 100% | 100% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 24341607 | 5326 | 127.824 | 5.326 | 2.5 | 2.5 | 2B+1S | 0 | 1072 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34498912 | 1086 | 203.9054 | 0% | 100% | 100% | 0% | 100% | 0% | 7661403 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 119 | 24346875 | 5268 | 126.432 | 5.268 | 2.2 | 2.2 | 2B+1S | 0 | 800 | 1084 | 0 | 1190 | N/A | N/A | N/A | N/A | 34499963 | 1051 | 199.5065 | 0% | 100% | 100% | 0% | 100% | 0% | 7661403 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 102 | 24351056 | 4181 | 100.344 | 4.181 | 2.8 | 2.8 | 2B | 0 | 0 | 1018 | 0 | 1199 | N/A | N/A | N/A | N/A | 34500728 | 765 | 182.9706 | 0% | 0% | 100% | 0% | 100% | 38% | 7662166 | 763 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 93 | 24355091 | 4035 | 96.84 | 4.035 | 3.9 | 3.9 | 2B | 0 | 0 | 925 | 0 | 1199 | N/A | N/A | N/A | N/A | 34501460 | 732 | 181.4126 | 0% | 0% | 100% | 0% | 100% | 38% | 7663188 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.8333 | 123034 | 123034 | 123.034 | 123.034 | [12 empty] | 26164 | 26164 | 212.6567 | [6 empty] | 7110 | 7110 | 0.94333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ : 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 6, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:54 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26176 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24355091 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34501460 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7663188 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 87 | 24358892 | 3801 | 91.224 | 3.801 | 5 | 5 | 2B | 0 | 0 | 920 | 0 | 1199 | N/A | N/A | N/A | N/A | 34502156 | 696 | 183.1097 | 0% | 0% | 100% | 0% | 100% | 40% | 7664195 | 1007 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 88 | 24362782 | 3890 | 93.36 | 3.89 | 6.3 | 6.3 | 2B | 0 | 0 | 880 | 0 | 1200 | N/A | N/A | N/A | N/A | 34502868 | 712 | 183.0334 | 0% | 0% | 100% | 0% | 100% | 40% | 7665365 | 1170 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 82 | 24365963 | 3181 | 76.344 | 3.181 | 7.3 | 7.3 | 2B | 0 | 0 | 854 | 0 | 1199 | N/A | N/A | N/A | N/A | 34503440 | 572 | 179.8177 | 0% | 0% | 100% | 0% | 100% | 40% | 7666396 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 87 | 24369436 | 3473 | 83.352 | 3.473 | 8.6 | 8.6 | 2B | 0 | 0 | 881 | 0 | 1199 | N/A | N/A | N/A | N/A | 34504068 | 628 | 180.8235 | 0% | 0% | 100% | 0% | 100% | 40% | 7667721 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 88 | 24373352 | 3916 | 93.984 | 3.916 | 9.5 | 9.5 | 2B | 0 | 0 | 942 | 0 | 1200 | N/A | N/A | N/A | N/A | 34504732 | 664 | 169.5608 | 0% | 0% | 100% | 0% | 100% | 40% | 7668332 | 611 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 119 | 24377946 | 4594 | 110.256 | 4.594 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1181 | N/A | N/A | N/A | N/A | 34505496 | 764 | 166.3039 | 0% | 0% | 100% | 0% | 100% | 0% | 7668332 | 0 | 1.1 | Normal operation schedule | Error - General | E | A. CABREROS / F. RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 24383798 | 5852 | 140.448 | 5.852 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 34506812 | 1316 | 224.8804 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 24390006 | 6208 | 148.992 | 6.208 | 8.7 | 8.7 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34508196 | 1384 | 222.9381 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 152 | 24396163 | 6157 | 147.768 | 6.157 | 7.9 | 7.9 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34509592 | 1396 | 226.7338 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 24402408 | 6245 | 149.88 | 6.245 | 7.1 | 7.1 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34511004 | 1412 | 226.1009 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 151 | 24408408 | 6000 | 144 | 6 | 6.4 | 6.4 | 3B+1S | 0 | 1106 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34512404 | 1400 | 233.3333 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 147 | 24414535 | 6127 | 147.048 | 6.127 | 5.5 | 5.5 | 3B+1S | 0 | 1141 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34513780 | 1376 | 224.5797 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 24420502 | 5967 | 143.208 | 5.967 | 5.1 | 5.1 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34515152 | 1372 | 229.9313 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 135 | 24426233 | 5731 | 137.544 | 5.731 | 4.8 | 4.8 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34516500 | 1348 | 235.212 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 24431897 | 5664 | 135.936 | 5.664 | 4.5 | 4.5 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34517796 | 1296 | 228.8136 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 24437523 | 5626 | 135.024 | 5.626 | 4.1 | 4.1 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34519133 | 1337 | 237.6466 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 24443113 | 5590 | 134.16 | 5.59 | 3.6 | 3.6 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34520438 | 1305 | 233.4526 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 131 | 24448657 | 5544 | 133.056 | 5.544 | 3.5 | 3.5 | 3B+1S | 0 | 1016 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34521710 | 1272 | 229.4372 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 129 | 24454190 | 5533 | 132.792 | 5.533 | 3.4 | 3.4 | 3B+1S | 0 | 999 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34522968 | 1258 | 227.3631 | 0% | 100% | 100% | 100% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 130 | 24459621 | 5431 | 130.344 | 5.431 | 2.7 | 2.7 | 2B+1S | 0 | 1112 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34524082 | 1114 | 205.1188 | 0% | 100% | 100% | 0% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 132 | 24464839 | 5218 | 125.232 | 5.218 | 2 | 2 | 2B+1S | 0 | 1064 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34525134 | 1052 | 201.6098 | 0% | 100% | 100% | 0% | 100% | 0% | 7668332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 119 | 24470021 | 5182 | 124.368 | 5.182 | 1.7 | 1.7 | 2B+1S | 0 | 1010 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 34526164 | 1030 | 198.765 | 0% | 100% | 100% | 0% | 100% | 0% | 7668332 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 99 | 24474416 | 4395 | 105.48 | 4.395 | 2.4 | 2.4 | 2B | 0 | 0 | 1120 | 0 | 1109 | N/A | N/A | N/A | N/A | 34526964 | 800 | 182.025 | 0% | 0% | 100% | 0% | 100% | 38% | 7669098 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 93 | 24478296 | 3880 | 93.12 | 3.88 | 3.4 | 3.4 | 2B | 0 | 0 | 1038 | 0 | 1110 | N/A | N/A | N/A | N/A | 34527636 | 672 | 173.1959 | 0% | 0% | 100% | 0% | 100% | 38% | 7670172 | 1074 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.125 | 123205 | 123205 | 123.205 | 123.205 | [12 empty] | 26176 | 26176 | 212.4589 | [6 empty] | 6984 | 6984 | 0.99833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 7, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:22 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ :10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25844 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24478296 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34527636 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7670172 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 86 | 24483101 | 4805 | 115.32 | 4.805 | 5.2 | 5.2 | 2B | 0 | 0 | 977 | 0 | 1110 | N/A | N/A | N/A | N/A | 34528454 | 818 | 170.2393 | 0% | 0% | 100% | 0% | 100% | 45% | 7671642 | 1470 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 104 | 24486621 | 3520 | 84.48 | 3.52 | 6.5 | 6.5 | 2B | 0 | 0 | 945 | 0 | 1110 | N/A | N/A | N/A | N/A | 34529026 | 572 | 162.5 | 0% | 0% | 100% | 0% | 100% | 45% | 7672844 | 1202 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 86 | 24489441 | 2820 | 67.68 | 2.82 | 7.4 | 7.4 | 2B | 0 | 0 | 955 | 0 | 1109 | N/A | N/A | N/A | N/A | 34529492 | 466 | 165.2482 | 0% | 0% | 100% | 0% | 100% | 45% | 7673940 | 1096 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 88 | 24493422 | 3981 | 95.544 | 3.981 | 9.3 | 9.3 | 2B | 0 | 0 | 891 | 0 | 1110 | N/A | N/A | N/A | N/A | 34530148 | 656 | 164.7827 | 0% | 0% | 100% | 0% | 100% | 45% | 7675695 | 1755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 91 | 24497361 | 3939 | 94.536 | 3.939 | 9.5 | 9.5 | 2B | 0 | 0 | 899 | 0 | 1109 | N/A | N/A | N/A | N/A | 34530724 | 576 | 146.23 | 0% | 0% | 100% | 0% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 102 | 24500906 | 3545 | 85.08 | 3.545 | 9.5 | 9.5 | 2B | 0 | 0 | 1056 | 0 | 1059 | N/A | N/A | N/A | N/A | 34531232 | 508 | 143.3004 | 0% | 0% | 100% | 0% | 100% | 0% | 7675695 | 0 | 1.1 | Normal operation schedule | Error - General | E | A. CABREROS / F. RAMOS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 139 | 24506493 | 5587 | 134.088 | 5.587 | 9.5 | 9.5 | 3B+1S | 0 | 977 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34532428 | 1196 | 214.0684 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 149 | 24512605 | 6112 | 146.688 | 6.112 | 9 | 9 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34533788 | 1360 | 222.5131 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 129 | 153 | 24518836 | 6231 | 149.544 | 6.231 | 8.1 | 8.1 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34535216 | 1428 | 229.1767 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 153 | 24525156 | 6320 | 151.68 | 6.32 | 7 | 7 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34536676 | 1460 | 231.0127 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 151 | 24531484 | 6328 | 151.872 | 6.328 | 6.1 | 6.1 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34538132 | 1456 | 230.0885 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 149 | 24537619 | 6135 | 147.24 | 6.135 | 5 | 5 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34539554 | 1422 | 231.7848 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 149 | 24543742 | 6123 | 146.952 | 6.123 | 3.9 | 3.9 | 3B+1S | 0 | 1168 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34540944 | 1390 | 227.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 150 | 24550057 | 6315 | 151.56 | 6.315 | 2.9 | 2.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34542476 | 1532 | 242.597 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 140 | 24555840 | 5783 | 138.792 | 5.783 | 2.3 | 2.3 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34543844 | 1368 | 236.5554 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 24561857 | 6017 | 144.408 | 6.017 | 1.6 | 1.6 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34545304 | 1460 | 242.6458 | 0% | 100% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 65 | 45.7746 | Automatic - Pressure Setting | 42.2535 | 43.662 | 47.8873 | 18 | A ONG | 16.7 | 123 | 120 | 24566962 | 5105 | 122.52 | 5.105 | 1.3 | 1.3 | 3B | 0 | 0 | 1025 | 1185 | 1059 | N/A | N/A | N/A | N/A | 34546388 | 1084 | 212.3408 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.7 | 127 | 125 | 24572037 | 5075 | 121.8 | 5.075 | 1.3 | 1.3 | 3B | 0 | 0 | 1068 | 1185 | 1059 | N/A | N/A | N/A | N/A | 34547372 | 984 | 193.8916 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A ONG | 16.6 | 127 | 125 | 24577320 | 5283 | 126.792 | 5.283 | 1.3 | 1.3 | 3B | 0 | 0 | 1068 | 1185 | 1059 | N/A | N/A | N/A | N/A | 34548408 | 1036 | 196.1007 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 137 | 130 | 24582639 | 5319 | 127.656 | 5.319 | 1.3 | 1.3 | 3B | 0 | 0 | 1196 | 1185 | 1108 | N/A | N/A | N/A | N/A | 34549540 | 1132 | 212.822 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 128 | 24587897 | 5258 | 126.192 | 5.258 | 1.3 | 1.3 | 3B | 0 | 0 | 1155 | 1185 | 1126 | N/A | N/A | N/A | N/A | 34550676 | 1136 | 216.0517 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 127 | 24593210 | 5313 | 127.512 | 5.313 | 1.3 | 1.3 | 3B | 0 | 0 | 971 | 1185 | 1109 | N/A | N/A | N/A | N/A | 34551812 | 1136 | 213.8152 | 0% | 0% | 100% | 100% | 100% | 0% | 7675695 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 103 | 24597764 | 4554 | 109.296 | 4.554 | 2.2 | 2.2 | 2B | 0 | 0 | 1154 | 0 | 1109 | N/A | N/A | N/A | N/A | 34552764 | 952 | 209.047 | 0% | 0% | 100% | 0% | 100% | 40% | 7676539 | 844 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 95 | 24601725 | 3961 | 95.064 | 3.961 | 3.1 | 3.1 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 34553480 | 716 | 180.7624 | 0% | 0% | 100% | 0% | 100% | 40% | 7677524 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.3333 | 123429 | 123429 | 123.429 | 123.429 | [12 empty] | 25844 | 25844 | 209.3835 | [6 empty] | 7352 | 7352 | 0.98833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:39 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 8, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 11,872
GENSET 1 WARMUP EXERCISED @ 4:01 PM
GENSET 2 WARMUP EXERCISED @ 4:11 PM
SP2 - STOPPED @ 4:20 PM DUE TO LOW WATER LEVEL
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:39 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25504 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24601725 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34553480 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7677524 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 95 | 24605981 | 4256 | 102.144 | 4.256 | 4.4 | 4.4 | 2B | 0 | 0 | 1050 | 0 | 1109 | N/A | N/A | N/A | N/A | 34554220 | 740 | 173.8722 | 0% | 0% | 100% | 0% | 100% | 45% | 7678636 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | CHRISTIAN DIO
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 24609691 | 3710 | 89.04 | 3.71 | 5.5 | 5.5 | 2B | 0 | 0 | 1005 | 0 | 1110 | N/A | N/A | N/A | N/A | 34554844 | 624 | 168.1941 | 0% | 0% | 100% | 0% | 100% | 45% | 7679750 | 1114 | 0.58 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | DENNIS GUANZON
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 24613472 | 3781 | 90.744 | 3.781 | 6.9 | 6.9 | 2B | 0 | 0 | 986 | 0 | 1110 | N/A | N/A | N/A | N/A | 34555476 | 632 | 167.1515 | 0% | 0% | 100% | 0% | 100% | 45% | 7681029 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | REIVIN M. MALLARI
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 88 | 24616906 | 3434 | 82.416 | 3.434 | 8.2 | 8.2 | 2B | 0 | 0 | 947 | 0 | 1110 | N/A | N/A | N/A | N/A | 34556044 | 568 | 165.4048 | 0% | 0% | 100% | 0% | 100% | 45% | 7682327 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | RANDY REGENCIA
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 91 | 24620644 | 3738 | 89.712 | 3.738 | 9.5 | 9.5 | 2B | 0 | 0 | 856 | 0 | 1109 | N/A | N/A | N/A | N/A | 34556644 | 600 | 160.5136 | 0% | 0% | 100% | 0% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS. SY
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 103 | 101 | 24624769 | 4125 | 99 | 4.125 | 9.5 | 9.5 | 2B | 0 | 0 | 938 | 0 | 1088 | N/A | N/A | N/A | N/A | 34557240 | 596 | 144.4848 | 0% | 0% | 100% | 0% | 100% | 0% | 7682327 | 0 | 1.19 | Normal operation schedule | Error - General | E | A. CABREROS / F. RAMOS
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 24630199 | 5430 | 130.32 | 5.43 | 9.5 | 9.5 | 3B | 0 | 0 | 1158 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34558308 | 1068 | 196.6851 | 0% | 0% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 141 | 24635962 | 5763 | 138.312 | 5.763 | 9.4 | 9.4 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34559580 | 1272 | 220.7184 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 149 | 24642158 | 6196 | 148.704 | 6.196 | 8.8 | 8.8 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34560972 | 1392 | 224.6611 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 152 | 24648349 | 6191 | 148.584 | 6.191 | 8 | 8 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34562372 | 1400 | 226.1347 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 150 | 24654508 | 6159 | 147.816 | 6.159 | 7.3 | 7.3 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34563756 | 1384 | 224.7118 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 142 | 24660482 | 5974 | 143.376 | 5.974 | 6.6 | 6.6 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34565140 | 1384 | 231.6706 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 24666351 | 5869 | 140.856 | 5.869 | 6.1 | 6.1 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34566440 | 1300 | 221.5028 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 234 | 137 | 24672233 | 5882 | 141.168 | 5.882 | 5.8 | 5.8 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34567828 | 1388 | 235.9742 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 137 | 24677931 | 5698 | 136.752 | 5.698 | 5.5 | 5.5 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34569148 | 1320 | 231.6602 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 140 | 24683550 | 5619 | 134.856 | 5.619 | 5.1 | 5.1 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34570464 | 1316 | 234.2054 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 24689278 | 5728 | 137.472 | 5.728 | 4.5 | 4.5 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34571812 | 1348 | 235.3352 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 24694872 | 5594 | 134.256 | 5.594 | 4.2 | 4.2 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34573072 | 1260 | 225.2413 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 24700541 | 5669 | 136.056 | 5.669 | 3.9 | 3.9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34574348 | 1276 | 225.0838 | 0% | 100% | 100% | 100% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 131 | 24705810 | 5269 | 126.456 | 5.269 | 3.3 | 3.3 | 2B+1S | 0 | 1088 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34575408 | 1060 | 201.1767 | 0% | 100% | 100% | 0% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 131 | 24711046 | 5236 | 125.664 | 5.236 | 2.8 | 2.8 | 2B+1S | 0 | 1098 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34576452 | 1044 | 199.3888 | 0% | 100% | 100% | 0% | 100% | 0% | 7682327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 128 | 24716192 | 5146 | 123.504 | 5.146 | 2.4 | 2.4 | 2B+1S | 0 | 993 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34577476 | 1024 | 198.9895 | 0% | 100% | 100% | 0% | 100% | 0% | 7682327 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 102 | 24720582 | 4390 | 105.36 | 4.39 | 3 | 3 | 2B | 0 | 0 | 1128 | 0 | 1110 | N/A | N/A | N/A | N/A | 34578276 | 800 | 182.2323 | 0% | 0% | 100% | 0% | 100% | 35% | 7684073 | 1746 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 91 | 24724712 | 4130 | 99.12 | 4.13 | 3.9 | 3.9 | 2B | 0 | 0 | 1038 | 0 | 1109 | N/A | N/A | N/A | N/A | 34578984 | 708 | 171.4286 | 0% | 0% | 100% | 0% | 100% | 35% | 7685033 | 960 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.875 | 122987 | 122987 | 122.987 | 122.987 | [12 empty] | 25504 | 25504 | 207.3715 | [6 empty] | 7509 | 7509 | 0.96167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:00 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 9, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:03 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26020 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24724712 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34578984 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7685033 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 92 | 24728565 | 3853 | 92.472 | 3.853 | 5.4 | 5.4 | 2B | 0 | 0 | 1038 | 0 | 1079 | N/A | N/A | N/A | N/A | 34579644 | 660 | 171.2951 | 0% | 0% | 100% | 0% | 100% | 45% | 7686393 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 88 | 24732112 | 3547 | 85.128 | 3.547 | 6.9 | 6.9 | 2B | 0 | 0 | 992 | 0 | 1079 | N/A | N/A | N/A | N/A | 34580232 | 588 | 165.7739 | 0% | 0% | 100% | 0% | 100% | 45% | 7687815 | 1422 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 85 | 24735487 | 3375 | 81 | 3.375 | 8.3 | 8.3 | 2B | 0 | 0 | 951 | 0 | 1080 | N/A | N/A | N/A | N/A | 34580780 | 548 | 162.3704 | 0% | 0% | 100% | 0% | 100% | 45% | 7689223 | 1408 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 86 | 24739279 | 3792 | 91.008 | 3.792 | 9.5 | 9.5 | 2B | 0 | 0 | 907 | 0 | 1079 | N/A | N/A | N/A | N/A | 34581372 | 592 | 156.1181 | 0% | 0% | 100% | 0% | 100% | 45% | 7690185 | 962 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 99 | 24743071 | 3792 | 91.008 | 3.792 | 9.5 | 9.5 | 2B | 0 | 0 | 959 | 0 | 1079 | N/A | N/A | N/A | N/A | 34581924 | 552 | 145.5696 | 0% | 0% | 100% | 0% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | A. CABREROS / F. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 116 | 24747729 | 4658 | 111.792 | 4.658 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1110 | N/A | N/A | N/A | N/A | 34582684 | 760 | 163.1602 | 0% | 0% | 100% | 0% | 100% | 0% | 7690185 | 0 | 1.29 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 24753503 | 5774 | 138.576 | 5.774 | 9.3 | 9.3 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34583972 | 1288 | 223.0689 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 151 | 24759753 | 6250 | 150 | 6.25 | 8.9 | 8.9 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34585372 | 1400 | 224 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 157 | 24765821 | 6068 | 145.632 | 6.068 | 8.4 | 8.4 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34586728 | 1356 | 223.4674 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 24771889 | 6068 | 145.632 | 6.068 | 7.9 | 7.9 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34588084 | 1356 | 223.4674 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 24777973 | 6084 | 146.016 | 6.084 | 7.3 | 7.3 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34589460 | 1376 | 226.167 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 147 | 24784058 | 6085 | 146.04 | 6.085 | 6.7 | 6.7 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34590836 | 1376 | 226.1298 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 24790013 | 5955 | 142.92 | 5.955 | 6 | 6 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34592216 | 1380 | 231.738 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 24795753 | 5740 | 137.76 | 5.74 | 5.6 | 5.6 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34593524 | 1308 | 227.8746 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 24801443 | 5690 | 136.56 | 5.69 | 5.2 | 5.2 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34594840 | 1316 | 231.283 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 24807134 | 5691 | 136.584 | 5.691 | 5 | 5 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34596156 | 1316 | 231.2423 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 24812789 | 5655 | 135.72 | 5.655 | 4.4 | 4.4 | 3B+1S | 0 | 1110 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34597492 | 1336 | 236.2511 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 133 | 24818480 | 5691 | 136.584 | 5.691 | 4.2 | 4.2 | 3B+1S | 0 | 991 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34598796 | 1304 | 229.1337 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 130 | 24824071 | 5591 | 134.184 | 5.591 | 3.9 | 3.9 | 3B+1S | 0 | 984 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34600020 | 1224 | 218.9233 | 0% | 100% | 100% | 100% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 133 | 24829663 | 5592 | 134.208 | 5.592 | 3 | 3 | 2B+1S | 0 | 1154 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34601244 | 1224 | 218.8841 | 0% | 100% | 100% | 0% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 131 | 24834938 | 5275 | 126.6 | 5.275 | 2.1 | 2.1 | 2B+1S | 0 | 1122 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34602328 | 1084 | 205.4976 | 0% | 100% | 100% | 0% | 100% | 0% | 7690185 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 121 | 24840206 | 5268 | 126.432 | 5.268 | 1.5 | 1.5 | 2B+1S | 0 | 1037 | 0 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34603396 | 1068 | 202.7335 | 0% | 100% | 0% | 100% | 100% | 0% | 7690185 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 105 | 24844706 | 4500 | 108 | 4.5 | 2 | 2 | 2B | 0 | 0 | 0 | 1185 | 1088 | N/A | N/A | N/A | N/A | 34604244 | 848 | 188.4444 | 0% | 0% | 0% | 100% | 100% | 35% | 7690861 | 676 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 98 | 24848930 | 4224 | 101.376 | 4.224 | 3 | 3 | 2B | 0 | 0 | 1049 | 1185 | 0 | N/A | N/A | N/A | N/A | 34605004 | 760 | 179.9242 | 0% | 0% | 100% | 100% | 0% | 35% | 7691808 | 947 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.75 | 124218 | 124218 | 124.218 | 124.218 | [12 empty] | 26020 | 26020 | 209.4704 | [6 empty] | 6775 | 6775 | 1.1067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:50 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 10, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
MONTHLY PREVENTIVE MAINTENANCE OF ALL UNITS
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
BP2 - RESTARTED @ 9:01 PM
BP1 - STOPPED @ 9:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
BP1 - RESTARTED @ 11:01PM
BP3 - STOPPED @ 11:01 PM
NORMAL OPERATION

## FEB 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26280 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24848930 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34605004 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7691808 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 98 | 24852974 | 4044 | 97.056 | 4.044 | 4.5 | 4.5 | 2B | 0 | 0 | 1081 | 0 | 1088 | N/A | N/A | N/A | N/A | 34605724 | 720 | 178.0415 | 0% | 0% | 100% | 0% | 100% | 47% | 7693168 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 92 | 24856922 | 3948 | 94.752 | 3.948 | 5.9 | 5.9 | 2B | 0 | 0 | 1066 | 0 | 1052 | N/A | N/A | N/A | N/A | 34606392 | 668 | 169.1996 | 0% | 0% | 100% | 0% | 100% | 47% | 7694596 | 1428 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 91 | 24860830 | 3908 | 93.792 | 3.908 | 7 | 7 | 2B | 0 | 0 | 1060 | 0 | 1052 | N/A | N/A | N/A | N/A | 34607020 | 628 | 160.696 | 0% | 0% | 100% | 0% | 100% | 47% | 7695969 | 1373 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 92 | 24864668 | 3838 | 92.112 | 3.838 | 8.8 | 8.8 | 2B | 0 | 0 | 1037 | 0 | 1059 | N/A | N/A | N/A | N/A | 34607636 | 616 | 160.5003 | 0% | 0% | 100% | 0% | 100% | 47% | 7697281 | 1312 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 101 | 24868705 | 4037 | 96.888 | 4.037 | 9.5 | 9.5 | 2B | 0 | 0 | 1010 | 0 | 1027 | N/A | N/A | N/A | N/A | 34608244 | 608 | 150.6069 | 0% | 0% | 100% | 0% | 100% | 47% | 7697845 | 564 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | A. CABREROS / F. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 120 | 24873335 | 4630 | 111.12 | 4.63 | 9.5 | 9.5 | 2B | 0 | 0 | 1140 | 0 | 1160 | N/A | N/A | N/A | N/A | 34608948 | 704 | 152.0518 | 0% | 0% | 100% | 0% | 100% | 0% | 7697845 | 0 | 0.87 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 147 | 24879337 | 6002 | 144.048 | 6.002 | 9.1 | 9.1 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34610292 | 1344 | 223.9254 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 149 | 24885453 | 6116 | 146.784 | 6.116 | 8.6 | 8.6 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34611664 | 1372 | 224.3296 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 148 | 24891653 | 6200 | 148.8 | 6.2 | 8 | 8 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34613050 | 1386 | 223.5484 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 24897842 | 6189 | 148.536 | 6.189 | 7.4 | 7.4 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34614460 | 1410 | 227.8236 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 143 | 24903881 | 6039 | 144.936 | 6.039 | 7 | 7 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34615820 | 1360 | 225.2028 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 140 | 24909842 | 5961 | 143.064 | 5.961 | 6.4 | 6.4 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34617192 | 1372 | 230.1627 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 24915649 | 5807 | 139.368 | 5.807 | 6 | 6 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34618540 | 1348 | 232.1336 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 24921397 | 5748 | 137.952 | 5.748 | 5.7 | 5.7 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34619872 | 1332 | 231.7328 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 24927048 | 5651 | 135.624 | 5.651 | 5.6 | 5.6 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34621189 | 1317 | 233.0561 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 24932654 | 5606 | 134.544 | 5.606 | 5.3 | 5.3 | 3B+1S | 0 | 1053 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34622495 | 1306 | 232.9647 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 135 | 24938215 | 5561 | 133.464 | 5.561 | 4.7 | 4.7 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34623792 | 1297 | 233.2314 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 134 | 24943863 | 5648 | 135.552 | 5.648 | 4.3 | 4.3 | 3B+1S | 0 | 1014 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34625096 | 1304 | 230.8782 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 24949489 | 5626 | 135.024 | 5.626 | 3.9 | 3.9 | 3B+1S | 0 | 1019 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34626382 | 1286 | 228.5816 | 0% | 100% | 100% | 100% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 127 | 24954987 | 5498 | 131.952 | 5.498 | 3 | 3 | 2B+1S | 0 | 1161 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34627536 | 1154 | 209.8945 | 0% | 100% | 100% | 0% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 24960407 | 5420 | 130.08 | 5.42 | 2.1 | 2.1 | 2B+1S | 0 | 1105 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34628630 | 1094 | 201.845 | 0% | 100% | 100% | 0% | 100% | 0% | 7697845 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 127 | 24965384 | 4977 | 119.448 | 4.977 | 1.5 | 1.5 | 2B+1S | 0 | 1044 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 34629628 | 998 | 200.5224 | 0% | 100% | 100% | 0% | 100% | 0% | 7697845 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 109 | 24970210 | 4826 | 115.824 | 4.826 | 2.1 | 2.1 | 2B | 0 | 0 | 1183 | 0 | 1109 | N/A | N/A | N/A | N/A | 34630524 | 896 | 185.661 | 0% | 0% | 100% | 0% | 100% | 40% | 7698582 | 737 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 107 | 24974491 | 4281 | 102.744 | 4.281 | 3.1 | 3.1 | 2B | 0 | 0 | 1108 | 0 | 1109 | N/A | N/A | N/A | N/A | 34631284 | 760 | 177.5286 | 0% | 0% | 100% | 0% | 100% | 40% | 7699647 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.6667 | 125561 | 125561 | 125.561 | 125.561 | [12 empty] | 26280 | 26280 | 209.3007 | [6 empty] | 7839 | 7839 | 1.015 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (47%) @ 12:01 AM
BP2 - STOPPED @ 12:25 AM
BP3 - RESTARTED @ 12:25 AM
XCV1 CLOSED @ 4:31 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 11, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 PM, NORMAL OPERATION
EXTERNAL AUDIT @ VILLAMOR PS. BY MR. MARK ORNIDO FROM ACCELENCE (2:00PM)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:26 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26040 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24974491 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34631284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7699647 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 91 | 24978701 | 4210 | 101.04 | 4.21 | 4.6 | 4.6 | 2B | 0 | 0 | 1035 | 0 | 1109 | N/A | N/A | N/A | N/A | 34632016 | 732 | 173.8717 | 0% | 0% | 100% | 0% | 100% | 48% | 7700931 | 1284 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 91 | 24982310 | 3609 | 86.616 | 3.609 | 5.8 | 5.8 | 2B | 0 | 0 | 998 | 0 | 1110 | N/A | N/A | N/A | N/A | 34632620 | 604 | 167.3594 | 0% | 0% | 100% | 0% | 100% | 48% | 7702095 | 1164 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 24986132 | 3822 | 91.728 | 3.822 | 7.1 | 7.1 | 2B | 0 | 0 | 966 | 0 | 1109 | N/A | N/A | N/A | N/A | 34633252 | 632 | 165.3585 | 0% | 0% | 100% | 0% | 100% | 48% | 7703380 | 1285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 92 | 24989974 | 3842 | 92.208 | 3.842 | 8.6 | 8.6 | 2B | 0 | 0 | 1001 | 0 | 1110 | N/A | N/A | N/A | N/A | 34633892 | 640 | 166.5799 | 0% | 0% | 100% | 0% | 100% | 48% | 7704740 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 97 | 24994001 | 4027 | 96.648 | 4.027 | 9.5 | 9.5 | 2B | 0 | 0 | 960 | 0 | 1110 | N/A | N/A | N/A | N/A | 34634536 | 644 | 159.9205 | 0% | 0% | 100% | 0% | 100% | 48% | 7705534 | 794 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | F. RAMOS
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 24998602 | 4601 | 110.424 | 4.601 | 9.5 | 9.5 | 2B | 0 | 0 | 1104 | 0 | 1198 | N/A | N/A | N/A | N/A | 34635324 | 788 | 171.2671 | 0% | 0% | 100% | 0% | 100% | 0% | 7705534 | 0 | 0.99 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 25004511 | 5909 | 141.816 | 5.909 | 9.2 | 9.2 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34636652 | 1328 | 224.7419 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 25010750 | 6239 | 149.736 | 6.239 | 8.6 | 8.6 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34638052 | 1400 | 224.3949 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 148 | 25016809 | 6059 | 145.416 | 6.059 | 8.1 | 8.1 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34639404 | 1352 | 223.1391 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 25022819 | 6010 | 144.24 | 6.01 | 7.6 | 7.6 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34640752 | 1348 | 224.2928 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 25028821 | 6002 | 144.048 | 6.002 | 7.3 | 7.3 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34642041 | 1289 | 214.7617 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 142 | 25034619 | 5798 | 139.152 | 5.798 | 6.9 | 6.9 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34643412 | 1371 | 236.4608 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 25040489 | 5870 | 140.88 | 5.87 | 6.6 | 6.6 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34644752 | 1340 | 228.2794 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 25046301 | 5812 | 139.488 | 5.812 | 6.4 | 6.4 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34646082 | 1330 | 228.8369 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 25052032 | 5731 | 137.544 | 5.731 | 6.1 | 6.1 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34647419 | 1337 | 233.2926 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 25057710 | 5678 | 136.272 | 5.678 | 5.8 | 5.8 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34648730 | 1311 | 230.8912 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 140 | 25063337 | 5627 | 135.048 | 5.627 | 5.3 | 5.3 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34650016 | 1286 | 228.541 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 25069032 | 5695 | 136.68 | 5.695 | 5.2 | 5.2 | 3B+1S | 0 | 960 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34651330 | 1314 | 230.7287 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 25074698 | 5666 | 135.984 | 5.666 | 5.1 | 5.1 | 3B+1S | 0 | 980 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34652632 | 1302 | 229.7917 | 0% | 100% | 100% | 100% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 123 | 25080110 | 5412 | 129.888 | 5.412 | 4.3 | 4.3 | 2B+1S | 0 | 1104 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34653737 | 1105 | 204.1759 | 0% | 100% | 100% | 0% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 25085407 | 5297 | 127.128 | 5.297 | 3.5 | 3.5 | 2B+1S | 0 | 1048 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34654794 | 1057 | 199.5469 | 0% | 100% | 100% | 0% | 100% | 0% | 7705534 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 120 | 25090561 | 5154 | 123.696 | 5.154 | 3.1 | 3.1 | 2B+1S | 0 | 1001 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 34655844 | 1050 | 203.7253 | 0% | 100% | 100% | 0% | 100% | 0% | 7705534 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 107 | 121 | 25095065 | 4504 | 108.096 | 4.504 | 3.4 | 3.4 | 2B | 0 | 0 | 1129 | 0 | 1199 | N/A | N/A | N/A | N/A | 34656624 | 780 | 173.1794 | 0% | 0% | 100% | 0% | 100% | 30% | 7705932 | 398 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 100 | 119 | 25099190 | 4125 | 99 | 4.125 | 4.2 | 4.2 | 2B | 0 | 0 | 1030 | 0 | 1128 | N/A | N/A | N/A | N/A | 34657324 | 700 | 169.697 | 0% | 0% | 100% | 0% | 100% | 30% | 7706625 | 693 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.7083 | 124699 | 124699 | 124.699 | 124.699 | [12 empty] | 26040 | 26040 | 208.8228 | [6 empty] | 6978 | 6978 | 0.99667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (48%) @ 12:01 AM
XCV1 CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 12, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:35 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:02 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24364 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25099190 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34657324 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7706625 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 96 | 25103034 | 3844 | 92.256 | 3.844 | 5.1 | 5.1 | 2B | 0 | 0 | 1010 | 0 | 1109 | N/A | N/A | N/A | N/A | 34657596 | 272 | 70.7596 | 0% | 0% | 100% | 0% | 100% | 40% | 7707411 | 786 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | GENSET LOAD TEST | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 92 | 25106810 | 3776 | 90.624 | 3.776 | 6.2 | 6.2 | 2B | 0 | 0 | 995 | 0 | 1110 | N/A | N/A | N/A | N/A | 34657596 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 40% | 7708642 | 1231 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | GENSET LOAD TEST | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 90 | 25110973 | 4163 | 99.912 | 4.163 | 7.5 | 7.5 | 2B | 0 | 0 | 973 | 0 | 1110 | N/A | N/A | N/A | N/A | 34657596 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 40% | 7710072 | 1430 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 98 | 25114431 | 3458 | 82.992 | 3.458 | 8.8 | 8.8 | 2B | 0 | 0 | 1020 | 0 | 1059 | N/A | N/A | N/A | N/A | 34658000 | 404 | 116.8305 | 0% | 0% | 100% | 0% | 100% | 40% | 7710993 | 921 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 96 | 25118237 | 3806 | 91.344 | 3.806 | 9.5 | 9.5 | 2B | 0 | 0 | 1059 | 0 | 1059 | N/A | N/A | N/A | N/A | 34658572 | 572 | 150.289 | 0% | 0% | 100% | 0% | 100% | 40% | 7711610 | 617 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | A. CABREROS / F. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 116 | 25123008 | 4771 | 114.504 | 4.771 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1190 | N/A | N/A | N/A | N/A | 34659372 | 800 | 167.6797 | 0% | 0% | 100% | 0% | 100% | 0% | 7711610 | 0 | 0.88 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 149 | 25128683 | 5675 | 136.2 | 5.675 | 9.3 | 9.3 | 3B+1S | 0 | 117 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34660636 | 1264 | 222.7313 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 148 | 25134778 | 6095 | 146.28 | 6.095 | 8.8 | 8.8 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34662012 | 1376 | 225.7588 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 147 | 25140917 | 6139 | 147.336 | 6.139 | 8.1 | 8.1 | 3B+1S | 0 | 1080 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34663408 | 1396 | 227.3986 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 25146896 | 5979 | 143.496 | 5.979 | 7.4 | 7.4 | 3B+1S | 0 | 1075 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34664760 | 1352 | 226.1248 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 | 1.1 | Normal operation schedule | GENSET LOAD TEST | GLT
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 144 | 25153056 | 6160 | 147.84 | 6.16 | 6.8 | 6.8 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34666164 | 1404 | 227.9221 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 140 | 25159050 | 5994 | 143.856 | 5.994 | 6.1 | 6.1 | 3B+1S | 0 | 1116 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34667548 | 1384 | 230.8976 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Normal operation schedule
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 25164888 | 5838 | 140.112 | 5.838 | 5.7 | 5.7 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34668884 | 1336 | 228.8455 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | UNITS
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 132 | 25170609 | 5721 | 137.304 | 5.721 | 5.3 | 5.3 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34670210 | 1326 | 231.7777 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 25176181 | 5572 | 133.728 | 5.572 | 5.2 | 5.2 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34671520 | 1310 | 235.1041 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 25181864 | 5683 | 136.392 | 5.683 | 5.1 | 5.1 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34672858 | 1338 | 235.439 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 25187492 | 5628 | 135.072 | 5.628 | 4.7 | 4.7 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34674152 | 1294 | 229.9218 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 25193197 | 5705 | 136.92 | 5.705 | 4.4 | 4.4 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34675472 | 1320 | 231.376 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 25198874 | 5677 | 136.248 | 5.677 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34676788 | 1316 | 231.8126 | 0% | 100% | 100% | 100% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 25204354 | 5480 | 131.52 | 5.48 | 3.1 | 3.1 | 2B+1S | 0 | 1184 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34677936 | 1148 | 209.4891 | 0% | 100% | 100% | 0% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 129 | 25209711 | 5357 | 128.568 | 5.357 | 2.1 | 2.1 | 2B+1S | 0 | 1115 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34679014 | 1078 | 201.232 | 0% | 100% | 100% | 0% | 100% | 0% | 7711610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 105 | 25214711 | 5000 | 120 | 5 | 1.5 | 1.5 | 2B+1S | 0 | 1056 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34680015 | 1001 | 200.2 | 0% | 100% | 100% | 0% | 100% | 0% | 7711610 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 106 | 25219591 | 4880 | 117.12 | 4.88 | 2.1 | 2.1 | 2B | 0 | 0 | 1159 | 0 | 1129 | N/A | N/A | N/A | N/A | 34680916 | 901 | 184.6311 | 0% | 0% | 100% | 0% | 100% | 40% | 7712303 | 693 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 103 | 25223941 | 4350 | 104.4 | 4.35 | 3.2 | 3.2 | 2B | 0 | 0 | 1082 | 0 | 1129 | N/A | N/A | N/A | N/A | 34681688 | 772 | 177.4713 | 0% | 0% | 100% | 0% | 100% | 40% | 7713406 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
[10 empty] | TOTAL |  |  |  | 124.5 | 124751 | 124751 | 124.751 | 124.751 | [12 empty] | 24364 | 24364 | 195.301 | [6 empty] | 6781 | 6781 | 1.005 |  | FLOW | MLD
[44 empty] | MLD | 1
NOTABLE REMARKS FOR THE DAY : | [43 empty] | m3/hr | 41.67
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area. | [43 empty] | Liter/sec | 11.575
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
As Per request of MR. Arturo Trinidad conduct load testing for the GENSET @ 12am
MONARK conduct the Technical Analysis level two inspection for the two unit of the GENSET performed by Mr. Christian Lariba and Mr. Mark Quintano started @ 12:00am
GENSET 1 STARTED @ 12:01 AM wIth load
GENSET 2 STARTED @ 12:23 AM wIth load
GENSET 1 STOPPED @ 1:40 AM
GENSET 2 STOPPED @ 3:11 AM
ATS GENERATOR STOPPED @3:00 AM
ATS GENSET TOTAL KW-HR = 73,345
MERALCO ATS RESUMED @ 3:05 AM
BP1 POWER RESUMED @ 3:06 AM
BP 3 POWER RESUMED @ 3:08 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:00 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 12, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:02 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | A. CABREROS / F. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26076 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25223941 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34681688 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7713406 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 92 | 25227946 | 4005 | 96.12 | 4.005 | 4.6 | 4.6 | 2B | 0 | 0 | 1028 | 0 | 1130 | N/A | N/A | N/A | N/A | 34682376 | 688 | 171.7853 | 0% | 0% | 100% | 0% | 100% | 50% | 7714537 | 1131 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 100 | 25231639 | 3693 | 88.632 | 3.693 | 5.7 | 5.7 | 2B | 0 | 0 | 992 | 0 | 1129 | N/A | N/A | N/A | N/A | 34683000 | 624 | 168.9683 | 0% | 0% | 100% | 0% | 100% | 50% | 7715713 | 1176 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 88 | 25235504 | 3865 | 92.76 | 3.865 | 7 | 7 | 2B | 0 | 0 | 962 | 0 | 1110 | N/A | N/A | N/A | N/A | 34683636 | 636 | 164.5537 | 0% | 0% | 100% | 0% | 100% | 50% | 7716937 | 1224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 92 | 25239260 | 3756 | 90.144 | 3.756 | 8.4 | 8.4 | 2B | 0 | 0 | 978 | 0 | 1110 | N/A | N/A | N/A | N/A | 34684232 | 596 | 158.6794 | 0% | 0% | 100% | 0% | 100% | 50% | 7718160 | 1223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 98 | 25243281 | 4021 | 96.504 | 4.021 | 9.5 | 9.5 | 2B | 0 | 0 | 953 | 0 | 1110 | N/A | N/A | N/A | N/A | 34684876 | 644 | 160.1592 | 0% | 0% | 100% | 0% | 100% | 50% | 7719214 | 1054 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | A. CABREROS / F. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 110 | 25247615 | 4334 | 104.016 | 4.334 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1151 | N/A | N/A | N/A | N/A | 34685572 | 696 | 160.5907 | 0% | 0% | 100% | 0% | 100% | 0% | 7719214 | 0 | 1.25 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 139 | 25253315 | 5700 | 136.8 | 5.7 | 9.4 | 9.4 | 3B+1S | 0 | 985 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34686860 | 1288 | 225.9649 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 25259299 | 5984 | 143.616 | 5.984 | 8.9 | 8.9 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34688204 | 1344 | 224.5989 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 151 | 25265472 | 6173 | 148.152 | 6.173 | 8.4 | 8.4 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34689592 | 1388 | 224.8502 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 151 | 25271719 | 6247 | 149.928 | 6.247 | 7.7 | 7.7 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34690996 | 1404 | 224.7479 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 148 | 25277731 | 6012 | 144.288 | 6.012 | 7.3 | 7.3 | 3B+1S | 0 | 1117 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34692340 | 1344 | 223.5529 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 144 | 25283781 | 6050 | 145.2 | 6.05 | 6.6 | 6.6 | 3B+1S | 0 | 1145 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34693724 | 1384 | 228.7603 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 25289717 | 5936 | 142.464 | 5.936 | 6.2 | 6.2 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34695076 | 1352 | 227.7628 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 141 | 25295504 | 5787 | 138.888 | 5.787 | 5.9 | 5.9 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34696412 | 1336 | 230.8623 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 25301266 | 5762 | 138.288 | 5.762 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34697741 | 1329 | 230.6491 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 25307004 | 5738 | 137.712 | 5.738 | 5.3 | 5.3 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34699086 | 1345 | 234.4022 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 25312719 | 5715 | 137.16 | 5.715 | 4.7 | 4.7 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34700448 | 1362 | 238.3202 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 25318352 | 5633 | 135.192 | 5.633 | 4.6 | 4.6 | 3B+1S | 0 | 997 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34701732 | 1284 | 227.9425 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 25323899 | 5547 | 133.128 | 5.547 | 4.4 | 4.4 | 3B+1S | 0 | 1004 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34702970 | 1238 | 223.1837 | 0% | 100% | 100% | 100% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 131 | 25329347 | 5448 | 130.752 | 5.448 | 3.5 | 3.5 | 2B+1S | 0 | 1123 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34704068 | 1098 | 201.5419 | 0% | 100% | 100% | 0% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 132 | 25334748 | 5401 | 129.624 | 5.401 | 2.7 | 2.7 | 2B+1S | 0 | 1115 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34705124 | 1056 | 195.5193 | 0% | 100% | 100% | 0% | 100% | 0% | 7719214 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 120 | 25340033 | 5285 | 126.84 | 5.285 | 2.3 | 2.3 | 2B+1S | 0 | 987 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34706213 | 1089 | 206.0549 | 0% | 100% | 100% | 0% | 100% | 0% | 7719214 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 106 | 25344591 | 4558 | 109.392 | 4.558 | 2.7 | 2.7 | 2B | 0 | 0 | 1174 | 0 | 1109 | N/A | N/A | N/A | N/A | 34707036 | 823 | 180.5616 | 0% | 0% | 100% | 0% | 100% | 35% | 7719821 | 607 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 100 | 25348821 | 4230 | 101.52 | 4.23 | 3.7 | 3.7 | 2B | 0 | 0 | 1093 | 0 | 1110 | N/A | N/A | N/A | N/A | 34707764 | 728 | 172.104 | 0% | 0% | 100% | 0% | 100% | 35% | 7720695 | 874 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 124880 | 124880 | 124.88 | 124.88 | [12 empty] | 26076 | 26076 | 208.8085 | [6 empty] | 7289 | 7289 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 5:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 14, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:28 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | F.A.RAMOS / A.CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26252 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25348821 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34707764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7720695 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 95 | 25353021 | 4200 | 100.8 | 4.2 | 4.7 | 4.7 | 2B | 0 | 0 | 1048 | 0 | 1110 | N/A | N/A | N/A | N/A | 34708480 | 716 | 170.4762 | 0% | 0% | 100% | 0% | 100% | 45% | 7721630 | 935 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 96 | 25356763 | 3742 | 89.808 | 3.742 | 5.8 | 5.8 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 34709100 | 620 | 165.6868 | 0% | 0% | 100% | 0% | 100% | 45% | 7722711 | 1081 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 25360501 | 3738 | 89.712 | 3.738 | 7.1 | 7.1 | 2B | 0 | 0 | 999 | 0 | 1110 | N/A | N/A | N/A | N/A | 34709724 | 624 | 166.9342 | 0% | 0% | 100% | 0% | 100% | 45% | 7723983 | 1272 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 93 | 25364444 | 3943 | 94.632 | 3.943 | 8.5 | 8.5 | 2B | 0 | 0 | 984 | 0 | 1110 | N/A | N/A | N/A | N/A | 34710360 | 636 | 161.2985 | 0% | 0% | 100% | 0% | 100% | 45% | 7725297 | 1314 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 90 | 25368161 | 3717 | 89.208 | 3.717 | 9.5 | 9.5 | 2B | 0 | 0 | 869 | 0 | 1110 | N/A | N/A | N/A | N/A | 34710956 | 596 | 160.3444 | 0% | 0% | 100% | 0% | 100% | 45% | 7726111 | 814 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 | 103 | 25372489 | 4328 | 103.872 | 4.328 | 9.5 | 9.5 | 2B | 0 | 0 | 1030 | 0 | 1050 | N/A | N/A | N/A | N/A | 34711564 | 608 | 140.4806 | 0% | 0% | 100% | 0% | 100% | 0% | 7726111 | 0 | 0.81 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 140 | 25378017 | 5528 | 132.672 | 5.528 | 9.5 | 9.5 | 3B+1S | 0 | 987 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34712756 | 1192 | 215.6295 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 149 | 25384182 | 6165 | 147.96 | 6.165 | 9 | 9 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34714132 | 1376 | 223.1955 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 129 | 149 | 25390278 | 6096 | 146.304 | 6.096 | 8.4 | 8.4 | 3B+1S | 0 | 1165 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34715441 | 1309 | 214.731 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 153 | 25396502 | 6224 | 149.376 | 6.224 | 7.8 | 7.8 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34716844 | 1403 | 225.4177 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 151 | 25402600 | 6098 | 146.352 | 6.098 | 7.1 | 7.1 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34718244 | 1400 | 229.5835 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 151 | 25408781 | 6181 | 148.344 | 6.181 | 6.2 | 6.2 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34719792 | 1548 | 250.4449 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 146 | 25414881 | 6100 | 146.4 | 6.1 | 5.4 | 5.4 | 3B+1S | 0 | 1161 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34721182 | 1390 | 227.8689 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 146 | 25421070 | 6189 | 148.536 | 6.189 | 4.7 | 4.7 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34722461 | 1279 | 206.657 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 140 | 25427009 | 5939 | 142.536 | 5.939 | 4 | 4 | 3B+1S | 0 | 1154 | 1171 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34723820 | 1359 | 228.8264 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 140 | 25432775 | 5766 | 138.384 | 5.766 | 3.5 | 3.5 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34725156 | 1336 | 231.7031 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 138 | 25438501 | 5726 | 137.424 | 5.726 | 2.9 | 2.9 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34726500 | 1344 | 234.7188 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 137 | 25444281 | 5780 | 138.72 | 5.78 | 2.3 | 2.3 | 3B+1S | 0 | 1081 | 1176 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34727820 | 1320 | 228.3737 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 130 | 25449882 | 5601 | 134.424 | 5.601 | 1.9 | 1.9 | 3B+1S | 0 | 1025 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 34729108 | 1288 | 229.9589 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 128 | 25455429 | 5547 | 133.128 | 5.547 | 1.8 | 1.8 | 3B+1S | 0 | 1002 | 1125 | 1185 | 1148 | N/A | N/A | N/A | N/A | 34730316 | 1208 | 217.7754 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 126 | 25460488 | 5059 | 121.416 | 5.059 | 1.7 | 1.7 | 3B+1S | 0 | 982 | 1125 | 1185 | 1109 | N/A | N/A | N/A | N/A | 34731468 | 1152 | 227.713 | 0% | 100% | 100% | 100% | 100% | 0% | 7726111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 120 | 25465798 | 5310 | 127.44 | 5.31 | 1.6 | 1.6 | 3B+1S | 0 | 900 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 34732532 | 1064 | 200.3766 | 0% | 100% | 100% | 0% | 100% | 0% | 7726111 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 100 | 25470051 | 4253 | 102.072 | 4.253 | 2.4 | 2.4 | 2B | 0 | 0 | 1142 | 0 | 1110 | N/A | N/A | N/A | N/A | 34733300 | 768 | 180.5784 | 0% | 0% | 100% | 0% | 100% | 40% | 7726942 | 831 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 98 | 25474171 | 4120 | 98.88 | 4.12 | 3.6 | 3.6 | 2B | 0 | 0 | 1069 | 0 | 1109 | N/A | N/A | N/A | N/A | 34734016 | 716 | 173.7864 | 0% | 0% | 100% | 0% | 100% | 40% | 7728088 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 125350 | 125350 | 125.35 | 125.35 | [12 empty] | 26252 | 26252 | 209.4296 | [6 empty] | 7393 | 7393 | 0.97167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:45 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:00 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 15, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | F.A.RAMOS / A.CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25712 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25474171 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34734016 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7728088 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 91 | 25477887 | 3716 | 89.184 | 3.716 | 4.8 | 4.8 | 2B | 0 | 0 | 1034 | 0 | 1109 | N/A | N/A | N/A | N/A | 34734652 | 636 | 171.1518 | 0% | 0% | 100% | 0% | 100% | 46% | 7729114 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 25481561 | 3674 | 88.176 | 3.674 | 5.9 | 5.9 | 2B | 0 | 0 | 988 | 0 | 1110 | N/A | N/A | N/A | N/A | 34735276 | 624 | 169.8421 | 0% | 0% | 100% | 0% | 100% | 46% | 7730225 | 1111 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 82 | 25485731 | 4170 | 100.08 | 4.17 | 7.4 | 7.4 | 2B | 0 | 0 | 952 | 0 | 1110 | N/A | N/A | N/A | N/A | 34735964 | 688 | 164.988 | 0% | 0% | 100% | 0% | 100% | 46% | 7731546 | 1321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 87 | 25490050 | 4319 | 103.656 | 4.319 | 9.2 | 9.2 | 2B | 0 | 0 | 931 | 0 | 1110 | N/A | N/A | N/A | N/A | 34736680 | 716 | 165.7791 | 0% | 0% | 100% | 0% | 100% | 46% | 7733310 | 1764 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 91 | 25492337 | 2287 | 54.888 | 2.287 | 9.5 | 9.5 | 2B | 0 | 0 | 850 | 0 | 1110 | N/A | N/A | N/A | N/A | 34737012 | 332 | 145.1683 | 0% | 0% | 100% | 0% | 100% | 46% | 7733556 | 246 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 24 | 16.9014 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 102 | 117 | 25496305 | 3968 | 95.232 | 3.968 | 9.5 | 9.5 | 2B | 0 | 0 | 995 | 0 | 1008 | N/A | N/A | N/A | N/A | 34737568 | 556 | 140.121 | 0% | 0% | 100% | 0% | 100% | 0% | 7733556 | 0 | 1.05 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 130 | 25501517 | 5212 | 125.088 | 5.212 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1129 | N/A | N/A | N/A | N/A | 34738584 | 1016 | 194.9348 | 0% | 0% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 140 | 25507188 | 5671 | 136.104 | 5.671 | 9.4 | 9.4 | 3B+1S | 0 | 981 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34739788 | 1204 | 212.3082 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 25513320 | 6132 | 147.168 | 6.132 | 9 | 9 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34741156 | 1368 | 223.092 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 151 | 25519529 | 6209 | 149.016 | 6.209 | 8.4 | 8.4 | 3B+1S | 0 | 1163 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34742540 | 1384 | 222.9022 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 149 | 25525602 | 6073 | 145.752 | 6.073 | 7.7 | 7.7 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34743911 | 1371 | 225.7533 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 148 | 25531710 | 6108 | 146.592 | 6.108 | 6.9 | 6.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34745292 | 1381 | 226.0969 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 148 | 25537773 | 6063 | 145.512 | 6.063 | 6.2 | 6.2 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34746654 | 1362 | 224.6413 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 25543805 | 6032 | 144.768 | 6.032 | 5.6 | 5.6 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34748038 | 1384 | 229.443 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 142 | 25549729 | 5924 | 142.176 | 5.924 | 4.9 | 4.9 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34749427 | 1389 | 234.47 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 25555621 | 5892 | 141.408 | 5.892 | 4 | 4 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34750805 | 1378 | 233.8764 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 141 | 25561482 | 5861 | 140.664 | 5.861 | 3.3 | 3.3 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34752172 | 1367 | 233.2366 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 142 | 25567175 | 5693 | 136.632 | 5.693 | 3 | 3 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34753506 | 1334 | 234.3229 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 136 | 25572794 | 5619 | 134.856 | 5.619 | 2.9 | 2.9 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34754788 | 1282 | 228.1545 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 | 131 | 25578290 | 5496 | 131.904 | 5.496 | 2.7 | 2.7 | 3B+1S | 0 | 1022 | 1145 | 1185 | 1148 | N/A | N/A | N/A | N/A | 34756008 | 1220 | 221.9796 | 0% | 100% | 100% | 100% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 115 | 25583638 | 5348 | 128.352 | 5.348 | 1.8 | 1.8 | 2B+1S | 0 | 1084 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34757110 | 1102 | 206.0583 | 0% | 100% | 100% | 0% | 100% | 0% | 7733556 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 120 | 25588942 | 5304 | 127.296 | 5.304 | 1.4 | 1.4 | 2B+1S | 0 | 1009 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34758160 | 1050 | 197.9638 | 0% | 100% | 100% | 0% | 100% | 0% | 7733556 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 110 | 25593172 | 4230 | 101.52 | 4.23 | 2 | 2 | 2B | 0 | 0 | 1139 | 0 | 1160 | N/A | N/A | N/A | N/A | 34758940 | 780 | 184.3972 | 0% | 0% | 100% | 0% | 100% | 39% | 7734263 | 707 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 99 | 25597594 | 4422 | 106.128 | 4.422 | 3.1 | 3.1 | 2B | 0 | 0 | 1049 | 0 | 1160 | N/A | N/A | N/A | N/A | 34759728 | 788 | 178.1999 | 0% | 0% | 100% | 0% | 100% | 39% | 7735388 | 1125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124 | 123423 | 123423 | 123.423 | 123.423 | [12 empty] | 25712 | 25712 | 208.3242 | [6 empty] | 7300 | 7300 | 1.0667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:45 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 16, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:35 PM, NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 11,473
GENSET 1 WARMUP EXERCISED @ 4:01 PM / STOPPED @ 4:11 PM
GENSET 2 WARMUP EXERCISED @ 4:11 PM / STOPPED @ 4:21 PM
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (39%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26160 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25597594 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34759728 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7735388 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 94 | 25601870 | 4276 | 102.624 | 4.276 | 4.6 | 4.6 | 2B | 0 | 0 | 1006 | 0 | 1160 | N/A | N/A | N/A | N/A | 34760484 | 756 | 176.8007 | 0% | 0% | 100% | 0% | 100% | 50% | 7736623 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 89 | 25605360 | 3490 | 83.76 | 3.49 | 5.7 | 5.7 | 2B | 0 | 0 | 972 | 0 | 1160 | N/A | N/A | N/A | N/A | 34761076 | 592 | 169.6275 | 0% | 0% | 100% | 0% | 100% | 50% | 7737710 | 1087 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 91 | 25610060 | 4700 | 112.8 | 4.7 | 7.5 | 7.5 | 2B | 0 | 0 | 951 | 0 | 1160 | N/A | N/A | N/A | N/A | 34761876 | 800 | 170.2128 | 0% | 0% | 100% | 0% | 100% | 50% | 7739505 | 1795 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 90 | 25612971 | 2911 | 69.864 | 2.911 | 8.7 | 8.7 | 2B | 0 | 0 | 945 | 0 | 1161 | N/A | N/A | N/A | N/A | 34762372 | 496 | 170.3882 | 0% | 0% | 100% | 0% | 100% | 50% | 7740680 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 100 | 25616888 | 3917 | 94.008 | 3.917 | 9.5 | 9.5 | 2B | 0 | 0 | 965 | 0 | 1110 | N/A | N/A | N/A | N/A | 34762988 | 616 | 157.2632 | 0% | 0% | 100% | 0% | 100% | 50% | 7741324 | 644 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 118 | 25621764 | 4876 | 117.024 | 4.876 | 9.5 | 9.5 | 2B | 0 | 0 | 1150 | 0 | 1160 | N/A | N/A | N/A | N/A | 34763780 | 792 | 162.4282 | 0% | 0% | 100% | 0% | 100% | 0% | 7741324 | 0 | 0.99 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 25627829 | 6065 | 145.56 | 6.065 | 9.1 | 9.1 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34765124 | 1344 | 221.5993 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 149 | 25633974 | 6145 | 147.48 | 6.145 | 8.5 | 8.5 | 3B+1S | 0 | 1125 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34766492 | 1368 | 222.62 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 153 | 25640207 | 6233 | 149.592 | 6.233 | 8 | 8 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34767851 | 1359 | 218.033 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 25646263 | 6056 | 145.344 | 6.056 | 7.5 | 7.5 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34769214 | 1363 | 225.0661 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 148 | 25652417 | 6154 | 147.696 | 6.154 | 7.2 | 7.2 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34770576 | 1362 | 221.3195 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 149 | 25658372 | 5955 | 142.92 | 5.955 | 6.7 | 6.7 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34771916 | 1340 | 225.021 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 150 | 25664230 | 5858 | 140.592 | 5.858 | 6.3 | 6.3 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34773236 | 1320 | 225.3329 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 25670098 | 5868 | 140.832 | 5.868 | 6 | 6 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34774564 | 1328 | 226.3122 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 134 | 25675770 | 5672 | 136.128 | 5.672 | 5.7 | 5.7 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34775896 | 1332 | 234.8378 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 131 | 25681377 | 5607 | 134.568 | 5.607 | 5.6 | 5.6 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34777196 | 1300 | 231.853 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 25687116 | 5739 | 137.736 | 5.739 | 5.2 | 5.2 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34778524 | 1328 | 231.3992 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 25692841 | 5725 | 137.4 | 5.725 | 5.1 | 5.1 | 3B+1S | 0 | 981 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34779828 | 1304 | 227.7729 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 132 | 25698512 | 5671 | 136.104 | 5.671 | 5 | 5 | 3B+1S | 0 | 988 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34781116 | 1288 | 227.1204 | 0% | 100% | 100% | 100% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 133 | 25703991 | 5479 | 131.496 | 5.479 | 4.2 | 4.2 | 2B+1S | 0 | 1138 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34782220 | 1104 | 201.4966 | 0% | 100% | 100% | 0% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 126 | 25709421 | 5430 | 130.32 | 5.43 | 3.2 | 3.2 | 2B+1S | 0 | 1127 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34783316 | 1096 | 201.8416 | 0% | 100% | 100% | 0% | 100% | 0% | 7741324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 123 | 25714671 | 5250 | 126 | 5.25 | 2.7 | 2.7 | 2B+1S | 0 | 1009 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34784356 | 1040 | 198.0952 | 0% | 100% | 100% | 0% | 100% | 0% | 7741324 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 107 | 25719226 | 4555 | 109.32 | 4.555 | 3.2 | 3.2 | 2B | 0 | 0 | 1140 | 0 | 1109 | N/A | N/A | N/A | N/A | 34785164 | 808 | 177.3875 | 0% | 0% | 100% | 0% | 100% | 30% | 7741890 | 566 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 97 | 25723474 | 4248 | 101.952 | 4.248 | 3.9 | 3.9 | 2B | 0 | 0 | 1048 | 0 | 1109 | N/A | N/A | N/A | N/A | 34785888 | 724 | 170.4331 | 0% | 0% | 100% | 0% | 100% | 30% | 7742565 | 675 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.125 | 125880 | 125880 | 125.88 | 125.88 | [12 empty] | 26160 | 26160 | 207.817 | [6 empty] | 7177 | 7177 | 1.0733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 17, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26292 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25723474 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34785888 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7742565 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 97 | 25727489 | 4015 | 96.36 | 4.015 | 4.8 | 4.8 | 2B | 0 | 0 | 1092 | 0 | 1109 | N/A | N/A | N/A | N/A | 34786591 | 703 | 175.0934 | 0% | 0% | 100% | 0% | 100% | 40% | 7743550 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 96 | 25731486 | 3997 | 95.928 | 3.997 | 5.9 | 5.9 | 2B | 0 | 0 | 1092 | 0 | 1109 | N/A | N/A | N/A | N/A | 34787276 | 685 | 171.3785 | 0% | 0% | 100% | 0% | 100% | 40% | 7744562 | 1012 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 95 | 25735340 | 3854 | 92.496 | 3.854 | 7.2 | 7.2 | 2B | 0 | 0 | 996 | 0 | 1109 | N/A | N/A | N/A | N/A | 34787897 | 621 | 161.1313 | 0% | 0% | 100% | 0% | 100% | 40% | 7745712 | 1150 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 94 | 25739042 | 3702 | 88.848 | 3.702 | 8.3 | 8.3 | 2B | 0 | 0 | 996 | 0 | 1109 | N/A | N/A | N/A | N/A | 34788486 | 589 | 159.1032 | 0% | 0% | 100% | 0% | 100% | 40% | 7746755 | 1043 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 125 | 97 | 25743047 | 4005 | 96.12 | 4.005 | 9 | 9 | 2B | 0 | 0 | 998 | 0 | 1109 | N/A | N/A | N/A | N/A | 34789116 | 630 | 157.3034 | 0% | 0% | 100% | 0% | 100% | 40% | 7747316 | 561 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 114 | 116 | 25747659 | 4612 | 110.688 | 4.612 | 9.5 | 9.5 | 2B | 0 | 0 | 1156 | 0 | 1140 | N/A | N/A | N/A | N/A | 34789884 | 768 | 166.5221 | 0% | 0% | 100% | 0% | 100% | 40% | 7747707 | 391 | 0.81 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 25753616 | 5957 | 142.968 | 5.957 | 9.1 | 9.1 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34791200 | 1316 | 220.9166 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 25759794 | 6178 | 148.272 | 6.178 | 8.6 | 8.6 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34792556 | 1356 | 219.4885 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 25765996 | 6202 | 148.848 | 6.202 | 8.1 | 8.1 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34793924 | 1368 | 220.574 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 25772252 | 6256 | 150.144 | 6.256 | 7.7 | 7.7 | 3B+1S | 0 | 1085 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34795312 | 1388 | 221.867 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 151 | 25778353 | 6101 | 146.424 | 6.101 | 7.3 | 7.3 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34796651 | 1339 | 219.4722 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 148 | 25784374 | 6021 | 144.504 | 6.021 | 6.7 | 6.7 | 3B+1S | 0 | 1107 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34798020 | 1369 | 227.3709 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 25790413 | 6039 | 144.936 | 6.039 | 6.3 | 6.3 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34799372 | 1352 | 223.8781 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 25796198 | 5785 | 138.84 | 5.785 | 6.1 | 6.1 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34800692 | 1320 | 228.1763 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 25801990 | 5792 | 139.008 | 5.792 | 5.6 | 5.6 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34802023 | 1331 | 229.7997 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 25807907 | 5917 | 142.008 | 5.917 | 5.2 | 5.2 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34803379 | 1356 | 229.1702 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 25813650 | 5743 | 137.832 | 5.743 | 4.6 | 4.6 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34804732 | 1353 | 235.5912 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 25819345 | 5695 | 136.68 | 5.695 | 4.4 | 4.4 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34806072 | 1340 | 235.2941 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 25825001 | 5656 | 135.744 | 5.656 | 4.2 | 4.2 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34807354 | 1282 | 226.662 | 0% | 100% | 100% | 100% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 131 | 25830392 | 5391 | 129.384 | 5.391 | 3.1 | 3.1 | 2B+1S | 0 | 1151 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34808456 | 1102 | 204.4148 | 0% | 100% | 100% | 0% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 25835827 | 5435 | 130.44 | 5.435 | 2.2 | 2.2 | 2B+1S | 0 | 1132 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34809574 | 1118 | 205.7038 | 0% | 100% | 100% | 0% | 100% | 0% | 7747707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 119 | 25840916 | 5089 | 122.136 | 5.089 | 1.8 | 1.8 | 2B+1S | 0 | 1027 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 34810580 | 1006 | 197.6813 | 0% | 100% | 100% | 0% | 100% | 0% | 7747707 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 107 | 25845651 | 4735 | 113.64 | 4.735 | 2.3 | 2.3 | 2B | 0 | 0 | 1140 | 0 | 1161 | N/A | N/A | N/A | N/A | 34811452 | 872 | 184.1605 | 0% | 0% | 100% | 0% | 100% | 36% | 7748335 | 628 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 98 | 25849751 | 4100 | 98.4 | 4.1 | 3.1 | 3.1 | 2B | 0 | 0 | 1053 | 0 | 1160 | N/A | N/A | N/A | N/A | 34812180 | 728 | 177.561 | 0% | 0% | 100% | 0% | 100% | 36% | 7749152 | 817 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.375 | 126277 | 126277 | 126.277 | 126.277 | [12 empty] | 26292 | 26292 | 208.2089 | [6 empty] | 6587 | 6587 | 0.945 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 4:43AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 18, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (36%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26228 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25849751 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34812180 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7749152 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 97 | 25854122 | 4371 | 104.904 | 4.371 | 4.2 | 4.2 | 2B | 0 | 0 | 1021 | 0 | 1160 | N/A | N/A | N/A | N/A | 34812948 | 768 | 175.7035 | 0% | 0% | 100% | 0% | 100% | 47% | 7750112 | 960 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 93 | 25857821 | 3699 | 88.776 | 3.699 | 5.2 | 5.2 | 2B | 0 | 0 | 997 | 0 | 1159 | N/A | N/A | N/A | N/A | 34813600 | 652 | 176.2639 | 0% | 0% | 100% | 0% | 100% | 47% | 7750991 | 879 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 91 | 25861690 | 3869 | 92.856 | 3.869 | 6.4 | 6.4 | 2B | 0 | 0 | 991 | 0 | 1161 | N/A | N/A | N/A | N/A | 34814276 | 676 | 174.7222 | 0% | 0% | 100% | 0% | 100% | 47% | 7752184 | 1193 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 106 | 96 | 25865641 | 3951 | 94.824 | 3.951 | 7.5 | 7.5 | 2B | 0 | 0 | 992 | 0 | 1160 | N/A | N/A | N/A | N/A | 34814960 | 684 | 173.1207 | 0% | 0% | 100% | 0% | 100% | 47% | 7753276 | 1092 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 146 | 100 | 25869682 | 4041 | 96.984 | 4.041 | 8.1 | 8.1 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 34815632 | 672 | 166.2955 | 0% | 0% | 100% | 0% | 100% | 47% | 7753855 | 579 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 119 | 25874204 | 4522 | 108.528 | 4.522 | 9.5 | 9.5 | 2B | 0 | 0 | 1100 | 0 | 1160 | N/A | N/A | N/A | N/A | 34816428 | 796 | 176.0283 | 0% | 0% | 100% | 0% | 100% | 0% | 7754715 | 860 | 0.94 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 25880167 | 5963 | 143.112 | 5.963 | 9.1 | 9.1 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34817716 | 1288 | 215.9987 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 25886347 | 6180 | 148.32 | 6.18 | 8.6 | 8.6 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34819084 | 1368 | 221.3592 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 151 | 25892487 | 6140 | 147.36 | 6.14 | 8.2 | 8.2 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34820436 | 1352 | 220.1954 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 25898534 | 6047 | 145.128 | 6.047 | 7.8 | 7.8 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34821780 | 1344 | 222.259 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 25904565 | 6031 | 144.744 | 6.031 | 7.4 | 7.4 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34823124 | 1344 | 222.8486 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 151 | 25910615 | 6050 | 145.2 | 6.05 | 7.1 | 7.1 | 3B+1S | 0 | 1134 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34824476 | 1352 | 223.4711 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 141 | 25916514 | 5899 | 141.576 | 5.899 | 6.6 | 6.6 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34825816 | 1340 | 227.1571 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 25922475 | 5961 | 143.064 | 5.961 | 6.3 | 6.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34827200 | 1384 | 232.1758 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 25928394 | 5919 | 142.056 | 5.919 | 5.9 | 5.9 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34828558 | 1358 | 229.4306 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 132 | 25934067 | 5673 | 136.152 | 5.673 | 5.7 | 5.7 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34829890 | 1332 | 234.7964 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 25939631 | 5564 | 133.536 | 5.564 | 5.3 | 5.3 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34831182 | 1292 | 232.207 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 25945320 | 5689 | 136.536 | 5.689 | 5 | 5 | 3B+1S | 0 | 1019 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34832452 | 1270 | 223.2378 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 25950992 | 5672 | 136.128 | 5.672 | 4.6 | 4.6 | 3B+1S | 0 | 1009 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34833724 | 1272 | 224.2595 | 0% | 100% | 100% | 100% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 25956479 | 5487 | 131.688 | 5.487 | 3.7 | 3.7 | 2B+1S | 0 | 1098 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34834838 | 1114 | 203.0253 | 0% | 100% | 100% | 0% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 25961830 | 5351 | 128.424 | 5.351 | 2.9 | 2.9 | 2B+1S | 0 | 1072 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34835884 | 1046 | 195.4775 | 0% | 100% | 100% | 0% | 100% | 0% | 7754715 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 25966901 | 5071 | 121.704 | 5.071 | 2.6 | 2.6 | 2B+1S | 0 | 1070 | 1190 | 0 | 1199 | N/A | N/A | N/A | N/A | 34836888 | 1004 | 197.9886 | 0% | 100% | 100% | 0% | 100% | 0% | 7754715 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 107 | 25971367 | 4466 | 107.184 | 4.466 | 3.1 | 3.1 | 2B | 0 | 0 | 1099 | 0 | 1160 | N/A | N/A | N/A | N/A | 34837684 | 796 | 178.2356 | 0% | 0% | 100% | 0% | 100% | 35% | 7755400 | 685 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 97 | 25975551 | 4184 | 100.416 | 4.184 | 4.1 | 4.1 | 2B | 0 | 0 | 1041 | 0 | 1160 | N/A | N/A | N/A | N/A | 34838408 | 724 | 173.0402 | 0% | 0% | 100% | 0% | 100% | 35% | 7756256 | 856 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.2917 | 125800 | 125800 | 125.8 | 125.8 | [12 empty] | 26228 | 26228 | 208.4897 | [6 empty] | 7104 | 7104 | 0.98333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (47%) @ 12:01 AM
XCV1 CLOSED @ 5:45 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 19, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
AUTOMATION OFFICER / ITS ISSUED & SET-UP SERVICE UNIT FOR SCADA
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:05 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26164 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25975551 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34838408 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7756256 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 97 | 25979789 | 4238 | 101.712 | 4.238 | 5.2 | 5.2 | 2B | 0 | 0 | 1041 | 0 | 1160 | N/A | N/A | N/A | N/A | 34839156 | 748 | 176.4983 | 0% | 0% | 100% | 0% | 100% | 50% | 7757380 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 25983755 | 3966 | 95.184 | 3.966 | 6.5 | 6.5 | 2B | 0 | 0 | 999 | 0 | 1160 | N/A | N/A | N/A | N/A | 34839852 | 696 | 175.4917 | 0% | 0% | 100% | 0% | 100% | 50% | 7758597 | 1217 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 25987384 | 3629 | 87.096 | 3.629 | 7.7 | 7.7 | 2B | 0 | 0 | 971 | 0 | 1161 | N/A | N/A | N/A | N/A | 34840472 | 620 | 170.846 | 0% | 0% | 100% | 0% | 100% | 50% | 7759717 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 91 | 25991170 | 3786 | 90.864 | 3.786 | 8.9 | 8.9 | 2B | 0 | 0 | 977 | 0 | 1160 | N/A | N/A | N/A | N/A | 34841116 | 644 | 170.1004 | 0% | 0% | 100% | 0% | 100% | 50% | 7760737 | 1020 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 101 | 25995201 | 4031 | 96.744 | 4.031 | 9.5 | 9.5 | 2B | 0 | 0 | 761 | 0 | 1160 | N/A | N/A | N/A | N/A | 34841756 | 640 | 158.7695 | 0% | 0% | 100% | 0% | 100% | 50% | 7761291 | 554 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 104 | 25999419 | 4218 | 101.232 | 4.218 | 9.5 | 9.5 | 2B | 0 | 0 | 999 | 0 | 1150 | N/A | N/A | N/A | N/A | 34842360 | 604 | 143.1958 | 0% | 0% | 100% | 0% | 100% | 0% | 7761291 | 0 | 0.98 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 140 | 26004731 | 5312 | 127.488 | 5.312 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1170 | N/A | N/A | N/A | N/A | 34843365 | 1005 | 189.1943 | 0% | 0% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 148 | 26010725 | 5994 | 143.856 | 5.994 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34844664 | 1299 | 216.7167 | 0% | 0% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 26016796 | 6071 | 145.704 | 6.071 | 9.1 | 9.1 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34846012 | 1348 | 222.0392 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 155 | 26022970 | 6174 | 148.176 | 6.174 | 8.4 | 8.4 | 3B+1S | 0 | 1135 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34847400 | 1388 | 224.8137 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 | 1 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 26029204 | 6234 | 149.616 | 6.234 | 7.7 | 7.7 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34848792 | 1392 | 223.2916 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 26035410 | 6206 | 148.944 | 6.206 | 6.9 | 6.9 | 3B+1S | 0 | 1141 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34850192 | 1400 | 225.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 146 | 26041449 | 6039 | 144.936 | 6.039 | 6.3 | 6.3 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34851564 | 1372 | 227.1899 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 142 | 26047545 | 6096 | 146.304 | 6.096 | 5.6 | 5.6 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34852956 | 1392 | 228.3465 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 26053339 | 5794 | 139.056 | 5.794 | 4.9 | 4.9 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34854294 | 1338 | 230.9285 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 26059220 | 5881 | 141.144 | 5.881 | 4.3 | 4.3 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34855662 | 1368 | 232.6135 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 144 | 26065190 | 5970 | 143.28 | 5.97 | 3.5 | 3.5 | 3B+1S | 0 | 1132 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34857052 | 1390 | 232.8308 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 26070993 | 5803 | 139.272 | 5.803 | 3.1 | 3.1 | 3B+1S | 0 | 1067 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34858398 | 1346 | 231.949 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 26076689 | 5696 | 136.704 | 5.696 | 2.9 | 2.9 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 34859700 | 1302 | 228.5815 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 128 | 26082223 | 5534 | 132.816 | 5.534 | 2.7 | 2.7 | 3B+1S | 0 | 994 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34860936 | 1236 | 223.3466 | 0% | 100% | 100% | 100% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 26087498 | 5275 | 126.6 | 5.275 | 2 | 2 | 2B+1S | 0 | 1091 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34862014 | 1078 | 204.3602 | 0% | 100% | 100% | 0% | 100% | 0% | 7761291 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 120 | 26092667 | 5169 | 124.056 | 5.169 | 1.6 | 1.6 | 2B+1S | 0 | 1008 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34863044 | 1030 | 199.2648 | 0% | 100% | 100% | 0% | 100% | 0% | 7761291 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 108 | 26096952 | 4285 | 102.84 | 4.285 | 2.3 | 2.3 | 2B | 0 | 0 | 1110 | 0 | 1160 | N/A | N/A | N/A | N/A | 34863816 | 772 | 180.1634 | 0% | 0% | 100% | 0% | 100% | 38% | 7762100 | 809 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 101 | 26101280 | 4328 | 103.872 | 4.328 | 3.4 | 3.4 | 2B | 0 | 0 | 1043 | 0 | 1161 | N/A | N/A | N/A | N/A | 34864572 | 756 | 174.6765 | 0% | 0% | 100% | 0% | 100% | 38% | 7763220 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.4583 | 125729 | 125729 | 125.729 | 125.729 | [12 empty] | 26164 | 26164 | 208.0984 | [6 empty] | 6964 | 6964 | 1 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (47%) @ 12:01 AM
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 19, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26064 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26101280 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34864572 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7763220 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 99 | 26105330 | 4050 | 97.2 | 4.05 | 4.7 | 4.7 | 2B | 0 | 0 | 1042 | 0 | 1160 | N/A | N/A | N/A | N/A | 34865320 | 748 | 184.6914 | 0% | 0% | 100% | 0% | 100% | 50% | 7764305 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 94 | 26109150 | 3820 | 91.68 | 3.82 | 5.9 | 5.9 | 2B | 0 | 0 | 1000 | 0 | 1160 | N/A | N/A | N/A | N/A | 34865988 | 668 | 174.8691 | 0% | 0% | 100% | 0% | 100% | 50% | 7765472 | 1167 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 94 | 26112971 | 3821 | 91.704 | 3.821 | 7.4 | 7.4 | 2B | 0 | 0 | 982 | 0 | 1160 | N/A | N/A | N/A | N/A | 34866660 | 672 | 175.8702 | 0% | 0% | 100% | 0% | 100% | 50% | 7766890 | 1418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 91 | 26116701 | 3730 | 89.52 | 3.73 | 8.8 | 8.8 | 2B | 0 | 0 | 969 | 0 | 1161 | N/A | N/A | N/A | N/A | 34867388 | 728 | 195.1743 | 0% | 0% | 100% | 0% | 100% | 50% | 7768264 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 96 | 26120651 | 3950 | 94.8 | 3.95 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1160 | N/A | N/A | N/A | N/A | 34867964 | 576 | 145.8228 | 0% | 0% | 100% | 0% | 100% | 50% | 7768859 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 118 | 26125332 | 4681 | 112.344 | 4.681 | 9.5 | 9.5 | 2B | 0 | 0 | 1109 | 0 | 1129 | N/A | N/A | N/A | N/A | 34868684 | 720 | 153.8133 | 0% | 0% | 100% | 0% | 100% | 0% | 7768859 | 0 | 1.06 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 26131260 | 5928 | 142.272 | 5.928 | 9.3 | 9.3 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34869956 | 1272 | 214.5749 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 26137304 | 6044 | 145.056 | 6.044 | 9 | 9 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34871300 | 1344 | 222.3693 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 26143477 | 6173 | 148.152 | 6.173 | 8.5 | 8.5 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34872668 | 1368 | 221.6102 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 26149522 | 6045 | 145.08 | 6.045 | 8.1 | 8.1 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34874008 | 1340 | 221.6708 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 26155643 | 6121 | 146.904 | 6.121 | 7.7 | 7.7 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34875372 | 1364 | 222.8394 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 26161569 | 5926 | 142.224 | 5.926 | 7.4 | 7.4 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34876700 | 1328 | 224.0972 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 144 | 26167438 | 5869 | 140.856 | 5.869 | 7 | 7 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34878036 | 1336 | 227.6367 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 136 | 26173341 | 5903 | 141.672 | 5.903 | 6.7 | 6.7 | 3B+1S | 0 | 993 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34879382 | 1346 | 228.0197 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 26179052 | 5711 | 137.064 | 5.711 | 6.4 | 6.4 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34880710 | 1328 | 232.5337 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 26184800 | 5748 | 137.952 | 5.748 | 6.1 | 6.1 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34882044 | 1334 | 232.0807 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 26190501 | 5701 | 136.824 | 5.701 | 5.6 | 5.6 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34883350 | 1306 | 229.0826 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 26196193 | 5692 | 136.608 | 5.692 | 5.3 | 5.3 | 3B+1S | 0 | 1001 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34884632 | 1282 | 225.2284 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 26201795 | 5602 | 134.448 | 5.602 | 5 | 5 | 3B+1S | 0 | 999 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 34885872 | 1240 | 221.3495 | 0% | 100% | 100% | 100% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 26207212 | 5417 | 130.008 | 5.417 | 4.2 | 4.2 | 2B+1S | 0 | 1123 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34886970 | 1098 | 202.6952 | 0% | 100% | 100% | 0% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 128 | 26212535 | 5323 | 127.752 | 5.323 | 3.2 | 3.2 | 2B+1S | 0 | 1108 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34888022 | 1052 | 197.6329 | 0% | 100% | 100% | 0% | 100% | 0% | 7768859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 122 | 26217607 | 5072 | 121.728 | 5.072 | 2.8 | 2.8 | 2B+1S | 0 | 1006 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34889044 | 1022 | 201.4984 | 0% | 100% | 100% | 0% | 100% | 0% | 7768859 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 109 | 26222224 | 4617 | 110.808 | 4.617 | 3.3 | 3.3 | 2B | 0 | 0 | 1115 | 0 | 1160 | N/A | N/A | N/A | N/A | 34889884 | 840 | 181.9363 | 0% | 0% | 100% | 0% | 100% | 40% | 7769443 | 584 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 106 | 26226484 | 4260 | 102.24 | 4.26 | 4.2 | 4.2 | 2B | 0 | 0 | 1067 | 0 | 1161 | N/A | N/A | N/A | N/A | 34890636 | 752 | 176.5258 | 0% | 0% | 100% | 0% | 100% | 40% | 7770281 | 838 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9167 | 125204 | 125204 | 125.204 | 125.204 | [12 empty] | 26064 | 26064 | 208.1723 | [6 empty] | 7061 | 7061 | 1.035 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
MR ALDWIN RAMIREZ AND TEAM OF PMD- PLANNING DEPT INSPECT THE SITE WITH A PLATE NUMBER OF NYQ-833
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 21, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, the site will monitoring by Sir Michael Buligan and his team
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26324 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26226484 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34890636 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7770281 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 99 | 26230695 | 4211 | 101.064 | 4.211 | 5.3 | 5.3 | 2B | 0 | 0 | 1051 | 0 | 1160 | N/A | N/A | N/A | N/A | 34891358 | 722 | 171.4557 | 0% | 0% | 100% | 0% | 100% | 50% | 7771323 | 1042 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 26234561 | 3866 | 92.784 | 3.866 | 6.5 | 6.5 | 2B | 0 | 0 | 1010 | 0 | 1161 | N/A | N/A | N/A | N/A | 34892072 | 714 | 184.687 | 0% | 0% | 100% | 0% | 100% | 50% | 7772463 | 1140 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 94 | 26238643 | 4082 | 97.968 | 4.082 | 7.9 | 7.9 | 2B | 0 | 0 | 976 | 0 | 1160 | N/A | N/A | N/A | N/A | 34892784 | 712 | 174.4243 | 0% | 0% | 100% | 0% | 100% | 50% | 7773743 | 1280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 92 | 26242221 | 3578 | 85.872 | 3.578 | 9 | 9 | 2B | 0 | 0 | 968 | 0 | 1161 | N/A | N/A | N/A | N/A | 34893392 | 608 | 169.9273 | 0% | 0% | 100% | 0% | 100% | 50% | 7774850 | 1107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 92 | 26246242 | 4021 | 96.504 | 4.021 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 0 | 1161 | N/A | N/A | N/A | N/A | 34894036 | 644 | 160.1592 | 0% | 0% | 100% | 0% | 100% | 50% | 7775199 | 349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 24 | 16.9014 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 107 | 26250471 | 4229 | 101.496 | 4.229 | 9.5 | 9.5 | 2B | 0 | 0 | 922 | 0 | 1160 | N/A | N/A | N/A | N/A | 34894644 | 608 | 143.7692 | 0% | 0% | 100% | 0% | 100% | 0% | 7775199 | 0 | 0.91 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 139 | 26256189 | 5718 | 137.232 | 5.718 | 9.5 | 9.5 | 3B | 0 | 0 | 1183 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34895820 | 1176 | 205.6663 | 0% | 0% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 26262284 | 6095 | 146.28 | 6.095 | 9.2 | 9.2 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34897164 | 1344 | 220.5086 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 153 | 26268473 | 6189 | 148.536 | 6.189 | 8.7 | 8.7 | 3B+1S | 0 | 1136 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34898532 | 1368 | 221.0373 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 154 | 26274697 | 6224 | 149.376 | 6.224 | 8.2 | 8.2 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34899911 | 1379 | 221.5617 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 155 | 26280870 | 6173 | 148.152 | 6.173 | 7.8 | 7.8 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34901252 | 1341 | 217.2364 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 146 | 26286985 | 6115 | 146.76 | 6.115 | 7.3 | 7.3 | 3B+1S | 0 | 1154 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34902612 | 1360 | 222.4039 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 26292966 | 5981 | 143.544 | 5.981 | 6.8 | 6.8 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34903956 | 1344 | 224.7116 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 26298927 | 5961 | 143.064 | 5.961 | 6.5 | 6.5 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34905241 | 1285 | 215.5679 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 26304826 | 5899 | 141.576 | 5.899 | 5.8 | 5.8 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34906651 | 1410 | 239.0236 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 143 | 26310727 | 5901 | 141.624 | 5.901 | 5.2 | 5.2 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34908062 | 1411 | 239.112 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 142 | 26316670 | 5943 | 142.632 | 5.943 | 4.4 | 4.4 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34909412 | 1350 | 227.158 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 141 | 26322420 | 5750 | 138 | 5.75 | 3.7 | 3.7 | 3B+1S | 0 | 1060 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34910724 | 1312 | 228.1739 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 26328195 | 5775 | 138.6 | 5.775 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34912044 | 1320 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 129 | 26333673 | 5478 | 131.472 | 5.478 | 3.1 | 3.1 | 3B+1S | 0 | 989 | 1135 | 1185 | 1138 | N/A | N/A | N/A | N/A | 34913264 | 1220 | 222.709 | 0% | 100% | 100% | 100% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 26339019 | 5346 | 128.304 | 5.346 | 2.6 | 2.6 | 2B+1S | 0 | 1076 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34914328 | 1064 | 199.0273 | 0% | 100% | 100% | 0% | 100% | 0% | 7775199 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 122 | 26344149 | 5130 | 123.12 | 5.13 | 2.2 | 2.2 | 2B+1S | 0 | 1024 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34915348 | 1020 | 198.8304 | 0% | 100% | 100% | 0% | 100% | 0% | 7775199 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 108 | 26348706 | 4557 | 109.368 | 4.557 | 2.8 | 2.8 | 2B | 0 | 0 | 1176 | 0 | 1109 | N/A | N/A | N/A | N/A | 34916180 | 832 | 182.5763 | 0% | 0% | 100% | 0% | 100% | 40% | 7775991 | 792 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 102 | 26353152 | 4446 | 106.704 | 4.446 | 3.8 | 3.8 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 34916960 | 780 | 175.4386 | 0% | 0% | 100% | 0% | 100% | 40% | 7776965 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.9583 | 126668 | 126668 | 126.668 | 126.668 | [12 empty] | 26324 | 26324 | 207.8189 | [6 empty] | 6684 | 6684 | 1.0017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 22, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:00 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:05 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25735 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26353152 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34916960 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7776965 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 100 | 26357326 | 4174 | 100.176 | 4.174 | 4.8 | 4.8 | 2B | 0 | 0 | 1098 | 0 | 1109 | N/A | N/A | N/A | N/A | 34917696 | 736 | 176.3297 | 0% | 0% | 100% | 0% | 100% | 55% | 7777720 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 96 | 26361337 | 4011 | 96.264 | 4.011 | 5.9 | 5.9 | 2B | 0 | 0 | 1071 | 0 | 1109 | N/A | N/A | N/A | N/A | 34918392 | 696 | 173.5228 | 0% | 0% | 100% | 0% | 100% | 55% | 7778819 | 1099 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 95 | 26365950 | 4613 | 110.712 | 4.613 | 7.3 | 7.3 | 2B | 0 | 0 | 1041 | 0 | 1109 | N/A | N/A | N/A | N/A | 34919180 | 788 | 170.8216 | 0% | 0% | 100% | 0% | 100% | 55% | 7780243 | 1424 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 97 | 26369134 | 3184 | 76.416 | 3.184 | 8.3 | 8.3 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 34919708 | 528 | 165.8291 | 0% | 0% | 100% | 0% | 100% | 55% | 7781190 | 947 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 92 | 26373021 | 3887 | 93.288 | 3.887 | 9.5 | 9.5 | 2B | 0 | 0 | 990 | 0 | 1110 | N/A | N/A | N/A | N/A | 34920324 | 616 | 158.477 | 0% | 0% | 100% | 0% | 100% | 55% | 7782165 | 975 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 29 | 20.4225 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 104 | 103 | 26377070 | 4049 | 97.176 | 4.049 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1008 | N/A | N/A | N/A | N/A | 34920860 | 536 | 132.3784 | 0% | 0% | 100% | 0% | 100% | 0% | 7782165 | 0 | 0.98 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 133 | 26382456 | 5386 | 129.264 | 5.386 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1159 | N/A | N/A | N/A | N/A | 34921892 | 1032 | 191.6079 | 0% | 0% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 26388392 | 5936 | 142.464 | 5.936 | 9.4 | 9.4 | 3B+1S | 0 | 986 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34923164 | 1272 | 214.2857 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 26394572 | 6180 | 148.32 | 6.18 | 9 | 9 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34924532 | 1368 | 221.3592 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 152 | 26400765 | 6193 | 148.632 | 6.193 | 8.6 | 8.6 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34925888 | 1356 | 218.9569 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 26406927 | 6162 | 147.888 | 6.162 | 8.2 | 8.2 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34927244 | 1356 | 220.0584 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 149 | 26412999 | 6072 | 145.728 | 6.072 | 7.8 | 7.8 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34928596 | 1352 | 222.6614 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 26418991 | 5992 | 143.808 | 5.992 | 7.2 | 7.2 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34929956 | 1360 | 226.9693 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 145 | 26424948 | 5957 | 142.968 | 5.957 | 6.7 | 6.7 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34931296 | 1340 | 224.9454 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 139 | 26430825 | 5877 | 141.048 | 5.877 | 6.2 | 6.2 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34932644 | 1348 | 229.3687 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 141 | 26436641 | 5816 | 139.584 | 5.816 | 5.7 | 5.7 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34933988 | 1344 | 231.0867 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 142 | 26442445 | 5804 | 139.296 | 5.804 | 5 | 5 | 3B+1S | 0 | 1110 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34935352 | 1364 | 235.0103 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 26448139 | 5694 | 136.656 | 5.694 | 4.8 | 4.8 | 3B+1S | 0 | 990 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34936644 | 1292 | 226.9055 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 26453794 | 5655 | 135.72 | 5.655 | 4.7 | 4.7 | 3B+1S | 0 | 980 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 34937932 | 1288 | 227.763 | 0% | 100% | 100% | 100% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 26459243 | 5449 | 130.776 | 5.449 | 3.8 | 3.8 | 2B+1S | 0 | 1102 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34939036 | 1104 | 202.606 | 0% | 100% | 100% | 0% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 123 | 26464469 | 5226 | 125.424 | 5.226 | 2.7 | 2.7 | 2B+1S | 0 | 1034 | 1195 | 0 | 1180 | N/A | N/A | N/A | N/A | 34940072 | 1036 | 198.2396 | 0% | 100% | 100% | 0% | 100% | 0% | 7782165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 118 | 26469695 | 5226 | 125.424 | 5.226 | 2.5 | 2.5 | 2B+1S | 0 | 984 | 1195 | 0 | 1170 | N/A | N/A | N/A | N/A | 34941108 | 1036 | 198.2396 | 0% | 100% | 100% | 0% | 100% | 0% | 7782165 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 109 | 26473894 | 4199 | 100.776 | 4.199 | 3.9 | 3.9 | 2B | 0 | 0 | 1099 | 0 | 1109 | N/A | N/A | N/A | N/A | 34941973 | 865 | 206.0014 | 0% | 0% | 100% | 0% | 100% | 45% | 7783075 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 105 | 26478076 | 4182 | 100.368 | 4.182 | 5.1 | 5.1 | 2B | 0 | 0 | 1089 | 0 | 1110 | N/A | N/A | N/A | N/A | 34942695 | 722 | 172.6447 | 0% | 0% | 100% | 0% | 100% | 45% | 7784084 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.8333 | 124924 | 124924 | 124.924 | 124.924 | [12 empty] | 25735 | 25735 | 206.0053 | [6 empty] | 7119 | 7119 | 1.03 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (55%) @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:17 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:38 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25AM, NORMAL OPERATION
MR. RENATO AND TEAM OF CITIPEST TEST CONTROL THE AREA OF VILLAMOR PS
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 23, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:17 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:12 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25773 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26478076 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34942695 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7784084 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 92 | 26482111 | 4035 | 96.84 | 4.035 | 6.2 | 6.2 | 2B | 0 | 0 | 1002 | 0 | 1109 | N/A | N/A | N/A | N/A | 34943350 | 655 | 162.3296 | 0% | 0% | 100% | 0% | 100% | 50% | 7785229 | 1145 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 89 | 26486130 | 4019 | 96.456 | 4.019 | 7.4 | 7.4 | 2B | 0 | 0 | 986 | 0 | 1109 | N/A | N/A | N/A | N/A | 34943986 | 636 | 158.2483 | 0% | 0% | 100% | 0% | 100% | 50% | 7786379 | 1150 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 90 | 26490159 | 4029 | 96.696 | 4.029 | 8.3 | 8.3 | 2B | 0 | 0 | 980 | 0 | 1110 | N/A | N/A | N/A | N/A | 34944632 | 646 | 160.3376 | 0% | 0% | 100% | 0% | 100% | 50% | 7787524 | 1145 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 94 | 26494369 | 4210 | 101.04 | 4.21 | 9.5 | 9.5 | 2B | 0 | 0 | 1002 | 0 | 1081 | N/A | N/A | N/A | N/A | 34945282 | 650 | 154.3943 | 0% | 0% | 100% | 0% | 100% | 50% | 7788569 | 1045 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 96 | 26498580 | 4211 | 101.064 | 4.211 | 9.5 | 9.5 | 2B | 0 | 0 | 1061 | 0 | 1069 | N/A | N/A | N/A | N/A | 34945932 | 650 | 154.3576 | 0% | 0% | 100% | 0% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 117 | 26502559 | 3979 | 95.496 | 3.979 | 9.5 | 9.5 | 2B | 0 | 0 | 1140 | 0 | 1110 | N/A | N/A | N/A | N/A | 34946504 | 572 | 143.7547 | 0% | 0% | 100% | 0% | 100% | 0% | 7788569 | 0 | 1.08 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 132 | 26508668 | 6109 | 146.616 | 6.109 | 9.3 | 9.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34947800 | 1296 | 212.146 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 26514778 | 6110 | 146.64 | 6.11 | 8.9 | 8.9 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34949156 | 1356 | 221.9313 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 26520976 | 6198 | 148.752 | 6.198 | 8.4 | 8.4 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34950532 | 1376 | 222.0071 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 26526986 | 6010 | 144.24 | 6.01 | 7.9 | 7.9 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34951864 | 1332 | 221.6306 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 | 1.17 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 26533063 | 6077 | 145.848 | 6.077 | 7.6 | 7.6 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34953212 | 1348 | 221.82 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 150 | 26539223 | 6160 | 147.84 | 6.16 | 7 | 7 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34954596 | 1384 | 224.6753 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 137 | 26545156 | 5933 | 142.392 | 5.933 | 6.6 | 6.6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34955932 | 1336 | 225.1812 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 26550967 | 5811 | 139.464 | 5.811 | 6.4 | 6.4 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34957248 | 1316 | 226.467 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 135 | 26556667 | 5700 | 136.8 | 5.7 | 6.1 | 6.1 | 3B+1S | 0 | 1011 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34958564 | 1316 | 230.8772 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 26562360 | 5693 | 136.632 | 5.693 | 5.8 | 5.8 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34959876 | 1312 | 230.4585 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 145 | 26568127 | 5767 | 138.408 | 5.767 | 5.4 | 5.4 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34961220 | 1344 | 233.0501 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 142 | 26573922 | 5795 | 139.08 | 5.795 | 4.7 | 4.7 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34962516 | 1296 | 223.6411 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 137 | 26579667 | 5745 | 137.88 | 5.745 | 4.3 | 4.3 | 3B+1S | 0 | 1023 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 34963804 | 1288 | 224.195 | 0% | 100% | 100% | 100% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 134 | 26585143 | 5476 | 131.424 | 5.476 | 3.5 | 3.5 | 2B+1S | 0 | 1164 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34964892 | 1088 | 198.6852 | 0% | 100% | 100% | 0% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 134 | 26590403 | 5260 | 126.24 | 5.26 | 3 | 3 | 2B+1S | 0 | 1101 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34965912 | 1020 | 193.9163 | 0% | 100% | 100% | 0% | 100% | 0% | 7788569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 124 | 26595630 | 5227 | 125.448 | 5.227 | 2.6 | 2.6 | 2B+1S | 0 | 992 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34966932 | 1020 | 195.1406 | 0% | 100% | 100% | 0% | 100% | 0% | 7788569 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 108 | 26600190 | 4560 | 109.44 | 4.56 | 3.1 | 3.1 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 34967728 | 796 | 174.5614 | 0% | 0% | 100% | 0% | 100% | 30% | 7789316 | 747 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 103 | 26604577 | 4387 | 105.288 | 4.387 | 3.9 | 3.9 | 2B | 0 | 0 | 1095 | 0 | 1110 | N/A | N/A | N/A | N/A | 34968468 | 740 | 168.6802 | 0% | 0% | 100% | 0% | 100% | 30% | 7790165 | 849 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.25 | 126501 | 126501 | 126.501 | 126.501 | [12 empty] | 25773 | 25773 | 203.7375 | [6 empty] | 6081 | 6081 | 1.035 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:48 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:45 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:23 AM, NORMAL OPERATION
MR. BELTRAN WATER SAMPLING/ CENTRAL LAB RES. 1.22MG/L
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:04 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 24, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:19 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:15 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25948 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26604577 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34968468 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7790165 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 106 | 102 | 26608727 | 4150 | 99.6 | 4.15 | 4.8 | 4.8 | 2B | 0 | 0 | 1137 | 0 | 1109 | N/A | N/A | N/A | N/A | 34969190 | 722 | 173.9759 | 0% | 0% | 100% | 0% | 100% | 50% | 7791145 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 104 | 100 | 26612805 | 4078 | 97.872 | 4.078 | 5.8 | 5.8 | 2B | 0 | 0 | 1100 | 0 | 1109 | N/A | N/A | N/A | N/A | 34969885 | 695 | 170.4267 | 0% | 0% | 100% | 0% | 100% | 50% | 7792195 | 1050 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 99 | 26616790 | 3985 | 95.64 | 3.985 | 7.2 | 7.2 | 2B | 0 | 0 | 1060 | 0 | 1109 | N/A | N/A | N/A | N/A | 34970556 | 671 | 168.3814 | 0% | 0% | 100% | 0% | 100% | 50% | 7793280 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 97 | 26620642 | 3852 | 92.448 | 3.852 | 8.4 | 8.4 | 2B | 0 | 0 | 1028 | 0 | 1109 | N/A | N/A | N/A | N/A | 34971196 | 640 | 166.1475 | 0% | 0% | 100% | 0% | 100% | 50% | 7794434 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 142 | 102 | 26624851 | 4209 | 101.016 | 4.209 | 9 | 9 | 2B | 0 | 0 | 1082 | 0 | 1067 | N/A | N/A | N/A | N/A | 34971876 | 680 | 161.5586 | 0% | 0% | 100% | 0% | 100% | 50% | 7795008 | 574 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 117 | 26629543 | 4692 | 112.608 | 4.692 | 9.5 | 9.5 | 2B | 0 | 0 | 1135 | 0 | 1140 | N/A | N/A | N/A | N/A | 34972612 | 736 | 156.8627 | 0% | 0% | 100% | 0% | 100% | 50% | 7795436 | 428 | 1.1 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 144 | 26635569 | 6026 | 144.624 | 6.026 | 9.3 | 9.3 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34973916 | 1304 | 216.3956 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 26641734 | 6165 | 147.96 | 6.165 | 8.6 | 8.6 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34975284 | 1368 | 221.8978 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 150 | 26647924 | 6190 | 148.56 | 6.19 | 8.1 | 8.1 | 3B+1S | 0 | 1110 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34976652 | 1368 | 221.0016 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 26654133 | 6209 | 149.016 | 6.209 | 7.6 | 7.6 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34978030 | 1378 | 221.9359 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 26660283 | 6150 | 147.6 | 6.15 | 7.2 | 7.2 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34979376 | 1346 | 218.8618 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 26666291 | 6008 | 144.192 | 6.008 | 6.8 | 6.8 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34980724 | 1348 | 224.3675 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 26672150 | 5859 | 140.616 | 5.859 | 6.5 | 6.5 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34982052 | 1328 | 226.6598 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 26677850 | 5700 | 136.8 | 5.7 | 6.3 | 6.3 | 3B+1S | 0 | 1022 | 1165 | 1185 | 1178 | N/A | N/A | N/A | N/A | 34983356 | 1304 | 228.7719 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 130 | 26683490 | 5640 | 135.36 | 5.64 | 6 | 6 | 3B+1S | 0 | 1009 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34984636 | 1280 | 226.9504 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 26689153 | 5663 | 135.912 | 5.663 | 5.7 | 5.7 | 3B+1S | 0 | 1080 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 34985836 | 1200 | 211.9018 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 146 | 26694948 | 5795 | 139.08 | 5.795 | 5.3 | 5.3 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34987090 | 1254 | 216.3934 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 26700705 | 5757 | 138.168 | 5.757 | 4.9 | 4.9 | 3B+1S | 0 | 1006 | 1163 | 1185 | 1168 | N/A | N/A | N/A | N/A | 34988372 | 1282 | 222.6854 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 138 | 26706401 | 5696 | 136.704 | 5.696 | 4.6 | 4.6 | 3B+1S | 0 | 1013 | 1165 | 1185 | 1168 | N/A | N/A | N/A | N/A | 34989636 | 1264 | 221.9101 | 0% | 100% | 100% | 100% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 135 | 26711870 | 5469 | 131.256 | 5.469 | 3.8 | 3.8 | 2B+1S | 0 | 1148 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34990720 | 1084 | 198.2081 | 0% | 100% | 100% | 0% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 128 | 26717257 | 5387 | 129.288 | 5.387 | 3.2 | 3.2 | 2B+1S | 0 | 1091 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 34991780 | 1060 | 196.77 | 0% | 100% |  | 0% | 100% | 0% | 7795436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 124 | 26722637 | 5380 | 129.12 | 5.38 | 2.7 | 2.7 | 2B+1S | 0 | 1089 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 34992844 | 1064 | 197.7695 | 0% | 100% |  | 0% | 100% | 0% | 7795436 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 107 | 26726927 | 4290 | 102.96 | 4.29 | 3.3 | 3.3 | 2B | 0 | 0 | 1185 | 0 | 1199 | N/A | N/A | N/A | N/A | 34993620 | 776 | 180.8858 | 0% | 0% |  | 0% | 100% | 45% | 7796188 | 752 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 101 | 26731452 | 4525 | 108.6 | 4.525 | 4.6 | 4.6 | 2B | 0 | 0 | 1112 | 0 | 1109 | N/A | N/A | N/A | N/A | 34994416 | 796 | 175.9116 | 0% | 0% |  | 0% | 100% | 45% | 7797320 | 1132 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.6667 | 126875 | 126875 | 126.875 | 126.875 | [12 empty] | 25948 | 25948 | 204.5163 | [6 empty] | 7155 | 7155 | 1.0017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 5:20 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:23 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:38 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:36 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18 AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 25, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:08 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:45 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:08 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26160 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26731452 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 34994416 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7797320 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 99 | 26735634 | 4182 | 100.368 | 4.182 | 5.6 | 5.6 | 2B | 0 | 0 | 1078 | 0 | 1109 | N/A | N/A | N/A | N/A | 34995140 | 724 | 173.1229 | 0% | 0% | 100% | 0% | 100% | 55% | 7798240 | 920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 98 | 26739673 | 4039 | 96.936 | 4.039 | 6.9 | 6.9 | 2B | 0 | 0 | 1044 | 0 | 1110 | N/A | N/A | N/A | N/A | 34995828 | 688 | 170.3392 | 0% | 0% | 100% | 0% | 100% | 55% | 7799524 | 1284 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 92 | 26743630 | 3957 | 94.968 | 3.957 | 8.2 | 8.2 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 34996476 | 648 | 163.7604 | 0% | 0% | 100% | 0% | 100% | 55% | 7800798 | 1274 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 102 | 95 | 26747495 | 3865 | 92.76 | 3.865 | 9.4 | 9.4 | 2B | 0 | 0 | 1016 | 0 | 1109 | N/A | N/A | N/A | N/A | 34997116 | 640 | 165.5886 | 0% | 0% | 100% | 0% | 100% | 55% | 7801850 | 1052 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 99 | 26751562 | 4067 | 97.608 | 4.067 | 9.5 | 9.5 | 2B | 0 | 0 | 970 | 0 | 1109 | N/A | N/A | N/A | N/A | 34997748 | 632 | 155.3971 | 0% | 0% | 100% | 0% | 100% | 55% | 7802023 | 173 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 112 | 108 | 26755896 | 4334 | 104.016 | 4.334 | 9.5 | 9.5 | 2B | 0 | 0 | 1016 | 0 | 1038 | N/A | N/A | N/A | N/A | 34998364 | 616 | 142.132 | 0% | 0% | 100% | 0% | 100% | 0% | 7802023 | 0 | 0.93 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 26761549 | 5653 | 135.672 | 5.653 | 9.5 | 9.5 | 3B+1S | 0 | 983 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 34999564 | 1200 | 212.2767 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 26767659 | 6110 | 146.64 | 6.11 | 9.1 | 9.1 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35000916 | 1352 | 221.2766 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 149 | 26773739 | 6080 | 145.92 | 6.08 | 8.5 | 8.5 | 3B+1S | 0 | 1093 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35002272 | 1356 | 223.0263 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 26779965 | 6226 | 149.424 | 6.226 | 7.9 | 7.9 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35003652 | 1380 | 221.6511 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 26786119 | 6154 | 147.696 | 6.154 | 7.4 | 7.4 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35005024 | 1372 | 222.9444 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 26792161 | 6042 | 145.008 | 6.042 | 7 | 7 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35006372 | 1348 | 223.1049 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 26798096 | 5935 | 142.44 | 5.935 | 6.5 | 6.5 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35007724 | 1352 | 227.8012 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 26803993 | 5897 | 141.528 | 5.897 | 6.3 | 6.3 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35009068 | 1344 | 227.9125 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 139 | 26809852 | 5859 | 140.616 | 5.859 | 5.8 | 5.8 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35010404 | 1336 | 228.0253 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 26815730 | 5878 | 141.072 | 5.878 | 5.3 | 5.3 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35011762 | 1358 | 231.031 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 144 | 26821680 | 5950 | 142.8 | 5.95 | 4.5 | 4.5 | 3B+1S | 0 | 1177 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35013138 | 1376 | 231.2605 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 142 | 26827614 | 5934 | 142.416 | 5.934 | 4 | 4 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35014492 | 1354 | 228.1766 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 141 | 26833503 | 5889 | 141.336 | 5.889 | 3.6 | 3.6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35015824 | 1332 | 226.1844 | 0% | 100% | 100% | 100% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 135 | 26839062 | 5559 | 133.416 | 5.559 | 2.6 | 2.6 | 2B+1S | 0 | 1189 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35016952 | 1128 | 202.9142 | 0% | 100% | 100% | 0% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 129 | 26844450 | 5388 | 129.312 | 5.388 | 1.8 | 1.8 | 2B+1S | 0 | 1128 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35018028 | 1076 | 199.703 | 0% | 100% | 100% | 0% | 100% | 0% | 7802023 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 118 | 26849588 | 5138 | 123.312 | 5.138 | 1.6 | 1.6 | 2B+1S | 0 | 987 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 35019020 | 992 | 193.0712 | 0% | 100% | 100% | 0% | 100% | 0% | 7802023 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 105 | 26854163 | 4575 | 109.8 | 4.575 | 2.2 | 2.2 | 2B | 0 | 0 | 1181 | 0 | 1199 | N/A | N/A | N/A | N/A | 35019848 | 828 | 180.9836 | 0% | 0% | 100% | 0% | 100% | 35% | 7802691 | 668 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 103 | 26858325 | 4162 | 99.888 | 4.162 | 3.1 | 3.1 | 2B | 0 | 0 | 1084 | 0 | 1109 | N/A | N/A | N/A | N/A | 35020576 | 728 | 174.9159 | 0% | 0% | 100% | 0% | 100% | 35% | 7803610 | 919 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.3333 | 126873 | 126873 | 126.873 | 126.873 | [12 empty] | 26160 | 26160 | 206.1904 | [6 empty] | 6290 | 6290 | 0.975 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (55%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20 AM, NORMAL OPERATION
XCV1 CLOSED @ 5:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20AM, NORMAL OPERATION
SP2 - STARTED @ 6:45 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 26, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:35 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:11 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26256 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26858325 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35020576 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7803610 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 100 | 26862531 | 4206 | 100.944 | 4.206 | 4.5 | 4.5 | 2B | 0 | 0 | 1102 | 0 | 1109 | N/A | N/A | N/A | N/A | 35021320 | 744 | 176.8902 | 0% | 0% | 100% | 0% | 100% | 55% | 7804861 | 1251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 93 | 26866551 | 4020 | 96.48 | 4.02 | 5.9 | 5.9 | 2B | 0 | 0 | 1152 | 0 | 1109 | N/A | N/A | N/A | N/A | 35022008 | 688 | 171.1443 | 0% | 0% | 100% | 0% | 100% | 55% | 7806259 | 1398 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 26870321 | 3770 | 90.48 | 3.77 | 7.4 | 7.4 | 2B | 0 | 0 | 1016 | 0 | 1110 | N/A | N/A | N/A | N/A | 35022644 | 636 | 168.7003 | 0% | 0% | 100% | 0% | 100% | 55% | 7807635 | 1376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 91 | 26874102 | 3781 | 90.744 | 3.781 | 8.6 | 8.6 | 2B | 0 | 0 | 1007 | 0 | 1110 | N/A | N/A | N/A | N/A | 35023276 | 632 | 167.1515 | 0% | 0% | 100% | 0% | 100% | 55% | 7808756 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 100 | 26878201 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 2B | 0 | 0 | 1011 | 0 | 1110 | N/A | N/A | N/A | N/A | 35023944 | 668 | 162.9666 | 0% | 0% | 100% | 0% | 100% | 55% | 7809555 | 799 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 116 | 26882924 | 4723 | 113.352 | 4.723 | 9.5 | 9.5 | 2B | 0 | 0 | 1167 | 0 | 1140 | N/A | N/A | N/A | N/A | 35024648 | 704 | 149.0578 | 0% | 0% | 100% | 0% | 100% | 0% | 7809555 | 0 | 0.98 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 26888912 | 5988 | 143.712 | 5.988 | 9.2 | 9.2 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35025992 | 1344 | 224.4489 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 26895022 | 6110 | 146.64 | 6.11 | 8.6 | 8.6 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35027336 | 1344 | 219.9673 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 26901212 | 6190 | 148.56 | 6.19 | 7.9 | 7.9 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35028732 | 1396 | 225.525 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 26907444 | 6232 | 149.568 | 6.232 | 7 | 7 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35030132 | 1400 | 224.647 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 | 1 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 26913599 | 6155 | 147.72 | 6.155 | 6.5 | 6.5 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35031516 | 1384 | 224.8578 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 26919553 | 5954 | 142.896 | 5.954 | 6.2 | 6.2 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35032840 | 1324 | 222.3715 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 26925373 | 5820 | 139.68 | 5.82 | 5.9 | 5.9 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35034168 | 1328 | 228.1787 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 26931158 | 5785 | 138.84 | 5.785 | 5.4 | 5.4 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35035506 | 1338 | 231.2878 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 131 | 26936902 | 5744 | 137.856 | 5.744 | 5.1 | 5.1 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35036838 | 1332 | 231.8942 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 26942583 | 5681 | 136.344 | 5.681 | 4.9 | 4.9 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35038174 | 1336 | 235.1699 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 140 | 26948183 | 5600 | 134.4 | 5.6 | 4.5 | 4.5 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35039478 | 1304 | 232.8571 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 26953905 | 5722 | 137.328 | 5.722 | 4.3 | 4.3 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35040786 | 1308 | 228.5914 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 26959671 | 5766 | 138.384 | 5.766 | 3.9 | 3.9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35042108 | 1322 | 229.2751 | 0% | 100% | 100% | 100% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 133 | 26965192 | 5521 | 132.504 | 5.521 | 3 | 3 | 2B+1S | 0 | 1162 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35043220 | 1112 | 201.4128 | 0% | 100% | 100% | 0% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 129 | 26970685 | 5493 | 131.832 | 5.493 | 2.2 | 2.2 | 2B+1S | 0 | 1115 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35044318 | 1098 | 199.8908 | 0% | 100% | 100% | 0% | 100% | 0% | 7809555 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 128 | 26975854 | 5169 | 124.056 | 5.169 | 1.6 | 1.6 | 2B+1S | 0 | 1050 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35045364 | 1046 | 202.3602 | 0% | 100% | 100% | 0% | 100% | 0% | 7809555 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 102 | 26980294 | 4440 | 106.56 | 4.44 | 2.1 | 2.1 | 2B | 0 | 0 | 1118 | 0 | 1109 | N/A | N/A | N/A | N/A | 35046156 | 792 | 178.3784 | 0% | 0% | 100% | 0% | 100% | 30% | 7810153 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 91 | 26984345 | 4051 | 97.224 | 4.051 | 2.9 | 2.9 | 2B | 0 | 0 | 1002 | 0 | 1109 | N/A | N/A | N/A | N/A | 35046832 | 676 | 166.8724 | 0% | 0% | 100% | 0% | 100% | 30% | 7811009 | 856 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5833 | 126020 | 126020 | 126.02 | 126.02 | [12 empty] | 26256 | 26256 | 208.3479 | [6 empty] | 7399 | 7399 | 0.99167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:14 AM, NORMAL OPERATION
XCV1 CLOSED @ 4:56 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:00 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 18, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:30 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:55 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12 PM, NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## FEB 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25852 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26984345 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35046832 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7811009 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 91 | 26988293 | 3948 | 94.752 | 3.948 | 4.7 | 4.7 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 35047524 | 692 | 175.2786 | 0% | 0% | 100% | 0% | 100% | 48% | 7812570 | 1561 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 89 | 26991920 | 3627 | 87.048 | 3.627 | 6.3 | 6.3 | 2B | 0 | 0 | 983 | 0 | 1110 | N/A | N/A | N/A | N/A | 35048140 | 616 | 169.8373 | 0% | 0% | 100% | 0% | 100% | 48% | 7814155 | 1585 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 85 | 26995473 | 3553 | 85.272 | 3.553 | 7.8 | 7.8 | 2B | 0 | 0 | 966 | 0 | 1110 | N/A | N/A | N/A | N/A | 35048740 | 600 | 168.8714 | 0% | 0% | 100% | 0% | 100% | 48% | 7815575 | 1420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 104 | 84 | 26998998 | 3525 | 84.6 | 3.525 | 9.2 | 9.2 | 2B | 0 | 0 | 976 | 0 | 1109 | N/A | N/A | N/A | N/A | 35049332 | 592 | 167.9433 | 0% | 0% | 100% | 0% | 100% | 48% | 7816840 | 1265 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 102 | 27002760 | 3762 | 90.288 | 3.762 | 9.5 | 9.5 | 2B | 0 | 0 | 922 | 0 | 1110 | N/A | N/A | N/A | N/A | 35049896 | 564 | 149.9203 | 0% | 0% | 100% | 0% | 100% | 48% | 7817131 | 291 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 115 | 27007494 | 4734 | 113.616 | 4.734 | 9.5 | 9.5 | 2B | 0 | 0 | 1131 | 0 | 1109 | N/A | N/A | N/A | N/A | 35050604 | 708 | 149.5564 | 0% | 0% | 100% | 0% | 100% | 0% | 7817131 | 0 | 0.9 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 154 | 27013555 | 6061 | 145.464 | 6.061 | 9.2 | 9.2 | 3B+1S | 0 | 1058 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35051924 | 1320 | 217.7858 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 27019726 | 6171 | 148.104 | 6.171 | 8.6 | 8.6 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35053292 | 1368 | 221.6821 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 150 | 27025932 | 6206 | 148.944 | 6.206 | 8.1 | 8.1 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35054658 | 1366 | 220.1096 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 27032145 | 6213 | 149.112 | 6.213 | 7.5 | 7.5 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35056052 | 1394 | 224.3683 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 27038100 | 5955 | 142.92 | 5.955 | 7.1 | 7.1 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35057341 | 1289 | 216.4568 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 143 | 27044084 | 5984 | 143.616 | 5.984 | 6.8 | 6.8 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35058720 | 1379 | 230.4479 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 27049968 | 5884 | 141.216 | 5.884 | 6.5 | 6.5 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35060052 | 1332 | 226.3766 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 27055670 | 5702 | 136.848 | 5.702 | 6.3 | 6.3 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35061360 | 1308 | 229.3932 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 27061293 | 5623 | 134.952 | 5.623 | 6 | 6 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35062644 | 1284 | 228.3479 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 27067011 | 5718 | 137.232 | 5.718 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35063988 | 1344 | 235.0472 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 27072698 | 5687 | 136.488 | 5.687 | 5.2 | 5.2 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35065304 | 1316 | 231.405 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 27078437 | 5739 | 137.736 | 5.739 | 5.1 | 5.1 | 3B+1S | 0 | 980 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35066614 | 1310 | 228.2628 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 27084155 | 5718 | 137.232 | 5.718 | 5 | 5 | 3B+1S | 0 | 994 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35067916 | 1302 | 227.702 | 0% | 100% | 100% | 100% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 130 | 27089664 | 5509 | 132.216 | 5.509 | 4 | 4 | 2B+1S | 0 | 1129 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35069030 | 1114 | 202.2146 | 0% | 100% | 100% | 0% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 131 | 27095080 | 5416 | 129.984 | 5.416 | 3.1 | 3.1 | 2B+1S | 0 | 1147 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 35070132 | 1102 | 203.4712 | 0% | 100% | 100% | 0% | 100% | 0% | 7817131 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 126 | 27100331 | 5251 | 126.024 | 5.251 | 2.5 | 2.5 | 2B+1S | 0 | 1012 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 35071176 | 1044 | 198.8193 | 0% | 100% | 100% | 0% | 100% | 0% | 7817131 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 103 | 27104741 | 4410 | 105.84 | 4.41 | 2.9 | 2.9 | 2B | 0 | 0 | 1150 | 0 | 1109 | N/A | N/A | N/A | N/A | 35071972 | 796 | 180.4989 | 0% | 0% | 100% | 0% | 100% | 30% | 7817597 | 466 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 100 | 27108882 | 4141 | 99.384 | 4.141 | 3.5 | 3.5 | 2B | 0 | 0 | 1060 | 0 | 1110 | N/A | N/A | N/A | N/A | 35072684 | 712 | 171.9391 | 0% | 0% | 100% | 0% | 100% | 30% | 7818250 | 653 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0833 | 124537 | 124537 | 124.537 | 124.537 | [12 empty] | 25852 | 25852 | 207.5849 | [6 empty] | 7241 | 7241 | 0.99667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (48%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:14 AM, NORMAL OPERATION
XCV1 CLOSED @ 4:3 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:05 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:15AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:26 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (FEB 28, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 78 psi @ 5:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 PM, NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:40 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:14 PM, NORMAL OPERATION
NORMAL OPERATION

## FEB 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | DENNIS GUANZON
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-02-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25888 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27108882 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35072684 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7818250 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 96 | 27112921 | 4039 | 96.936 | 4.039 | 4.6 | 4.6 | 2B | 0 | 0 | 1073 | 0 | 1110 | N/A | N/A | N/A | N/A | 35073388 | 704 | 174.3006 | 0% | 0% | 100% | 0% | 100% | 45% | 7819195 | 945 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 27116641 | 3720 | 89.28 | 3.72 | 5.9 | 5.9 | 2B | 0 | 0 | 1000 | 0 | 1110 | N/A | N/A | N/A | N/A | 35074024 | 636 | 170.9677 | 0% | 0% | 100% | 0% | 100% | 45% | 7820480 | 1285 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 85 | 27120318 | 3677 | 88.248 | 3.677 | 6.8 | 6.8 | 2B | 0 | 0 | 978 | 0 | 1110 | N/A | N/A | N/A | N/A | 35074652 | 628 | 170.7914 | 0% | 0% | 100% | 0% | 100% | 45% | 7822100 | 1620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 129 | 90 | 27123920 | 3602 | 86.448 | 3.602 | 9.1 | 9.1 | 2B | 0 | 0 | 959 | 0 | 1110 | N/A | N/A | N/A | N/A | 35075244 | 592 | 164.3531 | 0% | 0% | 100% | 0% | 100% | 45% | 7823652 | 1552 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 94 | 27127765 | 3845 | 92.28 | 3.845 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 35075816 | 572 | 148.7646 | 0% | 0% | 100% | 0% | 100% | 45% | 7823769 | 117 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 112 | 109 | 27131983 | 4218 | 101.232 | 4.218 | 9.5 | 9.5 | 2B | 0 | 0 | 1025 | 0 | 1048 | N/A | N/A | N/A | N/A | 35076396 | 580 | 137.5059 | 0% | 0% | 100% | 0% | 100% | 0% | 7823769 | 0 | 1.19 | Normal operation schedule | Error - General | E | F.A.RAMOS / A.CABREROS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 137 | 27137817 | 5834 | 140.016 | 5.834 | 9.4 | 9.4 | 3B+1S | 0 | 1088 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35077612 | 1216 | 208.4333 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 27143977 | 6160 | 147.84 | 6.16 | 8.9 | 8.9 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35078941 | 1329 | 215.7468 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 152 | 27150170 | 6193 | 148.632 | 6.193 | 8.4 | 8.4 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35080343 | 1402 | 226.3846 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 152 | 27156409 | 6239 | 149.736 | 6.239 | 7.8 | 7.8 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35081721 | 1378 | 220.8687 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 149 | 27162540 | 6131 | 147.144 | 6.131 | 7.4 | 7.4 | 3B+1S | 0 | 1166 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35083076 | 1355 | 221.008 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 152 | 27168680 | 6140 | 147.36 | 6.14 | 6.9 | 6.9 | 3B+1S | 0 | 1184 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35084444 | 1368 | 222.8013 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 146 | 27174666 | 5986 | 143.664 | 5.986 | 6.4 | 6.4 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35085814 | 1370 | 228.8674 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 143 | 27180535 | 5869 | 140.856 | 5.869 | 5.8 | 5.8 | 3B+1S | 0 | 1151 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35087144 | 1330 | 226.6144 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 141 | 27186430 | 5895 | 141.48 | 5.895 | 5.3 | 5.3 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35088492 | 1348 | 228.6684 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 27192157 | 5727 | 137.448 | 5.727 | 4.4 | 4.4 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35089796 | 1304 | 227.6934 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 27198004 | 5847 | 140.328 | 5.847 | 4.1 | 4.1 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35091144 | 1348 | 230.5456 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 141 | 27203799 | 5795 | 139.08 | 5.795 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35092468 | 1324 | 228.4728 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 122 | 135 | 27209543 | 5744 | 137.856 | 5.744 | 3.2 | 3.2 | 3B+1S | 0 | 1141 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35093788 | 1320 | 229.805 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 130 | 27215096 | 5553 | 133.272 | 5.553 | 2.8 | 2.8 | 3B+1S | 0 | 1029 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35095036 | 1248 | 224.7434 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 110 | 27220263 | 5167 | 124.008 | 5.167 | 2.6 | 2.6 | 3B+1S | 0 | 1128 | 1155 | 1185 | 1150 | N/A | N/A | N/A | N/A | 35096056 | 1020 | 197.4066 | 0% | 100% | 100% | 100% | 100% | 0% | 7823769 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 110 | 27225431 | 5168 | 124.032 | 5.168 | 2.5 | 2.5 | 2B+1S | 0 | 1120 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 35097076 | 1020 | 197.3684 | 0% | 100% | 100% | 0% | 100% | 0% | 7823769 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 108 | 27229761 | 4330 | 103.92 | 4.33 | 3.2 | 3.2 | 2B | 0 | 0 | 1186 | 0 | 1110 | N/A | N/A | N/A | N/A | 35097836 | 760 | 175.5196 | 0% | 0% | 100% | 0% | 100% | 35% | 7824523 | 754 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 101 | 27233970 | 4209 | 101.016 | 4.209 | 4.1 | 4.1 | 2B | 0 | 0 | 1084 | 0 | 1110 | N/A | N/A | N/A | N/A | 35098572 | 736 | 174.8634 | 0% | 0% | 100% | 0% | 100% | 35% | 7825280 | 757 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.9583 | 125088 | 125088 | 125.088 | 125.088 | [12 empty] | 25888 | 25888 | 206.9583 | [6 empty] | 7030 | 7030 | 1.0367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:13 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:19 AM, NORMAL OPERATION
XCV1 CLOSED @ 4:29 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:10 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:42 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:26 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:09 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 11,447
GENSET 1 WARMUP EXERCISED @ 4:01 PM / STOPPED @ 4:11 PM
GENSET 2 WARMUP EXERCISED @ 4:11 PM / STOPPED @ 4:21 PM
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION