## MAR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25636 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27233970 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35098572 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7825280 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 95 | 27238212 | 4242 | 101.808 | 4.242 | 5.2 | 5.2 | 2B | 0 | 0 | 1069 | 0 | 1110 | N/A | N/A | N/A | N/A | 35099316 | 744 | 175.389 | 0% | 0% | 100% | 0% | 100% | 45% | 7826265 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 89 | 27242002 | 3790 | 90.96 | 3.79 | 6.2 | 6.2 | 2B | 0 | 0 | 1017 | 0 | 1109 | N/A | N/A | N/A | N/A | 35099964 | 648 | 170.9763 | 0% | 0% | 100% | 0% | 100% | 45% | 7827350 | 1085 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 81 | 27245591 | 3589 | 86.136 | 3.589 | 7.4 | 7.4 | 2B | 0 | 0 | 983 | 0 | 1110 | N/A | N/A | N/A | N/A | 35100576 | 612 | 170.521 | 0% | 0% | 100% | 0% | 100% | 45% | 7828481 | 1131 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 86 | 27249222 | 3631 | 87.144 | 3.631 | 8.6 | 8.6 | 2B | 0 | 0 | 962 | 0 | 1109 | N/A | N/A | N/A | N/A | 35101180 | 604 | 166.3454 | 0% | 0% | 100% | 0% | 100% | 45% | 7829615 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 93 | 92 | 27252918 | 3696 | 88.704 | 3.696 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 35101788 | 608 | 164.5022 | 0% | 0% | 100% | 0% | 100% | 45% | 7830382 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 108 | 106 | 27256985 | 4067 | 97.608 | 4.067 | 9.5 | 9.5 | 2B | 0 | 0 | 910 | 0 | 1161 | N/A | N/A | N/A | N/A | 35102348 | 560 | 137.6936 | 0% | 0% | 100% | 0% | 100% | 0% | 7830382 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 136 | 27262612 | 5627 | 135.048 | 5.627 | 9.5 | 9.5 | 3B+1S | 0 | 1018 | 1138 | 1185 | 1160 | N/A | N/A | N/A | N/A | 35103468 | 1120 | 199.0403 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 27268732 | 6120 | 146.88 | 6.12 | 9.5 | 9.5 | 3B+1S | 0 | 1020 | 1154 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35104743 | 1275 | 208.3333 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 27275037 | 6305 | 151.32 | 6.305 | 8.9 | 8.9 | 3B+1S | 0 | 1104 | 1154 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35106132 | 1389 | 220.3013 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 162 | 27280931 | 5894 | 141.456 | 5.894 | 7.2 | 7.2 | 3B+1S | 0 | 1153 | 1155 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35107440 | 1308 | 221.9206 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 152 | 27287340 | 6409 | 153.816 | 6.409 | 7 | 7 | 3B+1S | 0 | 1137 | 1155 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35108855 | 1415 | 220.7833 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 147 | 27293302 | 5962 | 143.088 | 5.962 | 6.2 | 6.2 | 3B+1S | 0 | 1156 | 1155 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35110180 | 1325 | 222.2409 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 146 | 27299687 | 6385 | 153.24 | 6.385 | 5.5 | 5.5 | 3B+1S | 0 | 1074 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35111624 | 1444 | 226.1551 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 143 | 27305472 | 5785 | 138.84 | 5.785 | 5.1 | 5.1 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35112928 | 1304 | 225.4105 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 139 | 27311359 | 5887 | 141.288 | 5.887 | 4.8 | 4.8 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35114260 | 1332 | 226.2613 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 27317093 | 5734 | 137.616 | 5.734 | 4.6 | 4.6 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35115572 | 1312 | 228.8106 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 27322867 | 5774 | 138.576 | 5.774 | 3.9 | 3.9 | 3B+1S | 0 | 1046 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35116908 | 1336 | 231.3821 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 27328546 | 5679 | 136.296 | 5.679 | 3.7 | 3.7 | 3B+1S | 0 | 993 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35118220 | 1312 | 231.0266 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 130 | 27334310 | 5764 | 138.336 | 5.764 | 3.4 | 3.4 | 3B+1S | 0 | 996 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35119548 | 1328 | 230.3956 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 129 | 27339794 | 5484 | 131.616 | 5.484 | 2.8 | 2.8 | 3B+1S | 0 | 1103 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35120644 | 1096 | 199.8541 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 124 | 27345149 | 5355 | 128.52 | 5.355 | 2.1 | 2.1 | 3B+1S | 0 | 1043 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35121700 | 1056 | 197.1989 | 0% | 100% | 100% | 100% | 100% | 0% | 7830382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 118 | 27350150 | 5001 | 120.024 | 5.001 | 1.8 | 1.8 | 2B+1S | 0 | 1006 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35122692 | 992 | 198.3603 | 0% | 100% | 100% | 0% | 100% | 0% | 7830382 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 104 | 27354569 | 4419 | 106.056 | 4.419 | 2.9 | 2.9 | 2B | 0 | 0 | 1159 | 0 | 1109 | N/A | N/A | N/A | N/A | 35123492 | 800 | 181.0364 | 0% | 0% | 100% | 0% | 100% | 45% | 7831467 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 98 | 27358692 | 4123 | 98.952 | 4.123 | 4.4 | 4.4 | 2B | 0 | 0 | 1063 | 0 | 1109 | N/A | N/A | N/A | N/A | 35124208 | 716 | 173.66 | 0% | 0% | 100% | 0% | 100% | 45% | 7832853 | 1386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4167 | 124722 | 124722 | 124.722 | 124.722 | [12 empty] | 25636 | 25636 | 205.5451 | [6 empty] | 7573 | 7573 | 1.0517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:16 AM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:15 AM, NORMAL OPERATION
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 AM, NORMAL OPERATION
SP2 - STARTED @ 7:02 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 2, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25500 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27358692 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35124208 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7832853 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 93 | 27362481 | 3789 | 90.936 | 3.789 | 5.9 | 5.9 | 2B | 0 | 0 | 1089 | 0 | 1087 | N/A | N/A | N/A | N/A | 35124924 | 716 | 188.9681 | 0% | 0% | 100% | 0% | 100% | 50% | 7834109 | 1256 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 91 | 27366233 | 3752 | 90.048 | 3.752 | 7.3 | 7.3 | 2B | 0 | 0 | 1060 | 0 | 1087 | N/A | N/A | N/A | N/A | 35125552 | 628 | 167.3774 | 0% | 0% | 100% | 0% | 100% | 50% | 7835457 | 1348 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 27369872 | 3639 | 87.336 | 3.639 | 8.7 | 8.7 | 2B | 0 | 0 | 1040 | 0 | 1087 | N/A | N/A | N/A | N/A | 35126091 | 539 | 148.1176 | 0% | 0% | 100% | 0% | 100% | 50% | 7836846 | 1389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 85 | 27373391 | 3519 | 84.456 | 3.519 | 9.5 | 9.5 | 2B | 0 | 0 | 934 | 0 | 958 | N/A | N/A | N/A | N/A | 35126572 | 481 | 136.6866 | 0% | 0% | 100% | 0% | 100% | 50% | 7837665 | 819 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 95 | 27377287 | 3896 | 93.504 | 3.896 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 957 | N/A | N/A | N/A | N/A | 35127076 | 504 | 129.3634 | 0% | 0% | 100% | 0% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 121 | 27381918 | 4631 | 111.144 | 4.631 | 9.5 | 9.5 | 2B | 0 | 0 | 1109 | 0 | 1110 | N/A | N/A | N/A | N/A | 35127748 | 672 | 145.109 | 0% | 0% | 100% | 0% | 100% | 0% | 7837665 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 147 | 27387932 | 6014 | 144.336 | 6.014 | 9.3 | 9.3 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35129036 | 1288 | 214.1669 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 27394107 | 6175 | 148.2 | 6.175 | 8.9 | 8.9 | 3B+1S | 0 | 1195 | 1199 | 1185 | 1057 | N/A | N/A | N/A | N/A | 35130396 | 1360 | 220.2429 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 27400384 | 6277 | 150.648 | 6.277 | 8.3 | 8.3 | 3B+1S | 0 | 1100 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35131780 | 1384 | 220.4875 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 27406743 | 6359 | 152.616 | 6.359 | 7.7 | 7.7 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35133132 | 1352 | 212.612 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 | 1.17 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 27412857 | 6114 | 146.736 | 6.114 | 7 | 7 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35134548 | 1416 | 231.5996 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 27418995 | 6138 | 147.312 | 6.138 | 6.5 | 6.5 | 3B+1S | 0 | 1065 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35135916 | 1368 | 222.8739 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 27424785 | 5790 | 138.96 | 5.79 | 6.2 | 6.2 | 3B+1S | 0 | 1003 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35137228 | 1312 | 226.5976 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 140 | 140 | 27430548 | 5763 | 138.312 | 5.763 | 6.2 | 6.2 | 3B+1S | 0 | 988 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35138524 | 1296 | 224.8829 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 27436212 | 5664 | 135.936 | 5.664 | 6.1 | 6.1 | 3B+1S | 0 | 988 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35139804 | 1280 | 225.9887 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 135 | 27441851 | 5639 | 135.336 | 5.639 | 6 | 6 | 3B+1S | 0 | 1021 | 1175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35141076 | 1272 | 225.5719 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 27447512 | 5661 | 135.864 | 5.661 | 5.6 | 5.6 | 3B+1S | 0 | 1063 | 175 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35142380 | 1304 | 230.348 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 27453343 | 5831 | 139.944 | 5.831 | 5.5 | 5.5 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35143720 | 1340 | 229.8062 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 132 | 27458954 | 5611 | 134.664 | 5.611 | 5.3 | 5.3 | 3B+1S | 0 | 974 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35145020 | 1300 | 231.6878 | 0% | 100% | 100% | 100% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 131 | 27464472 | 5518 | 132.432 | 5.518 | 4.5 | 4.5 | 2B+1S | 0 | 1111 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35146124 | 1104 | 200.0725 | 0% | 100% | 100% | 0% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 125 | 27469881 | 5409 | 129.816 | 5.409 | 3.6 | 3.6 | 2B+1S | 0 | 1087 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35147208 | 1084 | 200.4067 | 0% | 100% | 100% | 0% | 100% | 0% | 7837665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 124 | 27474990 | 5109 | 122.616 | 5.109 | 3.1 | 3.1 | 2B+1S | 0 | 985 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35148228 | 1020 | 199.6477 | 0% | 100% | 100% | 0% | 100% | 0% | 7837665 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 106 | 27479374 | 4384 | 105.216 | 4.384 | 3.7 | 3.7 | 2B | 0 | 0 | 1075 | 0 | 1110 | N/A | N/A | N/A | N/A | 35148988 | 760 | 173.3577 | 0% | 0% | 100% | 0% | 100% | 0% | 7838291 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 100 | 27483662 | 4288 | 102.912 | 4.288 | 4.7 | 4.7 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 35149708 | 720 | 167.9104 | 0% | 0% | 100% | 0% | 100% | 0% | 7839072 | 781 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0417 | 124970 | 124970 | 124.97 | 124.97 | [12 empty] | 25500 | 25500 | 204.049 | [6 empty] | 6219 | 6219 | 1.09 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:54 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:28 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:23 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 3, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:12 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY O. REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27483662 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35149708 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7839072 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 89 | 27487299 | 3637 | 87.288 | 3.637 | 5.8 | 5.8 | 2B | 0 | 0 | 1052 | 0 | 1059 | N/A | N/A | N/A | N/A | 35150332 | 624 | 171.57 | 0% | 0% | 100% | 0% | 100% | 40% | 7840100 | 1028 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 87 | 27490940 | 3641 | 87.384 | 3.641 | 7 | 7 | 2B | 0 | 0 | 1023 | 0 | 1059 | N/A | N/A | N/A | N/A | 35150932 | 600 | 164.7899 | 0% | 0% | 100% | 0% | 100% | 40% | 7841436 | 1336 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 27494582 | 3642 | 87.408 | 3.642 | 8.2 | 8.2 | 2B | 0 | 0 | 1017 | 0 | 1029 | N/A | N/A | N/A | N/A | 35151504 | 572 | 157.0566 | 0% | 0% | 100% | 0% | 100% | 40% | 7842642 | 1206 | . | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY O. REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 87 | 27498313 | 3731 | 89.544 | 3.731 | 9.5 | 9.5 | 2B | 0 | 0 | 994 | 0 | 1029 | N/A | N/A | N/A | N/A | 35152068 | 564 | 151.1659 | 0% | 0% | 100% | 0% | 100% | 40% | 7843713 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 101 | 27502245 | 3932 | 94.368 | 3.932 | 9.5 | 9.5 | 2B | 0 | 0 | 969 | 0 | 1009 | N/A | N/A | N/A | N/A | 35152612 | 544 | 138.352 | 0% | 0% | 100% | 0% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 118 | 27506918 | 4673 | 112.152 | 4.673 | 9.5 | 9.5 | 2B | 0 | 0 | 1140 | 0 | 1110 | N/A | N/A | N/A | N/A | 35153308 | 696 | 148.9407 | 0% | 0% | 100% | 0% | 100% | 0% | 7843713 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 146 | 27513057 | 6139 | 147.336 | 6.139 | 9.3 | 9.3 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35154644 | 1336 | 217.625 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 27519245 | 6188 | 148.512 | 6.188 | 8.8 | 8.8 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35156016 | 1372 | 221.7195 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 27525440 | 6195 | 148.68 | 6.195 | 8 | 8 | 3B+1S | 0 | 1095 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35157386 | 1370 | 221.1461 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 27531535 | 6095 | 146.28 | 6.095 | 7.5 | 7.5 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35158752 | 1366 | 224.1181 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 | 1.28 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 27537532 | 5997 | 143.928 | 5.997 | 6.9 | 6.9 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35160100 | 1348 | 224.7791 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 27543463 | 5931 | 142.344 | 5.931 | 6.5 | 6.5 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35161432 | 1332 | 224.5827 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 27549341 | 5878 | 141.072 | 5.878 | 6.2 | 6.2 | 3B+1S | 0 | 1013 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35162767 | 1335 | 227.1181 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 137 | 27555182 | 5841 | 140.184 | 5.841 | 6 | 6 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35164034 | 1267 | 216.9149 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 134 | 27560861 | 5679 | 136.296 | 5.679 | 6 | 6 | 3B+1S | 0 | 944 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35165396 | 1362 | 239.831 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 27566500 | 5639 | 135.336 | 5.639 | 5.9 | 5.9 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35166700 | 1304 | 231.2467 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 27572319 | 5819 | 139.656 | 5.819 | 5.6 | 5.6 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35168028 | 1328 | 228.2179 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 136 | 27578047 | 5728 | 137.472 | 5.728 | 5.4 | 5.4 | 3B+1S | 0 | 990 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35169348 | 1320 | 230.4469 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 135 | 27583790 | 5743 | 137.832 | 5.743 | 5.2 | 5.2 | 3B+1S | 0 | 977 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35170656 | 1308 | 227.7555 | 0% | 100% | 100% | 100% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 27589265 | 5475 | 131.4 | 5.475 | 4.4 | 4.4 | 2B+1S | 0 | 1130 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35171776 | 1120 | 204.5662 | 0% | 100% | 100% | 0% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 128 | 27594752 | 5487 | 131.688 | 5.487 | 3.4 | 3.4 | 2B+1S | 0 | 1064 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35172876 | 1100 | 200.4738 | 0% | 100% | 100% | 0% | 100% | 0% | 7843713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 119 | 27599734 | 4982 | 119.568 | 4.982 | 3 | 3 | 2B+1S | 0 | 1002 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35173876 | 1000 | 200.7226 | 0% | 100% | 100% | 0% | 100% | 0% | 7843713 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 104 | 27604128 | 4394 | 105.456 | 4.394 | 3.6 | 3.6 | 2B | 0 | 0 | 1118 | 0 | 1109 | N/A | N/A | N/A | N/A | 35174656 | 780 | 177.5148 | 0% | 0% | 100% | 0% | 100% | 35% | 7844463 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 94 | 27608188 | 4060 | 97.44 | 4.06 | 4.7 | 4.7 | 2B | 0 | 0 | 1068 | 0 | 1068 | N/A | N/A | N/A | N/A | 35175356 | 700 | 172.4138 | 0% | 0% | 100% | 0% | 100% | 35% | 7845313 | 850 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.375 | 124526 | 124526 | 124.526 | 124.526 | [12 empty] | 25648 | 25648 | 205.965 | [6 empty] | 6241 | 6241 | 1.0917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:52 AM, NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:23 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:09 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:11 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 4, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:28 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25976 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27608188 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35175356 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7845313 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 27612083 | 3895 | 93.48 | 3.895 | 5.9 | 5.9 | 2B | 0 | 0 | 1068 | 0 | 1068 | N/A | N/A | N/A | N/A | 35175986 | 630 | 161.7458 | 0% | 0% | 1000% | 0% | 100% | 45% | 7846325 | 1012 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 91 | 27615838 | 3755 | 90.12 | 3.755 | 7 | 7 | 2B | 0 | 0 | 1040 | 0 | 1068 | N/A | N/A | N/A | N/A | 35176599 | 613 | 163.249 | 0% | 0% | 1000% | 0% | 100% | 45% | 7847439 | 1114 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 90 | 27619490 | 3652 | 87.648 | 3.652 | 8.2 | 8.2 | 2B | 0 | 0 | 1020 | 0 | 1068 | N/A | N/A | N/A | N/A | 35177206 | 607 | 166.2103 | 0% | 0% | 1000% | 0% | 100% | 45% | 7848738 | 1299 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 89 | 27623051 | 3561 | 85.464 | 3.561 | 9.5 | 9.5 | 2B | 0 | 0 | 960 | 0 | 987 | N/A | N/A | N/A | N/A | 35177796 | 590 | 165.6838 | 0% | 0% | 1000% | 0% | 100% | 45% | 7849921 | 1183 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 98 | 27626965 | 3914 | 93.936 | 3.914 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 1009 | N/A | N/A | N/A | N/A | 35178336 | 540 | 137.9663 | 0% | 0% | 1000% | 0% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 119 | 27631695 | 4730 | 113.52 | 4.73 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1188 | N/A | N/A | N/A | N/A | 35179044 | 708 | 149.6829 | 0% | 0% | 100% | 0% | 100% | 0% | 7849921 | 0 | 1.6 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 146 | 27637864 | 6169 | 148.056 | 6.169 | 9.2 | 9.2 | 3B+1S | 0 | 1050 | 1180 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35180384 | 1340 | 217.2151 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 152 | 27644192 | 6328 | 151.872 | 6.328 | 8.7 | 8.7 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35181773 | 1389 | 219.5006 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 151 | 27650083 | 5891 | 141.384 | 5.891 | 8.1 | 8.1 | 3B+1S | 0 | 1102 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35183076 | 1303 | 221.1849 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 27656483 | 6400 | 153.6 | 6.4 | 7.5 | 7.5 | 3B+1S | 0 | 1108 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35184500 | 1424 | 222.5 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 27662571 | 6088 | 146.112 | 6.088 | 7 | 7 | 3B+1S | 0 | 1059 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35185840 | 1340 | 220.1051 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 27668720 | 6149 | 147.576 | 6.149 | 6.4 | 6.4 | 3B+1S | 0 | 1113 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35187228 | 1388 | 225.7278 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 143 | 27674665 | 5945 | 142.68 | 5.945 | 5.9 | 5.9 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35188572 | 1344 | 226.0723 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 140 | 141 | 27680685 | 6020 | 144.48 | 6.02 | 5.7 | 5.7 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35189924 | 1352 | 224.5847 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 139 | 27686329 | 5644 | 135.456 | 5.644 | 5.6 | 5.6 | 3B+1S | 0 | 994 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35191228 | 1304 | 231.0418 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 27692017 | 5688 | 136.512 | 5.688 | 5.5 | 5.5 | 3B+1S | 0 | 997 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35192540 | 1312 | 230.661 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 27697737 | 5720 | 137.28 | 5.72 | 5.2 | 5.2 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35193860 | 1320 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 27703427 | 5690 | 136.56 | 5.69 | 4.9 | 4.9 | 3B+1S | 0 | 988 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35195164 | 1304 | 229.174 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 27709176 | 5749 | 137.976 | 5.749 | 4.7 | 4.7 | 3B+1S | 0 | 999 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35196484 | 1320 | 229.6051 | 0% | 100% | 100% | 100% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 131 | 27714717 | 5541 | 132.984 | 5.541 | 3.7 | 3.7 | 2B+1S | 0 | 1152 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35197624 | 1140 | 205.739 | 0% | 100% | 100% | 0% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 132 | 27720262 | 5545 | 133.08 | 5.545 | 2.8 | 2.8 | 2B+1S | 0 | 1143 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35198732 | 1108 | 199.8197 | 0% | 100% | 100% | 0% | 100% | 0% | 7849921 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 125 | 27725475 | 5213 | 125.112 | 5.213 | 2.1 | 2.1 | 2B+1S | 0 | 1042 | 0 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35199722 | 990 | 189.9098 | 0% | 100% | 0% | 100% | 100% | 0% | 7849921 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 104 | 27730018 | 4543 | 109.032 | 4.543 | 2.7 | 2.7 | 2B | 0 | 0 | 0 | 1185 | 1064 | N/A | N/A | N/A | N/A | 35200600 | 878 | 193.2644 | 0% | 0% | 0% | 100% | 100% | 35% | 7850689 | 768 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 95 | 27734172 | 4154 | 99.696 | 4.154 | 3.7 | 3.7 | 2B | 0 | 0 | 1002 | 1185 | 0 | N/A | N/A | N/A | N/A | 35201332 | 732 | 176.2157 | 0% | 0% | 100% | 100% | 0% | 35% | 7851586 | 897 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.8333 | 125984 | 125984 | 125.984 | 125.984 | [12 empty] | 25976 | 25976 | 206.1849 | [6 empty] | 6273 | 6273 | 1.1383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:43 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:13 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:38 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:16 AM , NORMAL OPERATION
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:12 PM , NORMAL OPERATION
BP1 - STOPPED @ 9:01 PM FOR REGREASING OF COUPLING, PUMP/MOTOR
BP2 - STARTED @ 9:01AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
BP3 - STOPPED @ 11:01 PM FOR REGREASING OF COUPLING,PUMP & MOTOR
BP1 - STARTED @ 11:01 PM
NORMAL OPERATION

## MAR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26048 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27734172 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35201332 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7851586 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 96 | 27738102 | 3930 | 94.32 | 3.93 | 5.2 | 5.2 | 2B | 0 | 0 | 991 | 1185 | 0 | N/A | N/A | N/A | N/A | 35202000 | 668 | 169.9746 | 0% | 0% | 100% | 100% | 0% | 50% | 7852960 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 93 | 27741803 | 3701 | 88.824 | 3.701 | 7 | 7 | 2B | 0 | 0 | 970 | 0 | 1058 | N/A | N/A | N/A | N/A | 35202623 | 623 | 168.3329 | 0% | 0% | 100% | 0% | 100% | 50% | 7854439 | 1479 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 27745385 | 3582 | 85.968 | 3.582 | 8.8 | 8.8 | 2B | 0 | 0 | 950 | 0 | 1058 | N/A | N/A | N/A | N/A | 35203235 | 612 | 170.8543 | 0% | 0% | 100% | 0% | 100% | 50% | 7855951 | 1512 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 81 | 27748899 | 3514 | 84.336 | 3.514 | 9.5 | 9.5 | 2B | 0 | 0 | 996 | 0 | 1018 | N/A | N/A | N/A | N/A | 35203828 | 593 | 168.7536 | 0% | 0% | 100% | 0% | 100% | 50% | 7856977 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 103 | 27752722 | 3823 | 91.752 | 3.823 | 9.5 | 9.5 | 2B | 0 | 0 | 988 | 0 | 978 | N/A | N/A | N/A | N/A | 35204372 | 544 | 142.2966 | 0% | 0% | 100% | 0% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 116 | 27757416 | 4694 | 112.656 | 4.694 | 9.5 | 9.5 | 2B | 0 | 0 | 1103 | 0 | 1110 | N/A | N/A | N/A | N/A | 35205056 | 684 | 145.7179 | 0% | 0% | 100% | 0% | 100% | 0% | 7856977 | 0 | 0.94 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 27763525 | 6109 | 146.616 | 6.109 | 9.2 | 9.2 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35206416 | 1360 | 222.6224 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 152 | 27769757 | 6232 | 149.568 | 6.232 | 8.5 | 8.5 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35207788 | 1372 | 220.154 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 27775997 | 6240 | 149.76 | 6.24 | 7.7 | 7.7 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35209200 | 1412 | 226.2821 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 153 | 27782347 | 6350 | 152.4 | 6.35 | 6.9 | 6.9 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35210546 | 1346 | 211.9685 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 | 1.06 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 148 | 27788542 | 6195 | 148.68 | 6.195 | 6.3 | 6.3 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35211972 | 1426 | 230.1856 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 27794664 | 6122 | 146.928 | 6.122 | 5.4 | 5.4 | 3B+1S | 0 | 1157 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35213392 | 1420 | 231.9503 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 27800596 | 5932 | 142.368 | 5.932 | 5 | 5 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35214748 | 1356 | 228.5907 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 27806335 | 5739 | 137.736 | 5.739 | 4.7 | 4.7 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35216062 | 1314 | 228.9597 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 27812074 | 5739 | 137.736 | 5.739 | 4.5 | 4.5 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35217376 | 1314 | 228.9597 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 27817816 | 5742 | 137.808 | 5.742 | 4.4 | 4.4 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35218706 | 1330 | 231.6266 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 27823559 | 5743 | 137.832 | 5.743 | 3.9 | 3.9 | 3B+1S | 0 | 1065 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35220036 | 1330 | 231.5863 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 131 | 27829395 | 5836 | 140.064 | 5.836 | 3.8 | 3.8 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35221368 | 1332 | 228.2385 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 27834978 | 5583 | 133.992 | 5.583 | 3.7 | 3.7 | 3B+1S | 0 | 990 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35222672 | 1304 | 233.5662 | 0% | 100% | 100% | 100% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 129 | 27840445 | 5467 | 131.208 | 5.467 | 3 | 3 | 2B+1S | 0 | 1133 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35223772 | 1100 | 201.2072 | 0% | 100% | 100% | 0% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 27845915 | 5470 | 131.28 | 5.47 | 2.1 | 2.1 | 2B+1S | 0 | 1077 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35224876 | 1104 | 201.8282 | 0% | 100% | 100% | 0% | 100% | 0% | 7856977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 119 | 27850934 | 5019 | 120.456 | 5.019 | 1.8 | 1.8 | 2B+1S | 0 | 1016 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35225880 | 1004 | 200.0398 | 0% | 100% | 100% | 0% | 100% | 0% | 7856977 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 102 | 27855427 | 4493 | 107.832 | 4.493 | 2.6 | 2.6 | 2B | 0 | 0 | 1136 | 0 | 1109 | N/A | N/A | N/A | N/A | 35226684 | 804 | 178.945 | 0% | 0% | 100% | 0% | 100% | 40% | 7857909 | 932 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 95 | 27859404 | 3977 | 95.448 | 3.977 | 3.8 | 3.8 | 2B | 0 | 0 | 1057 | 0 | 1109 | N/A | N/A | N/A | N/A | 35227380 | 696 | 175.0063 | 0% | 0% | 100% | 0% | 100% | 40% | 7859017 | 1108 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.3333 | 125232 | 125232 | 125.232 | 125.232 | [12 empty] | 26048 | 26048 | 207.998 | [6 empty] | 7431 | 7431 | 0.98333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
BP2-STOPPED @ 1:01 AM
BP3 - RESTARTED @ 1:01 AM
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:10 AM, NORMAL OPERATION
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:40 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:45 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 6, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:37 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 21604 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27859404 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35227380 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7859017 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 93 | 27863192 | 3788 | 90.912 | 3.788 | 5.1 | 5.1 | 2B | 0 | 0 | 1068 | 0 | 1109 | N/A | N/A | N/A | N/A | 35228034 | 654 | 172.6505 | 0% | 0% | 100% | 0% | 100% | 50% | 7860230 | 1213 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 91 | 27866834 | 3642 | 87.408 | 3.642 | 6.6 | 6.6 | 2B | 0 | 0 | 1044 | 0 | 1109 | N/A | N/A | N/A | N/A | 35228655 | 621 | 170.5107 | 0% | 0% | 100% | 0% | 100% | 50% | 7861569 | 1339 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 89 | 27870398 | 3564 | 85.536 | 3.564 | 8.5 | 8.5 | 2B | 0 | 0 | 1015 | 0 | 1109 | N/A | N/A | N/A | N/A | 35229257 | 602 | 168.9113 | 0% | 0% | 100% | 0% | 100% | 50% | 7863106 | 1537 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 87 | 27873970 | 3572 | 85.728 | 3.572 | 9.5 | 9.5 | 2B | 0 | 0 | 958 | 0 | 989 | N/A | N/A | N/A | N/A | 35229828 | 571 | 159.8544 | 0% | 0% | 100% | 0% | 100% | 50% | 7864194 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 100 | 27877839 | 3869 | 92.856 | 3.869 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 1008 | N/A | N/A | N/A | N/A | 35230380 | 552 | 142.6725 | 0% | 0% | 100% | 0% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 121 | 116 | 27882586 | 4747 | 113.928 | 4.747 | 9.5 | 9.5 | 2B | 0 | 0 | 1149 | 0 | 1008 | N/A | N/A | N/A | N/A | 35231104 | 724 | 152.5174 | 0% | 0% | 100% | 0% | 100% | 0% | 7864194 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 27888537 | 5951 | 142.824 | 5.951 | 9.3 | 9.3 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35232384 | 1280 | 215.0899 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 27894827 | 6290 | 150.96 | 6.29 | 8.6 | 8.6 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35233788 | 1404 | 223.2114 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 152 | 27901088 | 6261 | 150.264 | 6.261 | 7.9 | 7.9 | 3B+1S | 0 | 1110 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35235176 | 1388 | 221.6898 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 27907273 | 6185 | 148.44 | 6.185 | 7.1 | 7.1 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35236574 | 1398 | 226.0307 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 27913459 | 6186 | 148.464 | 6.186 | 6.4 | 6.4 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35237972 | 1398 | 225.9942 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 134 | 27919112 | 5653 | 135.672 | 5.653 | 6 | 6 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35239060 | 1088 | 192.4642 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 136 | 27924765 | 5653 | 135.672 | 5.653 | 5.2 | 5.2 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35239060 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 132 | 27929562 | 4797 | 115.128 | 4.797 | 5 | 5 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35239060 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 132 | 27934988 | 5426 | 130.224 | 5.426 | 5 | 5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35239060 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 136 | 27940396 | 5408 | 129.792 | 5.408 | 4.9 | 4.9 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35240252 | 1192 | 220.4142 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 137 | 27946385 | 5989 | 143.736 | 5.989 | 4.5 | 4.5 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35241652 | 1400 | 233.7619 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 27951775 | 5390 | 129.36 | 5.39 | 4.3 | 4.3 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35242900 | 1248 | 231.5399 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 135 | 27957357 | 5582 | 133.968 | 5.582 | 3.9 | 3.9 | 3B+1S | 0 | 993 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35244208 | 1308 | 234.3246 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 27962722 | 5365 | 128.76 | 5.365 | 3.8 | 3.8 | 3B+1S | 0 | 997 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 35245428 | 1220 | 227.3998 | 0% | 100% | 100% | 100% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 125 | 27967994 | 5272 | 126.528 | 5.272 | 3.2 | 3.2 | 2B+1S | 0 | 1046 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35246492 | 1064 | 201.8209 | 0% | 100% | 100% | 0% | 100% | 0% | 7864194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 120 | 27973074 | 5080 | 121.92 | 5.08 | 2.8 | 2.8 | 2B+1S | 0 | 1004 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35247508 | 1016 | 200 | 0% | 100% | 100% | 0% | 100% | 0% | 7864194 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 104 | 27977357 | 4283 | 102.792 | 4.283 | 3.4 | 3.4 | 2B | 0 | 0 | 1100 | 0 | 1109 | N/A | N/A | N/A | N/A | 35248268 | 760 | 177.4457 | 0% | 0% | 100% | 0% | 100% | 30% | 7864918 | 724 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 97 | 27981599 | 4242 | 101.808 | 4.242 | 4.4 | 4.4 | 2B | 0 | 0 | 1025 | 0 | 1109 | N/A | N/A | N/A | N/A | 35248984 | 716 | 168.7883 | 0% | 0% | 100% | 0% | 100% | 30% | 7865698 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.7917 | 122195 | 122195 | 122.195 | 122.195 | [12 empty] | 21604 | 21604 | 176.7994 | [6 empty] | 6681 | 6681 | 1.0533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:26 AM, NORMAL OPERATION
GENSET TESTING
MERALCO POWER STOP @ 11:50 AM
GENSET POWER ( G2 ) START @11:55 AM
RESTART NORMAL OPERATION @ 12:01 PM
GENSER 2 SWITCH TO GENSET 1 @ 1:25 PM
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
BP2 - STOP @ 11:50 AM / BP2 - RESTART NORMAL OPERATION @ 12:01 PM
BP1 - STOP @ 11:50 AM / BP1 - RESTART NORMAL OPERATION @ 12:01 PM
BP3 - STOP @ 11:50 AM / BP3 - RESTART NORMAL OPERATION @ 12:01 PM
SP2 - STARTED @ 6:44 AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STOP @ 11:50 AM / SP2 - RESTART NORMAL OPERATION @ 12:01 PM
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 7, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26280 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27981599 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35248984 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7865698 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 116 | 92 | 27985411 | 3812 | 91.488 | 3.812 | 5.3 | 5.3 | 2B | 0 | 0 | 1062 | 0 | 1068 | N/A | N/A | N/A | N/A | 35249634 | 650 | 170.5142 | 0% | 0% | 100% | 0% | 100% | 40% | 7866648 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 91 | 27989165 | 3754 | 90.096 | 3.754 | 6.3 | 6.3 | 2B | 0 | 0 | 1026 | 0 | 1068 | N/A | N/A | N/A | N/A | 35250236 | 602 | 160.3623 | 0% | 0% | 100% | 0% | 100% | 40% | 7867672 | 1024 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 90 | 27992850 | 3685 | 88.44 | 3.685 | 7.6 | 7.6 | 2B | 0 | 0 | 1002 | 0 | 1068 | N/A | N/A | N/A | N/A | 35250822 | 586 | 159.0231 | 0% | 0% | 100% | 0% | 100% | 40% | 7868890 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 89 | 27996402 | 3552 | 85.248 | 3.552 | 8.8 | 8.8 | 2B | 0 | 0 | 986 | 0 | 1068 | N/A | N/A | N/A | N/A | 35251396 | 574 | 161.5991 | 0% | 0% | 100% | 0% | 100% | 40% | 7870014 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 91 | 28000152 | 3750 | 90 | 3.75 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1008 | N/A | N/A | N/A | N/A | 35251976 | 580 | 154.6667 | 0% | 0% | 100% | 0% | 100% | 40% | 7870616 | 602 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 25 | 17.6056 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 113 | 109 | 28004433 | 4281 | 102.744 | 4.281 | 9.5 | 9.5 | 2B | 0 | 0 | 1011 | 0 | 1008 | N/A | N/A | N/A | N/A | 35252556 | 580 | 135.4824 | 0% | 0% | 100% | 0% | 100% | 0% | 7870616 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 146 | 28010493 | 6060 | 145.44 | 6.06 | 9.5 | 9.5 | 3B+1S | 0 | 992 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35253832 | 1276 | 210.5611 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 154 | 28016554 | 6061 | 145.464 | 6.061 | 9.2 | 9.2 | 3B+1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35255168 | 1336 | 220.4257 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 149 | 28022713 | 6159 | 147.816 | 6.159 | 8.4 | 8.4 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35256543 | 1375 | 223.2505 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 28029050 | 6337 | 152.088 | 6.337 | 7.5 | 7.5 | 3B+1S | 0 | 1189 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35257956 | 1413 | 222.9762 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 28035431 | 6381 | 153.144 | 6.381 | 6.7 | 6.7 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35259376 | 1420 | 222.5357 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 149 | 28041491 | 6060 | 145.44 | 6.06 | 5.8 | 5.8 | 3B+1S | 0 | 1199 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35260772 | 1396 | 230.363 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 146 | 28047696 | 6205 | 148.92 | 6.205 | 5.1 | 5.1 | 3B+1S | 0 | 1119 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35262184 | 1412 | 227.5584 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 145 | 28053718 | 6022 | 144.528 | 6.022 | 4.3 | 4.3 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35263580 | 1396 | 231.8167 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 142 | 28059650 | 5932 | 142.368 | 5.932 | 3.8 | 3.8 | 3B+1S | 0 | 1093 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35264932 | 1352 | 227.9164 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 28065438 | 5788 | 138.912 | 5.788 | 3.5 | 3.5 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35266256 | 1324 | 228.7491 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 140 | 28071246 | 5808 | 139.392 | 5.808 | 2.9 | 2.9 | 3B+1S | 0 | 1141 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35267604 | 1348 | 232.0937 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 28077007 | 5761 | 138.264 | 5.761 | 2.5 | 2.5 | 3B+1S | 0 | 1062 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35268934 | 1330 | 230.8627 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 137 | 28082708 | 5701 | 136.824 | 5.701 | 2.1 | 2.1 | 3B+1S | 0 | 1051 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35270248 | 1314 | 230.4859 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 28088247 | 5539 | 132.936 | 5.539 | 1.9 | 1.9 | 3B+1S | 0 | 998 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35271494 | 1246 | 224.9504 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 125 | 28093643 | 5396 | 129.504 | 5.396 | 1.7 | 1.7 | 3B+1S | 0 | 1009 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35272700 | 1206 | 223.4989 | 0% | 100% | 100% | 100% | 100% | 0% | 7870616 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 123 | 28098812 | 5169 | 124.056 | 5.169 | 1.4 | 1.4 | 2B+1S | 0 | 1018 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35273732 | 1032 | 199.6518 | 0% | 100% | 100% | 0% | 100% | 0% | 7870616 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 105 | 28103238 | 4426 | 106.224 | 4.426 | 2.2 | 2.2 | 2B | 0 | 0 | 1114 | 0 | 1149 | N/A | N/A | N/A | N/A | 35274532 | 800 | 180.7501 | 0% | 0% | 100% | 0% | 100% | 35% | 7871445 | 829 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 98 | 28107452 | 4214 | 101.136 | 4.214 | 3.1 | 3.1 | 2B | 0 | 0 | 1085 | 0 | 1109 | N/A | N/A | N/A | N/A | 35275264 | 732 | 173.7067 | 0% | 0% | 100% | 0% | 100% | 35% | 7872409 | 964 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126 | 125853 | 125853 | 125.853 | 125.853 | [12 empty] | 26280 | 26280 | 208.815 | [6 empty] | 6711 | 6711 | 1.0667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:52 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:14 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:20 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,904
GENSET 1 WARMUP EXERCISED @ 4:27 PM / STOPPED @ 4:37 PM
GENSET 2 WARMUP EXERCISED @ 4:17 PM / STOPPED @ 4:27 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
EMJAY FLORES & SARAH SIOTING OF EMD,CQESH CONDUCTED NOISE MONITORING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25588 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28107452 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35275264 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7872409 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 98 | 28111456 | 4004 | 96.096 | 4.004 | 4.6 | 4.6 | 2B | 0 | 0 | 1126 | 0 | 1110 | N/A | N/A | N/A | N/A | 35275972 | 708 | 176.8232 | 0% | 0% | 100% | 0% | 100% | 50% | 7873652 | 1243 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 28115354 | 3898 | 93.552 | 3.898 | 5.7 | 5.7 | 2B | 0 | 0 | 1100 | 0 | 1110 | N/A | N/A | N/A | N/A | 35276654 | 682 | 174.9615 | 0% | 0% | 100% | 0% | 100% | 50% | 7874881 | 1229 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 90 | 28119139 | 3785 | 90.84 | 3.785 | 6.9 | 6.9 | 2B | 0 | 0 | 1065 | 0 | 1110 | N/A | N/A | N/A | N/A | 35277298 | 644 | 170.1453 | 0% | 0% | 100% | 0% | 100% | 50% | 7876186 | 1305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 87 | 28122829 | 3690 | 88.56 | 3.69 | 8.4 | 8.4 | 2B | 0 | 0 | 1027 | 0 | 1037 | N/A | N/A | N/A | N/A | 35277900 | 602 | 163.1436 | 0% | 0% | 100% | 0% | 100% | 50% | 7877320 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 92 | 89 | 28126516 | 3687 | 88.488 | 3.687 | 9.5 | 9.5 | 2B | 0 | 0 | 892 | 0 | 907 | N/A | N/A | N/A | N/A | 35278460 | 560 | 151.885 | 0% | 0% | 100% | 0% | 100% | 50% | 7878326 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 28 | 19.7183 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 107 | 105 | 28130661 | 4145 | 99.48 | 4.145 | 9.5 | 9.5 | 2B | 0 | 0 | 1020 | 0 | 1108 | N/A | N/A | N/A | N/A | 35278956 | 496 | 119.6622 | 0% | 0% | 100% | 0% | 100% | 0% | 7878326 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 140 | 28136220 | 5559 | 133.416 | 5.559 | 9.5 | 9.5 | 3B+1S | 0 | 991 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35280128 | 1172 | 210.8293 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 28142050 | 5830 | 139.92 | 5.83 | 9 | 9 | 3B+1S | 0 | 1043 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35281370 | 1242 | 213.036 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 151 | 28148225 | 6175 | 148.2 | 6.175 | 8.4 | 8.4 | 3B+1S | 0 | 1038 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35282692 | 1322 | 214.0891 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 28154553 | 6328 | 151.872 | 6.328 | 7.9 | 7.9 | 3B+1S | 0 | 1088 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35284034 | 1342 | 212.0733 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 | 1.58 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 28160750 | 6197 | 148.728 | 6.197 | 7.3 | 7.3 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35285457 | 1423 | 229.6272 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 28166571 | 5821 | 139.704 | 5.821 | 6.8 | 6.8 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35286764 | 1307 | 224.5319 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 28172743 | 6172 | 148.128 | 6.172 | 6.2 | 6.2 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35288155 | 1391 | 225.3727 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 145 | 28178720 | 5977 | 143.448 | 5.977 | 5.6 | 5.6 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35289508 | 1353 | 226.3677 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 147 | 28184697 | 5977 | 143.448 | 5.977 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35290856 | 1348 | 225.5312 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 145 | 28190481 | 5784 | 138.816 | 5.784 | 4.9 | 4.9 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35292188 | 1332 | 230.2905 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 143 | 28196482 | 6001 | 144.024 | 6.001 | 4.4 | 4.4 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35293580 | 1392 | 231.9613 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 28202126 | 5644 | 135.456 | 5.644 | 3.8 | 3.8 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35294872 | 1292 | 228.9157 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 28207819 | 5693 | 136.632 | 5.693 | 3.5 | 3.5 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35296180 | 1308 | 229.7558 | 0% | 100% | 100% | 100% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 125 | 28213289 | 5470 | 131.28 | 5.47 | 2.7 | 2.7 | 2B+1S | 0 | 1105 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35297276 | 1096 | 200.3656 | 0% | 100% | 100% | 0% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 126 | 28218669 | 5380 | 129.12 | 5.38 | 2.1 | 2.1 | 2B+1S | 0 | 1041 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35298344 | 1068 | 198.513 | 0% | 100% | 100% | 0% | 100% | 0% | 7878326 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 124 | 28223714 | 5045 | 121.08 | 5.045 | 1.7 | 1.7 | 2B+1S | 0 | 1029 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35299348 | 1004 | 199.0089 | 0% | 100% | 100% | 0% | 100% | 0% | 7878326 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 102 | 28228045 | 4331 | 103.944 | 4.331 | 2.6 | 2.6 | 2B | 0 | 0 | 1139 | 0 | 1110 | N/A | N/A | N/A | N/A | 35300132 | 784 | 181.0205 | 0% | 0% | 100% | 0% | 100% | 40% | 7879338 | 1012 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 96 | 28232191 | 4146 | 99.504 | 4.146 | 3.9 | 3.9 | 2B | 0 | 0 | 1055 | 0 | 1109 | N/A | N/A | N/A | N/A | 35300852 | 720 | 173.6614 | 0% | 0% | 100% | 0% | 100% | 40% | 7880535 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.7083 | 124739 | 124739 | 124.739 | 124.739 | [12 empty] | 25588 | 25588 | 205.1323 | [6 empty] | 8126 | 8126 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM, NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:24 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25888 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28232191 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35300852 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7880535 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 94 | 28235966 | 3775 | 90.6 | 3.775 | 5.2 | 5.2 | 2B | 0 | 0 | 1073 | 0 | 1100 | N/A | N/A | N/A | N/A | 35301512 | 660 | 174.8344 | 0% | 0% | 100% | 0% | 100% | 50% | 7881735 | 1200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 93 | 28239651 | 3685 | 88.44 | 3.685 | 6.5 | 6.5 | 2B | 0 | 0 | 1042 | 0 | 1100 | N/A | N/A | N/A | N/A | 35302163 | 651 | 176.6621 | 0% | 0% | 100% | 0% | 100% | 50% | 7883059 | 1324 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 92 | 28243238 | 3587 | 86.088 | 3.587 | 8.3 | 8.3 | 2B | 0 | 0 | 1002 | 0 | 1100 | N/A | N/A | N/A | N/A | 35302775 | 612 | 170.6161 | 0% | 0% | 100% | 0% | 100% | 50% | 7884573 | 1514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 91 | 28246767 | 3529 | 84.696 | 3.529 | 9.5 | 9.5 | 2B | 0 | 0 | 985 | 0 | 987 | N/A | N/A | N/A | N/A | 35303292 | 517 | 146.5004 | 0% | 0% | 100% | 0% | 100% | 50% | 7885740 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 100 | 28250692 | 3925 | 94.2 | 3.925 | 9.5 | 9.5 | 2B | 0 | 0 | 1023 | 0 | 1022 | N/A | N/A | N/A | N/A | 35303868 | 576 | 146.7516 | 0% | 0% | 100% | 0% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 112 | 28255372 | 4680 | 112.32 | 4.68 | 9.5 | 9.5 | 2B | 0 | 0 | 1129 | 0 | 1109 | N/A | N/A | N/A | N/A | 35304572 | 704 | 150.4274 | 0% | 0% | 100% | 0% | 100% | 0% | 7885740 | 0 | 0.61 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 153 | 28261420 | 6048 | 145.152 | 6.048 | 9.3 | 9.3 | 3B+1S | 0 | 1037 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35305876 | 1304 | 215.6085 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 28267531 | 6111 | 146.664 | 6.111 | 8.9 | 8.9 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35307224 | 1348 | 220.5858 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 28273695 | 6164 | 147.936 | 6.164 | 8.3 | 8.3 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35308521 | 1297 | 210.4153 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 28279610 | 5915 | 141.96 | 5.915 | 7.7 | 7.7 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35309916 | 1395 | 235.8411 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 | 0.49 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 147 | 28285320 | 5710 | 137.04 | 5.71 | 7.1 | 7.1 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35311308 | 1392 | 243.7828 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 140 | 28291970 | 6650 | 159.6 | 6.65 | 6.4 | 6.4 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35312724 | 1416 | 212.9323 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 28297961 | 5991 | 143.784 | 5.991 | 5.9 | 5.9 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35314092 | 1368 | 228.3425 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 142 | 28303840 | 5879 | 141.096 | 5.879 | 5.6 | 5.6 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35315416 | 1324 | 225.2084 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 28309526 | 5686 | 136.464 | 5.686 | 5.5 | 5.5 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35316691 | 1275 | 224.235 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 28315199 | 5673 | 136.152 | 5.673 | 5.4 | 5.4 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35318000 | 1309 | 230.7421 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 28321047 | 5848 | 140.352 | 5.848 | 5.1 | 5.1 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35319344 | 1344 | 229.8222 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 143 | 28326830 | 5783 | 138.792 | 5.783 | 4.7 | 4.7 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35320660 | 1316 | 227.5635 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 140 | 28332710 | 5880 | 141.12 | 5.88 | 4.2 | 4.2 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35322020 | 1360 | 231.2925 | 0% | 100% | 100% | 100% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 135 | 28338431 | 5721 | 137.304 | 5.721 | 3.1 | 3.1 | 2B+1S | 0 | 1170 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35323184 | 1164 | 203.4609 | 0% | 100% | 100% | 0% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 133 | 28343742 | 5311 | 127.464 | 5.311 | 2.2 | 2.2 | 2B+1S | 0 | 1065 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35324252 | 1068 | 201.0921 | 0% | 100% | 100% | 0% | 100% | 0% | 7885740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 121 | 28348836 | 5094 | 122.256 | 5.094 | 1.9 | 1.9 | 2B+1S | 0 | 947 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35325260 | 1008 | 197.8799 | 0% | 100% | 100% | 0% | 100% | 0% | 7885740 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 114 | 28353219 | 4383 | 105.192 | 4.383 | 2.7 | 2.7 | 2B | 0 | 0 | 1107 | 0 | 1110 | N/A | N/A | N/A | N/A | 35326044 | 784 | 178.8729 | 0% | 0% | 100% | 0% | 100% | 0% | 7886538 | 798 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 90 | 28357259 | 4040 | 96.96 | 4.04 | 4 | 4 | 2B | 0 | 0 | 1017 | 0 | 1110 | N/A | N/A | N/A | N/A | 35326740 | 696 | 172.2772 | 0% | 0% | 100% | 0% | 100% | 0% | 7887725 | 1187 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.3333 | 125068 | 125068 | 125.068 | 125.068 | [12 empty] | 25888 | 25888 | 206.9914 | [6 empty] | 7190 | 7190 | 0.89333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 3:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:26 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:20 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 PM, NORMAL OPERATION
NORMAL OPERATION

## MAR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25560 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28357259 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35326740 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7887725 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 91 | 28361039 | 3780 | 90.72 | 3.78 | 5.4 | 5.4 | 2B | 0 | 0 | 1034 | 0 | 1100 | N/A | N/A | N/A | N/A | 35327396 | 656 | 173.545 | 0% | 0% | 100% | 0% | 100% | 45% | 7889071 | 1346 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 87 | 28364702 | 3663 | 87.912 | 3.663 | 6.8 | 6.8 | 2B | 0 | 0 | 1020 | 0 | 1048 | N/A | N/A | N/A | N/A | 35327996 | 600 | 163.8002 | 0% | 0% | 100% | 0% | 100% | 45% | 7890426 | 1355 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 88 | 28368366 | 3664 | 87.936 | 3.664 | 8 | 8 | 2B | 0 | 0 | 1012 | 0 | 1038 | N/A | N/A | N/A | N/A | 35328572 | 576 | 157.2052 | 0% | 0% | 100% | 0% | 100% | 45% | 7891595 | 1169 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 89 | 28372069 | 3703 | 88.872 | 3.703 | 9.2 | 9.2 | 2B | 0 | 0 | 1007 | 0 | 1018 | N/A | N/A | N/A | N/A | 35329140 | 568 | 153.3891 | 0% | 0% | 100% | 0% | 100% | 45% | 7892774 | 1179 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 88 | 28375889 | 3820 | 91.68 | 3.82 | 9.5 | 9.5 | 2B | 0 | 0 | 1003 | 0 | 1018 | N/A | N/A | N/A | N/A | 35329664 | 524 | 137.1728 | 0% | 0% | 100% | 0% | 100% | 45% | 7893009 | 235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 121 | 28380480 | 4591 | 110.184 | 4.591 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1079 | N/A | N/A | N/A | N/A | 35330384 | 720 | 156.8286 | 0% | 0% | 100% | 0% | 100% | 0% | 7893009 | 0 | 0.88 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 28386765 | 6285 | 150.84 | 6.285 | 9.5 | 9.5 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35331730 | 1346 | 214.1607 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 28392910 | 6145 | 147.48 | 6.145 | 8.9 | 8.9 | 3B+1S | 0 | 1066 | 11896 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35333034 | 1304 | 212.205 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 28398891 | 5981 | 143.544 | 5.981 | 8.4 | 8.4 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35334412 | 1378 | 230.3963 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 28404912 | 6021 | 144.504 | 6.021 | 7.9 | 7.9 | 3B+1S | 0 | 1076 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35335761 | 1349 | 224.0492 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 | 1.03 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 141 | 28411283 | 6371 | 152.904 | 6.371 | 7.4 | 7.4 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35337172 | 1411 | 221.4723 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 28417265 | 5982 | 143.568 | 5.982 | 7.1 | 7.1 | 3B+1S | 0 | 1019 | 1194 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35338504 | 1332 | 222.668 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 144 | 28423064 | 5799 | 139.176 | 5.799 | 6.8 | 6.8 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35339802 | 1298 | 223.8317 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 136 | 28428865 | 5801 | 139.224 | 5.801 | 6.5 | 6.5 | 3B+1S | 0 | 997 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35341144 | 1342 | 231.3394 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 28434573 | 5708 | 136.992 | 5.708 | 6.4 | 6.4 | 3B+1S | 0 | 994 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35342452 | 1308 | 229.1521 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 28440197 | 5624 | 134.976 | 5.624 | 6.3 | 6.3 | 3B+1S | 0 | 998 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35343729 | 1277 | 227.0626 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 28445966 | 5769 | 138.456 | 5.769 | 5.9 | 5.9 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35345048 | 1319 | 228.6358 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 137 | 28451723 | 5757 | 138.168 | 5.757 | 5.6 | 5.6 | 3B+1S | 0 | 1012 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35346356 | 1308 | 227.2017 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 28457472 | 5749 | 137.976 | 5.749 | 5.2 | 5.2 | 3B+1S | 0 | 1008 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35347656 | 1300 | 226.1263 | 0% | 100% | 100% | 100% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 130 | 28463099 | 5627 | 135.048 | 5.627 | 4.3 | 4.3 | 2B+1S | 0 | 1114 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35348788 | 1132 | 201.1729 | 0% | 100% | 100% | 0% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 28468532 | 5433 | 130.392 | 5.433 | 3.3 | 3.3 | 2B+1S | 0 | 1089 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35349868 | 1080 | 198.7852 | 0% | 100% | 100% | 0% | 100% | 0% | 7893009 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 121 | 28473573 | 5041 | 120.984 | 5.041 | 2.8 | 2.8 | 2B | 0 | 1006 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35350876 | 1008 | 199.9603 | 0% | 100% | 100% | 0% | 100% | 0% | 7893009 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 99 | 28478064 | 4491 | 107.784 | 4.491 | 3.3 | 3.3 | 2B | 0 | 0 | 1072 | 0 | 1110 | N/A | N/A | N/A | N/A | 35351664 | 788 | 175.462 | 0% | 0% | 100% | 0% | 100% | 25% | 7893459 | 450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 92 | 28482016 | 3952 | 94.848 | 3.952 | 3.9 | 3.9 | 2B | 0 | 0 | 1053 | 0 | 1048 | N/A | N/A | N/A | N/A | 35352300 | 636 | 160.9312 | 0% | 0% | 100% | 0% | 100% | 25% | 7894119 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.8333 | 124757 | 124757 | 124.757 | 124.757 | [12 empty] | 25560 | 25560 | 204.8783 | [6 empty] | 6394 | 6394 | 0.98667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:28 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:31 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:11 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:17 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24949 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28482016 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35352300 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7894119 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 | 90 | 28485861 | 3845 | 92.28 | 3.845 | 4.9 | 4.9 | 2B | 0 | 0 | 1037 | 0 | 1048 | N/A | N/A | N/A | N/A | 35352915 | 615 | 159.948 | 0% | 0% | 100% | 0% | 100% | 40% | 7895143 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 89 | 28489646 | 3785 | 90.84 | 3.785 | 6.1 | 6.1 | 2B | 0 | 0 | 1004 | 0 | 1048 | N/A | N/A | N/A | N/A | 35353495 | 580 | 153.2365 | 0% | 0% | 100% | 0% | 100% | 40% | 7896432 | 1289 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 87 | 28493300 | 3654 | 87.696 | 3.654 | 7.9 | 7.9 | 2B | 0 | 0 | 985 | 0 | 1048 | N/A | N/A | N/A | N/A | 35354069 | 574 | 157.0881 | 0% | 0% | 100% | 0% | 100% | 40% | 7897931 | 1499 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 85 | 28496804 | 3504 | 84.096 | 3.504 | 9.3 | 9.3 | 2B | 0 | 0 | 974 | 0 | 1008 | N/A | N/A | N/A | N/A | 35354632 | 563 | 160.6735 | 0% | 0% | 100% | 0% | 100% | 40% | 7899204 | 1273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 96 | 28500775 | 3971 | 95.304 | 3.971 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 988 | N/A | N/A | N/A | N/A | 35355192 | 560 | 141.0224 | 0% | 0% | 100% | 0% | 100% | 40% | 7899351 | 147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 122 | 28505459 | 4684 | 112.416 | 4.684 | 9.5 | 9.5 | 2B | 0 | 0 | 1129 | 0 | 1110 | N/A | N/A | N/A | N/A | 35355884 | 692 | 147.737 | 0% | 0% | 100% | 0% | 100% | 0% | 7899351 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 28511491 | 6032 | 144.768 | 6.032 | 9.4 | 9.4 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35357172 | 1288 | 213.5279 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 28517563 | 6072 | 145.728 | 6.072 | 8.9 | 8.9 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35358523 | 1351 | 222.4967 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 28523775 | 6212 | 149.088 | 6.212 | 8.3 | 8.3 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35359900 | 1377 | 221.6677 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 28529834 | 6059 | 145.416 | 6.059 | 7.8 | 7.8 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35361260 | 1360 | 224.4595 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 152 | 28535952 | 6118 | 146.832 | 6.118 | 7.5 | 7.5 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35362612 | 1352 | 220.9873 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 28541881 | 5929 | 142.296 | 5.929 | 7.4 | 7.4 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35363932 | 1320 | 222.6345 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 138 | 28547703 | 5822 | 139.728 | 5.822 | 7.1 | 7.1 | 3B+1S | 0 | 998 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35365244 | 1312 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 136 | 28553561 | 5858 | 140.592 | 5.858 | 6.9 | 6.9 | 3B+1S | 0 | 1012 | 1154 | 1185 | 1188 | N/A | N/A | N/A | N/A | 35366572 | 1328 | 226.6985 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 28559182 | 5621 | 134.904 | 5.621 | 6.8 | 6.8 | 3B+1S | 0 | 999 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35367836 | 1264 | 224.871 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 28564771 | 5589 | 134.136 | 5.589 | 6.7 | 6.7 | 3B+1S | 0 | 996 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35369100 | 1264 | 226.1585 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 28570155 | 5384 | 129.216 | 5.384 | 6.4 | 6.4 | 3B+1S | 0 | 1007 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35370332 | 1232 | 228.8262 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 134 | 28575674 | 5519 | 132.456 | 5.519 | 6.1 | 6.1 | 3B+1S | 0 | 1009 | 1154 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35371564 | 1232 | 223.2288 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 145 | 28581230 | 5556 | 133.344 | 5.556 | 6 | 6 | 3B+1S | 0 | 979 | 1156 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35372812 | 1248 | 224.622 | 0% | 100% | 100% | 100% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 123 | 28586653 | 5423 | 130.152 | 5.423 | 5.2 | 5.2 | 2B+1S | 0 | 1113 | 1176 | 0 | 1159 | N/A | N/A | N/A | N/A | 35373892 | 1080 | 199.1518 | 0% | 100% | 100% | 0% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 125 | 28591531 | 4878 | 117.072 | 4.878 | 4.6 | 4.6 | 2B+1S | 0 | 1007 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35374856 | 964 | 197.622 | 0% | 100% | 100% | 0% | 100% | 0% | 7899351 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 119 | 28596687 | 5156 | 123.744 | 5.156 | 4.4 | 4.4 | 2B | 0 | 974 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35375876 | 1020 | 197.8278 | 0% | 100% | 100% | 0% | 100% | 0% | 7899351 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 101 | 28600962 | 4275 | 102.6 | 4.275 | 4.8 | 4.8 | 2B | 0 | 0 | 1044 | 0 | 1110 | N/A | N/A | N/A | N/A | 35376596 | 720 | 168.4211 | 0% | 0% | 100% | 0% | 100% | 25% | 7899845 | 494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 93 | 28604937 | 3975 | 95.4 | 3.975 | 5.3 | 5.3 | 2B | 0 | 0 | 983 | 0 | 1110 | N/A | N/A | N/A | N/A | 35377249 | 653 | 164.2767 | 0% | 0% | 100% | 0% | 100% | 25% | 7900374 | 529 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.8333 | 122921 | 122921 | 122.921 | 122.921 | [12 empty] | 24949 | 24949 | 202.9678 | [6 empty] | 6255 | 6255 | 1.0417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:07 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:34 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:31 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:17 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:25PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25275 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28604937 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35377249 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7900374 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 93 | 28608762 | 3825 | 91.8 | 3.825 | 6.3 | 6.3 | 2B | 0 | 0 | 1036 | 0 | 1058 | N/A | N/A | N/A | N/A | 35377864 | 615 | 160.7843 | 0% | 0% | 100% | 0% | 100% | 35% | 7901287 | 913 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 92 | 28612487 | 3725 | 89.4 | 3.725 | 7.3 | 7.3 | 2B | 0 | 0 | 1021 | 0 | 1058 | N/A | N/A | N/A | N/A | 35378462 | 598 | 160.5369 | 0% | 0% | 100% | 0% | 100% | 35% | 7902232 | 945 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 91 | 28616101 | 3614 | 86.736 | 3.614 | 8.4 | 8.4 | 2B | 0 | 0 | 1004 | 0 | 1058 | N/A | N/A | N/A | N/A | 35379023 | 561 | 155.2297 | 0% | 0% | 100% | 0% | 100% | 35% | 7903252 | 1020 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 90 | 28619610 | 3509 | 84.216 | 3.509 | 9.4 | 9.4 | 2B | 0 | 0 | 986 | 0 | 987 | N/A | N/A | N/A | N/A | 35379532 | 509 | 145.0556 | 0% | 0% | 100% | 0% | 100% | 35% | 7904257 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 28623531 | 3921 | 94.104 | 3.921 | 9.5 | 9.5 | 2B | 0 | 0 | 993 | 0 | 987 | N/A | N/A | N/A | N/A | 35380060 | 528 | 134.6595 | 0% | 0% | 100% | 0% | 100% | 35% | 7904349 | 92 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 28628137 | 4606 | 110.544 | 4.606 | 9.5 | 9.5 | 2B | 0 | 0 | 1094 | 0 | 1109 | N/A | N/A | N/A | N/A | 35380716 | 656 | 142.4229 | 0% | 0% | 100% | 0% | 100% | 0% | 7904257 | -92 | 1.04 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 142 | 28634161 | 6024 | 144.576 | 6.024 | 9 | 9 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35382024 | 1308 | 217.1315 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 28640260 | 6099 | 146.376 | 6.099 | 8.5 | 8.5 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35383364 | 1340 | 219.7081 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 144 | 28646434 | 6174 | 148.176 | 6.174 | 7.9 | 7.9 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35384740 | 1376 | 222.8701 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 28652643 | 6209 | 149.016 | 6.209 | 7.1 | 7.1 | 3B+1S | 0 | 1105 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35386142 | 1402 | 225.8013 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 145 | 28658827 | 6184 | 148.416 | 6.184 | 6.4 | 6.4 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35387518 | 1376 | 222.5097 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 140 | 28664835 | 6008 | 144.192 | 6.008 | 6.1 | 6.1 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35388864 | 1346 | 224.0346 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 138 | 28670678 | 5843 | 140.232 | 5.843 | 5.7 | 5.7 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35390184 | 1320 | 225.9113 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 137 | 28676419 | 5741 | 137.784 | 5.741 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35391494 | 1310 | 228.1832 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 28682114 | 5695 | 136.68 | 5.695 | 5.5 | 5.5 | 3B+1S | 0 | 905 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35392796 | 1302 | 228.6216 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 28687400 | 5286 | 126.864 | 5.286 | 5.4 | 5.4 | 3B+1S | 0 | 1000 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35393988 | 1192 | 225.5013 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 28693204 | 5804 | 139.296 | 5.804 | 5.1 | 5.1 | 3B+1S | 0 | 1050 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35395340 | 1352 | 232.9428 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 138 | 28698917 | 5713 | 137.112 | 5.713 | 5 | 5 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35396636 | 1296 | 226.851 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 140 | 28704554 | 5637 | 135.288 | 5.637 | 4.9 | 4.9 | 3B+1S | 0 | 998 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35397916 | 1280 | 227.0711 | 0% | 100% | 100% | 100% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 131 | 28710135 | 5581 | 133.944 | 5.581 | 3.6 | 3.6 | 2B+1S | 0 | 1099 | 1175 | 0 | 1199 | N/A | N/A | N/A | N/A | 35399024 | 1108 | 198.5307 | 0% | 100% | 100% | 0% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 28715595 | 5460 | 131.04 | 5.46 | 3 | 3 | 2B+1S | 0 | 1056 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35400116 | 1092 | 200 | 0% | 100% | 100% | 0% | 100% | 0% | 7904257 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 118 | 28720597 | 5002 | 120.048 | 5.002 | 2.7 | 2.7 | 2B+1S | 0 | 999 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35401116 | 1000 | 199.92 | 0% | 100% | 100% | 0% | 100% | 0% | 7904257 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 100 | 28724956 | 4359 | 104.616 | 4.359 | 3.1 | 3.1 | 2B | 0 | 0 | 1076 | 0 | 1109 | N/A | N/A | N/A | N/A | 35401852 | 736 | 168.8461 | 0% | 0% | 100% | 0% | 100% | 25% | 7904874 | 617 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 97 | 28729049 | 4093 | 98.232 | 4.093 | 3.7 | 3.7 | 2B | 0 | 0 | 1053 | 0 | 1059 | N/A | N/A | N/A | N/A | 35402524 | 672 | 164.1828 | 0% | 0% | 100% | 0% | 100% | 25% | 7905466 | 592 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.5 | 124112 | 124112 | 124.112 | 124.112 | [12 empty] | 25275 | 25275 | 203.6467 | [6 empty] | 5092 | 5092 | 0.99 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:25 PM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 13, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25460 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28729049 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35402524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7905466 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 92 | 28732858 | 3809 | 91.416 | 3.809 | 4.8 | 4.8 | 2B | 0 | 0 | 1071 | 0 | 1079 | N/A | N/A | N/A | N/A | 35403149 | 625 | 164.0851 | 0% | 0% | 100% | 0% | 100% | 35% | 7906451 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | XS | 28736572 | 3714 | 89.136 | 3.714 | 6 | 6 | 2B | 0 | 0 | 1055 | 0 | 1079 | N/A | N/A | N/A | N/A | 35403746 | 597 | 160.7431 | 0% | 0% | 100% | 0% | 100% | 35% | 7907479 | 1028 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 86 | 28740198 | 3626 | 87.024 | 3.626 | 7.4 | 7.4 | 2B | 0 | 0 | 997 | 0 | 1008 | N/A | N/A | N/A | N/A | 35404321 | 575 | 158.5769 | 0% | 0% | 100% | 0% | 100% | 35% | 7908668 | 1189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 85 | 28743733 | 3535 | 84.84 | 3.535 | 8.3 | 8.3 | 2B | 0 | 0 | 981 | 0 | 1008 | N/A | N/A | N/A | N/A | 35404848 | 527 | 149.0806 | 0% | 0% | 100% | 0% | 100% | 35% | 7909726 | 1058 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 90 | 28747639 | 3906 | 93.744 | 3.906 | 9.5 | 9.5 | 2B | 0 | 0 | 968 | 0 | 1008 | N/A | N/A | N/A | N/A | 35405460 | 612 | 156.682 | 0% | 0% | 100% | 0% | 100% | 35% | 7910848 | 1122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 119 | 28752281 | 4642 | 111.408 | 4.642 | 9.5 | 9.5 | 2B | 0 | 0 | 1133 | 0 | 1110 | N/A | N/A | N/A | N/A | 35406148 | 688 | 148.212 | 0% | 0% | 100% | 0% | 100% | 0% | 7910848 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 150 | 28758400 | 6119 | 146.856 | 6.119 | 9.4 | 9.4 | 3B+1S | 0 | 1050 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35407452 | 1304 | 213.1067 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 154 | 28764671 | 6271 | 150.504 | 6.271 | 8.7 | 8.7 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35408824 | 1372 | 218.7849 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 153 | 28770804 | 6133 | 147.192 | 6.133 | 8.1 | 8.1 | 3B+1S | 0 | 1092 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35410188 | 1364 | 222.4034 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 154 | 28776873 | 6069 | 145.656 | 6.069 | 7.5 | 7.5 | 3B+1S | 0 | 1103 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35411540 | 1352 | 222.7715 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 | 1.34 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 28783285 | 6412 | 153.888 | 6.412 | 7 | 7 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35412964 | 1424 | 222.0836 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 149 | 28789222 | 5937 | 142.488 | 5.937 | 6.5 | 6.5 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35414300 | 1336 | 225.0295 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 28795175 | 5953 | 142.872 | 5.953 | 6.2 | 6.2 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35415656 | 1356 | 227.7843 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 28801021 | 5846 | 140.304 | 5.846 | 6 | 6 | 3B+1S | 0 | 996 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35416980 | 1324 | 226.4796 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 28806662 | 5641 | 135.384 | 5.641 | 5.9 | 5.9 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35418276 | 1296 | 229.7465 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 28812274 | 5612 | 134.688 | 5.612 | 5.8 | 5.8 | 3B+1S | 0 | 992 | 119 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35419580 | 1304 | 232.3592 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 28817970 | 5696 | 136.704 | 5.696 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35420912 | 1332 | 233.8483 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 131 | 28823466 | 5496 | 131.904 | 5.496 | 5.5 | 5.5 | 3B+1S | 0 | 955 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35422184 | 1272 | 231.441 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 130 | 28829015 | 5549 | 133.176 | 5.549 | 5.4 | 5.4 | 3B+1S | 0 | 984 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35423452 | 1268 | 228.5096 | 0% | 100% | 100% | 100% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 127 | 28834343 | 5328 | 127.872 | 5.328 | 4.7 | 4.7 | 2B+1S | 0 | 1066 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35424524 | 1072 | 201.2012 | 0% | 100% | 100% | 0% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 28839593 | 5250 | 126 | 5.25 | 4 | 4 | 2B+1S | 0 | 1040 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35425572 | 1048 | 199.619 | 0% | 100% | 100% | 0% | 100% | 0% | 7910848 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 28844551 | 4958 | 118.992 | 4.958 | 3.6 | 3.6 | 2B+1S | 0 | 977 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35426572 | 1000 | 201.6942 | 0% | 100% | 100% | 0% | 100% | 0% | 7910848 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 102 | 28848888 | 4337 | 104.088 | 4.337 | 4.2 | 4.2 | 2B | 0 | 0 | 1074 | 0 | 1110 | N/A | N/A | N/A | N/A | 35427316 | 744 | 171.5472 | 0% | 0% | 100% | 0% | 100% | 25% | 7911307 | 459 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 92 | 28852940 | 4052 | 97.248 | 4.052 | 4.8 | 4.8 | 2B | 0 | 0 | 1045 | 0 | 1058 | N/A | N/A | N/A | N/A | 35427984 | 668 | 164.8569 | 0% | 0% | 100% | 0% | 100% | 25% | 7911851 | 544 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126 | 123891 | 123891 | 123.891 | 123.891 | [12 empty] | 25460 | 25460 | 205.5032 | [6 empty] | 6385 | 6385 | 1.075 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 4:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:26 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:14 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26028 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28852940 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35427984 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7911851 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 91 | 28856795 | 3855 | 92.52 | 3.855 | 5.6 | 5.6 | 2B | 0 | 0 | 1056 | 0 | 1088 | N/A | N/A | N/A | N/A | 35428612 | 628 | 162.9053 | 0% | 0% | 100% | 0% | 100% | 35% | 7912750 | 899 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 89 | 28860529 | 3734 | 89.616 | 3.734 | 6.6 | 6.6 | 2B | 0 | 0 | 1019 | 0 | 1088 | N/A | N/A | N/A | N/A | 35429217 | 605 | 162.0246 | 0% | 0% | 100% | 0% | 100% | 35% | 7913749 | 999 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 87 | 28864188 | 3659 | 87.816 | 3.659 | 7.7 | 7.7 | 2B | 0 | 0 | 988 | 0 | 1088 | N/A | N/A | N/A | N/A | 35429811 | 594 | 162.3394 | 0% | 0% | 100% | 0% | 100% | 35% | 7914773 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 86 | 28867707 | 3519 | 84.456 | 3.519 | 8.6 | 8.6 | 2B | 0 | 0 | 1005 | 0 | 1008 | N/A | N/A | N/A | N/A | 35430376 | 565 | 160.557 | 0% | 0% | 100% | 0% | 100% | 35% | 7915578 | 805 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 92 | 28871384 | 3677 | 88.248 | 3.677 | 9.5 | 9.5 | 2B | 0 | 0 | 961 | 0 | 968 | N/A | N/A | N/A | N/A | 35430928 | 552 | 150.1224 | 0% | 0% | 100% | 0% | 100% | 35% | 7916327 | 749 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 23 | 16.1972 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 115 | 112 | 28875703 | 4319 | 103.656 | 4.319 | 9.5 | 9.5 | 2B | 0 | 0 | 1044 | 0 | 1140 | N/A | N/A | N/A | N/A | 35431524 | 596 | 137.9949 | 0% | 0% | 100% | 0% | 100% | 0% | 7916327 | 0 | 0.87 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 145 | 28881505 | 5802 | 139.248 | 5.802 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35432724 | 1200 | 206.8252 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 28887614 | 6109 | 146.616 | 6.109 | 8.8 | 8.8 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35434044 | 1320 | 216.0746 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 153 | 28894003 | 6389 | 153.336 | 6.389 | 8.2 | 8.2 | 3B+1S | 0 | 1145 | 1195 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35435452 | 1408 | 220.3788 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 156 | 28900421 | 6418 | 154.032 | 6.418 | 7.3 | 7.3 | 3B+1S | 0 | 1174 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35436740 | 1288 | 200.6856 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 28906833 | 6412 | 153.888 | 6.412 | 6.6 | 6.6 | 3B+1S | 0 | 1100 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35438312 | 1572 | 245.1653 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 28912882 | 6049 | 145.176 | 6.049 | 5.9 | 5.9 | 3B+1S | 0 | 1144 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35439658 | 1346 | 222.5161 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 149 | 28919262 | 6380 | 153.12 | 6.38 | 5.1 | 5.1 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35441116 | 1458 | 228.5266 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 146 | 28925261 | 5999 | 143.976 | 5.999 | 4.6 | 4.6 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35442458 | 1342 | 223.704 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 145 | 28931055 | 5794 | 139.056 | 5.794 | 4.1 | 4.1 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35443784 | 1326 | 228.8574 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 28936906 | 5851 | 140.424 | 5.851 | 3.6 | 3.6 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35445132 | 1348 | 230.388 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 145 | 28942812 | 5906 | 141.744 | 5.906 | 3.2 | 3.2 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35446500 | 1368 | 231.6289 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 143 | 28948625 | 5813 | 139.512 | 5.813 | 2.8 | 2.8 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35447850 | 1350 | 232.2381 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 28954401 | 5776 | 138.624 | 5.776 | 2.3 | 2.3 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35449168 | 1318 | 228.1856 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 133 | 28959932 | 5531 | 132.744 | 5.531 | 2.2 | 2.2 | 2B+1S | 0 | 998 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35450420 | 1252 | 226.3605 | 0% | 100% | 100% | 100% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 28965302 | 5370 | 128.88 | 5.37 | 1.7 | 1.7 | 2B+1S | 0 | 1075 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35451526 | 1106 | 205.959 | 0% | 100% | 100% | 0% | 100% | 0% | 7916327 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 122 | 28970287 | 4985 | 119.64 | 4.985 | 1.5 | 1.5 | 2B+1S | 0 | 1013 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35452468 | 942 | 188.9669 | 0% | 100% | 100% | 0% | 100% | 0% | 7916327 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 102 | 28974739 | 4452 | 106.848 | 4.452 | 2.3 | 2.3 | 2B | 0 | 0 | 1110 | 0 | 1139 | N/A | N/A | N/A | N/A | 35453292 | 824 | 185.0854 | 0% | 0% | 100% | 0% | 100% | 40% | 7917224 | 897 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 97 | 28978853 | 4114 | 98.736 | 4.114 | 3.5 | 3.5 | 2B | 0 | 0 | 1075 | 0 | 1109 | N/A | N/A | N/A | N/A | 35454012 | 720 | 175.0122 | 0% | 0% | 100% | 0% | 100% | 40% | 7918368 | 1144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127 | 125913 | 125913 | 125.913 | 125.913 | [12 empty] | 26028 | 26028 | 206.7142 | [6 empty] | 6517 | 6517 | 1.0533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 AM , NORMAL OPERATION
SP2 - STARTED @ 6:33 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 15, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25392 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 28978853 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35454012 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7918368 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 94 | 28982796 | 3943 | 94.632 | 3.943 | 4.8 | 4.8 | 2B | 0 | 0 | 109 | 0 | 1109 | N/A | N/A | N/A | N/A | 35454712 | 700 | 177.5298 | 0% | 0% | 100% | 0% | 100% | 40% | 7919440 | 1072 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 92 | 28986508 | 3712 | 89.088 | 3.712 | 6 | 6 | 2B | 0 | 0 | 1045 | 0 | 1109 | N/A | N/A | N/A | N/A | 35455370 | 658 | 177.2629 | 0% | 0% | 100% | 0% | 100% | 40% | 7920594 | 1154 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 28990163 | 3655 | 87.72 | 3.655 | 7.2 | 7.2 | 2B | 0 | 0 | 1022 | 0 | 1109 | N/A | N/A | N/A | N/A | 35455995 | 625 | 170.9986 | 0% | 0% | 100% | 0% | 100% | 40% | 7921946 | 1352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 85 | 28993746 | 3583 | 85.992 | 3.583 | 8.5 | 8.5 | 2B | 0 | 0 | 1010 | 0 | 1028 | N/A | N/A | N/A | N/A | 35456584 | 589 | 164.3874 | 0% | 0% | 100% | 0% | 100% | 40% | 7923201 | 1255 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 87 | 28997391 | 3645 | 87.48 | 3.645 | 9.5 | 9.5 | 2B | 0 | 0 | 970 | 0 | 967 | N/A | N/A | N/A | N/A | 35457116 | 532 | 145.9534 | 0% | 0% | 100% | 0% | 100% | 40% | 7923981 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 106 | 103 | 29001543 | 4152 | 99.648 | 4.152 | 9.5 | 9.5 | 2B | 0 | 0 | 1023 | 0 | 1160 | N/A | N/A | N/A | N/A | 35457616 | 500 | 120.4239 | 0% | 0% | 100% | 0% | 100% | 0% | 7923981 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 139 | 29007230 | 5687 | 136.488 | 5.687 | 9.5 | 9.5 | 3B+1S | 0 | 958 | 1155 | 1185 | 1189 | N/A | N/A | N/A | N/A | 35458812 | 1196 | 210.3042 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 141 | 29012981 | 5751 | 138.024 | 5.751 | 9.3 | 9.3 | 3B+1S | 0 | 1035 | 1165 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35460028 | 1216 | 211.4415 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 29019349 | 6368 | 152.832 | 6.368 | 8.6 | 8.6 | 3B+1S | 0 | 1107 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35461404 | 1376 | 216.0804 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 29025687 | 6338 | 152.112 | 6.338 | 8 | 8 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35462804 | 1400 | 220.8899 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 29031675 | 5988 | 143.712 | 5.988 | 7.5 | 7.5 | 3B+1S | 0 | 1061 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35464124 | 1320 | 220.4409 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 152 | 29037854 | 6179 | 148.296 | 6.179 | 6.8 | 6.8 | 3B+1S | 0 | 1123 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35465512 | 1388 | 224.6318 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 29044154 | 6300 | 151.2 | 6.3 | 6.3 | 6.3 | 3B+1S | 0 | 1080 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35466924 | 1412 | 224.127 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 145 | 29050072 | 5918 | 142.032 | 5.918 | 5.8 | 5.8 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35468252 | 1328 | 224.4001 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 147 | 29056164 | 6092 | 146.208 | 6.092 | 5.3 | 5.3 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35469636 | 1384 | 227.1832 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 29061973 | 5809 | 139.416 | 5.809 | 4.9 | 4.9 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35470952 | 1316 | 226.545 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 29067780 | 5807 | 139.368 | 5.807 | 4.5 | 4.5 | 3B+1S | 0 | 1043 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35472296 | 1344 | 231.4448 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 139 | 29073428 | 5648 | 135.552 | 5.648 | 4.3 | 4.3 | 3B+1S | 0 | 1009 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35473588 | 1292 | 228.7535 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 135 | 29079140 | 5712 | 137.088 | 5.712 | 4 | 4 | 3B+1S | 0 | 985 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35474892 | 1304 | 228.2913 | 0% | 100% | 100% | 100% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 127 | 29084577 | 5437 | 130.488 | 5.437 | 3.3 | 3.3 | 2B+1S | 0 | 1059 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35475972 | 1080 | 198.639 | 0% | 100% | 100% | 0% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 130 | 29089797 | 5220 | 125.28 | 5.22 | 2.9 | 2.9 | 2B+1S | 0 | 1048 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35476996 | 1024 | 196.1686 | 0% | 100% | 100% | 0% | 100% | 0% | 7923981 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 124 | 29094816 | 5019 | 120.456 | 5.019 | 2.6 | 2.6 | 2B+1S | 0 | 974 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35477996 | 1000 | 199.2429 | 0% | 100% | 100% | 0% | 100% | 0% | 7923981 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 101 | 29099122 | 4306 | 103.344 | 4.306 | 3.2 | 3.2 | 2B | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 35478744 | 748 | 173.7111 | 0% | 0% | 100% | 0% | 100% | 30% | 7924698 | 717 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 93 | 29103117 | 3995 | 95.88 | 3.995 | 4.1 | 4.1 | 2B | 0 | 0 | 1035 | 0 | 1059 | N/A | N/A | N/A | N/A | 35479404 | 660 | 165.2065 | 0% | 0% | 100% | 0% | 100% | 30% | 7925481 | 783 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7917 | 124264 | 124264 | 124.264 | 124.264 | [12 empty] | 25392 | 25392 | 204.3391 | [6 empty] | 7113 | 7113 | 1.0667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:29 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:17PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25604 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29103117 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35479404 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7925481 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 29106926 | 3809 | 91.416 | 3.809 | 5.5 | 5.5 | 2B | 0 | 0 | 1064 | 0 | 1058 | N/A | N/A | N/A | N/A | 35480052 | 648 | 170.1234 | 0% | 0% | 100% | 0% | 100% | 45% | 7926762 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 89 | 29110630 | 3704 | 88.896 | 3.704 | 6.7 | 6.7 | 2B | 0 | 0 | 1040 | 0 | 1058 | N/A | N/A | N/A | N/A | 35480655 | 603 | 162.797 | 0% | 0% | 100% | 0% | 100% | 45% | 7928025 | 1263 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 88 | 29114243 | 3613 | 86.712 | 3.613 | 8 | 8 | 2B | 0 | 0 | 1010 | 0 | 1058 | N/A | N/A | N/A | N/A | 35481224 | 569 | 157.4869 | 0% | 0% | 100% | 0% | 100% | 45% | 7929409 | 1384 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 87 | 29117749 | 3506 | 84.144 | 3.506 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 968 | N/A | N/A | N/A | N/A | 35481772 | 548 | 156.3035 | 0% | 0% | 100% | 0% | 100% | 45% | 7930501 | 1092 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 98 | 29121573 | 3824 | 91.776 | 3.824 | 9.5 | 9.5 | 2B | 0 | 0 | 1001 | 0 | 1009 | N/A | N/A | N/A | N/A | 35482292 | 520 | 135.9833 | 0% | 0% | 100% | 0% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 120 | 29126241 | 4668 | 112.032 | 4.668 | 9.5 | 9.5 | 2B | 0 | 0 | 1152 | 0 | 1110 | N/A | N/A | N/A | N/A | 35482988 | 696 | 149.1003 | 0% | 0% | 100% | 0% | 100% | 0% | 7930501 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 137 | 29132554 | 6313 | 151.512 | 6.313 | 9.3 | 9.3 | 3B+1S | 0 | 981 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35484340 | 1352 | 214.1613 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 29138621 | 6067 | 145.608 | 6.067 | 8.8 | 8.8 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35485672 | 1332 | 219.5484 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 29144723 | 6102 | 146.448 | 6.102 | 8.1 | 8.1 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35487036 | 1364 | 223.5333 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 29151124 | 6401 | 153.624 | 6.401 | 7.6 | 7.6 | 3B+1S | 0 | 1089 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35488456 | 1420 | 221.8403 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 29157012 | 5888 | 141.312 | 5.888 | 7.1 | 7.1 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35489760 | 1304 | 221.4674 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 146 | 29163385 | 6373 | 152.952 | 6.373 | 6.3 | 6.3 | 3B+1S | 0 | 1126 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35491220 | 1460 | 229.0915 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 145 | 29169226 | 5841 | 140.184 | 5.841 | 5.9 | 5.9 | 3B+1S | 0 | 1021 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35492540 | 1320 | 225.9887 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 29175030 | 5804 | 139.296 | 5.804 | 5.7 | 5.7 | 3B+1S | 0 | 1022 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35493864 | 1324 | 228.1185 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 29180678 | 5648 | 135.552 | 5.648 | 5.6 | 5.6 | 3B+1S | 0 | 995 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35495140 | 1276 | 225.9207 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 29186278 | 5600 | 134.4 | 5.6 | 5.5 | 5.5 | 3B+1S | 0 | 996 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35496428 | 1288 | 230 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 29192136 | 5858 | 140.592 | 5.858 | 5.2 | 5.2 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35497780 | 1352 | 230.7955 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 29197799 | 5663 | 135.912 | 5.663 | 5.1 | 5.1 | 3B+1S | 0 | 985 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35499084 | 1304 | 230.2666 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 29203406 | 5607 | 134.568 | 5.607 | 5 | 5 | 3B+1S | 0 | 980 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35500380 | 1296 | 231.1396 | 0% | 100% | 100% | 100% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 131 | 29208917 | 5511 | 132.264 | 5.511 | 4.2 | 4.2 | 2B+1S | 0 | 1104 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35501484 | 1104 | 200.3266 | 0% | 100% | 100% | 0% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 29214195 | 5278 | 126.672 | 5.278 | 3.3 | 3.3 | 2B+1S | 0 | 1054 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35502544 | 1060 | 200.8336 | 0% | 100% | 100% | 0% | 100% | 0% | 7930501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 118 | 29219268 | 5073 | 121.752 | 5.073 | 2.9 | 2.9 | 2B+1S | 0 | 986 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35503560 | 1016 | 200.276 | 0% | 100% | 100% | 0% | 100% | 0% | 7930501 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 101 | 29223658 | 4390 | 105.36 | 4.39 | 3.7 | 3.7 | 2B | 0 | 0 | 1083 | 0 | 1109 | N/A | N/A | N/A | N/A | 35504332 | 772 | 175.8542 | 0% | 0% | 100% | 0% | 100% | 35% | 7931291 | 790 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 92 | 29227660 | 4002 | 96.048 | 4.002 | 4.8 | 4.8 | 2B | 0 | 0 | 1038 | 0 | 1059 | N/A | N/A | N/A | N/A | 35505008 | 676 | 168.9155 | 0% | 0% | 100% | 0% | 100% | 35% | 7932229 | 938 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4167 | 124543 | 124543 | 124.543 | 124.543 | [12 empty] | 25604 | 25604 | 205.5836 | [6 empty] | 6748 | 6748 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:17 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
NOTE : Exponent arrived @ 2:50 pm and conducted an inspection at the GENSET's Hydrolic Hose (Fuel Filter). Left at 3:50pm
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:45 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25388 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29227660 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35505008 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7932229 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 90 | 29231547 | 3887 | 93.288 | 3.887 | 6.1 | 6.1 | 2B | 0 | 0 | 1049 | 0 | 1059 | N/A | N/A | N/A | N/A | 35505602 | 594 | 152.8171 | 0% | 0% | 100% | 0% | 100% | 45% | 7933353 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 86 | 29235262 | 3715 | 89.16 | 3.715 | 7.5 | 7.5 | 2B | 0 | 0 | 1012 | 0 | 1059 | N/A | N/A | N/A | N/A | 35506184 | 582 | 156.6622 | 0% | 0% | 100% | 0% | 100% | 45% | 7934496 | 1143 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 89 | 29238914 | 3652 | 87.648 | 3.652 | 8.7 | 8.7 | 2B | 0 | 0 | 946 | 0 | 1009 | N/A | N/A | N/A | N/A | 35506772 | 588 | 161.0077 | 0% | 0% | 100% | 0% | 100% | 45% | 7935727 | 1231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 88 | 29242271 | 3357 | 80.568 | 3.357 | 9.5 | 9.5 | 2B | 0 | 0 | 873 | 0 | 1009 | N/A | N/A | N/A | N/A | 35507338 | 566 | 168.6029 | 0% | 0% | 100% | 0% | 100% | 45% | 7936709 | 982 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 101 | 29246088 | 3817 | 91.608 | 3.817 | 9.5 | 9.5 | 2B | 0 | 0 | 941 | 0 | 1009 | N/A | N/A | N/A | N/A | 35507862 | 524 | 137.2806 | 0% | 0% | 100% | 0% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 121 | 29250721 | 4633 | 111.192 | 4.633 | 9.5 | 9.5 | 2B | 0 | 0 | 1171 | 0 | 1109 | N/A | N/A | N/A | N/A | 35508536 | 674 | 145.4781 | 0% | 0% | 100% | 0% | 100% | 0% | 7936709 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 148 | 29256763 | 6042 | 145.008 | 6.042 | 9.3 | 9.3 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35509832 | 1296 | 214.4985 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 29262932 | 6169 | 148.056 | 6.169 | 8.9 | 8.9 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35511184 | 1352 | 219.1603 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 152 | 29269214 | 6282 | 150.768 | 6.282 | 8.3 | 8.3 | 3B+1S | 0 | 1096 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35512572 | 1388 | 220.9487 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 152 | 29275455 | 6241 | 149.784 | 6.241 | 7.7 | 7.7 | 3B+1S | 0 | 1075 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35513948 | 1376 | 220.4775 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 29281756 | 6301 | 151.224 | 6.301 | 7.2 | 7.2 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35515340 | 1392 | 220.9173 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 29287507 | 5751 | 138.024 | 5.751 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35516628 | 1288 | 223.9611 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 29293428 | 5921 | 142.104 | 5.921 | 6.7 | 6.7 | 3B+1S | 0 | 984 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35517963 | 1335 | 225.4687 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 29299190 | 5762 | 138.288 | 5.762 | 6.6 | 6.6 | 3B+1S | 0 | 993 | 1195 | 1185 | 1184 | N/A | N/A | N/A | N/A | 35519315 | 1352 | 234.6407 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 29304696 | 5506 | 132.144 | 5.506 | 6.5 | 6.5 | 3B+1S | 0 | 962 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35520588 | 1273 | 231.2023 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 29310186 | 5490 | 131.76 | 5.49 | 6.4 | 6.4 | 3B+1S | 0 | 1001 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35521820 | 1232 | 224.408 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 29315888 | 5702 | 136.848 | 5.702 | 6.2 | 6.2 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35523132 | 1312 | 230.0947 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 29321577 | 5689 | 136.536 | 5.689 | 6.1 | 6.1 | 3B+1S | 0 | 995 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35524412 | 1280 | 224.9956 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 140 | 29327319 | 5742 | 137.808 | 5.742 | 5.8 | 5.8 | 3B+1S | 0 | 988 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35525700 | 1288 | 224.3121 | 0% | 100% | 100% | 100% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 29332866 | 5547 | 133.128 | 5.547 | 5 | 5 | 2B+1S | 0 | 1084 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35526804 | 1104 | 199.0265 | 0% | 100% | 100% | 0% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 29338339 | 5473 | 131.352 | 5.473 | 4 | 4 | 2B+1S | 0 | 1075 | 1199 | 0 | 1199 | N/A | N/A | N/A | N/A | 35527892 | 1088 | 198.7941 | 0% | 100% | 100% | 0% | 100% | 0% | 7936709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 122 | 29343504 | 5165 | 123.96 | 5.165 | 3.5 | 3.5 | 2B+1S | 0 | 1004 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35528912 | 1020 | 197.4831 | 0% | 100% | 100% | 0% | 100% | 0% | 7936709 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 107 | 29348010 | 4506 | 108.144 | 4.506 | 4 | 4 | 2B | 0 | 0 | 1111 | 0 | 1110 | N/A | N/A | N/A | N/A | 35529692 | 780 | 173.1025 | 0% | 0% | 100% | 0% | 100% | 25% | 7937173 | 464 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 98 | 29352224 | 4214 | 101.136 | 4.214 | 4.6 | 4.6 | 2B | 0 | 0 | 1066 | 0 | 1059 | N/A | N/A | N/A | N/A | 35530396 | 704 | 167.0622 | 0% | 0% | 100% | 0% | 100% | 25% | 7936709 | -464 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9167 | 124564 | 124564 | 124.564 | 124.564 | [12 empty] | 25388 | 25388 | 203.8149 | [6 empty] | 4480 | 4480 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:31 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:25 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:24 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
NOTE: MONARK delivered 10pcs. Fuel Filter, 6pcs. Engine Oil Filter, 4pcs. Drum of Engine Oil, 2pcs. Cartridge Grease, 2pcs. SOS-BTL.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25680 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29352224 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35530396 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7936709 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 94 | 29356158 | 3934 | 94.416 | 3.934 | 5.5 | 5.5 | 2B | 0 | 0 | 1052 | 0 | 1088 | N/A | N/A | N/A | N/A | 35531054 | 658 | 167.2598 | 0% | 0% | 100% | 0% | 100% | 40% | 7937998 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 92 | 29360045 | 3887 | 93.288 | 3.887 | 6.6 | 6.6 | 2B | 0 | 0 | 1010 | 0 | 1058 | N/A | N/A | N/A | N/A | 35531675 | 621 | 159.7633 | 0% | 0% | 100% | 0% | 100% | 40% | 7939396 | 1398 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 90 | 29363749 | 3704 | 88.896 | 3.704 | 7.8 | 7.8 | 2B | 0 | 0 | 958 | 0 | 1058 | N/A | N/A | N/A | N/A | 35532280 | 605 | 163.3369 | 0% | 0% | 100% | 0% | 100% | 40% | 7940831 | 1435 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 87 | 29367361 | 3612 | 86.688 | 3.612 | 9.2 | 9.2 | 2B | 0 | 0 | 930 | 0 | 1058 | N/A | N/A | N/A | N/A | 35532860 | 580 | 160.5759 | 0% | 0% | 100% | 0% | 100% | 40% | 7942159 | 1328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 98 | 29371231 | 3870 | 92.88 | 3.87 | 9.5 | 9.5 | 2B | 0 | 0 | 999 | 0 | 1008 | N/A | N/A | N/A | N/A | 35533404 | 544 | 140.5685 | 0% | 0% | 100% | 0% | 100% | 40% | 7942378 | 219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 121 | 29375951 | 4720 | 113.28 | 4.72 | 9.5 | 9.5 | 2B | 0 | 0 | 1153 | 0 | 1008 | N/A | N/A | N/A | N/A | 35534100 | 696 | 147.4576 | 0% | 0% | 100% | 0% | 100% | 0% | 7942378 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 152 | 29381962 | 6011 | 144.264 | 6.011 | 9.4 | 9.4 | 3B+1S | 0 | 1066 | 1194 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35535376 | 1276 | 212.2775 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 154 | 29388050 | 6088 | 146.112 | 6.088 | 8.9 | 8.9 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35536732 | 1356 | 222.7332 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 149 | 29394603 | 6553 | 157.272 | 6.553 | 8 | 8 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35538196 | 1464 | 223.4091 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 29400435 | 5832 | 139.968 | 5.832 | 7.5 | 7.5 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35539492 | 1296 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 29406584 | 6149 | 147.576 | 6.149 | 6.9 | 6.9 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35540852 | 1360 | 221.1742 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 29412634 | 6050 | 145.2 | 6.05 | 6.3 | 6.3 | 3B+1S | 0 | 1077 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35542228 | 1376 | 227.438 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 139 | 29418667 | 6033 | 144.792 | 6.033 | 6.1 | 6.1 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35543612 | 1384 | 229.4049 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 29424377 | 5710 | 137.04 | 5.71 | 5.9 | 5.9 | 3B+1S | 0 | 960 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35544912 | 1300 | 227.6708 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 29430060 | 5683 | 136.392 | 5.683 | 5.8 | 5.8 | 3B+1S | 0 | 1005 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35546196 | 1284 | 225.937 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 29435566 | 5506 | 132.144 | 5.506 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35547444 | 1248 | 226.6618 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 29441358 | 5792 | 139.008 | 5.792 | 5.3 | 5.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35548776 | 1332 | 229.9724 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 29447250 | 5892 | 141.408 | 5.892 | 5.2 | 5.2 | 3B+1S | 0 | 982 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35550132 | 1356 | 230.1426 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 29452732 | 5482 | 131.568 | 5.482 | 5.1 | 5.1 | 3B+1S | 0 | 975 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35551384 | 1252 | 228.3838 | 0% | 100% | 100% | 100% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 135 | 29458263 | 5531 | 132.744 | 5.531 | 4.5 | 4.5 | 2B+1S | 0 | 1095 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35552656 | 1272 | 229.9765 | 0% | 100% | 100% | 0% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 102 | 125 | 29463633 | 5370 | 128.88 | 5.37 | 4 | 4 | 2B+1S | 0 | 1123 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35553720 | 1064 | 198.1378 | 0% | 100% | 100% | 0% | 100% | 0% | 7942378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 120 | 29468603 | 4970 | 119.28 | 4.97 | 3.3 | 3.3 | 2B+1S | 0 | 1030 | 1155 | 0 | 1181 | N/A | N/A | N/A | N/A | 35554692 | 972 | 195.5734 | 0% | 100% | 100% | 0% | 100% | 0% | 7942378 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 98 | 29472877 | 4274 | 102.576 | 4.274 | 3.7 | 3.7 | 2B | 0 | 0 | 1058 | 0 | 1110 | N/A | N/A | N/A | N/A | 35555428 | 736 | 172.204 | 0% | 0% | 100% | 0% | 100% | 25% | 7942860 | 482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 108 | 92 | 29476872 | 3995 | 95.88 | 3.995 | 4.5 | 4.5 | 2B | 0 | 0 | 1032 | 0 | 1028 | N/A | N/A | N/A | N/A | 35556076 | 648 | 162.2028 | 0% | 0% | 100% | 0% | 100% | 25% | 7943471 | 611 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.7083 | 124648 | 124648 | 124.648 | 124.648 | [12 empty] | 25680 | 25680 | 206.0202 | [6 empty] | 6762 | 6762 | 1.0567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:37 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:21 AM , NORMAL OPERATION
MONARK arrived @ 9:50am and conducted preventive maintenance on GENSETs. CHANGE THE OIL, OIL FILTER AND FUEL FILTER.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:17 AM , NORMAL OPERATION
Conducted the Occular inspection with the NAR POWER SPECIALIST CORPORATION / EESI ELECTRICAL EQUIPMENT AND SYSTEM INTEGRATION / ACM ELECTROMECH / QUAD AM / BETA ELECTRIC CORP assisted by Sir Arturo Trinidad
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:12 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,891
GENSET 1 WARMUP EXERCISED @ 12:32PM / STOPPED @ 12:42PM
GENSET 2 WARMUP EXERCISED @ 12:21PM / STOPPED @ 12:31PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,878
GENSET 1 WARMUP EXERCISED @ 4:03PM / STOPPED @ 4:13PM
GENSET 2 WARMUP EXERCISED @ 5:04PM / STOPPED @ 5:14PM
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | REIVIN M. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29476872 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35556076 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7943471 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 91 | 29480687 | 3815 | 91.56 | 3.815 | 5.7 | 5.7 | 2B | 0 | 0 | 1036 | 0 | 1058 | N/A | N/A | N/A | N/A | 35556681 | 605 | 158.5845 | 0% | 0% | 100% | 0% | 100% | 40% | 7944560 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 89 | 29484416 | 3729 | 89.496 | 3.729 | 7 | 7 | 2B | 0 | 0 | 1010 | 0 | 1058 | N/A | N/A | N/A | N/A | 35557262 | 581 | 155.8058 | 0% | 0% | 100% | 0% | 100% | 40% | 7945754 | 1194 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 85 | 29488051 | 3635 | 87.24 | 3.635 | 8.4 | 8.4 | 2B | 0 | 0 | 989 | 0 | 1058 | N/A | N/A | N/A | N/A | 35557828 | 566 | 155.7084 | 0% | 0% | 100% | 0% | 100% | 40% | 7947062 | 1308 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 87 | 29491555 | 3504 | 84.096 | 3.504 | 9.5 | 9.5 | 2B | 0 | 0 | 965 | 0 | 978 | N/A | N/A | N/A | N/A | 35558364 | 536 | 152.968 | 0% | 0% | 100% | 0% | 100% | 40% | 7948258 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 93 | 29495463 | 3908 | 93.792 | 3.908 | 9.5 | 9.5 | 2B | 0 | 0 | 958 | 0 | 918 | N/A | N/A | N/A | N/A | 35558928 | 564 | 144.3193 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 119 | 29500104 | 4641 | 111.384 | 4.641 | 9.5 | 9.5 | 2B | 0 | 0 | 1110 | 0 | 1110 | N/A | N/A | N/A | N/A | 35559606 | 678 | 146.0892 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 | 1.04 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 146 | 29506128 | 6024 | 144.576 | 6.024 | 9.3 | 9.3 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35560908 | 1302 | 216.1355 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 29512292 | 6164 | 147.936 | 6.164 | 8.8 | 8.8 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35562284 | 1376 | 223.2317 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 29518432 | 6140 | 147.36 | 6.14 | 8.2 | 8.2 | 3B+1S | 0 | 1074 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35563676 | 1392 | 226.7101 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 29524570 | 6138 | 147.312 | 6.138 | 7.5 | 7.5 | 3B+1S | 0 | 1096 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35565054 | 1378 | 224.5031 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 29530731 | 6161 | 147.864 | 6.161 | 6.9 | 6.9 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35566420 | 1366 | 221.7173 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 150 | 29536931 | 6200 | 148.8 | 6.2 | 6.3 | 6.3 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35567810 | 1390 | 224.1935 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 143 | 29542877 | 5946 | 142.704 | 5.946 | 6 | 6 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35569144 | 1334 | 224.3525 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 29548762 | 5885 | 141.24 | 5.885 | 5.7 | 5.7 | 3B+1S | 0 | 1017 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35570494 | 1350 | 229.3968 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 29554648 | 5886 | 141.264 | 5.886 | 5.6 | 5.6 | 3B+1S | 0 | 996 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35571844 | 1350 | 229.3578 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 29560020 | 5372 | 128.928 | 5.372 | 5.5 | 5.5 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35573092 | 1248 | 232.3157 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 29565802 | 5782 | 138.768 | 5.782 | 5.1 | 5.1 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35574428 | 1336 | 231.0619 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 139 | 29571536 | 5734 | 137.616 | 5.734 | 4.9 | 4.9 | 3B+1S | 0 | 987 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35575740 | 1312 | 228.8106 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 139 | 29577317 | 5781 | 138.744 | 5.781 | 4.8 | 4.8 | 3B+1S | 0 | 991 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35577060 | 1320 | 228.3342 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 132 | 29582774 | 5457 | 130.968 | 5.457 | 3.9 | 3.9 | 2B+1S | 0 | 1124 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35578164 | 1104 | 202.309 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 29588206 | 5432 | 130.368 | 5.432 | 3.1 | 3.1 | 2B+1S | 0 | 1066 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35579244 | 1080 | 198.8218 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 131 | 118 | 29593369 | 5163 | 123.912 | 5.163 | 2.7 | 2.7 | 2B+1S | 0 | 995 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 35580272 | 1028 | 199.109 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 98 | 29597745 | 4376 | 105.024 | 4.376 | 3 | 3 | 2B | 0 | 0 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 35581100 | 828 | 189.2139 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 95 | 29601768 | 4023 | 96.552 | 4.023 | 4 | 4 | 2B | 0 | 0 | 1121 | 0 | 1110 | N/A | N/A | N/A | N/A | 35581956 | 856 | 212.7765 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.8333 | 124896 | 124896 | 124.896 | 124.896 | [12 empty] | 25880 | 25880 | 207.2124 | [6 empty] | 4787 | 4787 | 1.0117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:55 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:05 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 20, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:18 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV4 - OPENED (15%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26326 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29601768 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35581956 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7948258 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 110 | 88 | 29605593 | 3825 | 91.8 | 3.825 | 5 | 5 | 2B | 0 | 0 | 1038 | 0 | 1110 | N/A | N/A | N/A | N/A | 35582708 | 752 | 196.6013 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 87 | 29609387 | 3794 | 91.056 | 3.794 | 5.9 | 5.9 | 2B | 0 | 0 | 1081 | 0 | 1059 | N/A | N/A | N/A | N/A | 35583368 | 660 | 173.9589 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 86 | 29612999 | 3612 | 86.688 | 3.612 | 6.9 | 6.9 | 2B | 0 | 0 | 1062 | 0 | 1110 | N/A | N/A | N/A | N/A | 35584070 | 702 | 194.3522 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 85 | 29616561 | 3562 | 85.488 | 3.562 | 8 | 8 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 35584772 | 702 | 197.0803 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 92 | 29620448 | 3887 | 93.288 | 3.887 | 9.5 | 9.5 | 2B | 0 | 0 | 975 | 0 | 988 | N/A | N/A | N/A | N/A | 35585604 | 832 | 214.0468 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 29624941 | 4493 | 107.832 | 4.493 | 9.5 | 9.5 | 2B | 0 | 0 | 1174 | 0 | 1058 | N/A | N/A | N/A | N/A | 35586252 | 648 | 144.2243 | 0% | 0% | 100% | 0% | 100% | 0% | 7948258 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 29630940 | 5999 | 143.976 | 5.999 | 9.4 | 9.4 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35587528 | 1276 | 212.7021 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 29637142 | 6202 | 148.848 | 6.202 | 8.7 | 8.7 | 3B+1S | 0 | 1097 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35588896 | 1368 | 220.574 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 29643493 | 6351 | 152.424 | 6.351 | 7.9 | 7.9 | 3B+1S | 0 | 1109 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35590324 | 1428 | 224.8465 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 29649734 | 6241 | 149.784 | 6.241 | 7.1 | 7.1 | 3B+1S | 0 | 1105 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35591740 | 1416 | 226.8867 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 29656075 | 6341 | 152.184 | 6.341 | 6.5 | 6.5 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35593148 | 1408 | 222.047 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 29662007 | 5932 | 142.368 | 5.932 | 6 | 6 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35594508 | 1360 | 229.265 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 29667928 | 5921 | 142.104 | 5.921 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35595864 | 1356 | 229.0154 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 134 | 29673729 | 5801 | 139.224 | 5.801 | 5.6 | 5.6 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 35597184 | 1320 | 227.547 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 29679314 | 5585 | 134.04 | 5.585 | 5.5 | 5.5 | 3B+1S | 0 | 995 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35598468 | 1284 | 229.9015 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 29684905 | 5591 | 134.184 | 5.591 | 5.4 | 5.4 | 3B+1S | 0 | 995 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35599772 | 1304 | 233.232 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 29690615 | 5710 | 137.04 | 5.71 | 5.3 | 5.3 | 3B+1S | 0 | 1023 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35601092 | 1320 | 231.1734 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 29696211 | 5596 | 134.304 | 5.596 | 5.2 | 5.2 | 3B+1S | 0 | 977 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35602372 | 1280 | 228.7348 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 134 | 29701766 | 5555 | 133.32 | 5.555 | 5.1 | 5.1 | 3B+1S | 0 | 989 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35603652 | 1280 | 230.423 | 0% | 100% | 100% | 100% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 131 | 29707211 | 5445 | 130.68 | 5.445 | 4.2 | 4.2 | 2B+1S | 0 | 1078 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35604760 | 1108 | 203.4894 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 29712405 | 5194 | 124.656 | 5.194 | 3.4 | 3.4 | 2B+1S | 0 | 1030 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35605796 | 1036 | 199.4609 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 114 | 29717472 | 5067 | 121.608 | 5.067 | 3.2 | 3.2 | 2B+1S | 0 | 1010 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35606820 | 1024 | 202.092 | 0% | 100% | 100% | 0% | 100% | 0% | 7948258 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 103 | 29721673 | 4201 | 100.824 | 4.201 | 3.4 | 3.4 | 2B | 0 | 0 | 1084 | 0 | 1110 | N/A | N/A | N/A | N/A | 35607540 | 720 | 171.3878 | 0% | 0% | 100% | 0% | 100% | 25% | 7948589 | 331 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 100 | 29725801 | 4128 | 99.072 | 4.128 | 4 | 4 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 35608282 | 742 | 179.7481 | 0% | 0% | 100% | 0% | 100% | 25% | 7949118 | 529 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.3333 | 124033 | 124033 | 124.033 | 124.033 | [12 empty] | 26326 | 26326 | 212.25 | [6 empty] | 860 | 860 | 1.0333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:40 AM , NORMAL OPERATION
XCV4 CLOSED @ 4:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:33 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:13 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:17PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:30 PM FOR REFILLING
NORMAL OPERATION

## MAR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24946 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29725801 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35608282 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7949118 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 92 | 29729709 | 3908 | 93.792 | 3.908 | 5 | 5 | 2B | 0 | 0 | 1038 | 0 | 1067 | N/A | N/A | N/A | N/A | 35608888 | 606 | 155.0665 | 0% | 0% | 100% | 0% | 100% | 40% | 7950011 | 893 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 90 | 29733604 | 3895 | 93.48 | 3.895 | 5.8 | 5.8 | 2B | 0 | 0 | 1021 | 0 | 1067 | N/A | N/A | N/A | N/A | 35609487 | 599 | 153.7869 | 0% | 0% | 100% | 0% | 100% | 40% | 7951356 | 1345 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 29737392 | 3788 | 90.912 | 3.788 | 6.8 | 6.8 | 2B | 0 | 0 | 1010 | 0 | 1067 | N/A | N/A | N/A | N/A | 35610076 | 589 | 155.491 | 0% | 0% | 100% | 0% | 100% | 40% | 7952788 | 1432 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 92 | 29741855 | 4463 | 107.112 | 4.463 | 7.9 | 7.9 | 2B | 0 | 0 | 1012 | 0 | 1067 | N/A | N/A | N/A | N/A | 35610684 | 608 | 136.2312 | 0% | 0% | 100% | 0% | 100% | 40% | 7954135 | 1347 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 120 | 110 | 29745254 | 3399 | 81.576 | 3.399 | 9.4 | 9.4 | 2B | 0 | 0 | 1025 | 0 | 1088 | N/A | N/A | N/A | N/A | 35611340 | 656 | 192.9979 | 0% | 0% | 100% | 0% | 100% | 40% | 7954195 | 60 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 133 | 138 | 29748590 | 3336 | 80.064 | 3.336 | 9.5 | 9.5 | 2B | 0 | 0 | 1060 | 0 | 1190 | N/A | N/A | N/A | N/A | 35611776 | 436 | 130.6954 | 0% | 0% | 100% | 0% | 100% | 0% | 7954195 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 148 | 29754633 | 6043 | 145.032 | 6.043 | 9.3 | 9.3 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35613004 | 1228 | 203.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 29761051 | 6418 | 154.032 | 6.418 | 8.9 | 8.9 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35614404 | 1400 | 218.1365 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 131 | 29767032 | 5981 | 143.544 | 5.981 | 8.1 | 8.1 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35615756 | 1352 | 226.0492 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 150 | 29773545 | 6513 | 156.312 | 6.513 | 7.1 | 7.1 | 3B+1S | 0 | 1191 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35617244 | 1488 | 228.4661 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 | 1.25 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 155 | 29779726 | 6181 | 148.344 | 6.181 | 6.2 | 6.2 | 3B+1S | 0 | 1137 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35618644 | 1400 | 226.5006 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Normal operation schedule
59:00 | 12:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 53 | 72 | 29783725 | 3999 | 95.976 | 3.999 | 5.7 | 5.7 | 3B+1S | 0 | 1105 | 1194 | 1185 | 1192 | N/A | N/A | N/A | N/A | 35619496 | 852 | 213.0533 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 29788431 | 4706 | 112.944 | 4.706 | 4.9 | 4.9 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35620532 | 1036 | 220.1445 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 135 | 29794333 | 5902 | 141.648 | 5.902 | 4.7 | 4.7 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35621892 | 1360 | 230.4304 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 138 | 29799861 | 5528 | 132.672 | 5.528 | 4.4 | 4.4 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35623196 | 1304 | 235.89 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 29805422 | 5561 | 133.464 | 5.561 | 4.2 | 4.2 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35624506 | 1310 | 235.5691 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 29811011 | 5589 | 134.136 | 5.589 | 3.7 | 3.7 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35625824 | 1318 | 235.8204 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 133 | 29816782 | 5771 | 138.504 | 5.771 | 3.4 | 3.4 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35627156 | 1332 | 230.8092 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 29822504 | 5722 | 137.328 | 5.722 | 3.1 | 3.1 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35628478 | 1322 | 231.0381 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 29828052 | 5548 | 133.152 | 5.548 | 2.8 | 2.8 | 3B+1S | 0 | 1011 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35629734 | 1256 | 226.3879 | 0% | 100% | 100% | 100% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 127 | 29833411 | 5359 | 128.616 | 5.359 | 2.1 | 2.1 | 2B+1S | 0 | 1148 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35630810 | 1076 | 200.7837 | 0% | 100% | 100% | 0% | 100% | 0% | 7954195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 117 | 29838519 | 5108 | 122.592 | 5.108 | 1.8 | 1.8 | 2B+1S | 0 | 1004 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35631804 | 994 | 194.5967 | 0% | 100% | 100% | 0% | 100% | 0% | 7954195 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 91 | 29842631 | 4112 | 98.688 | 4.112 | 2.7 | 2.7 | 2B | 0 | 0 | 1087 | 0 | 1110 | N/A | N/A | N/A | N/A | 35632560 | 756 | 183.8521 | 0% | 0% | 100% | 0% | 100% | 40% | 7955147 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 89 | 29846401 | 3770 | 90.48 | 3.77 | 4 | 4 | 2B | 0 | 0 | 1069 | 0 | 1059 | N/A | N/A | N/A | N/A | 35633228 | 668 | 177.1883 | 0% | 0% | 100% | 0% | 100% | 40% | 7956378 | 1231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.8333 | 120600 | 120600 | 120.6 | 120.6 | [12 empty] | 24946 | 24946 | 206.8491 | [6 empty] | 7260 | 7260 | 1.0817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
ALL MOV FAULT @ 4:26 AM RESUME NORMAL OPERATION @4:36 AM
XCV1 CLOSED @ 5:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
ALL MOV FAULT @ 5:34 AM RESUME NORMAL OPERATION @5:45 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET PRESSURE
ALL MOV FAULT @ 6:01 AM RESUME NORMAL OPERATION @ 6:20AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:24 AM , NORMAL OPERATION
CONDUCTED and Inspection and repair Mr. Drazen Reyes the ACTUATOR XCV1-XCV3-XCV4-XCV5 arrived at 10:10am
ALL MOV FAULT @ 11:22 AM RESUME NORMAL OPERATION @ 11:30AM
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 22, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:05 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25128 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29846401 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35633228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7956378 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 84 | 29850105 | 3704 | 88.896 | 3.704 | 5 | 5 | 2B | 0 | 0 | 1069 | 0 | 1059 | N/A | N/A | N/A | N/A | 35633848 | 620 | 167.3866 | 0% | 0% | 100% | 0% | 100% | 40% | 7957306 | 928 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 83 | 29853717 | 3612 | 86.688 | 3.612 | 6.1 | 6.1 | 2B | 0 | 0 | 1069 | 0 | 1059 | N/A | N/A | N/A | N/A | 35634452 | 604 | 167.2204 | 0% | 0% | 100% | 0% | 100% | 40% | 7958311 | 1005 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 82 | 29857240 | 3523 | 84.552 | 3.523 | 7.3 | 7.3 | 2B | 0 | 0 | 1051 | 0 | 1059 | N/A | N/A | N/A | N/A | 35635036 | 584 | 165.7678 | 0% | 0% | 100% | 0% | 100% | 40% | 7959417 | 1106 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 91 | 29860940 | 3700 | 88.8 | 3.7 | 8.5 | 8.5 | 2B | 0 | 0 | 1051 | 0 | 1059 | N/A | N/A | N/A | N/A | 35635640 | 604 | 163.2432 | 0% | 0% | 100% | 0% | 100% | 40% | 7960427 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 118 | 92 | 29864830 | 3890 | 93.36 | 3.89 | 9.5 | 9.5 | 2B | 0 | 0 | 1003 | 0 | 1004 | N/A | N/A | N/A | N/A | 35636244 | 604 | 155.2699 | 0% | 0% | 100% | 0% | 100% | 40% | 7961423 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 108 | 29869072 | 4242 | 101.808 | 4.242 | 9.5 | 9.5 | 2B | 0 | 0 | 1013 | 0 | 1008 | N/A | N/A | N/A | N/A | 35636780 | 536 | 126.3555 | 0% | 0% | 100% | 0% | 100% | 0% | 7961423 | 0 | 0.87 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 138 | 29874529 | 5457 | 130.968 | 5.457 | 9.5 | 9.5 | 3B | 0 | 0 | 1083 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35637900 | 1120 | 205.241 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 140 | 29880444 | 5915 | 141.96 | 5.915 | 9.5 | 9.5 | 3B | 0 | 0 | 1179 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35639148 | 1248 | 210.989 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 144 | 29886642 | 6198 | 148.752 | 6.198 | 9.3 | 9.3 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35640532 | 1384 | 223.2978 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 143 | 29892655 | 6013 | 144.312 | 6.013 | 8.7 | 8.7 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35641853 | 1321 | 219.6907 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 29898771 | 6116 | 146.784 | 6.116 | 8.1 | 8.1 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35643198 | 1345 | 219.915 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 150 | 29904980 | 6209 | 149.016 | 6.209 | 7.6 | 7.6 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35644572 | 1374 | 221.2917 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 143 | 29911059 | 6079 | 145.896 | 6.079 | 6.9 | 6.9 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35645948 | 1376 | 226.353 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 144 | 29917147 | 6088 | 146.112 | 6.088 | 6.5 | 6.5 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35647324 | 1376 | 226.0184 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 29922937 | 5790 | 138.96 | 5.79 | 6.2 | 6.2 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35648644 | 1320 | 227.9793 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 29928621 | 5684 | 136.416 | 5.684 | 5.9 | 5.9 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35649948 | 1304 | 229.4159 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 29934445 | 5824 | 139.776 | 5.824 | 5.6 | 5.6 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35651300 | 1352 | 232.1429 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 29940086 | 5641 | 135.384 | 5.641 | 5.5 | 5.5 | 3B+1S | 0 | 980 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35652596 | 1296 | 229.7465 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 29945547 | 5461 | 131.064 | 5.461 | 5.3 | 5.3 | 3B+1S | 0 | 980 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35653868 | 1272 | 232.9244 | 0% | 100% | 100% | 100% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 131 | 29951014 | 5467 | 131.208 | 5.467 | 4.5 | 4.5 | 2B+1S | 0 | 1100 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35654976 | 1108 | 202.6706 | 0% | 100% | 100% | 0% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 128 | 29956191 | 5177 | 124.248 | 5.177 | 3.7 | 3.7 | 2B+1S | 0 | 1005 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35656020 | 1044 | 201.6612 | 0% | 100% | 100% | 0% | 100% | 0% | 7961423 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 116 | 29961120 | 4929 | 118.296 | 4.929 | 3.6 | 3.6 | 2B+1S | 0 | 1000 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35656992 | 972 | 197.2002 | 0% | 100% | 100% | 0% | 100% | 0% | 7961423 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 117 | 101 | 29965315 | 4195 | 100.68 | 4.195 | 4.2 | 4.2 | 2B | 0 | 0 | 1049 | 0 | 1110 | N/A | N/A | N/A | N/A | 35657700 | 708 | 168.7723 | 0% | 0% | 100% | 0% | 100% | 25% | 7961992 | 569 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 97 | 29969347 | 4032 | 96.768 | 4.032 | 4.9 | 4.9 | 2B | 0 | 0 | 1030 | 0 | 1058 | N/A | N/A | N/A | N/A | 35658356 | 656 | 162.6984 | 0% | 0% | 100% | 0% | 100% | 25% | 7962607 | 615 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.8333 | 122946 | 122946 | 122.946 | 122.946 | [12 empty] | 25128 | 25128 | 204.3824 | [6 empty] | 6229 | 6229 | 1.0033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 8:36 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:31 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | DENNIS GUANZON
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24950 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 29969347 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35658356 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7962607 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 98 | 92 | 29973301 | 3954 | 94.896 | 3.954 | 5.9 | 5.9 | 2B | 0 | 0 | 1077 | 0 | 1058 | N/A | N/A | N/A | N/A | 35658978 | 622 | 157.3091 | 0% | 0% | 100% | 0% | 100% | 35% | 7963595 | 988 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 91 | 29977164 | 3863 | 92.712 | 3.863 | 7 | 7 | 2B | 0 | 0 | 1066 | 0 | 1058 | N/A | N/A | N/A | N/A | 35659580 | 602 | 155.8374 | 0% | 0% | 100% | 0% | 100% | 35% | 7964623 | 1028 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 90 | 29980923 | 3759 | 90.216 | 3.759 | 8.2 | 8.2 | 2B | 0 | 0 | 1010 | 0 | 1058 | N/A | N/A | N/A | N/A | 35660158 | 578 | 153.7643 | 0% | 0% | 100% | 0% | 100% | 35% | 7965832 | 1209 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 87 | 29984619 | 3696 | 88.704 | 3.696 | 9.5 | 9.5 | 2B | 0 | 0 | 988 | 0 | 987 | N/A | N/A | N/A | N/A | 35660676 | 518 | 140.1515 | 0% | 0% | 100% | 0% | 100% | 35% | 7966946 | 1114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 97 | 29987813 | 3194 | 76.656 | 3.194 | 9.5 | 9.5 | 2B | 0 | 0 | 992 | 0 | 988 | N/A | N/A | N/A | N/A | 35661176 | 500 | 156.5435 | 0% | 0% | 100% | 0% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 115 | 29992297 | 4484 | 107.616 | 4.484 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1088 | N/A | N/A | N/A | N/A | 35661816 | 640 | 142.7297 | 0% | 0% | 100% | 0% | 100% | 0% | 7966946 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 138 | 29998111 | 5814 | 139.536 | 5.814 | 9.5 | 9.5 | 3B | 0 | 0 | 1185 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35663048 | 1232 | 211.9023 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 30003934 | 5823 | 139.752 | 5.823 | 9.4 | 9.4 | 3B+1S | 0 | 997 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35664342 | 1294 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 30010141 | 6207 | 148.968 | 6.207 | 9.1 | 9.1 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35665696 | 1354 | 218.1408 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 30016195 | 6054 | 145.296 | 6.054 | 8.5 | 8.5 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35667044 | 1348 | 222.6627 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 142 | 30022159 | 5964 | 143.136 | 5.964 | 8.1 | 8.1 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35668372 | 1328 | 222.6693 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 30028122 | 5963 | 143.112 | 5.963 | 7.8 | 7.8 | 3B+1S | 0 | 1041 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35669708 | 1336 | 224.0483 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 30033967 | 5845 | 140.28 | 5.845 | 7.5 | 7.5 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35671028 | 1320 | 225.834 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 141 | 30040219 | 6252 | 150.048 | 6.252 | 7.4 | 7.4 | 3B+1S | 0 | 910 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35672436 | 1408 | 225.2079 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 30045362 | 5143 | 123.432 | 5.143 | 7.3 | 7.3 | 3B+1S | 0 | 993 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35673604 | 1168 | 227.1048 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 140 | 30051049 | 5687 | 136.488 | 5.687 | 7.1 | 7.1 | 3B+1S | 0 | 1018 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35674876 | 1272 | 223.668 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 30056718 | 5669 | 136.056 | 5.669 | 6.4 | 6.4 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35676172 | 1296 | 228.6117 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 30062423 | 5705 | 136.92 | 5.705 | 6.2 | 6.2 | 3B+1S | 0 | 971 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35677476 | 1304 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 30067903 | 5480 | 131.52 | 5.48 | 6.1 | 6.1 | 3B+1S | 0 | 976 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35678728 | 1252 | 228.4672 | 0% | 100% | 100% | 100% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 30073374 | 5471 | 131.304 | 5.471 | 5.3 | 5.3 | 2B+1S | 0 | 1081 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35679820 | 1092 | 199.5979 | 0% | 100% | 100% | 0% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 30078806 | 5432 | 130.368 | 5.432 | 4.6 | 4.6 | 2B+1S | 0 | 1029 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35680884 | 1064 | 195.8763 | 0% | 100% | 100% | 0% | 100% | 0% | 7966946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 30083854 | 5048 | 121.152 | 5.048 | 4.3 | 4.3 | 2B+1S | 0 | 980 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35681884 | 1000 | 198.0983 | 0% | 100% | 100% | 0% | 100% | 0% | 7966946 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 106 | 30088172 | 4318 | 103.632 | 4.318 | 4.9 | 4.9 | 2B | 0 | 0 | 1085 | 0 | 1099 | N/A | N/A | N/A | N/A | 35682624 | 740 | 171.3756 | 0% | 0% | 100% | 0% | 100% | 30% | 7967584 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 95 | 30092263 | 4091 | 98.184 | 4.091 | 5.6 | 5.6 | 2B | 0 | 0 | 1026 | 0 | 1099 | N/A | N/A | N/A | N/A | 35683306 | 682 | 166.7074 | 0% | 0% | 100% | 0% | 100% | 30% | 7968263 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.1667 | 122916 | 122916 | 122.916 | 122.916 | [12 empty] | 24950 | 24950 | 202.9842 | [6 empty] | 5656 | 5656 | 0.95667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:34 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:31 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25346 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30092263 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35683306 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7968263 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 96 | 91 | 30096150 | 3887 | 93.288 | 3.887 | 6.6 | 6.6 | 2B | 0 | 0 | 1040 | 0 | 1058 | N/A | N/A | N/A | N/A | 35683908 | 602 | 154.8752 | 0% | 0% | 100% | 0% | 100% | 40% | 7969159 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 94 | 30099983 | 3833 | 91.992 | 3.833 | 7.7 | 7.7 | 2B | 0 | 0 | 997 | 0 | 1057 | N/A | N/A | N/A | N/A | 35684502 | 594 | 154.97 | 0% | 0% | 100% | 0% | 100% | 40% | 7970163 | 1004 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 99 | 92 | 30103788 | 3805 | 91.32 | 3.805 | 8.9 | 8.9 | 2B | 0 | 0 | 985 | 0 | 988 | N/A | N/A | N/A | N/A | 35685090 | 588 | 154.5335 | 0% | 0% | 100% | 0% | 100% | 40% | 7971291 | 1128 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 95 | 30107130 | 3342 | 80.208 | 3.342 | 9.5 | 9.5 | 2B | 0 | 0 | 969 | 0 | 988 | N/A | N/A | N/A | N/A | 35685654 | 564 | 168.7612 | 0% | 0% | 100% | 0% | 100% | 40% | 7971973 | 682 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 101 | 30110986 | 3856 | 92.544 | 3.856 | 9.5 | 9.5 | 2B | 0 | 0 | 1001 | 0 | 1009 | N/A | N/A | N/A | N/A | 35686212 | 558 | 144.7095 | 0% | 0% | 100% | 0% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 47.8989 | 19 | A ONG | 13.1 | 121 | 115 | 30115620 | 4634 | 111.216 | 4.634 | 9.5 | 9.5 | 2B | 0 | 0 | 1123 | 0 | 1109 | N/A | N/A | N/A | N/A | 35686920 | 708 | 152.7838 | 0% | 0% | 100% | 0% | 100% | 0% | 7971973 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 16.7 | 140 | 146 | 30121723 | 6103 | 146.472 | 6.103 | 9.4 | 9.4 | 3B | 0 | 1024 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35688224 | 1304 | 213.6654 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 30127741 | 6018 | 144.432 | 6.018 | 8.8 | 8.8 | 3B+1S | 0 | 1073 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35689548 | 1324 | 220.0066 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 152 | 30134072 | 6331 | 151.944 | 6.331 | 8.1 | 8.1 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35690956 | 1408 | 222.3977 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 30140474 | 6402 | 153.648 | 6.402 | 7.4 | 7.4 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35692372 | 1416 | 221.1809 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 144 | 30146235 | 5761 | 138.264 | 5.761 | 7.2 | 7.2 | 3B+1S | 0 | 1010 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35693660 | 1288 | 223.5723 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 142 | 30152597 | 6362 | 152.688 | 6.362 | 6.9 | 6.9 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35695058 | 1398 | 219.7422 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 30158289 | 5692 | 136.608 | 5.692 | 6.6 | 6.6 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35696356 | 1298 | 228.0394 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 30164509 | 6220 | 149.28 | 6.22 | 6.4 | 6.4 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35697764 | 1408 | 226.3666 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 30169945 | 5436 | 130.464 | 5.436 | 6.3 | 6.3 | 3B+1S | 0 | 986 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35699000 | 1236 | 227.3731 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 131 | 30175477 | 5532 | 132.768 | 5.532 | 6.2 | 6.2 | 3B+1S | 0 | 987 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35700260 | 1260 | 227.7657 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 137 | 30181012 | 5535 | 132.84 | 5.535 | 5.8 | 5.8 | 3B+1S | 0 | 1010 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35701532 | 1272 | 229.8103 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 126 | 30186632 | 5620 | 134.88 | 5.62 | 5.7 | 5.7 | 3B+1S | 0 | 1013 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35702796 | 1264 | 224.911 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 138 | 30192309 | 5677 | 136.248 | 5.677 | 5.6 | 5.6 | 3B+1S | 0 | 1012 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35704052 | 1256 | 221.2436 | 0% | 100% | 100% | 100% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 134 | 30197653 | 5344 | 128.256 | 5.344 | 4.7 | 4.7 | 2B+1S | 0 | 1081 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35705196 | 1144 | 214.0719 | 0% | 100% | 100% | 0% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 30202924 | 5271 | 126.504 | 5.271 | 3.9 | 3.9 | 2B+1S | 0 | 1049 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35706236 | 1040 | 197.306 | 0% | 100% | 100% | 0% | 100% | 0% | 7971973 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 30207894 | 4970 | 119.28 | 4.97 | 3.6 | 3.6 | 2B+1S | 0 | 1004 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35707275 | 1039 | 209.0543 | 0% | 100% | 100% | 0% | 100% | 0% | 7971973 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 99 | 30212141 | 4247 | 101.928 | 4.247 | 4.1 | 4.1 | 2B | 0 | 0 | 1061 | 0 | 1110 | N/A | N/A | N/A | N/A | 35707988 | 713 | 167.8832 | 0% | 0% | 100% | 0% | 100% | 25% | 7972506 | 533 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 97 | 30216137 | 3996 | 95.904 | 3.996 | 4.8 | 4.8 | 2B | 0 | 0 | 1024 | 0 | 1059 | N/A | N/A | N/A | N/A | 35708652 | 664 | 166.1662 | 0% | 0% | 100% | 0% | 100% | 25% | 7973103 | 597 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7917 | 123874 | 123874 | 123.874 | 123.874 | [12 empty] | 25346 | 25346 | 204.6111 | [6 empty] | 4840 | 4840 | 1.0433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:39 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:31 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:31 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:21PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30216137 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35708652 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7973103 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 11 | 11 | 11 | Automatic - Pressure Setting | 2.8169 | 4.2254 | 8.4507 | 14 | A.ONG | 11.4 | 117 | 90 | 30219952 | 3815 | 91.56 | 3.815 | 5.8 | 5.8 | 2B | 0 | 0 | 1048 | 0 | 1060 | N/A | N/A | N/A | N/A | 35709256 | 604 | 158.3224 | 0% | 0% | 100% | 0% | 100% | 35% | 7974053 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 89 | 30223657 | 3705 | 88.92 | 3.705 | 6.9 | 6.9 | 2B | 0 | 0 | 1022 | 0 | 1060 | N/A | N/A | N/A | N/A | 35709844 | 588 | 158.7045 | 0% | 0% | 100% | 0% | 100% | 35% | 7975117 | 1064 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 88 | 30227261 | 3604 | 86.496 | 3.604 | 8 | 8 | 2B | 0 | 0 | 1010 | 0 | 1060 | N/A | N/A | N/A | N/A | 35710419 | 575 | 159.545 | 0% | 0% | 100% | 0% | 100% | 35% | 7976276 | 1159 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 87 | 30230718 | 3457 | 82.968 | 3.457 | 9.2 | 9.2 | 2B | 0 | 0 | 1009 | 0 | 1009 | N/A | N/A | N/A | N/A | 35710968 | 549 | 158.8082 | 0% | 0% | 100% | 0% | 100% | 35% | 7977333 | 1057 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 93 | 30234494 | 3776 | 90.624 | 3.776 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 948 | N/A | N/A | N/A | N/A | 35711508 | 540 | 143.0085 | 0% | 0% | 100% | 0% | 100% | 35% | 7977627 | 294 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 102 | 30238725 | 4231 | 101.544 | 4.231 | 9.5 | 9.5 | 2B | 0 | 0 | 1079 | 0 | 1110 | N/A | N/A | N/A | N/A | 35712112 | 604 | 142.7558 | 0% | 0% | 100% | 0% | 100% | 0% | 7977627 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 147 | 30244894 | 6169 | 148.056 | 6.169 | 9.4 | 9.4 | 3B | 0 | 1022 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35713420 | 1308 | 212.0279 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 30251123 | 6229 | 149.496 | 6.229 | 8.9 | 8.9 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35714792 | 1372 | 220.2601 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 30257521 | 6398 | 153.552 | 6.398 | 8.3 | 8.3 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35716220 | 1428 | 223.1947 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 30263522 | 6001 | 144.024 | 6.001 | 7.8 | 7.8 | 3B+1S | 0 | 1054 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35717572 | 1352 | 225.2958 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 | 1.24 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 30269406 | 5884 | 141.216 | 5.884 | 7.6 | 7.6 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35718884 | 1312 | 222.9776 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 30275338 | 5932 | 142.368 | 5.932 | 7 | 7 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35720224 | 1340 | 225.8935 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 137 | 30281489 | 6151 | 147.624 | 6.151 | 6.7 | 6.7 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35721620 | 1396 | 226.955 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 144 | 30287309 | 5820 | 139.68 | 5.82 | 6.5 | 6.5 | 3B+1S | 0 | 1007 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35722948 | 1328 | 228.1787 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 30292941 | 5632 | 135.168 | 5.632 | 6.3 | 6.3 | 3B+1S | 0 | 987 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35724252 | 1304 | 231.5341 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 30298521 | 5580 | 133.92 | 5.58 | 6.2 | 6.2 | 3B+1S | 0 | 990 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35725516 | 1264 | 226.5233 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 30304229 | 5708 | 136.992 | 5.708 | 5.8 | 5.8 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35726836 | 1320 | 231.2544 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 30309778 | 5549 | 133.176 | 5.549 | 5.7 | 5.7 | 3B+1S | 0 | 980 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35728108 | 1272 | 229.2305 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 30315286 | 5508 | 132.192 | 5.508 | 5.6 | 5.6 | 3B+1S | 0 | 981 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35729316 | 1208 | 219.3174 | 0% | 100% | 100% | 100% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 126 | 30320680 | 5394 | 129.456 | 5.394 | 5.1 | 5.1 | 2B+1S | 0 | 1060 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35730404 | 1088 | 201.7056 | 0% | 100% | 100% | 0% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 30325821 | 5141 | 123.384 | 5.141 | 4.5 | 4.5 | 2B+1S | 0 | 1010 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35731424 | 1020 | 198.405 | 0% | 100% | 100% | 0% | 100% | 0% | 7977627 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 114 | 30330770 | 4949 | 118.776 | 4.949 | 4.2 | 4.2 | 2B+1S | 0 | 999 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35732412 | 988 | 199.6363 | 0% | 100% | 100% | 0% | 100% | 0% | 7977627 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 104 | 30334999 | 4229 | 101.496 | 4.229 | 4.8 | 4.8 | 2B | 0 | 0 | 1090 | 0 | 1078 | N/A | N/A | N/A | N/A | 35733136 | 724 | 171.1989 | 0% | 0% | 100% | 0% | 100% | 25% | 7978149 | 522 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 92 | 30339040 | 4041 | 96.984 | 4.041 | 5.1 | 5.1 | 2B | 0 | 0 | 1018 | 0 | 1047 | N/A | N/A | N/A | N/A | 35733788 | 652 | 161.3462 | 0% | 0% | 100% | 0% | 100% | 25% | 7978768 | 619 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.0833 | 122903 | 122903 | 122.903 | 122.903 | [12 empty] | 25136 | 25136 | 204.519 | [6 empty] | 5665 | 5665 | 1.0417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (25%) @ 12:01 AM
XCV1 CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:33 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:16 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:13 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | R. MALLARI / J. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25356 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30339040 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35733788 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7978768 |  | mg /l |  | Automatic - i2O | AI | R. MALLARI / J. GALINATO
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 109 | 84 | 30342725 | 3685 | 88.44 | 3.685 | 6.2 | 6.2 | 2B | 0 | 0 | 1004 | 0 | 1028 | N/A | N/A | N/A | N/A | 35734388 | 600 | 162.8223 | 0% | 0% | 100% | 0% | 100% | 30% | 7979560 | 792 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 84 | 30346270 | 3545 | 85.08 | 3.545 | 7.1 | 7.1 | 2B | 0 | 0 | 988 | 0 | 1008 | N/A | N/A | N/A | N/A | 35734932 | 544 | 153.4556 | 0% | 0% | 100% | 0% | 100% | 30% | 7980468 | 908 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 88 | 30349886 | 3616 | 86.784 | 3.616 | 8 | 8 | 2B | 0 | 0 | 986 | 0 | 1009 | N/A | N/A | N/A | N/A | 35735476 | 544 | 150.4425 | 0% | 0% | 100% | 0% | 100% | 30% | 7981346 | 878 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 88 | 30353540 | 3654 | 87.696 | 3.654 | 8.9 | 8.9 | 2B | 0 | 0 | 1005 | 0 | 990 | N/A | N/A | N/A | N/A | 35736020 | 544 | 148.8779 | 0% | 0% | 100% | 0% | 100% | 30% | 7982185 | 839 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 94 | 30357410 | 3870 | 92.88 | 3.87 | 9.5 | 9.5 | 2B | 0 | 0 | 930 | 0 | 927 | N/A | N/A | N/A | N/A | 35736564 | 544 | 140.5685 | 0% | 0% | 100% | 0% | 100% | 30% | 7982707 | 522 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 110 | 111 | 30361757 | 4347 | 104.328 | 4.347 | 9.5 | 9.5 | 2B | 0 | 0 | 107 | 0 | 110 | N/A | N/A | N/A | N/A | 35737140 | 576 | 132.5052 | 0% | 0% | 100% | 0% | 100% | 0% | 7982707 | 0 | 0.94 | Normal operation schedule | Error - General | E | J. GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 30368169 | 6412 | 153.888 | 6.412 | 9.3 | 9.3 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35738516 | 1376 | 214.5976 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 151 | 30373950 | 5781 | 138.744 | 5.781 | 8.9 | 8.9 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35739812 | 1296 | 224.1827 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 30379974 | 6024 | 144.576 | 6.024 | 8.4 | 8.4 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35741164 | 1352 | 224.4356 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 143 | 30386235 | 6261 | 150.264 | 6.261 | 7.8 | 7.8 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35742592 | 1428 | 228.0786 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 30392223 | 5988 | 143.712 | 5.988 | 7.4 | 7.4 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35743900 | 1308 | 218.4369 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 147 | 30398389 | 6166 | 147.984 | 6.166 | 6.8 | 6.8 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35745296 | 1396 | 226.4029 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 30404399 | 6010 | 144.24 | 6.01 | 6.1 | 6.1 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35746676 | 1380 | 229.6173 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 137 | 30410215 | 5816 | 139.584 | 5.816 | 5.9 | 5.9 | 3B+1S | 0 | 999 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35748018 | 1342 | 230.7428 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 30415755 | 5540 | 132.96 | 5.54 | 5.8 | 5.8 | 3B+1S | 0 | 991 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35749300 | 1282 | 231.4079 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 30421405 | 5650 | 135.6 | 5.65 | 5.7 | 5.7 | 3B+1S | 0 | 993 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35750628 | 1328 | 235.0442 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 30427174 | 5769 | 138.456 | 5.769 | 5.3 | 5.3 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35751964 | 1336 | 231.5826 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 134 | 30432779 | 5605 | 134.52 | 5.605 | 5.2 | 5.2 | 3B+1S | 0 | 979 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35753244 | 1280 | 228.3675 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 30438439 | 5660 | 135.84 | 5.66 | 5.1 | 5.1 | 3B+1S | 0 | 950 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35754540 | 1296 | 228.9753 | 0% | 100% | 100% | 100% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 132 | 30443903 | 5464 | 131.136 | 5.464 | 4.4 | 4.4 | 2B+1S | 0 | 1085 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35755652 | 1112 | 203.5139 | 0% | 100% | 100% | 0% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 30449284 | 5381 | 129.144 | 5.381 | 3.6 | 3.6 | 2B+1S | 0 | 1040 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35756732 | 1080 | 200.7062 | 0% | 100% | 100% | 0% | 100% | 0% | 7982707 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 123 | 30454272 | 4988 | 119.712 | 4.988 | 3.1 | 3.1 | 2B+1S | 0 | 999 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35757732 | 1000 | 200.4812 | 0% | 100% | 100% | 0% | 100% | 0% | 7982707 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 101 | 30458570 | 4298 | 103.152 | 4.298 | 3.6 | 3.6 | 2B | 0 | 0 | 1077 | 0 | 1085 | N/A | N/A | N/A | N/A | 35758476 | 744 | 173.1038 | 0% | 0% | 100% | 0% | 100% | 25% | 7983249 | 542 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 94 | 30462625 | 4055 | 97.32 | 4.055 | 4.4 | 4.4 | 2B | 0 | 0 | 1041 | 0 | 1045 | N/A | N/A | N/A | N/A | 35759144 | 668 | 164.7349 | 0% | 0% | 100% | 0% | 100% | 25% | 7983872 | 623 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5417 | 123585 | 123585 | 123.585 | 123.585 | [12 empty] | 25356 | 25356 | 205.1705 | [6 empty] | 5104 | 5104 | 0.95667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (30%) @ 12:01 AM
XCV1 CLOSED @ 4:39 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:40 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:45 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 27, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:35 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25388 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30462625 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35759144 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7983872 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 91 | 30466410 | 3785 | 90.84 | 3.785 | 5.4 | 5.4 | 2B | 0 | 0 | 1062 | 0 | 1047 | N/A | N/A | N/A | N/A | 35759764 | 620 | 163.8045 | 0% | 0% | 100% | 0% | 100% | 35% | 7984900 | 1028 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 89 | 30470055 | 3645 | 87.48 | 3.645 | 6.6 | 6.6 | 2B | 0 | 0 | 1044 | 0 | 1047 | N/A | N/A | N/A | N/A | 35760366 | 602 | 165.1578 | 0% | 0% | 100% | 0% | 100% | 35% | 7986014 | 1114 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 87 | 30473643 | 3588 | 86.112 | 3.588 | 7.8 | 7.8 | 2B | 0 | 0 | 1022 | 0 | 1047 | N/A | N/A | N/A | N/A | 35760926 | 560 | 156.0758 | 0% | 0% | 100% | 0% | 100% | 35% | 7987229 | 1215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 85 | 30477123 | 3480 | 83.52 | 3.48 | 9 | 9 | 2B | 0 | 0 | 1009 | 0 | 999 | N/A | N/A | N/A | N/A | 35761452 | 526 | 151.1494 | 0% | 0% | 100% | 0% | 100% | 35% | 7988244 | 1015 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 95 | 92 | 30480875 | 3752 | 90.048 | 3.752 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 957 | N/A | N/A | N/A | N/A | 35761988 | 536 | 142.8571 | 0% | 0% | 100% | 0% | 100% | 35% | 7988713 | 469 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 117 | 115 | 30485121 | 4246 | 101.904 | 4.246 | 9.5 | 9.5 | 2B | 0 | 0 | 1197 | 0 | 1008 | N/A | N/A | N/A | N/A | 35762580 | 592 | 139.4253 | 0% | 0% | 100% | 0% | 100% | 0% | 7988713 | 0 | 1.15 | Normal operation schedule | Error - General | E | D. GUANZON /
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 30491113 | 5992 | 143.808 | 5.992 | 9.4 | 9.4 | 3B | 0 | 1001 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35763860 | 1280 | 213.6182 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 30497030 | 5917 | 142.008 | 5.917 | 9 | 9 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35765180 | 1320 | 223.086 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 30503346 | 6316 | 151.584 | 6.316 | 8.4 | 8.4 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35766588 | 1408 | 222.9259 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 30509562 | 6216 | 149.184 | 6.216 | 7.9 | 7.9 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35767964 | 1376 | 221.3642 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 | 1.24 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 141 | 30515585 | 6023 | 144.552 | 6.023 | 7.5 | 7.5 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35769328 | 1364 | 226.4652 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 30521437 | 5852 | 140.448 | 5.852 | 7 | 7 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35770652 | 1324 | 226.2474 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 30527428 | 5991 | 143.784 | 5.991 | 6.6 | 6.6 | 3B+1S | 0 | 996 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35772012 | 1360 | 227.0072 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 137 | 30533308 | 5880 | 141.12 | 5.88 | 6.5 | 6.5 | 3B+1S | 0 | 992 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35773348 | 1336 | 227.2109 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 30538950 | 5642 | 135.408 | 5.642 | 6.4 | 6.4 | 3B+1S | 0 | 986 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35774644 | 1296 | 229.7058 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 30544450 | 5500 | 132 | 5.5 | 6.3 | 6.3 | 3B+1S | 0 | 994 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35775900 | 1256 | 228.3636 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 136 | 30550305 | 5855 | 140.52 | 5.855 | 5.9 | 5.9 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35777252 | 1352 | 230.9137 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 30556128 | 5823 | 139.752 | 5.823 | 5.6 | 5.6 | 3B+1S | 0 | 986 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35778572 | 1320 | 226.6873 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 141 | 30561769 | 5641 | 135.384 | 5.641 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35779852 | 1280 | 226.9101 | 0% | 100% | 100% | 100% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 130 | 30567303 | 5534 | 132.816 | 5.534 | 4.5 | 4.5 | 2B+1S | 0 | 1110 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35780960 | 1108 | 200.2168 | 0% | 100% | 100% | 0% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 128 | 30572839 | 5536 | 132.864 | 5.536 | 3.6 | 3.6 | 2B+1S | 0 | 1056 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35782052 | 1092 | 197.2543 | 0% | 100% | 100% | 0% | 100% | 0% | 7988713 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 119 | 30577906 | 5067 | 121.608 | 5.067 | 3.2 | 3.2 | 2B+1S | 0 | 1004 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35783068 | 1016 | 200.5131 | 0% | 100% | 100% | 0% | 100% | 0% | 7988713 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 105 | 30582248 | 4342 | 104.208 | 4.342 | 3.6 | 3.6 | 2B | 0 | 0 | 1113 | 0 | 1109 | N/A | N/A | N/A | N/A | 35783828 | 760 | 175.0345 | 0% | 0% | 100% | 0% | 100% | 25% | 7989163 | 450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 103 | 30586499 | 4251 | 102.024 | 4.251 | 4.3 | 4.3 | 2B | 0 | 0 | 1034 | 0 | 1110 | N/A | N/A | N/A | N/A | 35784532 | 704 | 165.6081 | 0% | 0% | 100% | 0% | 100% | 25% | 7989753 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.8333 | 123874 | 123874 | 123.874 | 123.874 | [12 empty] | 25388 | 25388 | 204.9502 | [6 empty] | 5881 | 5881 | 1.1033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (25%) @ 12:01 AM
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:36 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:18 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:35 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:22PM, NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | J.GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26176 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate |  | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30586499 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35784532 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7989753 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 109 | 95 | 30590439 | 3940 | 94.56 | 3.94 | 5 | 5 | 2B | 0 | 0 | 1038 | 0 | 1059 | N/A | N/A | N/A | N/A | 35785180 | 648 | 164.467 | 0% | 0% | 100% | 0% | 100% | 35% | 7990379 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 106 | 87 | 30594122 | 3683 | 88.392 | 3.683 | 5.7 | 5.7 | 2B | 0 | 0 | 981 | 0 | 1059 | N/A | N/A | N/A | N/A | 35785772 | 592 | 160.7385 | 0% | 0% | 100% | 0% | 100% | 35% | 7991053 | 674 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 | 85 | 30597764 | 3642 | 87.408 | 3.642 | 6.4 | 6.4 | 2B | 0 | 0 | 991 | 0 | 1008 | N/A | N/A | N/A | N/A | 35786344 | 572 | 157.0566 | 0% | 0% | 100% | 0% | 100% | 35% | 7991764 | 711 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 88 | 30601406 | 3642 | 87.408 | 3.642 | 7.2 | 7.2 | 2B | 0 | 0 | 978 | 0 | 1008 | N/A | N/A | N/A | N/A | 35786888 | 544 | 149.3685 | 0% | 0% | 100% | 0% | 100% | 35% | 7992459 | 695 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 152 | 95 | 30605041 | 3635 | 87.24 | 3.635 | 8.6 | 8.6 | 2B | 0 | 0 | 1056 | 0 | 1048 | N/A | N/A | N/A | N/A | 35787464 | 576 | 158.4594 | 0% | 0% | 100% | 0% | 100% | 35% | 7993909 | 1450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 113 | 30609312 | 4271 | 102.504 | 4.271 | 9.5 | 9.5 | 2B | 0 | 0 | 1133 | 0 | 1048 | N/A | N/A | N/A | N/A | 35788100 | 636 | 148.9113 | 0% | 0% | 100% | 0% | 100% | 35% | 7994788 | 879 | 1.34 | Normal operation schedule | Error - General | E | J.GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 148 | 30615234 | 5922 | 142.128 | 5.922 | 9.4 | 9.4 | 3B | 0 | 994 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35789368 | 1268 | 214.1169 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 30621561 | 6327 | 151.848 | 6.327 | 8.8 | 8.8 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35790768 | 1400 | 221.2739 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 30627773 | 6212 | 149.088 | 6.212 | 8.2 | 8.2 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35792144 | 1376 | 221.5068 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 30633935 | 6162 | 147.888 | 6.162 | 7.4 | 7.4 | 3B+1S | 0 | 1153 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35793524 | 1380 | 223.9533 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 30640486 | 6551 | 157.224 | 6.551 | 6.6 | 6.6 | 3B+1S | 0 | 1084 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35794992 | 1468 | 224.0879 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 151 | 30646568 | 6082 | 145.968 | 6.082 | 5.8 | 5.8 | 3B+1S | 0 | 1163 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35796388 | 1396 | 229.5298 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 30652347 | 5779 | 138.696 | 5.779 | 5.1 | 5.1 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35797708 | 1320 | 228.4132 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 146 | 30658539 | 6192 | 148.608 | 6.192 | 4.7 | 4.7 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35799108 | 1400 | 226.0982 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 145 | 30664425 | 5886 | 141.264 | 5.886 | 4.3 | 4.3 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35800446 | 1338 | 227.3191 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 30670327 | 5902 | 141.648 | 5.902 | 4 | 4 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35801802 | 1356 | 229.7526 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 30676293 | 5966 | 143.184 | 5.966 | 3.4 | 3.4 | 3B+1S | 0 | 1118 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35803176 | 1374 | 230.3051 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 30682084 | 5791 | 138.984 | 5.791 | 3.1 | 3.1 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35804512 | 1336 | 230.7028 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 30687849 | 5765 | 138.36 | 5.765 | 2.8 | 2.8 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35805828 | 1316 | 228.2741 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 135 | 30693378 | 5529 | 132.696 | 5.529 | 2.7 | 2.7 | 3B+1S | 0 | 991 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35807088 | 1260 | 227.8893 | 0% | 100% | 100% | 100% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 129 | 30698691 | 5313 | 127.512 | 5.313 | 2.3 | 2.3 | 2B+1S | 0 | 1061 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35808154 | 1066 | 200.6399 | 0% | 100% | 100% | 0% | 100% | 0% | 7994788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 124 | 30703974 | 5283 | 126.792 | 5.283 | 2.2 | 2.2 | 2B+1S | 0 | 968 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35809164 | 1010 | 191.1793 | 0% | 100% | 100% | 0% | 100% | 0% | 7994788 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 105 | 30708442 | 4468 | 107.232 | 4.468 | 2.9 | 2.9 | 2B | 0 | 0 | 1106 | 0 | 1160 | N/A | N/A | N/A | N/A | 35809988 | 824 | 184.4226 | 0% | 0% | 100% | 0% | 100% | 35% | 7995609 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 98 | 30712512 | 4070 | 97.68 | 4.07 | 4 | 4 | 2B | 0 | 0 | 1063 | 0 | 1109 | N/A | N/A | N/A | N/A | 35810708 | 720 | 176.9042 | 0% | 0% | 100% | 0% | 100% | 35% | 7996602 | 993 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.4167 | 126013 | 126013 | 126.013 | 126.013 | [12 empty] | 26176 | 26176 | 207.7246 | [6 empty] | 6849 | 6849 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 5:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:37 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:08 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:19 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:05 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:50 PM, NORMAL OPERATION
NORMAL OPERATION

## MAR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | DENNIS GUANZON
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25744 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30712512 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35810708 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 7996602 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 94 | 30716465 | 3953 | 94.872 | 3.953 | 5 | 5 | 2B | 0 | 0 | 1064 | 0 | 1088 | N/A | N/A | N/A | N/A | 35811404 | 696 | 176.0688 | 0% | 0% | 100% | 0% | 100% | 40% | 7997469 | 867 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 90 | 30720243 | 3778 | 90.672 | 3.778 | 6 | 6 | 2B | 0 | 0 | 1051 | 0 | 1058 | N/A | N/A | N/A | N/A | 35812040 | 636 | 168.343 | 0% | 0% | 100% | 0% | 100% | 40% | 7998483 | 1014 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 80 | 30723875 | 3632 | 87.168 | 3.632 | 7.1 | 7.1 | 2B | 0 | 0 | 1025 | 0 | 1048 | N/A | N/A | N/A | N/A | 35812644 | 604 | 166.2996 | 0% | 0% | 100% | 0% | 100% | 40% | 7999524 | 999 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 101 | 30727523 | 3648 | 87.552 | 3.648 | 8.1 | 8.1 | 2B | 0 | 0 | 1025 | 0 | 1038 | N/A | N/A | N/A | N/A | 35813236 | 592 | 162.2807 | 0% | 0% | 100% | 0% | 100% | 40% | 8000550 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 90 | 30731257 | 3734 | 89.616 | 3.734 | 9.5 | 9.5 | 2B | 0 | 0 | 948 | 0 | 949 | N/A | N/A | N/A | N/A | 35813804 | 568 | 152.1157 | 0% | 0% | 100% | 0% | 100% | 40% | 8001736 | 1186 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 22 | 15.493 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 112 | 108 | 30735561 | 4304 | 103.296 | 4.304 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 949 | N/A | N/A | N/A | N/A | 35814384 | 580 | 134.7584 | 0% | 0% | 100% | 0% | 100% | 0% | 8001736 | 0 | 1.34 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 143 | 30741473 | 5912 | 141.888 | 5.912 | 9.4 | 9.4 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35815648 | 1264 | 213.8024 | 0% | 0% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 144 | 30747122 | 5649 | 135.576 | 5.649 | 9.3 | 9.3 | 3B+1S | 0 | 986 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35816852 | 1204 | 213.1351 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 154 | 30753554 | 6432 | 154.368 | 6.432 | 9.1 | 9.1 | 3B+1S | 0 | 1055 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35818254 | 1402 | 217.9726 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 155 | 30759965 | 6411 | 153.864 | 6.411 | 8.5 | 8.5 | 3B+1S | 0 | 1074 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35819676 | 1422 | 221.8063 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 30765956 | 5991 | 143.784 | 5.991 | 8.1 | 8.1 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35821004 | 1328 | 221.6658 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 155 | 30772097 | 6141 | 147.384 | 6.141 | 7.4 | 7.4 | 3B+1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35822388 | 1384 | 225.3705 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 30778328 | 6231 | 149.544 | 6.231 | 6.9 | 6.9 | 3B+1S | 0 | 1059 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35823800 | 1412 | 226.6089 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 143 | 30784449 | 6121 | 146.904 | 6.121 | 6.5 | 6.5 | 3B+1S | 0 | 1024 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35825184 | 1384 | 226.1068 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 30789940 | 5491 | 131.784 | 5.491 | 6.2 | 6.2 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35826436 | 1252 | 228.0095 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 30796112 | 6172 | 148.128 | 6.172 | 5.9 | 5.9 | 3B+1S | 0 | 1022 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35827844 | 1408 | 228.127 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 30801834 | 5722 | 137.328 | 5.722 | 5.4 | 5.4 | 3B+1S | 0 | 1057 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35829172 | 1328 | 232.0867 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 140 | 30807683 | 5849 | 140.376 | 5.849 | 5.2 | 5.2 | 3B+1S | 0 | 1024 | 1196 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35830508 | 1336 | 228.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 30813201 | 5518 | 132.432 | 5.518 | 4.9 | 4.9 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35831760 | 1252 | 226.8938 | 0% | 100% | 100% | 100% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 133 | 30818768 | 5567 | 133.608 | 5.567 | 4 | 4 | 3B+1S | 0 | 1133 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35832892 | 1132 | 203.3411 | 0% | 100% | 100% | 0% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 127 | 30824175 | 5407 | 129.768 | 5.407 | 3.3 | 3.3 | 2B+1S | 0 | 1047 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35833956 | 1064 | 196.7819 | 0% | 100% | 100% | 0% | 100% | 0% | 8001736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 120 | 30829284 | 5109 | 122.616 | 5.109 | 2.9 | 2.9 | 2B+1S | 0 | 1004 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35834968 | 1012 | 198.0818 | 0% | 100% | 100% | 0% | 100% | 0% | 8001736 | 0 | 90 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 104 | 30833748 | 4464 | 107.136 | 4.464 | 3.5 | 3.5 | 2B | 0 | 0 | 1090 | 0 | 1110 | N/A | N/A | N/A | N/A | 35835756 | 788 | 176.5233 | 0% | 0% | 100% | 0% | 100% | 25% | 8002423 | 687 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 95 | 30837824 | 4076 | 97.824 | 4.076 | 4.4 | 4.4 | 2B | 0 | 0 | 1066 | 0 | 1088 | N/A | N/A | N/A | N/A | 35836452 | 696 | 170.7556 | 0% | 0% | 100% | 0% | 100% | 25% | 8003178 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.75 | 125312 | 125312 | 125.312 | 125.312 | [12 empty] | 25744 | 25744 | 205.4392 | [6 empty] | 6576 | 6534 | 15.9017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 7:31 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:21 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:20 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ :930 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | J. GALINATO / R. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26104 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30837824 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35836452 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8003178 |  | mg /l |  | Automatic - i2O | AI | J. GALINATO / R. MALLARI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 98 | 30841849 | 4025 | 96.6 | 4.025 | 5.5 | 5.5 | 2B | 0 | 0 | 1046 | 0 | 1078 | N/A | N/A | N/A | N/A | 35837132 | 680 | 168.9441 | 0% | 0% | 100% | 0% | 100% | 40% | 8004297 | 1119 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 30845565 | 3716 | 89.184 | 3.716 | 6.7 | 6.7 | 2B | 0 | 0 | 1037 | 0 | 1033 | N/A | N/A | N/A | N/A | 35837732 | 600 | 161.4639 | 0% | 0% | 100% | 0% | 100% | 40% | 8005531 | 1234 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 86 | 30849208 | 3643 | 87.432 | 3.643 | 8.3 | 8.3 | 2B | 0 | 0 | 1010 | 0 | 1018 | N/A | N/A | N/A | N/A | 35838316 | 584 | 160.3074 | 0% | 0% | 100% | 0% | 100% | 40% | 8006763 | 1232 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 89 | 30852869 | 3661 | 87.864 | 3.661 | 9.3 | 9.3 | 2B | 0 | 0 | 1000 | 0 | 1018 | N/A | N/A | N/A | N/A | 35838876 | 560 | 152.9637 | 0% | 0% | 100% | 0% | 100% | 40% | 8007924 | 1161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 91 | 30856624 | 3755 | 90.12 | 3.755 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 948 | N/A | N/A | N/A | N/A | 35839388 | 512 | 136.3515 | 0% | 0% | 100% | 0% | 100% | 40% | 8008011 | 87 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 30861320 | 4696 | 112.704 | 4.696 | 9.5 | 9.5 | 2B | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35840052 | 664 | 141.3969 | 0% | 0% | 100% | 0% | 100% | 0% | 8008011 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 150 | 30867423 | 6103 | 146.472 | 6.103 | 9.3 | 9.3 | 3B | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35841348 | 1296 | 212.3546 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 151 | 30873704 | 6281 | 150.744 | 6.281 | 8.8 | 8.8 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35842724 | 1376 | 219.0734 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 153 | 30879654 | 5950 | 142.8 | 5.95 | 7.9 | 7.9 | 3B+1S | 0 | 1152 | 1195 | 11185 | 1198 | N/A | N/A | N/A | N/A | 35844058 | 1334 | 224.2017 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 158 | 30886484 | 6830 | 163.92 | 6.83 | 6.9 | 6.9 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35845612 | 1554 | 227.5256 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 30893041 | 6557 | 157.368 | 6.557 | 5.9 | 5.9 | 3B+1S | 0 | 1152 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35847084 | 1472 | 224.4929 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 150 | 30899275 | 6234 | 149.616 | 6.234 | 5 | 5 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35848524 | 1440 | 230.9913 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 148 | 30905338 | 6063 | 145.512 | 6.063 | 4 | 4 | 3B+1S | 0 | 1122 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35849904 | 1380 | 227.6101 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 149 | 30911446 | 6108 | 146.592 | 6.108 | 3.3 | 3.3 | 3B+1S | 0 | 1053 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35851284 | 1380 | 225.9332 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 144 | 30917489 | 6043 | 145.032 | 6.043 | 3.1 | 3.1 | 3B+1S | 0 | 1165 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35852692 | 1408 | 232.9969 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 30923463 | 5974 | 143.376 | 5.974 | 3 | 3 | 3B+1S | 0 | 1180 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35854124 | 1432 | 239.7054 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 139 | 30929214 | 5751 | 138.024 | 5.751 | 2.4 | 2.4 | 3B+1S | 0 | 1174 | 1155 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35855536 | 1412 | 245.5225 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 138 | 30934981 | 5767 | 138.408 | 5.767 | 1.9 | 1.9 | 3B+1S | 0 | 1080 | 1155 | 1185 | 1170 | N/A | N/A | N/A | N/A | 35856880 | 1344 | 233.0501 | 0% | 100% | 100% | 100% | 100% | 0% | 8008011 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 62 | 43.662 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 18 | A ONG | 16.6 | 121 | 122 | 30940650 | 5669 | 136.056 | 5.669 | 1.3 | 1.3 | 3B | 0 | 0 | 1105 | 1185 | 1109 | N/A | N/A | N/A | N/A | 35858164 | 1284 | 226.495 | 0% | 0% | 100% | 100% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 62 | 43.662 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 18 | A ONG | 16.6 | 122 | 118 | 30945562 | 4912 | 117.888 | 4.912 | 1.3 | 1.3 | 2B | 0 | 0 | 1178 | 0 | 1190 | N/A | N/A | N/A | N/A | 35859124 | 960 | 195.4397 | 0% | 0% | 100% | 0% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A ONG | 16.1 | 126 | 122 | 30950544 | 4982 | 119.568 | 4.982 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1199 | N/A | N/A | N/A | N/A | 35860004 | 880 | 176.6359 | 0% | 0% | 100% | 0% | 100% | 0% | 8008011 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 64 | 45.0704 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 12.6 | 125 | 120 | 30955372 | 4828 | 115.872 | 4.828 | 1.3 | 1.3 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35860924 | 920 | 190.5551 | 0% | 0% | 100% | 0% | 100% | 0% | 8008011 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 111 | 30960281 | 4909 | 117.816 | 4.909 | 1.9 | 1.9 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 35861764 | 840 | 171.1143 | 0% | 0% | 100% | 0% | 100% | 35% | 8008618 | 607 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 112 | 30964819 | 4538 | 108.912 | 4.538 | 2.9 | 2.9 | 2B | 0 | 0 | 1162 | 0 | 1162 | N/A | N/A | N/A | N/A | 35862556 | 792 | 174.5262 | 0% | 0% | 100% | 0% | 100% | 35% | 8009503 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.875 | 126995 | 126995 | 126.995 | 126.995 | [12 empty] | 26104 | 26104 | 205.5514 | [6 empty] | 6325 | 6325 | 1.085 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:02 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
Conducted the Occular inspection with the HOMETRUST CORP/ELECTRICAL EQUIPMENT AND SYSTEM INTEGRATION / EXPONENT will be assisted by Sir Michael Buligan and Sir Gerry Bautista and Sir Arturo Trinidad arrived at 10:20am to 10:50am
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:32 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV4 - OPENED 10% @ 2:23PM DUE TO LOW WATER LEVEL ON RESERVOIR.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:23 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 6:48PM DUE TO LOW WATER LEVEL ON RESERVOIR. (1.3M)
Target Discharge Pressure set to 62 psi @ 6:48 pm due to low water level
BP2 - STOPPED @ 7:01 PM DUE TO LOW SUCTION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:50 PM, NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr.Edmundo Llagas Jr (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## MAR 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | J. GALINATO / R. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-03-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 20712 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 30964819 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35862556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8009503 |  | mg /l |  | Automatic - i2O | AI | J. GALINATO / R. MALLARI
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 101 | 30969195 | 4376 | 105.024 | 4.376 | 4.1 | 4.1 | 2B | 0 | 0 | 1115 | 0 | 1128 | N/A | N/A | N/A | N/A | 35863340 | 784 | 179.159 | 0% | 0% | 100% | 0% | 100% | 50% | 8010637 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 97 | 30973355 | 4160 | 99.84 | 4.16 | 5.6 | 5.6 | 2B | 0 | 0 | 1082 | 0 | 1100 | N/A | N/A | N/A | N/A | 35864069 | 729 | 175.2404 | 0% | 0% | 100% | 0% | 100% | 50% | 8011896 | 1259 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 98 | 30977463 | 4108 | 98.592 | 4.108 | 7 | 7 | 2B | 0 | 0 | 1068 | 0 | 1059 | N/A | N/A | N/A | N/A | 35864756 | 687 | 167.2347 | 0% | 0% | 100% | 0% | 100% | 50% | 8013333 | 1437 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 94 | 30981305 | 3842 | 92.208 | 3.842 | 8.2 | 8.2 | 2B | 0 | 0 | 1066 | 0 | 1058 | N/A | N/A | N/A | N/A | 35865376 | 620 | 161.3743 | 0% | 0% | 100% | 0% | 100% | 50% | 8014549 | 1216 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 140 | 103 | 30985513 | 4208 | 100.992 | 4.208 | 9.2 | 9.2 | 2B | 0 | 0 | 1075 | 0 | 1078 | N/A | N/A | N/A | N/A | 35866048 | 672 | 159.6958 | 0% | 0% | 100% | 0% | 100% | 50% | 8015518 | 969 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 125 | 123 | 30990121 | 4608 | 110.592 | 4.608 | 9.5 | 9.5 | 2B | 0 | 0 | 1184 | 0 | 1079 | N/A | N/A | N/A | N/A | 35866724 | 676 | 146.7014 | 0% | 0% | 100% | 0% | 100% | 50% | 8015673 | 155 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 154 | 30996413 | 6292 | 151.008 | 6.292 | 9.4 | 9.4 | 3B | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35868020 | 1296 | 205.9758 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 159 | 31002902 | 6489 | 155.736 | 6.489 | 8.9 | 8.9 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35869424 | 1404 | 216.3662 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 142 | 31009372 | 6470 | 155.28 | 6.47 | 8.1 | 8.1 | 3B+1S | 0 | 1177 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35870840 | 1416 | 218.8563 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 161 | 31015609 | 6237 | 149.688 | 6.237 | 7.4 | 7.4 | 3B+1S | 0 | 1169 | 1190 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35872221 | 1381 | 221.4206 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 | 1.17 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 152 | 31022110 | 6501 | 156.024 | 6.501 | 6.8 | 6.8 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35873652 | 1431 | 220.12 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 150 | 31028204 | 6094 | 146.256 | 6.094 | 6 | 6 | 3B+1S | 0 | 1178 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35875020 | 1368 | 224.4831 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 31034207 | 6003 | 144.072 | 6.003 | 5.5 | 5.5 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35876354 | 1334 | 222.2222 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 148 | 31040358 | 6151 | 147.624 | 6.151 | 5.2 | 5.2 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35877748 | 1394 | 226.6298 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 31046442 | 6084 | 146.016 | 6.084 | 5 | 5 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35879133 | 1385 | 227.6463 | 0% | 100% | 100% | 100% | 100% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 0 | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 38 | 55 | 31049526 | 3084 | 74.016 | 3.084 | 3.8 | 3.8 | 3B+1S | 0 | 782 | 0 | 0 | 989 | N/A | N/A | N/A | N/A | 35879708 | 575 | 186.4462 | 0% | 100% | 0% | 0% | 100% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 0 | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 37 | 50 | 31051885 | 2359 | 56.616 | 2.359 | 3.1 | 3.1 | 3B+1S | 0 | 695 | 0 | 0 | 987 | N/A | N/A | N/A | N/A | 35880056 | 348 | 147.5201 | 0% | 100% | 0% | 0% | 100% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 0 | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 32 | 48 | 31053917 | 2032 | 48.768 | 2.032 | 2.5 | 2.5 | 3B+1S | 0 | 839 | 0 | 0 | 916 | N/A | N/A | N/A | N/A | 35880356 | 300 | 147.6378 | 0% | 100% | 0% | 0% | 100% | 0% | 8015673 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 0 | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 0 | 25 | 31055526 | 1609 | 38.616 | 1.609 | 1.6 | 1.6 | 3B | 0 | 902 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 35880612 | 256 | 159.105 | 0% | 100% | 0% | 0% | 0% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 0 | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 66 | 98 | 31055526 | 0 | 0 | 0 | 1.3 | 1.3 | 2B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 35880612 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 63 | 31056652 | 1126 | 27.024 | 1.126 | 1.3 | 1.3 | 2B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 35880772 | 160 | 142.0959 | 0% | 0% | 0% | 0% | 0% | 0% | 8015673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 129 | 31061507 | 4855 | 116.52 | 4.855 | 1.3 | 1.3 | 2B | 0 | 0 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 35881572 | 800 | 164.7786 | 0% | 0% | 100% | 0% | 100% | 0% | 8015673 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 111 | 31066331 | 4824 | 115.776 | 4.824 | 2.3 | 2.3 | 2B | 0 | 0 | 1130 | 0 | 1149 | N/A | N/A | N/A | N/A | 35882444 | 872 | 180.7629 | 0% | 0% | 100% | 0% | 100% | 35% | 8016554 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 111 | 31070953 | 4622 | 110.928 | 4.622 | 3.4 | 3.4 | 2B | 0 | 0 | 1121 | 0 | 1149 | N/A | N/A | N/A | N/A | 35883268 | 824 | 178.2778 | 0% | 0% | 100% | 0% | 100% | 35% | 8017655 | 1101 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 110.75 | 106134 | 106134 | 106.134 | 106.134 | [12 empty] | 20712 | 20712 | 195.1495 | [6 empty] | 8152 | 8152 | 1.06 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Joyjl Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 5:06 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET PRESSURE
SP2 - STARTED @ 6:43 AM TO MEET 83 PSI TARGET PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (MARCH 1, 2015) as per request of Engr. Frances Joyjl Morla(SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:00 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 PM , NORMAL OPERATION
BP2 - STOPPED @ 3:12PM DUE TO LOW SUCTION PRESSURE
BP1 - STOPPED @ 3:30PM DUE TO LOW SUCTION AS PER INSTRUCTION OF ENGR. BULIGAN
BP3 - STOPPED @ 6:38PM DUE TO LOW SUCTION PRESSURE
SP2 - STOPPED @ 7:12 PM DUE TO LOW WATER LEVEL@ THE RESERVOIR
BP3-STARTED @ 8:40 PM AS PER INSTRUCTION OF ENGR ALVIN CRUZ (SPM)
BP1-STARTED @ 9:01 PM TO INCREASE DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:36 PM , NORMAL OPERATION