## APR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26132 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31070953 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35883268 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8017655 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 141 | 108 | 31075414 | 4461 | 107.064 | 4.461 | 4.7 | 4.7 | 2B | 0 | 0 | 1121 | 0 | 1130 | N/A | N/A | N/A | N/A | 35884064 | 796 | 178.4353 | 0% | 0% | 100% | 0% | 100% | 50% | 8018796 | 1141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 143 | 106 | 31079866 | 4452 | 106.848 | 4.452 | 6.1 | 6.1 | 2B | 0 | 0 | 1106 | 0 | 1110 | N/A | N/A | N/A | N/A | 35884824 | 760 | 170.7098 | 0% | 0% | 100% | 0% | 100% | 50% | 8020133 | 1337 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 137 | 109 | 31084252 | 4386 | 105.264 | 4.386 | 8.3 | 8.3 | 2B | 0 | 0 | 1040 | 0 | 1088 | N/A | N/A | N/A | N/A | 35885546 | 722 | 164.6147 | 0% | 0% | 100% | 0% | 100% | 50% | 8021609 | 1476 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 139 | 102 | 31088381 | 4129 | 99.096 | 4.129 | 9.1 | 9.1 | 2B | 0 | 0 | 980 | 0 | 978 | N/A | N/A | N/A | N/A | 35886204 | 658 | 159.3606 | 0% | 0% | 100% | 0% | 100% | 50% | 8023011 | 1402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 104 | 31092606 | 4225 | 101.4 | 4.225 | 9.5 | 9.5 | 2B | 0 | 0 | 1045 | 0 | 1059 | N/A | N/A | N/A | N/A | 35886796 | 592 | 140.1183 | 0% | 0% | 100% | 0% | 100% | 50% | 8023353 | 342 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 21 | 14.7887 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 119 | 31097271 | 4665 | 111.96 | 4.665 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1110 | N/A | N/A | N/A | N/A | 35887428 | 632 | 135.477 | 0% | 0% | 100% | 0% | 100% | 0% | 8023353 | 0 | 0.98 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 147 | 31103696 | 6425 | 154.2 | 6.425 | 9.4 | 9.4 | 3B | 0 | 1022 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35888772 | 1344 | 209.1829 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 149 | 31109904 | 6208 | 148.992 | 6.208 | 8.9 | 8.9 | 3B+1S | 0 | 1031 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35890124 | 1352 | 217.7835 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 151 | 31116125 | 6221 | 149.304 | 6.221 | 8.3 | 8.3 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35891512 | 1388 | 223.1153 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 31122383 | 6258 | 150.192 | 6.258 | 7.6 | 7.6 | 3B+1S | 0 | 1144 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 35892918 | 1406 | 224.6724 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 31128672 | 6289 | 150.936 | 6.289 | 6.7 | 6.7 | 3B+1S | 0 | 1152 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35894324 | 1406 | 223.565 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 31134747 | 6075 | 145.8 | 6.075 | 5.9 | 5.9 | 3B+1S | 0 | 1110 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35895732 | 1408 | 231.7695 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 140 | 31140747 | 6000 | 144 | 6 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35897130 | 1398 | 233 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 31146525 | 5778 | 138.672 | 5.778 | 5.2 | 5.2 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35898539 | 1409 | 243.856 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 31152201 | 5676 | 136.224 | 5.676 | 5 | 5 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35899740 | 1201 | 211.5927 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 131 | 31158118 | 5917 | 142.008 | 5.917 | 4.9 | 4.9 | 3B+1S | 0 | 1081 | 1146 | 1185 | 1148 | N/A | N/A | N/A | N/A | 35901108 | 1368 | 231.1982 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 131 | 31163662 | 5544 | 133.056 | 5.544 | 4.5 | 4.5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35902396 | 1288 | 232.3232 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 31169214 | 5552 | 133.248 | 5.552 | 4.1 | 4.1 | 3B+1S | 0 | 1037 | 1186 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35903706 | 1310 | 235.951 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 121 | 120 | 31174523 | 5309 | 127.416 | 5.309 | 4 | 4 | 3B+1S | 0 | 1048 | 1189 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35904908 | 1202 | 226.408 | 0% | 100% | 100% | 100% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 125 | 31180101 | 5578 | 133.872 | 5.578 | 3.1 | 3.1 | 2B+1S | 0 | 1069 | 1187 | 0 | 1170 | N/A | N/A | N/A | N/A | 35906032 | 1124 | 201.5059 | 0% | 100% | 100% | 0% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 148 | 31184882 | 4781 | 114.744 | 4.781 | 2.7 | 2.7 | 2B+1S | 0 | 1034 | 1186 | 0 | 1170 | N/A | N/A | N/A | N/A | 35906974 | 942 | 197.0299 | 0% | 100% | 100% | 0% | 100% | 0% | 8023353 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 115 | 31189970 | 5088 | 122.112 | 5.088 | 2.5 | 2.5 | 2B+1S | 0 | 1019 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35907980 | 1006 | 197.7201 | 0% | 100% | 100% | 0% | 100% | 0% | 8023353 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 97 | 31193944 | 3974 | 95.376 | 3.974 | 3.3 | 3.3 | 2B | 0 | 0 | 1074 | 0 | 1109 | N/A | N/A | N/A | N/A | 35908684 | 704 | 177.1515 | 0% | 0% | 100% | 0% | 100% | 35% | 8024207 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 98 | 31198209 | 4265 | 102.36 | 4.265 | 4.6 | 4.6 | 2B | 0 | 0 | 1069 | 0 | 1077 | N/A | N/A | N/A | N/A | 35909400 | 716 | 167.8781 | 0% | 0% | 100% | 0% | 100% | 35% | 8025263 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.875 | 127256 | 127256 | 127.256 | 127.256 | [12 empty] | 26132 | 26132 | 205.3498 | [6 empty] | 7608 | 7608 | 6.03 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:35 AM,NORMAL OPERATION
XCV1 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:05 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:10 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (APRIL 2, 2015) as per request of Engr. Frances Joyjl Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:23 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:23 PM , NORMAL OPERATION and assisted the EXPONENT PERSONNEL
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:50 PM,NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24028 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31198209 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35909400 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8025263 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 104 | 31202233 | 4024 | 96.576 | 4.024 | 5.7 | 5.7 | 2B | 0 | 0 | 1025 | 0 | 1078 | N/A | N/A | N/A | N/A | 35910068 | 668 | 166.004 | 0% | 0% | 100% | 0% | 100% | 40% | 8026399 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 31206169 | 3936 | 94.464 | 3.936 | 6.9 | 6.9 | 2B | 0 | 0 | 1001 | 0 | 1079 | N/A | N/A | N/A | N/A | 35910700 | 632 | 160.5691 | 0% | 0% | 100% | 0% | 100% | 40% | 8027554 | 1155 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 31209996 | 3827 | 91.848 | 3.827 | 8.7 | 8.7 | 2B | 0 | 0 | 986 | 0 | 1008 | N/A | N/A | N/A | N/A | 35911298 | 598 | 156.2582 | 0% | 0% | 100% | 0% | 100% | 40% | 8028895 | 1341 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 88 | 31213517 | 3521 | 84.504 | 3.521 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 1008 | N/A | N/A | N/A | N/A | 35911846 | 548 | 155.6376 | 0% | 0% | 100% | 0% | 100% | 40% | 8029961 | 1066 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 85 | 31217072 | 3555 | 85.32 | 3.555 | 9.5 | 9.5 | 2B | 0 | 0 | 885 | 0 | 886 | N/A | N/A | N/A | N/A | 35912278 | 432 | 121.519 | 0% | 0% | 100% | 0% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 27 | 19.0141 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 107 | 31221163 | 4091 | 98.184 | 4.091 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 1009 | N/A | N/A | N/A | N/A | 35912752 | 474 | 115.8641 | 0% | 0% | 100% | 0% | 100% | 0% | 8029961 | 0 | 0.95 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 141 | 31226693 | 5530 | 132.72 | 5.53 | 9.5 | 9.5 | 3B | 0 | 0 | 1080 | 1185 | 1109 | N/A | N/A | N/A | N/A | 35913792 | 1040 | 188.0651 | 0% | 0% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 144 | 31232472 | 5779 | 138.696 | 5.779 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1155 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35914952 | 1160 | 200.7268 | 0% | 0% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 146 | 144 | 31238483 | 6011 | 144.264 | 6.011 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35916212 | 1260 | 209.6157 | 0% | 0% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 31244492 | 6009 | 144.216 | 6.009 | 9.3 | 9.3 | 3B+1S | 0 | 997 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35917544 | 1332 | 221.6675 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 147 | 31250524 | 6032 | 144.768 | 6.032 | 9.1 | 9.1 | 3B+1S | 0 | 983 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35918864 | 1320 | 218.8329 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 31256592 | 6068 | 145.632 | 6.068 | 8.8 | 8.8 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35920244 | 1380 | 227.4225 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 31262492 | 5900 | 141.6 | 5.9 | 8.4 | 8.4 | 3B+1S | 0 | 984 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35921540 | 1296 | 219.661 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 31268355 | 5863 | 140.712 | 5.863 | 8.2 | 8.2 | 3B+1S | 0 | 994 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35922884 | 1344 | 229.2342 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 31274001 | 5646 | 135.504 | 5.646 | 8 | 8 | 3B+1S | 0 | 982 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35924196 | 1312 | 232.3769 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 31279494 | 5493 | 131.832 | 5.493 | 7.9 | 7.9 | 3B+1S | 0 | 971 | 1196 | 1185 | 1190 | N/A | N/A | N/A | N/A | 35925476 | 1280 | 233.0238 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 31284802 | 5308 | 127.392 | 5.308 | 7.6 | 7.6 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35926708 | 1232 | 232.1025 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 31290473 | 5671 | 136.104 | 5.671 | 7.5 | 7.5 | 3B+1S | 0 | 957 | 1175 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35927988 | 1280 | 225.7098 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 135 | 31296033 | 5560 | 133.44 | 5.56 | 7.4 | 7.4 | 3B+1S | 0 | 980 | 1175 | 1185 | 1138 | N/A | N/A | N/A | N/A | 35929228 | 1240 | 223.0216 | 0% | 100% | 100% | 100% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 129 | 31301336 | 5303 | 127.272 | 5.303 | 6.7 | 6.7 | 2B+1S | 0 | 1027 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 35930276 | 1048 | 197.624 | 0% | 100% | 100% | 0% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 121 | 31306501 | 5165 | 123.96 | 5.165 | 6.3 | 6.3 | 2B+1S | 0 | 984 | 1197 | 0 | 1170 | N/A | N/A | N/A | N/A | 35931280 | 1004 | 194.3853 | 0% | 100% | 100% | 0% | 100% | 0% | 8029961 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 19 | 13.3803 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 115 | 31311153 | 4652 | 111.648 | 4.652 | 6.2 | 6.2 | 2B+1S | 0 | 954 | 1136 | 0 | 1130 | N/A | N/A | N/A | N/A | 35932136 | 856 | 184.0069 | 0% | 100% | 100% | 0% | 100% | 0% | 8029961 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 104 | 31315447 | 4294 | 103.056 | 4.294 | 6.8 | 6.8 | 2B | 0 | 0 | 1054 | 0 | 1058 | N/A | N/A | N/A | N/A | 35932838 | 702 | 163.4839 | 0% | 0% | 100% | 0% | 100% | 25% | 8030556 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 92 | 31319401 | 3954 | 94.896 | 3.954 | 7.7 | 7.7 | 2B | 0 | 0 | 994 | 0 | 998 | N/A | N/A | N/A | N/A | 35933428 | 590 | 149.216 | 0% | 0% | 100% | 0% | 100% | 25% | 8031379 | 823 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.125 | 121192 | 121192 | 121.192 | 121.192 | [12 empty] | 24028 | 24028 | 198.2639 | [6 empty] | 6116 | 6116 | 6.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM , NORMAL OPERATION
SP2 - STARTED @ 9:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:23 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01pm to 5am (APRIL 3, 2015) as per request of Engr. Frances Joyjl Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
MR. MELANIO MARIONO AND COMPANY OF TELEMETRY ARRIVED @ 12:20PM FOR SIM CARD REPLACEMENT AT GP
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:22 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:35 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 21978 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31319401 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35933428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8031379 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 111 | 88 | 31323159 | 3758 | 90.192 | 3.758 | 8.5 | 8.5 | 2B | 0 | 0 | 1019 | 0 | 1009 | N/A | N/A | N/A | N/A | 35934004 | 576 | 153.273 | 0% | 0% | 100% | 0% | 100% | 30% | 8032161 | 782 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 87 | 31326839 | 3680 | 88.32 | 3.68 | 9.4 | 9.4 | 2B | 0 | 0 | 980 | 0 | 1008 | N/A | N/A | N/A | N/A | 35934544 | 540 | 146.7391 | 0% | 0% | 100% | 0% | 100% | 30% | 8033015 | 854 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 86 | 31330450 | 3611 | 86.664 | 3.611 | 9.5 | 9.5 | 2B | 0 | 0 | 890 | 0 | 1008 | N/A | N/A | N/A | N/A | 35935028 | 484 | 134.0349 | 0% | 0% | 100% | 0% | 100% | 30% | 8033147 | 132 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 33 | 23.2394 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 88 | 31334035 | 3585 | 86.04 | 3.585 | 9.5 | 9.5 | 2B | 0 | 0 | 874 | 0 | 1008 | N/A | N/A | N/A | N/A | 35935470 | 442 | 123.2915 | 0% | 0% | 100% | 0% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 38 | 26.7606 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 87 | 83 | 31337594 | 3559 | 85.416 | 3.559 | 9.5 | 9.5 | 2B | 0 | 0 | 793 | 0 | 857 | N/A | N/A | N/A | N/A | 35935866 | 396 | 111.2672 | 0% | 0% | 100% | 0% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 30 | 21.1268 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 100 | 102 | 31341420 | 3826 | 91.824 | 3.826 | 9.5 | 9.5 | 2B | 0 | 0 | 952 | 0 | 958 | N/A | N/A | N/A | N/A | 35936230 | 364 | 95.1385 | 0% | 0% | 100% | 0% | 100% | 0% | 8033147 | 0 | 1.05 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 18 | 12.6761 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 138 | 31346738 | 5318 | 127.632 | 5.318 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1109 | N/A | N/A | N/A | N/A | 35937224 | 994 | 186.9124 | 0% | 0% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 137 | 31352399 | 5661 | 135.864 | 5.661 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1160 | N/A | N/A | N/A | N/A | 35938332 | 1108 | 195.7251 | 0% | 0% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 144 | 31358258 | 5859 | 140.616 | 5.859 | 9.5 | 9.5 | 3B | 0 | 0 | 1173 | 1185 | 1179 | N/A | N/A | N/A | N/A | 35939524 | 1192 | 203.4477 | 0% | 0% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 147 | 145 | 31364182 | 5924 | 142.176 | 5.924 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35940772 | 1248 | 210.6685 | 0% | 0% | 100% | 100% | 100% | 0% | 8033147 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 147 | 144 | 31370155 | 5973 | 143.352 | 5.973 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35942048 | 1276 | 213.628 | 0% | 0% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 31376053 | 5898 | 141.552 | 5.898 | 9.2 | 9.2 | 3B+1S | 0 | 991 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 35943324 | 1276 | 216.3445 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 135 | 31381918 | 5865 | 140.76 | 5.865 | 8.9 | 8.9 | 3B+1S | 0 | 1007 | 1125 | 1185 | 1129 | N/A | N/A | N/A | N/A | 35944588 | 1264 | 215.5158 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 133 | 31387553 | 5635 | 135.24 | 5.635 | 8.6 | 8.6 | 3B+1S | 0 | 995 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35945788 | 1200 | 212.9547 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 132 | 31392928 | 5375 | 129 | 5.375 | 8.4 | 8.4 | 3B+1S | 0 | 967 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35946948 | 1160 | 215.814 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 129 | 31398161 | 5233 | 125.592 | 5.233 | 8.3 | 8.3 | 3B+1S | 0 | 973 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35948096 | 1148 | 219.377 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 130 | 31403604 | 5443 | 130.632 | 5.443 | 8 | 8 | 3B+1S | 0 | 990 | 1126 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35949284 | 1188 | 218.262 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 123 | 129 | 31408832 | 5228 | 125.472 | 5.228 | 7.8 | 7.8 | 3B+1S | 0 | 995 | 1104 | 1185 | 1057 | N/A | N/A | N/A | N/A | 35950380 | 1096 | 209.6404 | 0% | 100% | 100% | 100% | 100% | 0% | 8033147 | 0 | 0.69 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 14 | 9.8592 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 118 | 131 | 31414365 | 5533 | 132.792 | 5.533 | 7.1 | 7.1 | 2B+1S | 0 | 1034 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 35951436 | 1056 | 190.8549 | 0% | 100% | 100% | 0% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 125 | 31419536 | 5171 | 124.104 | 5.171 | 6.8 | 6.8 | 2B+1S | 0 | 967 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 35952444 | 1008 | 194.9333 | 0% | 100% | 100% | 0% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 121 | 31424534 | 4998 | 119.952 | 4.998 | 6.5 | 6.5 | 2B+1S | 0 | 957 | 1176 | 0 | 1171 | N/A | N/A | N/A | N/A | 35953388 | 944 | 188.8756 | 0% | 100% | 100% | 0% | 100% | 0% | 8033147 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 22 | 15.493 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 110 | 31429299 | 4765 | 114.36 | 4.765 | 6.4 | 6.4 | 2B+1S | 0 | 954 | 1115 | 0 | 1110 | N/A | N/A | N/A | N/A | 35954248 | 860 | 180.4827 | 0% | 100% | 100% | 0% | 100% | 0% | 8033147 | 0 | 0.73 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 95 | 31433484 | 4185 | 100.44 | 4.185 | 7 | 7 | 2B | 0 | 0 | 985 | 0 | 1008 | N/A | N/A | N/A | N/A | 35954892 | 644 | 153.8829 | 0% | 0% | 100% | 0% | 100% | 25% | 8033794 | 647 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 106 | 89 | 31437210 | 3726 | 89.424 | 3.726 | 7.8 | 7.8 | 2B | 0 | 0 | 980 | 0 | 969 | N/A | N/A | N/A | N/A | 35955406 | 514 | 137.9495 | 0% | 0% | 100% | 0% | 100% | 25% | 8034600 | 806 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.5 | 117809 | 117809 | 117.809 | 117.809 | [12 empty] | 21978 | 21978 | 186.5562 | [6 empty] | 3221 | 3221 | 0.965 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (30%) @ 12:01 AM
XCV1 CLOSED @ 2:09 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,846
GENSET 1 WARMUP EXERCISED @ 10:29PM / STOPPED @ 10:39PM
GENSET 2 WARMUP EXERCISED @ 10:19PM / STOPPED @ 10:29PM
SP2 - STARTED @ 11:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01pm to 5am (APRIL 4, 2015) as per request of Engr. Frances Joyjl Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81 psi @ 12:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:28 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 6:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:19 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:45 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23928 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31437210 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35955406 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8034600 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 106 | 31440919 | 3709 | 89.016 | 3.709 | 8.7 | 8.7 | 2B | 0 | 0 | 914 | 0 | 968 | N/A | N/A | N/A | N/A | 35955908 | 502 | 135.3465 | 0% | 0% | 100% | 0% | 100% | 30% | 8035414 | 814 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 102 | 31444602 | 3683 | 88.392 | 3.683 | 9.5 | 9.5 | 2B | 0 | 0 | 902 | 0 | 968 | N/A | N/A | N/A | N/A | 35956396 | 488 | 132.5007 | 0% | 0% | 100% | 0% | 100% | 30% | 8036196 | 782 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 89 | 31448243 | 3641 | 87.384 | 3.641 | 9.5 | 9.5 | 2B | 0 | 0 | 878 | 0 | 968 | N/A | N/A | N/A | N/A | 35956882 | 486 | 133.4798 | 0% | 0% | 100% | 0% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 84 | 31451778 | 3535 | 84.84 | 3.535 | 9.5 | 9.5 | 2B | 0 | 0 | 834 | 0 | 968 | N/A | N/A | N/A | N/A | 35957344 | 462 | 130.6931 | 0% | 0% | 100% | 0% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 36 | 25.3521 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 89 | 83 | 31455148 | 3370 | 80.88 | 3.37 | 9.5 | 9.5 | 2B | 0 | 0 | 829 | 0 | 846 | N/A | N/A | N/A | N/A | 35957716 | 372 | 110.3858 | 0% | 0% | 100% | 0% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 29 | 20.4225 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 111 | 107 | 31459229 | 4081 | 97.944 | 4.081 | 9.5 | 9.5 | 2B | 0 | 0 | 979 | 0 | 998 | N/A | N/A | N/A | N/A | 35958156 | 440 | 107.8167 | 0% | 0% | 100% | 0% | 100% | 0% | 8036196 | 0 | 0.78 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 31464878 | 5649 | 135.576 | 5.649 | 9.5 | 9.5 | 3B | 0 | 0 | 1142 | 1185 | 1148 | N/A | N/A | N/A | N/A | 35959162 | 1006 | 178.0846 | 0% | 0% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 150 | 143 | 31470950 | 6072 | 145.728 | 6.072 | 9.5 | 9.5 | 3B | 0 | 0 | 1182 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35960367 | 1205 | 198.4519 | 0% | 0% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 146 | 152 | 31477036 | 6086 | 146.064 | 6.086 | 9.4 | 9.4 | 3B+1S | 0 | 995 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35961756 | 1389 | 228.2287 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 152 | 31483303 | 6267 | 150.408 | 6.267 | 9 | 9 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35963132 | 1376 | 219.5628 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 | 0.84 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 144 | 31489679 | 6376 | 153.024 | 6.376 | 8.5 | 8.5 | 3B+1S | 0 | 1009 | 1197 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35964524 | 1392 | 218.3187 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 144 | 31495739 | 6060 | 145.44 | 6.06 | 8.3 | 8.3 | 3B+1S | 0 | 989 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 35965904 | 1380 | 227.7228 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 125 | 145 | 31501624 | 5885 | 141.24 | 5.885 | 7.7 | 7.7 | 3B+1S | 0 | 1128 | 1197 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35967116 | 1212 | 205.9473 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 140 | 31507678 | 6054 | 145.296 | 6.054 | 7 | 7 | 3B+1S | 0 | 1040 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 35968444 | 1328 | 219.3591 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 138 | 31513498 | 5820 | 139.68 | 5.82 | 6.8 | 6.8 | 3B+1S | 0 | 993 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35969748 | 1304 | 224.055 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 31519275 | 5777 | 138.648 | 5.777 | 6.6 | 6.6 | 3B+1S | 0 | 1000 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35971060 | 1312 | 227.1075 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 31525107 | 5832 | 139.968 | 5.832 | 6.2 | 6.2 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35972396 | 1336 | 229.0809 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 137 | 31530793 | 5686 | 136.464 | 5.686 | 6.1 | 6.1 | 3B+1S | 0 | 970 | 1175 | 1185 | 1199 | N/A | N/A | N/A | N/A | 35973688 | 1292 | 227.2248 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 31536374 | 5581 | 133.944 | 5.581 | 6 | 6 | 3B+1S | 0 | 993 | 1135 | 1185 | 1149 | N/A | N/A | N/A | N/A | 35974916 | 1228 | 220.0323 | 0% | 100% | 100% | 100% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 31541898 | 5524 | 132.576 | 5.524 | 5.3 | 5.3 | 2B+1S | 0 | 1050 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35975988 | 1072 | 194.0623 | 0% | 100% | 100% | 0% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 124 | 31547239 | 5341 | 128.184 | 5.341 | 4.8 | 4.8 | 2B+1S | 0 | 993 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 35977024 | 1036 | 193.9712 | 0% | 100% | 100% | 0% | 100% | 0% | 8036196 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 112 | 31552264 | 5025 | 120.6 | 5.025 | 4.7 | 4.7 | 2B+1S | 0 | 968 | 1156 | 0 | 1160 | N/A | N/A | N/A | N/A | 35978010 | 986 | 196.2189 | 0% | 100% | 100% |  | 100% | 0% | 8036196 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 114 | 101 | 31556426 | 4162 | 99.888 | 4.162 | 5.2 | 5.2 | 2B | 0 | 0 | 1061 | 0 | 1068 | N/A | N/A | N/A | N/A | 35978700 | 690 | 165.7857 | 0% | 0% | 100% |  | 100% | 25% | 8036740 | 544 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 94 | 31560438 | 4012 | 96.288 | 4.012 | 5.8 | 5.8 | 2B | 0 | 0 | 1025 | 0 | 1028 | N/A | N/A | N/A | N/A | 35979334 | 634 | 158.0259 | 0% | 0% | 100% |  | 100% | 25% | 8037369 | 629 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.2083 | 123228 | 123228 | 123.228 | 123.228 | [12 empty] | 23928 | 23928 | 194.1766 | [6 empty] | 2769 | 2769 | 0.865 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am to 5:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (30%) @ 12:01 AM
XCV1 CLOSED @ 1:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:40 AM , NORMAL OPERATION
SP2 - STARTED @8:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 5, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:16 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:13 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:53 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23622 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31560438 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 35979334 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8037369 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 87 | 31564181 | 3743 | 89.832 | 3.743 | 6.9 | 6.9 | 2B | 0 | 0 | 998 | 0 | 1008 | N/A | N/A | N/A | N/A | 35979932 | 598 | 159.7649 | 0% | 0% | 100% | 0% | 100% | 35% | 8038404 | 1035 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 86 | 31567897 | 3716 | 89.184 | 3.716 | 8.1 | 8.1 | 2B | 0 | 0 | 1015 | 0 | 998 | N/A | N/A | N/A | N/A | 35980514 | 582 | 156.62 | 0% | 0% | 100% | 0% | 100% | 35% | 8039506 | 1102 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 106 | 84 | 31571595 | 3698 | 88.752 | 3.698 | 9.3 | 9.3 | 2B | 0 | 0 | 991 | 0 | 997 | N/A | N/A | N/A | N/A | 35981010 | 496 | 134.1266 | 0% | 0% | 100% | 0% | 100% | 35% | 8040710 | 1204 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 86 | 31575236 | 3641 | 87.384 | 3.641 | 9.5 | 9.5 | 2B | 0 | 0 | 869 | 0 | 997 | N/A | N/A | N/A | N/A | 35981494 | 484 | 132.9305 | 0% | 0% | 100% | 0% | 100% | 35% | 8040892 | 182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 88 | 31578742 | 3506 | 84.144 | 3.506 | 9.5 | 9.5 | 2B | 0 | 0 | 842 | 0 | 998 | N/A | N/A | N/A | N/A | 35981886 | 392 | 111.8083 | 0% | 0% | 100% | 0% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 26 | 18.3099 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 109 | 104 | 31582675 | 3933 | 94.392 | 3.933 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 998 | N/A | N/A | N/A | N/A | 35982436 | 550 | 139.8424 | 0% | 0% | 100% | 0% | 100% | 0% | 8040892 | 0 | 0.82 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 135 | 31588116 | 5441 | 130.584 | 5.441 | 9.5 | 9.5 | 3B | 0 | 0 | 1109 | 1185 | 1119 | N/A | N/A | N/A | N/A | 35983456 | 1020 | 187.4655 | 0% | 0% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 151 | 147 | 31594137 | 6021 | 144.504 | 6.021 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35984660 | 1204 | 199.9668 | 0% | 0% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 31600136 | 5999 | 143.976 | 5.999 | 9.3 | 9.3 | 3B+1S | 0 | 1027 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 35985924 | 1264 | 210.7018 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 156 | 31606476 | 6340 | 152.16 | 6.34 | 8.7 | 8.7 | 3B+1S | 0 | 1046 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35987276 | 1352 | 213.2492 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 144 | 31612715 | 6239 | 149.736 | 6.239 | 8.2 | 8.2 | 3B+1S | 0 | 1039 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35988624 | 1348 | 216.0603 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 147 | 31618812 | 6097 | 146.328 | 6.097 | 7.9 | 7.9 | 3B+1S | 0 | 1009 | 1177 | 1185 | 1180 | N/A | N/A | N/A | N/A | 35989932 | 1308 | 214.5317 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 125 | 167 | 31624822 | 6010 | 144.24 | 6.01 | 7.2 | 7.2 | 3B+1S | 0 | 1094 | 1125 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35991214 | 1282 | 213.3111 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 141 | 31630907 | 6085 | 146.04 | 6.085 | 6.6 | 6.6 | 3B+1S | 0 | 1037 | 1155 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35992514 | 1300 | 213.6401 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 | 0.5 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 31636401 | 5494 | 131.856 | 5.494 | 6.3 | 6.3 | 3B+1S | 0 | 1009 | 1156 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35993732 | 1218 | 221.6964 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 31641763 | 5362 | 128.688 | 5.362 | 6.1 | 6.1 | 3B+1S | 0 | 1017 | 1156 | 1185 | 1159 | N/A | N/A | N/A | N/A | 35994928 | 1196 | 223.0511 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 31647632 | 5869 | 140.856 | 5.869 | 5.6 | 5.6 | 3B+1S | 0 | 1064 | 1156 | 1185 | 1150 | N/A | N/A | N/A | N/A | 35996240 | 1312 | 223.5475 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 31653194 | 5562 | 133.488 | 5.562 | 5.4 | 5.4 | 3B+1S | 0 | 990 | 1135 | 1185 | 1128 | N/A | N/A | N/A | N/A | 35997448 | 1208 | 217.1881 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 31658645 | 5451 | 130.824 | 5.451 | 5.2 | 5.2 | 3B+1S | 0 | 989 | 1136 | 1185 | 1119 | N/A | N/A | N/A | N/A | 35998624 | 1176 | 215.7402 | 0% | 100% | 100% | 100% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 131 | 31664026 | 5381 | 129.144 | 5.381 | 4.6 | 4.6 | 2B+1S | 0 | 1031 | 1197 | 0 | 1191 | N/A | N/A | N/A | N/A | 35999668 | 1044 | 194.016 | 0% | 100% | 100% | 0% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 124 | 31669318 | 5292 | 127.008 | 5.292 | 4.1 | 4.1 | 2B+1S | 0 | 1007 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 36000692 | 1024 | 193.4996 | 0% | 100% | 100% | 0% | 100% | 0% | 8040892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 93 | 115 | 31674416 | 5098 | 122.352 | 5.098 | 3.9 | 3.9 | 2B+1S | 0 | 1077 | 1165 | 0 | 1008 | N/A | N/A | N/A | N/A | 36001684 | 992 | 194.5861 | 0% | 100% | 100% | 0% | 100% | 0% | 8040892 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 90 | 31678553 | 4137 | 99.288 | 4.137 | 4.5 | 4.5 | 2B | 0 | 0 | 992 | 0 | 1110 | N/A | N/A | N/A | N/A | 36002348 | 664 | 160.5028 | 0% | 0% | 100% | 0% | 100% | 25% | 8041550 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 89 | 31682412 | 3859 | 92.616 | 3.859 | 5.3 | 5.3 | 2B | 0 | 0 | 913 | 0 | 1110 | N/A | N/A | N/A | N/A | 36002956 | 608 | 157.5538 | 0% | 0% | 100% | 0% | 100% | 25% | 8042346 | 796 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.2917 | 121974 | 121974 | 121.974 | 121.974 | [12 empty] | 23622 | 23622 | 193.6642 | [6 empty] | 4977 | 4977 | 0.835 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am to 5:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:50 AM , NORMAL OPERATION
SP2 - STARTED @8:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 6, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:19 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26116 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31682412 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36002956 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8042346 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 84 | 31686111 | 3699 | 88.776 | 3.699 | 6.6 | 6.6 | 2B | 0 | 0 | 930 | 0 | 1110 | N/A | N/A | N/A | N/A | 36003564 | 608 | 164.3687 | 0% | 0% | 100% | 0% | 100% | 35% | 8043614 | 1268 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 100 | 31689643 | 3532 | 84.768 | 3.532 | 7.9 | 7.9 | 2B | 0 | 0 | 909 | 0 | 1110 | N/A | N/A | N/A | N/A | 36004132 | 568 | 160.8154 | 0% | 0% | 100% | 0% | 100% | 35% | 8044912 | 1298 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 87 | 31693230 | 3587 | 86.088 | 3.587 | 9.3 | 9.3 | 2B | 0 | 0 | 967 | 0 | 988 | N/A | N/A | N/A | N/A | 36004668 | 536 | 149.4285 | 0% | 0% | 100% | 0% | 100% | 35% | 8046187 | 1275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 102 | 86 | 31696852 | 3622 | 86.928 | 3.622 | 9.5 | 9.5 | 2B | 0 | 0 | 861 | 0 | 988 | N/A | N/A | N/A | N/A | 36005160 | 492 | 135.8366 | 0% | 0% | 100% | 0% | 100% | 35% | 8046260 | 73 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 91 | 85 | 31700439 | 3587 | 86.088 | 3.587 | 9.5 | 9.5 | 2B | 0 | 0 | 842 | 0 | 988 | N/A | N/A | N/A | N/A | 36005624 | 464 | 129.356 | 0% | 0% | 100% | 0% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 122 | 119 | 31705059 | 4620 | 110.88 | 4.62 | 9.5 | 9.5 | 2B | 0 | 0 | 1113 | 0 | 1110 | N/A | N/A | N/A | N/A | 36006180 | 556 | 120.3463 | 0% | 0% | 100% | 0% | 100% | 0% | 8046260 | 0 | 0.96 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 148 | 31711150 | 6091 | 146.184 | 6.091 | 9.4 | 9.4 | 3B+1S | 0 | 1002 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36007468 | 1288 | 211.4595 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 155 | 31717299 | 6149 | 147.576 | 6.149 | 8.9 | 8.9 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36008790 | 1322 | 214.9943 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 154 | 31723786 | 6487 | 155.688 | 6.487 | 8.1 | 8.1 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36010240 | 1450 | 223.524 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 152 | 31730287 | 6501 | 156.024 | 6.501 | 7.3 | 7.3 | 3B+1S | 0 | 1155 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36011692 | 1452 | 223.3503 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 153 | 31736533 | 6246 | 149.904 | 6.246 | 6.5 | 6.5 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36013076 | 1384 | 221.5818 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 31742688 | 6155 | 147.72 | 6.155 | 5.9 | 5.9 | 3B+1S | 0 | 1125 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36014476 | 1400 | 227.4574 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 148 | 31748716 | 6028 | 144.672 | 6.028 | 5.3 | 5.3 | 3B+1S | 0 | 1168 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36015864 | 1388 | 230.2588 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 31754776 | 6060 | 145.44 | 6.06 | 4.7 | 4.7 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36017218 | 1354 | 223.4323 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 | 0.4 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 31760898 | 6122 | 146.928 | 6.122 | 4.3 | 4.3 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36018628 | 1410 | 230.3169 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 31766483 | 5585 | 134.04 | 5.585 | 4 | 4 | 3B+1S | 0 | 1049 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36019900 | 1272 | 227.7529 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 140 | 31772523 | 6040 | 144.96 | 6.04 | 3.3 | 3.3 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36021300 | 1400 | 231.7881 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 144 | 31778479 | 5956 | 142.944 | 5.956 | 2.8 | 2.8 | 3B+1S | 0 | 1099 | 1186 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36022644 | 1344 | 225.6548 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 | 0.71 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 139 | 31784049 | 5570 | 133.68 | 5.57 | 2.3 | 2.3 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36023908 | 1264 | 226.93 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 128 | 31789594 | 5545 | 133.08 | 5.545 | 2.1 | 2.1 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36025200 | 1292 | 233.0027 | 0% | 100% | 100% | 100% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 124 | 31794905 | 5311 | 127.464 | 5.311 | 1.9 | 1.9 | 2B+1S | 0 | 1188 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36026416 | 1216 | 228.9588 | 0% | 100% | 100% | 0% | 100% | 0% | 8046260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 126 | 31800271 | 5366 | 128.784 | 5.366 | 1.4 | 1.4 | 2B+1S | 0 | 1029 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36027548 | 1132 | 210.9579 | 0% | 100% | 100% | 0% | 100% | 0% | 8046260 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 108 | 31804760 | 4489 | 107.736 | 4.489 | 2.4 | 2.4 | 2B | 0 | 0 | 1129 | 0 | 1120 | N/A | N/A | N/A | N/A | 36028356 | 808 | 179.9955 | 0% | 0% | 100% | 0% | 100% | 40% | 8047485 | 1225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 98 | 31808902 | 4142 | 99.408 | 4.142 | 4 | 4 | 2B. | 0 | 0 | 1070 | 0 | 1110 | N/A | N/A | N/A | N/A | 36029072 | 716 | 172.8634 | 0% | 0% | 100% | 0% | 100% | 40% | 8048779 | 1294 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.0417 | 126490 | 126490 | 126.49 | 126.49 | [12 empty] | 26116 | 26116 | 206.4669 | [6 empty] | 6433 | 6433 | 0.81 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 3:04 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:55 PM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 7, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:14 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:23 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:19 PM , NORMAL OPERATION
NORMAL

## APR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25428 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31808902 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36029072 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8048779 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 89 | 31812868 | 3966 | 95.184 | 3.966 | 5.6 | 5.6 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 36029756 | 684 | 172.466 | 0% | 0% | 100% | 0% | 100% | 45% | 8050169 | 1390 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 84 | 31816569 | 3701 | 88.824 | 3.701 | 7.1 | 7.1 | 2B | 0 | 0 | 1004 | 0 | 1059 | N/A | N/A | N/A | N/A | 36030380 | 624 | 168.6031 | 0% | 0% | 100% | 0% | 100% | 45% | 8051642 | 1473 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 31820059 | 3490 | 83.76 | 3.49 | 8.6 | 8.6 | 2B | 0 | 0 | 991 | 0 | 1008 | N/A | N/A | N/A | N/A | 36030932 | 552 | 158.1662 | 0% | 0% | 100% | 0% | 100% | 45% | 8053048 | 1406 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 88 | 31823643 | 3584 | 86.016 | 3.584 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 978 | N/A | N/A | N/A | N/A | 36031452 | 520 | 145.0893 | 0% | 0% | 100% | 0% | 100% | 45% | 8053903 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 96 | 31827416 | 3773 | 90.552 | 3.773 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 957 | N/A | N/A | N/A | N/A | 36031916 | 464 | 122.9791 | 0% | 0% | 100% | 0% | 100% | 45% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 120 | 31831941 | 4525 | 108.6 | 4.525 | 9.5 | 9.5 | 2B | 0 | 0 | 1115 | 0 | 1130 | N/A | N/A | N/A | N/A | 36032536 | 620 | 137.0166 | 0% | 0% | 100% | 0% | 100% | 0% | 8053903 | 0 | 1.08 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 150 | 31838110 | 6169 | 148.056 | 6.169 | 9.3 | 9.3 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36033852 | 1316 | 213.3247 | 0% | 0% | 100% | 0% | 100% | 0% | 8053903 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 31844594 | 6484 | 155.616 | 6.484 | 8.7 | 8.7 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36035272 | 1420 | 219.0006 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 153 | 31850748 | 6154 | 147.696 | 6.154 | 8.1 | 8.1 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36036636 | 1364 | 221.6445 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 153 | 31857067 | 6319 | 151.656 | 6.319 | 7.4 | 7.4 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36038036 | 1400 | 221.554 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 31863375 | 6308 | 151.392 | 6.308 | 6.8 | 6.8 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36039436 | 1400 | 221.9404 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 31869487 | 6112 | 146.688 | 6.112 | 6.4 | 6.4 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36040796 | 1360 | 222.5131 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 143 | 31875508 | 6021 | 144.504 | 6.021 | 6.1 | 6.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36042156 | 1360 | 225.8761 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 134 | 31881520 | 6012 | 144.288 | 6.012 | 5.9 | 5.9 | 3B+1S | 0 | 543 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36043532 | 1376 | 228.8756 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 126 | 138 | 31886912 | 5392 | 129.408 | 5.392 | 5.8 | 5.8 | 3B+1S | 0 | 997 | 1159 | 1185 | 1138 | N/A | N/A | N/A | N/A | 36044756 | 1224 | 227.003 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 129 | 31892375 | 5463 | 131.112 | 5.463 | 5.5 | 5.5 | 3B+1S | 0 | 1042 | 1156 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36045980 | 1224 | 224.0527 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 136 | 31897994 | 5619 | 134.856 | 5.619 | 4.8 | 4.8 | 3B+1S | 0 | 1113 | 1185 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36047268 | 1288 | 229.2223 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 135 | 31903745 | 5751 | 138.024 | 5.751 | 4.3 | 4.3 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36048580 | 1312 | 228.1342 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 31909154 | 5409 | 129.816 | 5.409 | 3.9 | 3.9 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36049804 | 1224 | 226.2895 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 125 | 31914432 | 5278 | 126.672 | 5.278 | 3.7 | 3.7 | 3B+1S | 0 | 981 | 1196 | 1185 | 1129 | N/A | N/A | N/A | N/A | 36050984 | 1180 | 223.5695 | 0% | 100% | 100% | 100% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 122 | 31919773 | 5341 | 128.184 | 5.341 | 3.2 | 3.2 | 2B+1S | 0 | 1029 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36052068 | 1084 | 202.9582 | 0% | 100% | 100% | 0% | 100% | 0% | 8053903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 113 | 31924904 | 5131 | 123.144 | 5.131 | 3 | 3 | 2B+1S | 0 | 986 | 1179 | 0 | 1199 | N/A | N/A | N/A | N/A | 36053100 | 1032 | 201.1304 | 0% | 100% | 100% | 0% | 100% | 0% | 8053903 | 0 | 0.76 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 98 | 31929039 | 4135 | 99.24 | 4.135 | 3.5 | 3.5 | 2B | 0 | 0 | 977 | 0 | 1199 | N/A | N/A | N/A | N/A | 36053828 | 728 | 176.058 | 0% | 0% | 100% | 0% | 100% | 25% | 8054498 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 65 | 31932861 | 3822 | 91.728 | 3.822 | 4.4 | 4.4 | 2B. | 0 | 0 | 889 | 0 | 1199 | N/A | N/A | N/A | N/A | 36054500 | 672 | 175.8242 | 0% | 0% | 100% | 0% | 100% | 40% | 8055240 | 742 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.25 | 123959 | 123959 | 123.959 | 123.959 | [12 empty] | 25428 | 25428 | 205.1323 | [6 empty] | 6461 | 6461 | 0.93333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 3:21 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:42 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:36 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 PM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 8, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,839
GENSET 1 WARMUP EXERCISED @ 12:08PM / STOPPED @ 12:18PM
GENSET 2 WARMUP EXERCISED @ 12:19PM / STOPPED @ 12:29PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:28 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:38 PM , NORMAL OPERATION
NORMAL

## APR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / F.A.RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24904 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 31932861 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36054500 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8055240 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 85 | 31936499 | 3638 | 87.312 | 3.638 | 5.8 | 5.8 | 2B | 0 | 0 | 893 | 0 | 1199 | N/A | N/A | N/A | N/A | 36055176 | 676 | 185.8164 | 0% | 0% | 100% | 0% | 100% | 40% | 8056673 | 1433 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 82 | 31939770 | 3271 | 78.504 | 3.271 | 7.3 | 7.3 | 2B | 0 | 0 | 914 | 0 | 1110 | N/A | N/A | N/A | N/A | 36055732 | 556 | 169.9786 | 0% | 0% | 100% | 0% | 100% | 40% | 8058113 | 1440 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 80 | 31943721 | 3951 | 94.824 | 3.951 | 9.1 | 9.1 | 2B | 0 | 0 | 886 | 0 | 1109 | N/A | N/A | N/A | N/A | 36056396 | 664 | 168.0587 | 0% | 0% | 100% | 0% | 100% | 40% | 8059800 | 1687 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 82 | 31946803 | 3082 | 73.968 | 3.082 | 9.5 | 9.5 | 2B | 0 | 0 | 833 | 0 | 1110 | N/A | N/A | N/A | N/A | 36056876 | 480 | 155.743 | 0% | 0% | 100% | 0% | 100% | 40% | 8060077 | 277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 91 | 31950496 | 3693 | 88.632 | 3.693 | 9.5 | 9.5 | 2B | 0 | 0 | 818 | 0 | 1110 | N/A | N/A | N/A | N/A | 36057412 | 536 | 145.1395 | 0% | 0% | 100% | 0% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 19 | 13.3803 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 116 | 31954827 | 4331 | 103.944 | 4.331 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 0 | 1109 | N/A | N/A | N/A | N/A | 36058012 | 600 | 138.5361 | 0% | 0% | 100% | 0% | 100% | 0% | 8060077 | 0 | 1.28 | Normal operation schedule | Error - General | E | J. GALINATO / F.A.RAMOS
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 127 | 31959894 | 5067 | 121.608 | 5.067 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36059144 | 1132 | 223.4064 | 0% | 0% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 129 | 31965700 | 5806 | 139.344 | 5.806 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36060492 | 1348 | 232.1736 | 0% | 0% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 128 | 126 | 31970861 | 5161 | 123.864 | 5.161 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36061692 | 1200 | 232.5131 | 0% | 0% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 156 | 31976048 | 5187 | 124.488 | 5.187 | 9.4 | 9.4 | 3B+1 S | 0 | 1135 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36062804 | 1112 | 214.3821 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 | 0.65 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 152 | 31982685 | 6637 | 159.288 | 6.637 | 8.7 | 8.7 | 3B+1 S | 0 | 1046 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36064260 | 1456 | 219.3762 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 131 | 31989517 | 6832 | 163.968 | 6.832 | 8.3 | 8.3 | 3B+1 S | 0 | 1025 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36065780 | 1520 | 222.4824 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 125 | 143 | 31994423 | 4906 | 117.744 | 4.906 | 7.7 | 7.7 | 3B+1 S | 0 | 1017 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36066904 | 1124 | 229.1072 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 32000735 | 6312 | 151.488 | 6.312 | 7.5 | 7.5 | 3B+1 S | 0 | 1003 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36068336 | 1432 | 226.8695 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 | 0.44 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 32006218 | 5483 | 131.592 | 5.483 | 7.2 | 7.2 | 3B+1 S | 0 | 984 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36069612 | 1276 | 232.7193 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 32011892 | 5674 | 136.176 | 5.674 | 7.1 | 7.1 | 3B+1 S | 0 | 996 | 1196 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36070932 | 1320 | 232.6401 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 136 | 32017653 | 5761 | 138.264 | 5.761 | 6.6 | 6.6 | 3B+1 S | 0 | 1066 | 1195 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36072268 | 1336 | 231.9042 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 32023376 | 5723 | 137.352 | 5.723 | 6.2 | 6.2 | 3B+1 S | 0 | 1002 | 1195 | 1185 | 1181 | N/A | N/A | N/A | N/A | 36073584 | 1316 | 229.9493 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 | 0.4 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 134 | 32029201 | 5825 | 139.8 | 5.825 | 5.9 | 5.9 | 2B+1 S | 0 | 980 | 1195 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36074908 | 1324 | 227.2961 | 0% | 100% | 100% | 100% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 127 | 32034453 | 5252 | 126.048 | 5.252 | 5.3 | 5.3 | 2B+1 S | 0 | 1001 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36075972 | 1064 | 202.5895 | 0% | 100% | 100% | 0% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 32039482 | 5029 | 120.696 | 5.029 | 4.7 | 4.7 | 2B+1 S | 0 | 1024 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36076976 | 1004 | 199.6421 | 0% | 100% | 100% | 0% | 100% | 0% | 8060077 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 118 | 32044743 | 5261 | 126.264 | 5.261 | 4.4 | 4.4 | 2B+1 S | 0 | 969 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 36078028 | 1052 | 199.962 | 0% | 100% | 100% | 0% | 100% | 0% | 8060077 | 0 | 0.71 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 95 | 32048903 | 4160 | 99.84 | 4.16 | 4.9 | 4.9 | 2B | 0 | 0 | 1072 | 0 | 1099 | N/A | N/A | N/A | N/A | 36078750 | 722 | 173.5577 | 0% | 0% | 100% | 0% | 100% | 25% | 8060583 | 506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 90 | 32052791 | 3888 | 93.312 | 3.888 | 5.5 | 5.5 | 2B | 0 | 0 | 1011 | 0 | 1048 | N/A | N/A | N/A | N/A | 36079404 | 654 | 168.2099 | 0% | 0% | 100% | 0% | 100% | 25% | 8061204 | 621 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.625 | 119930 | 119930 | 119.93 | 119.93 | [12 empty] | 24904 | 24904 | 207.6545 | [6 empty] | 5964 | 5964 | 0.71667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:28 AM , NORMAL OPERATION
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:22 AM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT AT 4:39AM RESUME 6:22AM NORMAL OPERATION
SP2 - STARTED @ 9:24 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:16 AM , NORMAL OPERATION
CONDUCTED SITE INSPECTION WITH SIR MICHAEL BULIGAN AND SIR ARTURO TRINIDAD TOGETHER WITH QUAD AM PERSONNEL ARRIVED AT 11:05AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 9, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:17 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25196 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32052791 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36079404 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8061204 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 84 | 32056375 | 3584 | 86.016 | 3.584 | 6.7 | 6.7 | 2B | 0 | 0 | 1012 | 0 | 1028 | N/A | N/A | N/A | N/A | 36079990 | 586 | 163.5045 | 0% | 0% | 100% | 0% | 100% | 35% | 8062272 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 82 | 32059895 | 3520 | 84.48 | 3.52 | 7.8 | 7.8 | 2B | 0 | 0 | 988 | 0 | 1008 | N/A | N/A | N/A | N/A | 36080522 | 532 | 151.1364 | 0% | 0% | 100% | 0% | 100% | 35% | 8063352 | 1080 | 0.59 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 104 | 78 | 32063341 | 3446 | 82.704 | 3.446 | 9 | 9 | 2B | 0 | 0 | 924 | 0 | 988 | N/A | N/A | N/A | N/A | 36081040 | 518 | 150.3192 | 0% | 0% | 100% | 0% | 100% | 35% | 8064456 | 1104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 85 | 84 | 32066713 | 3372 | 80.928 | 3.372 | 9.5 | 9.5 | 2B | 0 | 0 | 889 | 0 | 988 | N/A | N/A | N/A | N/A | 36081548 | 508 | 150.6524 | 0% | 0% | 100% | 0% | 100% | 35% | 8065040 | 584 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 91 | 32070381 | 3668 | 88.032 | 3.668 | 9.5 | 9.5 | 2B | 0 | 0 | 912 | 0 | 948 | N/A | N/A | N/A | N/A | 36082036 | 488 | 133.0425 | 0% | 0% | 100% | 0% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 118 | 116 | 32074538 | 4157 | 99.768 | 4.157 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1109 | N/A | N/A | N/A | N/A | 36082620 | 584 | 140.4859 | 0% | 0% | 100% | 0% | 100% | 0% | 8065040 | 0 | 0.81 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 148 | 145 | 32080462 | 5924 | 142.176 | 5.924 | 94 | 94 | 3B | 0 | 970 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36083876 | 1256 | 212.0189 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 149 | 32086692 | 6230 | 149.52 | 6.23 | 9.1 | 9.1 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36085244 | 1368 | 219.5827 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 152 | 32093015 | 6323 | 151.752 | 6.323 | 8.5 | 8.5 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36086652 | 1408 | 222.6791 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 32099264 | 6249 | 149.976 | 6.249 | 7.6 | 7.6 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36088048 | 1396 | 223.3957 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 | 0.53 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 32105623 | 6359 | 152.616 | 6.359 | 6.9 | 6.9 | 3B+1S | 0 | 1078 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36089468 | 1420 | 223.3056 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 32111848 | 6225 | 149.4 | 6.225 | 6.5 | 6.5 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36090844 | 1376 | 221.0442 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 142 | 142 | 32117822 | 5974 | 143.376 | 5.974 | 6.2 | 6.2 | 3B+1S | 0 | 992 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36092188 | 1344 | 224.9749 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 32123731 | 5909 | 141.816 | 5.909 | 6 | 6 | 3B+1S | 0 | 1027 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36093520 | 1332 | 225.4189 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 | 1.323 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 81 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 32130012 | 6281 | 150.744 | 6.281 | 5.7 | 5.7 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36094960 | 1440 | 229.2629 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 32135214 | 5202 | 124.848 | 5.202 | 5.5 | 5.5 | 3B+1S | 0 | 1017 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36096148 | 1188 | 228.3737 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 32140873 | 5659 | 135.816 | 5.659 | 5 | 5 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 36097468 | 1320 | 233.2568 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 32146701 | 5828 | 139.872 | 5.828 | 4.8 | 4.8 | 3B+1S | 0 | 983 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36098828 | 1360 | 233.3562 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 131 | 32152312 | 5611 | 134.664 | 5.611 | 4.7 | 4.7 | 3B+1S | 0 | 988 | 1176 | 1185 | 1160 | N/A | N/A | N/A | N/A | 36100138 | 1310 | 233.47 | 0% | 100% | 100% | 100% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 128 | 32157346 | 5034 | 120.816 | 5.034 | 4 | 4 | 2B+1S | 0 | 1111 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 36101148 | 1010 | 200.6357 | 0% | 100% | 100% | 0% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 122 | 32162727 | 5381 | 129.144 | 5.381 | 3.2 | 3.2 | 2B+1S | 0 | 1063 | 1197 | 0 | 1198 | N/A | N/A | N/A | N/A | 36102236 | 1088 | 202.1929 | 0% | 100% | 100% | 0% | 100% | 0% | 8065040 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 114 | 32167718 | 4991 | 119.784 | 4.991 | 2.9 | 2.9 | 2B+1S | 0 | 987 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36103236 | 1000 | 200.3606 | 0% | 100% | 100% | 0% | 100% | 0% | 8065040 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 98 | 32171832 | 4114 | 98.736 | 4.114 | 3.4 | 3.4 | 2B | 0 | 0 | 1040 | 0 | 1110 | N/A | N/A | N/A | N/A | 36103948 | 712 | 173.0676 | 0% | 0% | 100% | 0% | 100% | 25% | 8065607 | 567 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 112 | 91 | 32175804 | 3972 | 95.328 | 3.972 | 4.3 | 4.3 | 2B | 0 | 0 | 966 | 0 | 1109 | N/A | N/A | N/A | N/A | 36104600 | 652 | 164.149 | 0% | 0% | 100% | 0% | 100% | 25% | 8066338 | 731 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5 | 123013 | 123013 | 123.013 | 123.013 | [12 empty] | 25196 | 25196 | 204.8239 | [6 empty] | 5134 | 5134 | 0.84883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:22 AM , NORMAL OPERATION
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:14 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 10, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:13 PM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT AT 6:21AM RESUME 6:22AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:16 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:21 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25496 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32175804 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36104600 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8066338 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 78 | 32179385 | 3581 | 85.944 | 3.581 | 5.7 | 5.7 | 2B | 0 | 0 | 953 | 0 | 1110 | N/A | N/A | N/A | N/A | 36105204 | 604 | 168.668 | 0% | 0% | 100% | 0% | 100% | 40% | 8067802 | 1464 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 77 | 32182826 | 3441 | 82.584 | 3.441 | 7.4 | 7.4 | 2B | 0 | 0 | 912 | 0 | 1110 | N/A | N/A | N/A | N/A | 36105780 | 576 | 167.3932 | 0% | 0% | 100% | 0% | 100% | 40% | 8069417 | 1615 | 0.77 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 80 | 32186432 | 3606 | 86.544 | 3.606 | 9.4 | 9.4 | 2B | 0 | 0 | 904 | 0 | 1109 | N/A | N/A | N/A | N/A | 36106466 | 686 | 190.2385 | 0% | 0% | 100% | 0% | 100% | 40% | 8071001 | 1584 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 82 | 32189620 | 3188 | 76.512 | 3.188 | 9.5 | 9.5 | 2B | 0 | 0 | 747 | 0 | 1110 | N/A | N/A | N/A | N/A | 36106876 | 410 | 128.6073 | 0% | 0% | 100% | 0% | 100% | 40% | 8071269 | 268 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 88 | 32193234 | 3614 | 86.736 | 3.614 | 9.5 | 9.5 | 2B | 0 | 0 | 850 | 0 | 1110 | N/A | N/A | N/A | N/A | 36107392 | 516 | 142.7781 | 0% | 0% | 100% | 0% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 127 | 123 | 32197751 | 4517 | 108.408 | 4.517 | 9.5 | 9.5 | 2B | 0 | 0 | 1174 | 0 | 1199 | N/A | N/A | N/A | N/A | 36108068 | 676 | 149.6569 | 0% | 0% | 100% | 0% | 100% | 0% | 8071269 | 0 | 1.02 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 151 | 32203845 | 6094 | 146.256 | 6.094 | 9 | 9 | 3B+1S | 0 | 1004 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36109368 | 1300 | 213.3246 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 32210148 | 6303 | 151.272 | 6.303 | 8.6 | 8.6 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36110756 | 1388 | 220.2126 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 153 | 32216361 | 6213 | 149.112 | 6.213 | 7.9 | 7.9 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36112136 | 1380 | 222.1149 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 153 | 32222853 | 6492 | 155.808 | 6.492 | 7 | 7 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36113620 | 1484 | 228.589 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 32228916 | 6063 | 145.512 | 6.063 | 6.4 | 6.4 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36114930 | 1310 | 216.0647 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 143 | 32235011 | 6095 | 146.28 | 6.095 | 5.9 | 5.9 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36116332 | 1402 | 230.0246 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 145 | 32240907 | 5896 | 141.504 | 5.896 | 5.7 | 5.7 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36117658 | 1326 | 224.8982 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 32246765 | 5858 | 140.592 | 5.858 | 5.3 | 5.3 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36119012 | 1354 | 231.1369 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 32252547 | 5782 | 138.768 | 5.782 | 5.1 | 5.1 | 3B+1S | 0 | 1024 | 1185 | 1185 | 1179 | N/A | N/A | N/A | N/A | 36120344 | 1332 | 230.3701 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 32257752 | 5205 | 124.92 | 5.205 | 4.9 | 4.9 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1189 | N/A | N/A | N/A | N/A | 36121556 | 1212 | 232.853 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 32263634 | 5882 | 141.168 | 5.882 | 4.4 | 4.4 | 3B+1S | 0 | 1093 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36122916 | 1360 | 231.2139 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 141 | 32269334 | 5700 | 136.8 | 5.7 | 4.1 | 4.1 | 3B+1S | 0 | 1007 | 1186 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36124212 | 1296 | 227.3684 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 133 | 32275179 | 5845 | 140.28 | 5.845 | 3.8 | 3.8 | 3B+1S | 0 | 966 | 1145 | 1185 | 1128 | N/A | N/A | N/A | N/A | 36125532 | 1320 | 225.834 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 127 | 32280279 | 5100 | 122.4 | 5.1 | 3.6 | 3.6 | 3B+1S | 0 | 976 | 1113 | 1185 | 1118 | N/A | N/A | N/A | N/A | 36126632 | 1100 | 215.6863 | 0% | 100% | 100% | 100% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 120 | 32285552 | 5273 | 126.552 | 5.273 | 3.2 | 3.2 | 2B+1S | 0 | 1019 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36127700 | 1068 | 202.5412 | 0% | 100% | 100% | 0% | 100% | 0% | 8071269 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 110 | 32290556 | 5004 | 120.096 | 5.004 | 3 | 3 | 2B+1S | 0 | 1082 | 1156 | 0 | 1149 | N/A | N/A | N/A | N/A | 36128692 | 992 | 198.2414 | 0% | 100% | 100% | 0% | 100% | 0% | 8071269 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 99 | 32294711 | 4155 | 99.72 | 4.155 | 3.6 | 3.6 | 2B | 0 | 0 | 1085 | 0 | 1099 | N/A | N/A | N/A | N/A | 36129436 | 744 | 179.0614 | 0% | 0% | 100% | 0% | 100% | 30% | 8071981 | 712 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 91 | 32298629 | 3918 | 94.032 | 3.918 | 4.7 | 4.7 | 2B | 0 | 0 | 1035 | 0 | 1059 | N/A | N/A | N/A | N/A | 36130096 | 660 | 168.4533 | 0% | 0% | 100% | 0% | 100% | 30% | 8072821 | 840 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.1667 | 122825 | 122825 | 122.825 | 122.825 | [12 empty] | 25496 | 25496 | 207.5799 | [6 empty] | 6483 | 6483 | 0.94 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:27 AM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT AT 3:57AM RESUME 5:26AM NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:14 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:23 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 11, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:21 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:55 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | 889 |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | 940 |  | 1185 |  | 800 |  |  | 25436 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32298629 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36130096 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8072821 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 92 | 32302349 | 3720 | 89.28 | 3.72 | 6 | 6 | 2B | 0 | 0 | 985 | 0 | 998 | N/A | N/A | N/A | N/A | 36130720 | 624 | 167.7419 | 0% | 0% | 100% | 0% | 100% | 40% | 8074067 | 1246 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 83 | 32305950 | 3601 | 86.424 | 3.601 | 7.4 | 7.4 | 2B | 0 | 0 | 971 | 0 | 998 | N/A | N/A | N/A | N/A | 36131308 | 588 | 163.288 | 0% | 0% | 100% | 0% | 100% | 40% | 8075308 | 1241 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 104 | 84 | 32309447 | 3497 | 83.928 | 3.497 | 8.6 | 8.6 | 2B | 0 | 0 | 926 | 0 | 998 | N/A | N/A | N/A | N/A | 36131834 | 526 | 150.4146 | 0% | 0% | 100% | 0% | 100% | 40% | 8076637 | 1329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 88 | 32312841 | 3394 | 81.456 | 3.394 | 9.5 | 9.5 | 2B | 0 | 0 | 889 | 0 | 998 | N/A | N/A | N/A | N/A | 36132310 | 476 | 140.2475 | 0% | 0% | 100% | 0% | 100% | 40% | 8077421 | 784 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 93 | 32316548 | 3707 | 88.968 | 3.707 | 9.5 | 9.5 | 2B | 0 | 0 | 940 | 0 | 948 | N/A | N/A | N/A | N/A | 36132820 | 510 | 137.5776 | 0% | 0% | 100% | 0% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 17 | 11.9718 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 120 | 119 | 32321035 | 4487 | 107.688 | 4.487 | 9.5 | 9.5 | 2B | 0 | 0 | 1129 | 0 | 1110 | N/A | N/A | N/A | N/A | 36133460 | 640 | 142.6343 | 0% | 0% | 100% | 0% | 100% | 0% | 8077421 | 0 | 0.84 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 144 | 32326846 | 5811 | 139.464 | 5.811 | 9.3 | 9.3 | 3B+1S | 0 | 1016 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36134708 | 1248 | 214.7651 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 150 | 32333389 | 6543 | 157.032 | 6.543 | 8.9 | 8.9 | 3B+1S | 0 | 1091 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36136142 | 1434 | 219.1655 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 150 | 32339299 | 5910 | 141.84 | 5.91 | 8.3 | 8.3 | 3B+1S | 0 | 1082 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36137456 | 1314 | 222.335 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 155 | 32345736 | 6437 | 154.488 | 6.437 | 7.4 | 7.4 | 3B+1S | 0 | 1126 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36138492 | 1036 | 160.9445 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 32352083 | 6347 | 152.328 | 6.347 | 6.8 | 6.8 | 3B+1S | 0 | 1084 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36140292 | 1800 | 283.5986 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 151 | 32358241 | 6158 | 147.792 | 6.158 | 6.1 | 6.1 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36141654 | 1362 | 221.1757 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 32364365 | 6124 | 146.976 | 6.124 | 5.8 | 5.8 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36143036 | 1382 | 225.6695 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 144 | 32370392 | 6027 | 144.648 | 6.027 | 5.4 | 5.4 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36144412 | 1376 | 228.306 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 32376119 | 5727 | 137.448 | 5.727 | 5.1 | 5.1 | 3B+1S | 0 | 999 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36145716 | 1304 | 227.6934 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 32381963 | 5844 | 140.256 | 5.844 | 5 | 5 | 3B+1S | 0 | 989 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36147060 | 1344 | 229.9795 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 141 | 32387624 | 5661 | 135.864 | 5.661 | 4.6 | 4.6 | 3B+1S | 0 | 1048 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36148364 | 1304 | 230.348 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 137 | 32393407 | 5783 | 138.792 | 5.783 | 4.3 | 4.3 | 3B+1S | 0 | 990 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36149684 | 1320 | 228.2552 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 136 | 32399075 | 5668 | 136.032 | 5.668 | 4.2 | 4.2 | 3B+1S | 0 | 916 | 1175 | 1185 | 1179 | N/A | N/A | N/A | N/A | 36150988 | 1304 | 230.0635 | 0% | 100% | 100% | 100% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 124 | 32404479 | 5404 | 129.696 | 5.404 | 3.5 | 3.5 | 2B+1S | 0 | 1050 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36152052 | 1064 | 196.8912 | 0% | 100% | 100% | 0% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 125 | 32409702 | 5223 | 125.352 | 5.223 | 3 | 3 | 2B+1S | 0 | 1007 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36153084 | 1032 | 197.5876 | 0% | 100% | 100% | 0% | 100% | 0% | 8077421 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 119 | 32414665 | 4963 | 119.112 | 4.963 | 2.9 | 2.9 | 2B+1S | 0 | 994 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 36154060 | 976 | 196.6552 | 0% | 100% | 100% | 0% | 100% | 0% | 8077421 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 98 | 32418921 | 4256 | 102.144 | 4.256 | 3.8 | 3.8 | 2B | 0 | 0 | 1101 | 0 | 1109 | N/A | N/A | N/A | N/A | 36154828 | 768 | 180.4511 | 0% | 0% | 100% | 0% | 100% | 35% | 8078326 | 905 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 95 | 32422970 | 4049 | 97.176 | 4.049 | 4.9 | 4.9 | 2B | 0 | 0 | 1069 | 0 | 1109 | N/A | N/A | N/A | N/A | 36155532 | 704 | 173.8701 | 0% | 0% | 100% | 0% | 100% | 35% | 8079248 | 922 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0417 | 124341 | 124341 | 124.341 | 124.341 | [12 empty] | 25436 | 25436 | 204.5665 | [6 empty] | 6427 | 6427 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
MAGALLANES IN-LINE FAULT AT 4:45 @ RESUME 6:15AM NORMAL OPERATION
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:01 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:40 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 12, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:16 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25176 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32422970 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36155532 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8079248 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 89 | 32426787 | 3817 | 91.608 | 3.817 | 6.1 | 6.1 | 2B | 0 | 0 | 1046 | 0 | 1059 | N/A | N/A | N/A | N/A | 36156164 | 632 | 165.5751 | 0% | 0% | 100% | 0% | 100% | 40% | 8080338 | 1090 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 86 | 32430542 | 3755 | 90.12 | 3.755 | 7.3 | 7.3 | 2B | 0 | 0 | 1038 | 0 | 1029 | N/A | N/A | N/A | N/A | 36156758 | 594 | 158.1891 | 0% | 0% | 100% | 0% | 100% | 40% | 8081444 | 1106 | 0.77 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 83 | 32434190 | 3648 | 87.552 | 3.648 | 8.5 | 8.5 | 2B | 0 | 0 | 1011 | 0 | 1028 | N/A | N/A | N/A | N/A | 36157310 | 552 | 151.3158 | 0% | 0% | 100% | 0% | 100% | 40% | 8082608 | 1164 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 84 | 32437796 | 3606 | 86.544 | 3.606 | 9.5 | 9.5 | 2B | 0 | 0 | 954 | 0 | 988 | N/A | N/A | N/A | N/A | 36157826 | 516 | 143.0948 | 0% | 0% | 100% | 0% | 100% | 40% | 8083680 | 1072 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 90 | 88 | 32441349 | 3553 | 85.272 | 3.553 | 9.5 | 9.5 | 2B | 0 | 0 | 912 | 0 | 988 | N/A | N/A | N/A | N/A | 36158314 | 488 | 137.3487 | 0% | 0% | 100% | 0% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 112 | 32445332 | 3983 | 95.592 | 3.983 | 9.5 | 9.5 | 2B | 0 | 0 | 1056 | 0 | 1108 | N/A | N/A | N/A | N/A | 36158924 | 610 | 153.1509 | 0% | 0% | 100% | 0% | 100% | 0% | 8083680 | 0 | 0.52 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 139 | 32451147 | 5815 | 139.56 | 5.815 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36160148 | 1224 | 210.4901 | 0% | 0% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 32457141 | 5994 | 143.856 | 5.994 | 9.3 | 9.3 | 3B+1S | 0 | 1041 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36161416 | 1268 | 211.5449 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 138 | 32463337 | 6196 | 148.704 | 6.196 | 8.7 | 8.7 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36162772 | 1356 | 218.8509 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 153 | 32469738 | 6401 | 153.624 | 6.401 | 8 | 8 | 3B+1S | 0 | 1098 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36164192 | 1420 | 221.8403 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 | 0.42 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 32475967 | 6229 | 149.496 | 6.229 | 7.3 | 7.3 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36165572 | 1380 | 221.5444 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 32482151 | 6184 | 148.416 | 6.184 | 6.9 | 6.9 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36166944 | 1372 | 221.8629 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 143 | 140 | 32488209 | 6058 | 145.392 | 6.058 | 6.7 | 6.7 | 3B+1S | 0 | 990 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36168292 | 1348 | 222.5157 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 141 | 32494066 | 5857 | 140.568 | 5.857 | 6.6 | 6.6 | 3B+1S | 0 | 1014 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36169620 | 1328 | 226.7372 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 | 0.49 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 32499885 | 5819 | 139.656 | 5.819 | 6.2 | 6.2 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36170956 | 1336 | 229.5927 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 32505782 | 5897 | 141.528 | 5.897 | 6 | 6 | 3B+1S | 0 | 1005 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36172311 | 1355 | 229.7779 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 134 | 32511396 | 5614 | 134.736 | 5.614 | 5.5 | 5.5 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1189 | N/A | N/A | N/A | N/A | 36173588 | 1277 | 227.467 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 32517301 | 5905 | 141.72 | 5.905 | 5.1 | 5.1 | 3B+1S | 0 | 1018 | 1176 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36174940 | 1352 | 228.9585 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 | 0.42 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 32522793 | 5492 | 131.808 | 5.492 | 4.8 | 4.8 | 3B+1S | 0 | 1012 | 1176 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36176172 | 1232 | 224.3263 | 0% | 100% | 100% | 100% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 127 | 32528145 | 5352 | 128.448 | 5.352 | 4 | 4 | 2B+1S | 0 | 1062 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36177244 | 1072 | 200.299 | 0% | 100% | 100% | 0% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 121 | 32533402 | 5257 | 126.168 | 5.257 | 3.4 | 3.4 | 2B+1S | 0 | 1011 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36178292 | 1048 | 199.3532 | 0% | 100% | 100% | 0% | 100% | 0% | 8083680 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 112 | 32538608 | 5206 | 124.944 | 5.206 | 3.3 | 3.3 | 2B+1S | 0 | 1013 | 1186 | 0 | 1180 | N/A | N/A | N/A | N/A | 36179320 | 1028 | 197.4645 | 0% | 100% | 100% | 0% | 100% | 0% | 8083680 | 0 | 0.51 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 101 | 32542593 | 3985 | 95.64 | 3.985 | 3.9 | 3.9 | 2B | 0 | 0 | 1095 | 0 | 1109 | N/A | N/A | N/A | N/A | 36180012 | 692 | 173.6512 | 0% | 0% | 100% | 0% | 100% | 30% | 8084337 | 657 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 96 | 32546701 | 4108 | 98.592 | 4.108 | 4.9 | 4.9 | 2B | 0 | 0 | 999 | 0 | 1110 | N/A | N/A | N/A | N/A | 36180708 | 696 | 169.4255 | 0% | 0% | 100% | 0% | 100% | 30% | 8085203 | 866 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.125 | 123731 | 123731 | 123.731 | 123.731 | [12 empty] | 25176 | 25176 | 203.4737 | [6 empty] | 5955 | 5955 | 0.52167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM , NORMAL OPERATION
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:10 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @10 25: AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 13, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @1:24PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @4:24PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:21PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:16PM , NORMAL OPERATION
NORMAL OPERATION

## APR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / F.A.RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26108 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32546701 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36180708 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8085203 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 95 | 32550312 | 3611 | 86.664 | 3.611 | 6 | 6 | 2B | 0 | 0 | 991 | 0 | 1109 | N/A | N/A | N/A | N/A | 36181332 | 624 | 172.8053 | 0% | 0% | 100% | 0% | 100% | 40% | 8086359 | 1156 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 106 | 32553747 | 3435 | 82.44 | 3.435 | 7.3 | 7.3 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 36181916 | 584 | 170.0146 | 0% | 0% | 100% | 0% | 100% | 40% | 8087617 | 1258 | 0.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 84 | 32557192 | 3445 | 82.68 | 3.445 | 8.6 | 8.6 | 2B | 0 | 0 | 935 | 0 | 1110 | N/A | N/A | N/A | N/A | 36182492 | 576 | 167.1988 | 0% | 0% | 100% | 0% | 100% | 40% | 8088840 | 1223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 87 | 32560814 | 3622 | 86.928 | 3.622 | 9.5 | 9.5 | 2B | 0 | 0 | 838 | 0 | 1111 | N/A | N/A | N/A | N/A | 36183052 | 560 | 154.6107 | 0% | 0% | 100% | 0% | 100% | 40% | 8089518 | 678 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 110 | 32564709 | 3895 | 93.48 | 3.895 | 9.5 | 9.5 | 2B | 0 | 0 | 866 | 0 | 1110 | N/A | N/A | N/A | N/A | 36183616 | 564 | 144.801 | 0% | 0% | 100% | 0% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 124 | 32569418 | 4709 | 113.016 | 4.709 | 9.5 | 9.5 | 2B | 0 | 0 | 1193 | 0 | 1149 | N/A | N/A | N/A | N/A | 36184340 | 724 | 153.7481 | 0% | 0% | 100% | 0% | 100% | 0% | 8089518 | 0 | 0.42 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 151 | 32575345 | 5927 | 142.248 | 5.927 | 8.9 | 8.9 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36185644 | 1304 | 220.0101 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Normal operation schedule | Power Interruption | PI | J. GALINATO / F.A.RAMOS
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 151 | 32581921 | 6576 | 157.824 | 6.576 | 8.3 | 8.3 | 3B+1S | 0 | 1095 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36187084 | 1440 | 218.9781 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 156 | 32588042 | 6121 | 146.904 | 6.121 | 7.7 | 7.7 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36188436 | 1352 | 220.8789 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 32594439 | 6397 | 153.528 | 6.397 | 7 | 7 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36189852 | 1416 | 221.3538 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 | 0.7 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 32600302 | 5863 | 140.712 | 5.863 | 6.6 | 6.6 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36191156 | 1304 | 222.4117 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 150 | 32606588 | 6286 | 150.864 | 6.286 | 6.2 | 6.2 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36192540 | 1384 | 220.1718 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 32612619 | 6031 | 144.744 | 6.031 | 6.2 | 6.2 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36193908 | 1368 | 226.8281 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 32618649 | 6030 | 144.72 | 6.03 | 5.2 | 5.2 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36195272 | 1364 | 226.2023 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 | 0.46 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 32624285 | 5636 | 135.264 | 5.636 | 4.9 | 4.9 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 36196572 | 1300 | 230.66 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 138 | 32630169 | 5884 | 141.216 | 5.884 | 4.7 | 4.7 | 3B+1S | 0 | 1042 | 1196 | 1185 | 1160 | N/A | N/A | N/A | N/A | 36197908 | 1336 | 227.0564 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 139 | 32635887 | 5718 | 137.232 | 5.718 | 3.9 | 3.9 | 3B+1S | 0 | 1168 | 1195 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36199228 | 1320 | 230.8499 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 138 | 32641612 | 5725 | 137.4 | 5.725 | 3.3 | 3.3 | 3B+1S | 0 | 1064 | 1176 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36200524 | 1296 | 226.3755 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 | 0.41 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 137 | 32647428 | 5816 | 139.584 | 5.816 | 2.8 | 2.8 | 3B+1S | 0 | 1072 | 1175 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36201820 | 1296 | 222.8336 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 32653086 | 5658 | 135.792 | 5.658 | 2.4 | 2.4 | 3B+1S | 0 | 1029 | 1145 | 1185 | 1138 | N/A | N/A | N/A | N/A | 36203092 | 1272 | 224.8144 | 0% | 100% | 100% | 100% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 128 | 32658186 | 5100 | 122.4 | 5.1 | 1.6 | 1.6 | 2B+1S | 0 | 1120 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36204156 | 1064 | 208.6275 | 0% | 100% | 100% | 0% | 100% | 0% | 8089518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 127 | 130 | 32663702 | 5516 | 132.384 | 5.516 | 1.3 | 1.3 | 3B | 0 | 0 | 998 | 1185 | 1160 | N/A | N/A | N/A | N/A | 36205276 | 1120 | 203.0457 | 0% | 0% | 100% | 100% | 100% | 0% | 8089518 | 0 | 0.64 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 99 | 32668070 | 4368 | 104.832 | 4.368 | 2.4 | 2.4 | 2B | 0 | 0 | 1060 | 1185 | 0 | N/A | N/A | N/A | N/A | 36206084 | 808 | 184.9817 | 0% | 0% | 100% | 100% | 0% | 40% | 8090569 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 93 | 32672087 | 4017 | 96.408 | 4.017 | 3.8 | 3.8 | 2B | 0 | 0 | 994 | 1185 | 0 | N/A | N/A | N/A | N/A | 36206816 | 732 | 182.2255 | 0% | 0% | 100% | 100% | 0% | 40% | 8091963 | 1394 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.625 | 125386 | 125386 | 125.386 | 125.386 | [12 empty] | 26108 | 26108 | 208.221 | [6 empty] | 6760 | 6760 | 0.49 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:24 AM , NORMAL OPERATION
XCV1 CLOSED @ 3:31 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
MAGALLANES IN-LINE FAULT AT 4:38 @ RESUME 5:23AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:13 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:23 AM , NORMAL OPERATION
SIROS PERSONNEL CHANGE THE DEFECTIVE FLUORESCENT LIGHTS 2PCS AND 1PC BALLAST OF THE ENGINEERING ROOM / ISOLATION TRANSFORMER ROOM 2PCS / VFD / SST ROOM - MOTOR CONTROL ROOM 2PCS AND 1PC BALLAST
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 14, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:22 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:13 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER 1 DEFECTIVE / BOOSTER 3 MANUAL OPERATION @ 7:40 PM
ENGR. ARTURO TRINIDAD AND MAINTENANCE TEAM ARRIVED @ 8:00PM FOR MONTHLY PREVENTIVE MAINTENANCE.
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:28 PM DUE TO LOW LOW WATER LEVEL
BP2 - STARTED @ 9:28 PM
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R.REGEMCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | J. GALINATO / F.A.RAMOS
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26156 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32672087 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36206816 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8091963 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 89 | 32675787 | 3700 | 88.8 | 3.7 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 950 | N/A | N/A | N/A | N/A | 36207492 | 676 | 182.7027 | 0% | 0% | 0% | 100% | 100% | 40% | 8093436 | 1473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 81 | 32679302 | 3515 | 84.36 | 3.515 | 7.1 | 7.1 | 2B | 0 | 0 | 1005 | 0 | 1042 | N/A | N/A | N/A | N/A | 36208104 | 612 | 174.111 | 0% | 0% | 100% | 0% | 100% | 35% | 8094980 | 1544 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 81 | 32682712 | 3410 | 81.84 | 3.41 | 8.3 | 8.3 | 2B | 0 | 0 | 1105 | 0 | 1000 | N/A | N/A | N/A | N/A | 36208644 | 540 | 158.3578 | 0% | 0% | 100% | 0% | 100% | 35% | 8096185 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 87 | 89 | 32686265 | 3553 | 85.272 | 3.553 | 9.5 | 9.5 | 2B | 0 | 0 | 954 | 0 | 937 | N/A | N/A | N/A | N/A | 36209168 | 524 | 147.481 | 0% | 0% | 100% | 0% | 100% | 35% | 8097286 | 1101 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 98 | 32690105 | 3840 | 92.16 | 3.84 | 9.5 | 9.5 | 2B | 0 | 0 | 954 | 0 | 989 | N/A | N/A | N/A | N/A | 36209708 | 540 | 140.625 | 0% | 0% | 100% | 0% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 122 | 32694793 | 4688 | 112.512 | 4.688 | 9.5 | 9.5 | 2B | 0 | 0 | 1155 | 0 | 1164 | N/A | N/A | N/A | N/A | 36210428 | 720 | 153.5836 | 0% | 0% | 100% | 0% | 100% | 0% | 8097286 | 0 | 0.84 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 149 | 32700839 | 6046 | 145.104 | 6.046 | 8.9 | 8.9 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36211772 | 1344 | 222.2957 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Normal operation schedule | Power Interruption | PI | J. GALINATO / R.REGEMCIA
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 153 | 32707123 | 6284 | 150.816 | 6.284 | 8.3 | 8.3 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36213148 | 1376 | 218.9688 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Normal operation schedule | Water Interruption | WI | J. GALINATO / F.A.RAMOS
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 157 | 32713456 | 6333 | 151.992 | 6.333 | 7.5 | 7.5 | 3B+1S | 0 | 1140 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36214564 | 1416 | 223.5907 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 32719713 | 6257 | 150.168 | 6.257 | 6.8 | 6.8 | 3B+1S | 0 | 1136 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36215955 | 1391 | 222.311 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 | 0.69 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 32726117 | 6404 | 153.696 | 6.404 | 6.1 | 6.1 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36217340 | 1385 | 216.2711 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 153 | 32732255 | 6138 | 147.312 | 6.138 | 5.7 | 5.7 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36218744 | 1404 | 228.739 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 32738314 | 6059 | 145.416 | 6.059 | 5.3 | 5.3 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36220110 | 1366 | 225.4497 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 142 | 32744375 | 6061 | 145.464 | 6.061 | 4.9 | 4.9 | 3B+1S | 0 | 1057 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36221476 | 1366 | 225.3754 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 | 0.45 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 32750252 | 5877 | 141.048 | 5.877 | 4.6 | 4.6 | 3B+1S | 0 | 1059 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36222810 | 1334 | 226.9866 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 136 | 32755518 | 5266 | 126.384 | 5.266 | 4.4 | 4.4 | 3B+1S | 0 | 1051 | 1164 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36224020 | 1210 | 229.7759 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 143 | 32761252 | 5734 | 137.616 | 5.734 | 3.8 | 3.8 | 3B+1S | 0 | 1189 | 1165 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36225332 | 1312 | 228.8106 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 138 | 32767007 | 5755 | 138.12 | 5.755 | 3.3 | 3.3 | 3B+1S | 0 | 1173 | 1165 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36226648 | 1316 | 228.6707 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 | 0.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 133 | 32772635 | 5628 | 135.072 | 5.628 | 3 | 3 | 3B+1S | 0 | 1189 | 1165 | 1185 | 1149 | N/A | N/A | N/A | N/A | 36227996 | 1348 | 239.5167 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 127 | 32778012 | 5377 | 129.048 | 5.377 | 2.8 | 2.8 | 3B+1S | 0 | 1101 | 1145 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36229288 | 1292 | 240.2827 | 0% | 100% | 100% | 100% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 128 | 32783017 | 5005 | 120.12 | 5.005 | 2.4 | 2.4 | 2B+1S | 0 | 1150 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36230388 | 1100 | 219.7802 | 0% | 100% | 100% | 0% | 100% | 0% | 8097286 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 125 | 32788401 | 5384 | 129.216 | 5.384 | 1.9 | 1.9 | 2B+1S | 0 | 1000 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 36231476 | 1088 | 202.0802 | 0% | 100% | 100% | 0% | 100% | 0% | 8097286 | 0 | 0.41 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 102 | 32792740 | 4339 | 104.136 | 4.339 | 2.8 | 2.8 | 2B | 0 | 0 | 1131 | 0 | 1109 | N/A | N/A | N/A | N/A | 36232278 | 802 | 184.8352 | 0% | 0% | 100% | 0% | 100% | 35% | 8098215 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 98 | 32796729 | 3989 | 95.736 | 3.989 | 4 | 4 | 2B | 0 | 0 | 1069 | 0 | 1079 | N/A | N/A | N/A | N/A | 36232972 | 694 | 173.9784 | 0% | 0% | 100% | 0% | 100% | 35% | 8099277 | 1062 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9167 | 124642 | 124642 | 124.642 | 124.642 | [12 empty] | 26156 | 26156 | 209.849 | [6 empty] | 7314 | 7314 | 0.595 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
BP1 - STOPPED @ 12:17 AM
BP3 - STARTED @ 12:18 AM
BP2 - STOPPED @ 1:13 AM
BP1 - STARTED @ 1:14 AM
XCV1 CLOSED @ 3:54 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT AT 5:48 @ RESUME 6:53 AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:55 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:10 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 15, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:31 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM TO 3:10 PM WITH SIR GERRY BAUTISTA @ DANFOSS COMPANY MR. ROMEWELLE GO, TO PERFORM STATIC TEST @ PHYSICAL INSPECTION OF VFD.BUSTED POWER CARD FUSE @ 1PC. POWER CARD
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:50 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:22 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:02 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED SITE INSPECTION WITH SIR MARIANITO BARAHAN AND SIR MICHAEL BULIGAN AND SIR ARTURO TRINIDAD TO ASSISTED THE DELIVERY TRUCK TO UNLOADING THE ONE UNIT OF PUMP MOTOR AT VILLAMOR PS
NORMAL OPERATION

## APR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO / R. MALLARI
WATER NETWORK | [12 empty] | 2pm - 10pm | J. GALINATO / F.A.RAMOS
[13 empty] | 10pm - 6am | J. GALINATO / F.A.RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26460 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32796729 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36232972 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8099277 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 89 | 32800478 | 3749 | 89.976 | 3.749 | 5.4 | 5.4 | 2B | 0 | 0 | 1069 | 0 | 1079 | N/A | N/A | N/A | N/A | 36233630 | 658 | 175.5135 | 0% | 0% | 100% | 0% | 100% | 45% | 8100548 | 1271 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 85 | 32804087 | 3609 | 86.616 | 3.609 | 6.7 | 6.7 | 2B | 0 | 0 | 1040 | 0 | 1059 | N/A | N/A | N/A | N/A | 36234252 | 622 | 172.3469 | 0% | 0% | 100% | 0% | 100% | 45% | 8101850 | 1302 | 0.72 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 84 | 32807628 | 3541 | 84.984 | 3.541 | 8.2 | 8.2 | 2B | 0 | 0 | 1023 | 0 | 1037 | N/A | N/A | N/A | N/A | 36234834 | 582 | 164.3604 | 0% | 0% | 100% | 0% | 100% | 45% | 8103178 | 1328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 86 | 32811203 | 3575 | 85.8 | 3.575 | 9.5 | 9.5 | 2B | 0 | 0 | 958 | 0 | 959 | N/A | N/A | N/A | N/A | 36235388 | 554 | 154.965 | 0% | 0% | 100% | 0% | 100% | 45% | 8104450 | 1272 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 95 | 32815009 | 3806 | 91.344 | 3.806 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 0 | 969 | N/A | N/A | N/A | N/A | 36235956 | 568 | 149.238 | 0% | 0% | 100% | 0% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 124 | 32819622 | 4613 | 110.712 | 4.613 | 9.5 | 9.5 | 2B | 0 | 0 | 1154 | 0 | 1160 | N/A | N/A | N/A | N/A | 36236652 | 696 | 150.878 | 0% | 0% | 100% | 0% | 100% | 0% | 8104450 | 0 | 0.54 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 151 | 32825708 | 6086 | 146.064 | 6.086 | 8.9 | 8.9 | 3B+1S | 0 | 1077 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36238004 | 1352 | 222.1492 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Normal operation schedule | Power Interruption | PI | J. GALINATO / F.A.RAMOS
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 153 | 32832006 | 6298 | 151.152 | 6.298 | 8.2 | 8.2 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36239411 | 1407 | 223.4043 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 154 | 32838390 | 6384 | 153.216 | 6.384 | 7.5 | 7.5 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36240828 | 1417 | 221.9612 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 153 | 32844687 | 6297 | 151.128 | 6.297 | 6.8 | 6.8 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36242221 | 1393 | 221.2165 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 | 0.79 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 32851031 | 6344 | 152.256 | 6.344 | 6.1 | 6.1 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36243536 | 1315 | 207.2825 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 32857213 | 6182 | 148.368 | 6.182 | 5.5 | 5.5 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36245012 | 1476 | 238.7577 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 149 | 32863346 | 6133 | 147.192 | 6.133 | 5 | 5 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36246340 | 1328 | 216.5335 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 148 | 32869298 | 5952 | 142.848 | 5.952 | 4.5 | 4.5 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36247740 | 1400 | 235.2151 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 | 0.69 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 143 | 32875222 | 5924 | 142.176 | 5.924 | 4.1 | 4.1 | 3B+1S | 0 | 1088 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36249068 | 1328 | 224.1729 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 142 | 32880966 | 5744 | 137.856 | 5.744 | 3.7 | 3.7 | 3B+1S | 0 | 1127 | 1177 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36250352 | 1284 | 223.5376 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 142 | 32887115 | 6149 | 147.576 | 6.149 | 3.1 | 3.1 | 3B+1S | 0 | 1099 | 1176 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36251756 | 1404 | 228.3298 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 137 | 32892841 | 5726 | 137.424 | 5.726 | 2.6 | 2.6 | 3B+1S | 0 | 1143 | 1186 | 1185 | 1168 | N/A | N/A | N/A | N/A | 36253092 | 1336 | 233.3217 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 | 0.59 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 141 | 32898534 | 5693 | 136.632 | 5.693 | 2.2 | 2.2 | 3B+1S | 0 | 1188 | 1186 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36254468 | 1376 | 241.7003 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 134 | 32903930 | 5396 | 129.504 | 5.396 | 2.1 | 2.1 | 3B+1S | 0 | 1001 | 1176 | 1185 | 1171 | N/A | N/A | N/A | N/A | 36255768 | 1300 | 240.9192 | 0% | 100% | 100% | 100% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 134 | 136 | 32909405 | 5475 | 131.4 | 5.475 | 1.4 | 1.4 | 2B+1S | 0 | 1002 | 1185 | 0 | 1198 | N/A | N/A | N/A | N/A | 36257120 | 1352 | 246.9406 | 0% | 100% | 100% | 0% | 100% | 0% | 8104450 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 117 | 32914357 | 4952 | 118.848 | 4.952 | 1.3 | 1.3 | 2B | 0 | 0 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36257868 | 748 | 151.0501 | 0% | 0% | 100% | 0% | 100% | 0% | 8104450 | 0 | 0.5 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 102 | 32918563 | 4206 | 100.944 | 4.206 | 1.9 | 1.9 | 2B | 0 | 0 | 1186 | 0 | 1110 | N/A | N/A | N/A | N/A | 36258644 | 776 | 184.4983 | 0% | 0% | 100% | 0% | 100% | 30% | 8105008 | 558 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 97 | 32923018 | 4455 | 106.92 | 4.455 | 2.8 | 2.8 | 2B | 0 | 0 | 1069 | 0 | 1088 | N/A | N/A | N/A | N/A | 36259432 | 788 | 176.8799 | 0% | 0% | 100% | 0% | 100% | 30% | 8105899 | 891 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.625 | 126289 | 126289 | 126.289 | 126.289 | [12 empty] | 26460 | 26460 | 209.5194 | [6 empty] | 6622 | 6622 | 0.63833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 3:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:12 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:21 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:23 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 16, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:47 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:22 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:28 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,826
GENSET 1 WARMUP EXERCISED @ 4:17PM / STOPPED @ 4:27PM
GENSET 2 WARMUP EXERCISED @ 4:06PM / STOPPED @ 4:16PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:16 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:00 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:00 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:05 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:03 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:00 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | R. REGENCIA / J. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26470 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 32923018 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36259432 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8105899 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 90 | 32926832 | 3814 | 91.536 | 3.814 | 4.5 | 4.5 | 2B | 0 | 0 | 1083 | 0 | 1088 | N/A | N/A | N/A | N/A | 36260116 | 684 | 179.3393 | 0% | 0% | 100% | 0% | 100% | 40% | 8107203 | 1304 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 91 | 32930697 | 3865 | 92.76 | 3.865 | 5.7 | 5.7 | 2B | 0 | 0 | 1041 | 0 | 1088 | N/A | N/A | N/A | N/A | 36260788 | 672 | 173.868 | 0% | 0% | 100% | 0% | 100% | 40% | 8108647 | 1444 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 87 | 32934251 | 3554 | 85.296 | 3.554 | 7.6 | 7.6 | 2B | 0 | 0 | 991 | 0 | 1087 | N/A | N/A | N/A | N/A | 36261588 | 800 | 225.0985 | 0% | 0% | 100% | 0% | 100% | 40% | 8110408 | 1761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 87 | 32937788 | 3537 | 84.888 | 3.537 | 8.6 | 8.6 | 2B | 0 | 0 | 987 | 0 | 1109 | N/A | N/A | N/A | N/A | 36262400 | 812 | 229.5731 | 0% | 0% | 100% | 0% | 100% | 40% | 8111281 | 873 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 96 | 32941799 | 4011 | 96.264 | 4.011 | 9.5 | 9.5 | 2B | 0 | 0 | 902 | 0 | 1110 | N/A | N/A | N/A | N/A | 36262988 | 588 | 146.5969 | 0% | 0% | 100% | 0% | 100% | 40% | 8112081 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 127 | 128 | 32946281 | 4482 | 107.568 | 4.482 | 9.5 | 9.5 | 2B | 0 | 0 | 1160 | 0 | 1169 | N/A | N/A | N/A | N/A | 36263540 | 552 | 123.1593 | 0% | 0% | 100% | 0% | 100% | 0% | 8112081 | 0 | 1.04 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 155 | 32952654 | 6373 | 152.952 | 6.373 | 8.7 | 8.7 | 3B+1S | 0 | 1104 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36264748 | 1208 | 189.5497 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Normal operation schedule | Power Interruption | PI | R. REGENCIA / J. GALINATO
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 154 | 32959027 | 6373 | 152.952 | 6.373 | 8.1 | 8.1 | 3B+1S | 0 | 1160 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36266164 | 1416 | 222.1874 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 152 | 32965348 | 6321 | 151.704 | 6.321 | 7.2 | 7.2 | 3B+1S | 0 | 1122 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36267572 | 1408 | 222.7496 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 32971649 | 6301 | 151.224 | 6.301 | 6.5 | 6.5 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36268988 | 1416 | 224.7262 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 32977889 | 6240 | 149.76 | 6.24 | 5.8 | 5.8 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36270380 | 1392 | 223.0769 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 32984016 | 6127 | 147.048 | 6.127 | 5.4 | 5.4 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36271748 | 1368 | 223.274 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 32989836 | 5820 | 139.68 | 5.82 | 5.3 | 5.3 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36273050 | 1302 | 223.7113 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 32995721 | 5885 | 141.24 | 5.885 | 4.7 | 4.7 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36274416 | 1366 | 232.1155 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 | 0.54 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 33001479 | 5758 | 138.192 | 5.758 | 4.5 | 4.5 | 3B+1S | 0 | 1036 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36275732 | 1316 | 228.5516 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 33006935 | 5456 | 130.944 | 5.456 | 4.4 | 4.4 | 3B+1S | 0 | 1044 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36276996 | 1264 | 231.6716 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 144 | 33012761 | 5826 | 139.824 | 5.826 | 3.6 | 3.6 | 3B+1S | 0 | 1182 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36278354 | 1358 | 233.093 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 137 | 33018681 | 5920 | 142.08 | 5.92 | 3 | 3 | 3B+1S | 0 | 1071 | 1176 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36279708 | 1354 | 228.7162 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 136 | 33024302 | 5621 | 134.904 | 5.621 | 2.7 | 2.7 | 3B+1S | 0 | 1070 | 1186 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36280996 | 1288 | 229.1407 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 130 | 33029957 | 5655 | 135.72 | 5.655 | 2.5 | 2.5 | 3B+1S | 0 | 997 | 1164 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36282308 | 1312 | 232.0071 | 0% | 100% | 100% | 100% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 125 | 33035163 | 5206 | 124.944 | 5.206 | 1.8 | 1.8 | 2B+1S | 0 | 1188 | 1186 | 0 | 1169 | N/A | N/A | N/A | N/A | 36283404 | 1096 | 210.5263 | 0% | 100% | 100% | 0% | 100% | 0% | 8112081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 108 | 33040360 | 5197 | 124.728 | 5.197 | 1.3 | 1.3 | 2B | 0 | 0 | 1154 | 0 | 1109 | N/A | N/A | N/A | N/A | 36284372 | 968 | 186.2613 | 0% | 0% | 100% | 0% | 100% | 0% | 8112081 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 100 | 33044477 | 4117 | 98.808 | 4.117 | 2.4 | 2.4 | 2B | 0 | 0 | 1103 | 0 | 1160 | N/A | N/A | N/A | N/A | 36285152 | 780 | 189.4583 | 0% | 0% | 100% | 0% | 100% | 40% | 8113085 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 98 | 33048451 | 3974 | 95.376 | 3.974 | 4.6 | 4.6 | 2B | 0 | 0 | 998 | 0 | 1131 | N/A | N/A | N/A | N/A | 36285902 | 750 | 188.7267 | 0% | 0% | 100% | 0% | 100% | 40% | 8114280 | 1195 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9167 | 125433 | 125433 | 125.433 | 125.433 | [12 empty] | 26470 | 26470 | 211.029 | [6 empty] | 8381 | 8381 | 0.91 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:56 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:56 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:18 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:23 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:05 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 17, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:18 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:19 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:30 PM DUE TO LOW WATER LEVEL ( 1.3M )
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:00 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:00 PM TO 6:00AM VFD NORMAL OPERATIONAL RESUMED 5:40AM AND INSTALLED THE 1 UNIT OF BOX FOR SUCTION AND DISCHARGE
NORMAL OPERATION

## APR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | A.CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26030 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33048451 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36285902 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8114280 |  | mg /l |  | Automatic - i2O | AI | A.CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 98 | 33052141 | 3690 | 88.56 | 3.69 | 5.8 | 5.8 | 2B | 0 | 0 | 999 | 0 | 1115 | N/A | N/A | N/A | N/A | 36286547 | 645 | 174.7967 | 0% | 0% | 100% | 0% | 100% | 48% | 8115601 | 1321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 33055831 | 3690 | 88.56 | 3.69 | 6.5 | 6.5 | 2B | 0 | 0 | 995 | 0 | 1119 | N/A | N/A | N/A | N/A | 36287192 | 645 | 174.7967 | 0% | 0% | 100% | 0% | 100% | 48% | 8116922 | 1321 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 87 | 33059434 | 3603 | 86.472 | 3.603 | 8.2 | 8.2 | 2B | 0 | 0 | 986 | 0 | 1109 | N/A | N/A | N/A | N/A | 36287797 | 605 | 167.9156 | 0% | 0% | 100% | 0% | 100% | 48% | 8118320 | 1398 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 96 | 33063027 | 3593 | 86.232 | 3.593 | 9.1 | 9.1 | 2B | 0 | 0 | 991 | 0 | 1110 | N/A | N/A | N/A | N/A | 36288382 | 585 | 162.8166 | 0% | 0% | 100% | 0% | 100% | 48% | 8119718 | 1398 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 96 | 33066610 | 3583 | 85.992 | 3.583 | 9.5 | 9.5 | 2B | 0 | 0 | 876 | 0 | 1100 | N/A | N/A | N/A | N/A | 36288948 | 566 | 157.9682 | 0% | 0% | 100% | 0% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 14 | 9.8592 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 123 | 33071283 | 4673 | 112.152 | 4.673 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1100 | N/A | N/A | N/A | N/A | 36289660 | 712 | 152.3646 | 0% | 0% | 100% | 0% | 100% | 0% | 8119718 | 0 | 0.72 | Normal operation schedule | Error - General | E | J. GALINATO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 151 | 33077416 | 6133 | 147.192 | 6.133 | 8.8 | 8.8 | 3B+1S | 0 | 1168 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36291020 | 1360 | 221.7512 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 155 | 33083697 | 6281 | 150.744 | 6.281 | 8.2 | 8.2 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36292412 | 1392 | 221.6208 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 154 | 33090014 | 6317 | 151.608 | 6.317 | 7.5 | 7.5 | 3B+1S | 0 | 1127 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36293812 | 1400 | 221.6242 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 33096408 | 6394 | 153.456 | 6.394 | 6.8 | 6.8 | 3B+1S | 0 | 1152 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36295244 | 1432 | 223.96 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 | 0.84 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 33102559 | 6151 | 147.624 | 6.151 | 6.1 | 6.1 | 3B+1S | 0 | 1083 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36296620 | 1376 | 223.7035 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 33108569 | 6010 | 144.24 | 6.01 | 5.7 | 5.7 | 3B+1S | 0 | 1070 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36298014 | 1394 | 231.9468 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 147 | 33114785 | 6216 | 149.184 | 6.216 | 5.1 | 5.1 | 3B+1S | 0 | 1083 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36299348 | 1334 | 214.6075 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 33120597 | 5812 | 139.488 | 5.812 | 4.7 | 4.7 | 3B+1S | 0 | 1040 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36300732 | 1384 | 238.128 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 | 0.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 33126588 | 5991 | 143.784 | 5.991 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36302124 | 1392 | 232.3485 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 33132136 | 5548 | 133.152 | 5.548 | 4.4 | 4.4 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1189 | N/A | N/A | N/A | N/A | 36303432 | 1308 | 235.7606 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 143 | 33138123 | 5987 | 143.688 | 5.987 | 3.6 | 3.6 | 3B+1S | 0 | 1142 | 1196 | 1185 | 1183 | N/A | N/A | N/A | N/A | 36304841 | 1409 | 235.3432 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 132 | 33143484 | 5361 | 128.664 | 5.361 | 3.4 | 3.4 | 3B+1S | 0 | 1060 | 1164 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36306060 | 1219 | 227.383 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 138 | 33149035 | 5551 | 133.224 | 5.551 | 3.1 | 3.1 | 3B+1S | 0 | 1045 | 1165 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36307308 | 1248 | 224.8244 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 133 | 33154489 | 5454 | 130.896 | 5.454 | 2.9 | 2.9 | 3B+1S | 0 | 990 | 1155 | 185 | 1148 | N/A | N/A | N/A | N/A | 36308544 | 1236 | 226.6227 | 0% | 100% | 100% | 100% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 105 | 125 | 33159800 | 5311 | 127.464 | 5.311 | 2.1 | 2.1 | 2B+1S | 0 | 1189 | 1156 | 0 | 1148 | N/A | N/A | N/A | N/A | 36309612 | 1068 | 201.0921 | 0% | 100% | 100% | 0% | 100% | 0% | 8119718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 | 122 | 33164820 | 5020 | 120.48 | 5.02 | 1.4 | 1.4 | 2B+1S | 0 | 1012 | 1155 | 0 | 1148 | N/A | N/A | N/A | N/A | 36310564 | 952 | 189.6414 | 0% | 100% | 100% | 0% | 100% | 0% | 8119718 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 90 | 33168743 | 3923 | 94.152 | 3.923 | 2.7 | 2.7 | 2B | 0 | 0 | 1071 | 0 | 1110 | N/A | N/A | N/A | N/A | 36311292 | 728 | 185.5723 | 0% | 0% | 100% | 0% | 100% | 45% | 8121130 | 1412 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 84 | 33172269 | 3526 | 84.624 | 3.526 | 4.6 | 4.6 | 2B | 0 | 0 | 1000 | 0 | 1110 | N/A | N/A | N/A | N/A | 36311932 | 640 | 181.5088 | 0% | 0% | 100% | 0% | 100% | 45% | 8122729 | 1599 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9583 | 123818 | 123818 | 123.818 | 123.818 | [12 empty] | 26030 | 26030 | 210.2279 | [6 empty] | 8449 | 8449 | 0.84667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (48%) @ 12:01 AM
XCV1 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:32 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:14 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:00 AM TO 6:00 PM WITH MR. FELIX OF EXPONENT
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:06 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:23 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:52 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:26 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:24 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JR. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25884 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33172269 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36311932 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8122729 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 77 | 33175529 | 3260 | 78.24 | 3.26 | 6.5 | 6.5 | 2B | 0 | 0 | 985 | 0 | 1088 | N/A | N/A | N/A | N/A | 36312524 | 592 | 181.5951 | 0% | 0% | 100% | 0% | 100% | 50% | 8124412 | 1683 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 81 | 33179004 | 3475 | 83.4 | 3.475 | 8.3 | 8.3 | 2B | 0 | 0 | 920 | 0 | 1068 | N/A | N/A | N/A | N/A | 36313110 | 586 | 168.6331 | 0% | 0% | 100% | 0% | 100% | 50% | 8126092 | 1680 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 88 | 33182479 | 3475 | 83.4 | 3.475 | 9.5 | 9.5 | 2B | 0 | 0 | 877 | 0 | 1067 | N/A | N/A | N/A | N/A | 36313696 | 586 | 168.6331 | 0% | 0% | 100% | 0% | 100% | 50% | 8127372 | 1280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 90 | 33186171 | 3692 | 88.608 | 3.692 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 1008 | N/A | N/A | N/A | N/A | 36314216 | 520 | 140.8451 | 0% | 0% | 100% | 0% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 95 | 33189864 | 3693 | 88.632 | 3.693 | 9.5 | 9.5 | 2B | 0 | 0 | 901 | 0 | 1009 | N/A | N/A | N/A | N/A | 36314716 | 500 | 135.3913 | 0% | 0% | 100% | 0% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 99 | 119 | 33194369 | 4505 | 108.12 | 4.505 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1199 | N/A | N/A | N/A | N/A | 36315400 | 684 | 151.8313 | 0% | 0% | 100% | 0% | 100% | 0% | 8127372 | 0 | 0.84 | Normal operation schedule | Error - General | E | JR. GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 147 | 33200415 | 6046 | 145.104 | 6.046 | 9.4 | 9.4 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36316688 | 1288 | 213.0334 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 151 | 33206834 | 6419 | 154.056 | 6.419 | 8.9 | 8.9 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36318092 | 1404 | 218.7257 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 152 | 33213115 | 6281 | 150.744 | 6.281 | 8.3 | 8.3 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36319508 | 1416 | 225.4418 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 156 | 33219482 | 6367 | 152.808 | 6.367 | 7.6 | 7.6 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36320950 | 1442 | 226.4803 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 33225799 | 6317 | 151.608 | 6.317 | 6.9 | 6.9 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36322370 | 1420 | 224.7902 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 149 | 33232141 | 6342 | 152.208 | 6.342 | 6.4 | 6.4 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36323802 | 1432 | 225.7963 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 33238227 | 6086 | 146.064 | 6.086 | 6 | 6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36325106 | 1304 | 214.2622 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 141 | 33244298 | 6071 | 145.704 | 6.071 | 5.6 | 5.6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36326390 | 1284 | 211.4973 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 33250072 | 5774 | 138.576 | 5.774 | 5.4 | 5.4 | 3B+1S | 0 | 1001 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36327700 | 1310 | 226.8791 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 33255872 | 5800 | 139.2 | 5.8 | 5.1 | 5.1 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36329020 | 1320 | 227.5862 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 33261650 | 5778 | 138.672 | 5.778 | 4.7 | 4.7 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36330348 | 1328 | 229.8373 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 33267469 | 5819 | 139.656 | 5.819 | 4.4 | 4.4 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36331672 | 1324 | 227.5305 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 139 | 33273270 | 5801 | 139.224 | 5.801 | 4 | 4 | 3B+1S | 0 | 1015 | 1133 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36332976 | 1304 | 224.7888 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 129 | 33278730 | 5460 | 131.04 | 5.46 | 3.7 | 3.7 | 3B+1S | 0 | 999 | 1103 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36334212 | 1236 | 226.3736 | 0% | 100% | 100% | 100% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 126 | 33284040 | 5310 | 127.44 | 5.31 | 2.9 | 2.9 | 2B+1S | 0 | 1063 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 36335292 | 1080 | 203.3898 | 0% | 100% | 100% | 0% | 100% | 0% | 8127372 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 123 | 33289163 | 5123 | 122.952 | 5.123 | 2.6 | 2.6 | 2B+1S | 0 | 998 | 1195 | 0 | 1199 | N/A | N/A | N/A | N/A | 36336312 | 1020 | 199.1021 | 0% | 100% | 100% | 0% | 100% | 0% | 8127372 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 99 | 33293496 | 4333 | 103.992 | 4.333 | 3.4 | 3.4 | 2B | 0 | 0 | 1119 | 0 | 1110 | N/A | N/A | N/A | N/A | 36337100 | 788 | 181.8601 | 0% | 0% | 100% | 0% | 100% | 35% | 8128216 | 844 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 97 | 33297571 | 4075 | 97.8 | 4.075 | 4.6 | 4.6 | 2B | 0 | 0 | 1056 | 0 | 1110 | N/A | N/A | N/A | N/A | 36337816 | 716 | 175.7055 | 0% | 0% | 100% | 0% | 100% | 35% | 8129202 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 125302 | 125302 | 125.302 | 125.302 | [12 empty] | 25884 | 25884 | 206.5729 | [6 empty] | 6473 | 6473 | 0.98833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:43 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT AT 4:32 @ RESUME 6:44 AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:44 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:14 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:09 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 19, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:14 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:36 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JR. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25548 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33297571 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36337816 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8129202 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 91 | 33301354 | 3783 | 90.792 | 3.783 | 5.7 | 5.7 | 2B | 0 | 0 | 1034 | 0 | 1110 | N/A | N/A | N/A | N/A | 36338484 | 668 | 176.5794 | 0% | 0% | 100% | 0% | 100% | 42% | 8130223 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 85 | 33304975 | 3621 | 86.904 | 3.621 | 6.9 | 6.9 | 2B | 0 | 0 | 1044 | 0 | 1049 | N/A | N/A | N/A | N/A | 36339116 | 632 | 174.5374 | 0% | 0% | 100% | 0% | 100% | 42% | 8131413 | 1190 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 87 | 33308524 | 3549 | 85.176 | 3.549 | 8.2 | 8.2 | 2B | 0 | 0 | 1008 | 0 | 1049 | N/A | N/A | N/A | N/A | 36339708 | 592 | 166.8076 | 0% | 0% | 100% | 0% | 100% | 42% | 8132604 | 1191 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 86 | 33312083 | 3559 | 85.416 | 3.559 | 9.3 | 9.3 | 2B | 0 | 0 | 1014 | 0 | 1008 | N/A | N/A | N/A | N/A | 36340264 | 556 | 156.2237 | 0% | 0% | 100% | 0% | 100% | 42% | 8133802 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 94 | 92 | 33315785 | 3702 | 88.848 | 3.702 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 0 | 957 | N/A | N/A | N/A | N/A | 36340772 | 508 | 137.2231 | 0% | 0% | 100% | 0% | 100% | 42% | 8133875 | 73 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 116 | 114 | 33320096 | 4311 | 103.464 | 4.311 | 9.5 | 9.5 | 3B | 0 | 0 | 1094 | 0 | 1198 | N/A | N/A | N/A | N/A | 36341384 | 612 | 141.9624 | 0% | 0% | 100% | 100% | 100% | 0% | 8133875 | 0 | 0.72 | Normal operation schedule | Error - General | E | JR. GALINATO
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 145 | 33325780 | 5684 | 136.416 | 5.684 | 9.5 | 9.5 | 3B | 0 | 0 | 1194 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36342580 | 1196 | 210.4152 | 0% | 0% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 150 | 33331827 | 6047 | 145.128 | 6.047 | 9.4 | 9.4 | 3B+1S | 0 | 1000 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36343872 | 1292 | 213.6597 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 153 | 33338072 | 6245 | 149.88 | 6.245 | 9 | 9 | 3B+1S | 0 | 1051 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36345232 | 1360 | 217.7742 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 152 | 33344430 | 6358 | 152.592 | 6.358 | 8.3 | 8.3 | 3B+1S | 0 | 1052 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36346640 | 1408 | 221.4533 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 156 | 33350772 | 6342 | 152.208 | 6.342 | 7.7 | 7.7 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36348036 | 1396 | 220.1198 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 33357093 | 6321 | 151.704 | 6.321 | 7.1 | 7.1 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36349428 | 1392 | 220.2183 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 143 | 33363119 | 6026 | 144.624 | 6.026 | 6.8 | 6.8 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36350760 | 1332 | 221.0422 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 141 | 33369097 | 5978 | 143.472 | 5.978 | 6.5 | 6.5 | 3B+1S | 0 | 999 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36352118 | 1358 | 227.1663 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 | 0.55 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 33375043 | 5946 | 142.704 | 5.946 | 6.1 | 6.1 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36353452 | 1334 | 224.3525 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 138 | 33380682 | 5639 | 135.336 | 5.639 | 5.9 | 5.9 | 3B+1S | 0 | 1015 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36354728 | 1276 | 226.2813 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 140 | 33386285 | 5603 | 134.472 | 5.603 | 5.3 | 5.3 | 3B+1S | 0 | 1096 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36356044 | 1316 | 234.8742 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 33392128 | 5843 | 140.232 | 5.843 | 4.9 | 4.9 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1179 | N/A | N/A | N/A | N/A | 36357372 | 1328 | 227.2805 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 | 0.49 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 138 | 33397661 | 5533 | 132.792 | 5.533 | 4.7 | 4.7 | 3B+1S | 0 | 983 | 1187 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36358624 | 1252 | 226.2787 | 0% | 100% | 100% | 100% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 131 | 33403260 | 5599 | 134.376 | 5.599 | 3.7 | 3.7 | 3B+1S | 0 | 1140 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 36359756 | 1132 | 202.179 | 0% | 100% | 100% | 0% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 124 | 33408720 | 5460 | 131.04 | 5.46 | 2.8 | 2.8 | 3B+1S | 0 | 1091 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 36360868 | 1112 | 203.663 | 0% | 100% | 100% | 0% | 100% | 0% | 8133875 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 124 | 33413679 | 4959 | 119.016 | 4.959 | 2.3 | 2.3 | 3B+1S | 0 | 1023 | 1196 | 0 | 1191 | N/A | N/A | N/A | N/A | 36361864 | 996 | 200.8469 | 0% | 100% | 100% | 0% | 100% | 0% | 8133875 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 96 | 33418129 | 4450 | 106.8 | 4.45 | 2.8 | 2.8 | 2B | 0 | 0 | 1103 | 0 | 1109 | N/A | N/A | N/A | N/A | 36362676 | 812 | 182.4719 | 0% | 0% | 100% | 0% | 100% | 30% | 8134523 | 648 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 96 | 33422109 | 3980 | 95.52 | 3.98 | 3.7 | 3.7 | 2B | 0 | 0 | 1037 | 0 | 1109 | N/A | N/A | N/A | N/A | 36363364 | 688 | 172.8643 | 0% | 0% | 100% | 0% | 100% | 30% | 8135361 | 838 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.2917 | 124538 | 124538 | 124.538 | 124.538 | [12 empty] | 25548 | 25548 | 205.1422 | [6 empty] | 6159 | 6159 | 0.77833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (42%) @ 12:01 AM
XCV1 CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:17 AM , NORMAL OPERATION
SP2 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:07 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:08 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 20, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:31 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:35 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JR. GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | J. GALINATO / R. REGENCIA
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26168 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33422109 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36363364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8135361 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 88 | 33425849 | 3740 | 89.76 | 3.74 | 5.1 | 5.1 | 2B | 0 | 0 | 1027 | 0 | 1110 | N/A | N/A | N/A | N/A | 36364020 | 656 | 175.4011 | 0% | 0% | 100% | 0% | 100% | 40% | 8136563 | 1202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | J. GALINATO / R. REGENCIA
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 88 | 33429342 | 3493 | 83.832 | 3.493 | 6.3 | 6.3 | 2B | 0 | 0 | 966 | 0 | 1109 | N/A | N/A | N/A | N/A | 36364628 | 608 | 174.0624 | 0% | 0% | 100% | 0% | 100% | 40% | 8137876 | 1313 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 85 | 33432761 | 3419 | 82.056 | 3.419 | 7.9 | 7.9 | 2B | 0 | 0 | 934 | 0 | 1110 | N/A | N/A | N/A | N/A | 36365204 | 576 | 168.4703 | 0% | 0% | 100% | 0% | 100% | 40% | 8139286 | 1410 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 82 | 33436194 | 3433 | 82.392 | 3.433 | 9.4 | 9.4 | 2B | 0 | 0 | 931 | 0 | 1110 | N/A | N/A | N/A | N/A | 36365772 | 568 | 165.453 | 0% | 0% | 100% | 0% | 100% | 40% | 8140675 | 1389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 94 | 33440090 | 3896 | 93.504 | 3.896 | 9.5 | 9.5 | 2B | 0 | 0 | 863 | 0 | 1110 | N/A | N/A | N/A | N/A | 36366348 | 576 | 147.8439 | 0% | 0% | 100% | 0% | 100% | 40% | 8140756 | 81 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 128 | 123 | 33444787 | 4697 | 112.728 | 4.697 | 9.5 | 9.5 | 2B | 0 | 0 | 1170 | 0 | 1087 | N/A | N/A | N/A | N/A | 36367092 | 744 | 158.399 | 0% | 0% | 100% | 0% | 100% | 0% | 8140756 | 0 | 0.44 | Normal operation schedule | Error - General | E | JR. GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 149 | 33450850 | 6063 | 145.512 | 6.063 | 9.1 | 9.1 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36368420 | 1328 | 219.0335 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 33457148 | 6298 | 151.152 | 6.298 | 8.5 | 8.5 | 3B+1S | 0 | 1072 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36369796 | 1376 | 218.4821 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 33463591 | 6443 | 154.632 | 6.443 | 7.7 | 7.7 | 3B+1S | 0 | 1082 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36371220 | 1424 | 221.0151 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 33469876 | 6285 | 150.84 | 6.285 | 7 | 7 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36372616 | 1396 | 222.1161 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 33476198 | 6322 | 151.728 | 6.322 | 6.3 | 6.3 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36374020 | 1404 | 222.0816 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 33482320 | 6122 | 146.928 | 6.122 | 5.8 | 5.8 | 3B+1S | 0 | 1061 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36375384 | 1364 | 222.803 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 138 | 33488486 | 6166 | 147.984 | 6.166 | 5.3 | 5.3 | 3B+1S | 0 | 1073 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36376772 | 1388 | 225.1054 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 33494443 | 5957 | 142.968 | 5.957 | 4.8 | 4.8 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36378132 | 1360 | 228.3028 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 33500162 | 5719 | 137.256 | 5.719 | 4.5 | 4.5 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36379436 | 1304 | 228.0119 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 33505848 | 5686 | 136.464 | 5.686 | 4.4 | 4.4 | 3B+1S | 0 | 1000 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36380736 | 1300 | 228.6317 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 33511674 | 5826 | 139.824 | 5.826 | 4.2 | 4.2 | 3B+1S | 0 | 1020 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36382060 | 1324 | 227.2571 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 138 | 33517367 | 5693 | 136.632 | 5.693 | 3.7 | 3.7 | 3B+1S | 0 | 1009 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36383340 | 1280 | 224.8375 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 140 | 33523099 | 5732 | 137.568 | 5.732 | 3.3 | 3.3 | 3B+1S | 0 | 1010 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36384612 | 1272 | 221.9121 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 138 | 33528649 | 5550 | 133.2 | 5.55 | 3 | 3 | 3B+1S | 0 | 999 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36385856 | 1244 | 224.1441 | 0% | 100% | 100% | 100% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 33533983 | 5334 | 128.016 | 5.334 | 2.2 | 2.2 | 2B+1S | 0 | 1064 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36386948 | 1092 | 204.7244 | 0% | 100% | 100% | 0% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 124 | 33539199 | 5216 | 125.184 | 5.216 | 1.7 | 1.7 | 2B+1S | 0 | 1015 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36387988 | 1040 | 199.3865 | 0% | 100% | 100% | 0% | 100% | 0% | 8140756 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 104 | 33543629 | 4430 | 106.32 | 4.43 | 2.6 | 2.6 | 2B | 0 | 0 | 1154 | 0 | 1110 | N/A | N/A | N/A | N/A | 36388812 | 824 | 186.0045 | 0% | 0% | 100% | 0% | 100% | 35% | 8141586 | 830 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 93 | 33547668 | 4039 | 96.936 | 4.039 | 3.7 | 3.7 | 2B | 0 | 0 | 1121 | 0 | 1110 | N/A | N/A | N/A | N/A | 36389532 | 720 | 178.2619 | 0% | 0% | 100% | 0% | 100% | 35% | 8142655 | 1069 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.25 | 125559 | 125559 | 125.559 | 125.559 | [12 empty] | 26168 | 26168 | 208.412 | [6 empty] | 7294 | 7294 | 0.93 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
MAGALLANES IN-LINE FAULT AT 4:08 @ RESUME 5:28 AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT AT 5:32 @ RESUME 7:09 AM NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:08 AM , NORMAL OPERATION
MR. E BELTRAN OF CENTRAL LAB. ARRIVE @ 10:00 AM FOR WATER SAMPLING RES.CL2 - 1.12mg/l
NOTE: COLORIMETER IS NOT WORKING PROPERLY. NEEDS TO CALIBRATE.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:29 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:26 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:25 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / J. GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25892 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33547668 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36389532 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8142655 |  | mg /l |  | Automatic - i2O | AI | R. REGENCIA / J. GALINATO
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 92 | 33551447 | 3779 | 90.696 | 3.779 | 5.1 | 5.1 | 2B | 0 | 0 | 1025 | 0 | 1110 | N/A | N/A | N/A | N/A | 36390200 | 668 | 176.7663 | 0% | 0% | 100% | 0% | 100% | 40% | 8143992 | 1337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 85 | 33555055 | 3608 | 86.592 | 3.608 | 6.6 | 6.6 | 2B | 0 | 0 | 1020 | 0 | 1038 | N/A | N/A | N/A | N/A | 36390812 | 612 | 169.6231 | 0% | 0% | 100% | 0% | 100% | 40% | 8145366 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 84 | 33558517 | 3462 | 83.088 | 3.462 | 8 | 8 | 2B | 0 | 0 | 996 | 0 | 1038 | N/A | N/A | N/A | N/A | 36391380 | 568 | 164.067 | 0% | 0% | 100% | 0% | 100% | 40% | 8146748 | 1382 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 88 | 33562043 | 3526 | 84.624 | 3.526 | 9.5 | 9.5 | 2B | 0 | 0 | 1000 | 0 | 1008 | N/A | N/A | N/A | N/A | 36391924 | 544 | 154.2825 | 0% | 0% | 100% | 0% | 100% | 40% | 8148093 | 1345 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 33565898 | 3855 | 92.52 | 3.855 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 36392492 | 568 | 147.3411 | 0% | 0% | 100% | 0% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 124 | 33570623 | 4725 | 113.4 | 4.725 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1191 | 0 | 1160 | N/A | N/A | N/A | N/A | 36393236 | 744 | 157.4603 | 0% | 0% | 100% | 0% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 153 | 33576647 | 6024 | 144.576 | 6.024 | 9 | 9 | 3B+1S | 0 | 1087 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36394556 | 1320 | 219.1235 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 153 | 33582990 | 6343 | 152.232 | 6.343 | 8.5 | 8.5 | 3B+1S | 0 | 1188 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36395944 | 1388 | 218.8239 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 155 | 33589228 | 6238 | 149.712 | 6.238 | 8 | 8 | 3B+1S | 0 | 1171 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36397312 | 1368 | 219.3011 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 154 | 33595649 | 6421 | 154.104 | 6.421 | 7.2 | 7.2 | 3B+1S | 0 | 1160 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36398732 | 1420 | 221.1494 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 | 1.37 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 33601928 | 6279 | 150.696 | 6.279 | 6.5 | 6.5 | 3B+1S | 0 | 1153 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36400132 | 1400 | 222.9654 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 150 | 33608162 | 6234 | 149.616 | 6.234 | 5.6 | 5.6 | 3B+1S | 0 | 1152 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36401556 | 1424 | 228.4248 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 146 | 33614194 | 6032 | 144.768 | 6.032 | 5.3 | 5.3 | 3B+1S | 0 | 1066 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36402912 | 1356 | 224.8011 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 33619944 | 5750 | 138 | 5.75 | 5 | 5 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36404228 | 1316 | 228.8696 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 33625456 | 5512 | 132.288 | 5.512 | 4.9 | 4.9 | 3B+1S | 0 | 990 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36405456 | 1228 | 222.7866 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 33631051 | 5595 | 134.28 | 5.595 | 4.8 | 4.8 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36406764 | 1308 | 233.7802 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 127 | 33636782 | 5731 | 137.544 | 5.731 | 4.5 | 4.5 | 3B+1S | 0 | 1063 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36408088 | 1324 | 231.0243 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 33642436 | 5654 | 135.696 | 5.654 | 4.4 | 4.4 | 3B+1S | 0 | 987 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36409404 | 1316 | 232.7556 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 33647960 | 5524 | 132.576 | 5.524 | 4.3 | 4.3 | 3B+1S | 0 | 987 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36410700 | 1296 | 234.6126 | 0% | 100% | 100% | 100% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 108 | 132 | 33653466 | 5506 | 132.144 | 5.506 | 3.2 | 3.2 | 2B+1S | 0 | 1167 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36411844 | 1144 | 207.7733 | 0% | 100% | 100% | 0% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 131 | 33658700 | 5234 | 125.616 | 5.234 | 2.5 | 2.5 | 2B+1S | 0 | 1090 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36412900 | 1056 | 201.7577 | 0% | 100% | 100% | 0% | 100% | 0% | 8148093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 118 | 33663782 | 5082 | 121.968 | 5.082 | 2.8 | 2.8 | 2B+1S | 0 | 998 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36413924 | 1024 | 201.4955 | 0% | 100% | 100% | 0% | 100% | 0% | 8148093 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 62 | 43.662 | Automatic - Pressure Setting | 38.7324 | 40.1408 | 44.3662 | 14 | A ONG | 11.9 | 120 | 102 | 33668090 | 4308 | 103.392 | 4.308 | 2.8 | 2.8 | 2B | 0 | 0 | 1125 | 0 | 1110 | N/A | N/A | N/A | N/A | 36414724 | 800 | 185.701 | 0% | 0% | 100% | 0% | 100% | 30% | 8148810 | 717 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 62 | 43.662 | Automatic - Pressure Setting | 38.7324 | 40.1408 | 44.3662 | 14 | A ONG | 11.5 | 117 | 93 | 33672036 | 3946 | 94.704 | 3.946 | 3.7 | 3.7 | 2B | 0 | 0 | 1037 | 0 | 1110 | N/A | N/A | N/A | N/A | 36415424 | 700 | 177.3948 | 0% | 0% | 100% | 0% | 100% | 30% | 8149700 | 890 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9167 | 124368 | 124368 | 124.368 | 124.368 | [12 empty] | 25892 | 25892 | 208.1886 | [6 empty] | 7045 | 7045 | 1.055 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
NOTE: COLORIMETER IS NOT WORKING PROPERLY. NEEDS TO CALIBRATE.
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:11 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:08 AM , NORMAL OPERATION
MR. KUNIMORI CHIKAZAWA,ARIEL MULA & JOSE SAYSON OF KBT TRADING CONDUCTED INSTALLATION FOR KUBOTA PUMP & MOTOR ARRIVED @9:28 AM
MR. FRANCIS LOVETE OF MCC CONDUCTED INSPECTION FOR SCADA ARRIVE @9:55 AM
SIR. JOSEPH DELA ROSA, SIR. MICHEAL BULIGAN, SIR. ARTURO TRINIDAD & MAINTENANCE TEAM CONDUCTED MONTHLY PREVENTIVE MAINTENANCE OF ALL PUMPS ARRIVE @ 10:30 AM
CITIPEST BENJIE PALAGANAS, RODERICK VILLAREAL, PATRICK DE GUZMAN. CONDUCTED MONTHLY PEST CONTROL FOR THE FACILITIES OF VILLAMOR PS ARRIVED @10:30 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:23 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 22, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:28 PM , NORMAL OPERATION
NOTE: ALL PUMPS STOPPED DUE TO POWER FLUCTUATION @ 2:30PM
BP2 - RESTARTED @ 2:35 PM
BP3 - RESTARTED @ 2:36 PM
BP1 - RESTARTED @ 2:37 PM
SP2 - RESTARTED @ 2:38 PM
BACK TO NORMAL OPERATION @ 2:40 PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:12 PM , NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | R. REGENCIA / J. GALINATO
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26492 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33672036 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36415424 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8149700 |  | mg /l |  | Automatic - i2O | AI | R. REGENCIA / J. GALINATO
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 114 | 89 | 33675775 | 3739 | 89.736 | 3.739 | 5.2 | 5.2 | 2B | 0 | 0 | 1077 | 0 | 1110 | N/A | N/A | N/A | N/A | 36416084 | 660 | 176.5178 | 0% | 0% | 100% | 0% | 100% | 40% | 8150881 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 87 | 33679449 | 3674 | 88.176 | 3.674 | 6.3 | 6.3 | 2B | 0 | 0 | 1033 | 0 | 1110 | N/A | N/A | N/A | N/A | 36416740 | 656 | 178.552 | 0% | 0% | 100% | 0% | 100% | 40% | 8152090 | 1209 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 33683012 | 3563 | 85.512 | 3.563 | 7.7 | 7.7 | 2B | 0 | 0 | 1044 | 0 | 1058 | N/A | N/A | N/A | N/A | 36417368 | 628 | 176.256 | 0% | 0% | 100% | 0% | 100% | 40% | 8153363 | 1273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 90 | 33686769 | 3757 | 90.168 | 3.757 | 9.1 | 9.1 | 2B | 0 | 0 | 1045 | 0 | 1058 | N/A | N/A | N/A | N/A | 36417982 | 614 | 163.4283 | 0% | 0% | 100% | 0% | 100% | 40% | 8154633 | 1270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 101 | 33690677 | 3908 | 93.792 | 3.908 | 9.5 | 9.5 | 2B | 0 | 0 | 1003 | 0 | 1008 | N/A | N/A | N/A | N/A | 36418572 | 590 | 150.9724 | 0% | 0% | 100% | 0% | 100% | 40% | 8155188 | 555 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 115 | 33695237 | 4560 | 109.44 | 4.56 | 9.5 | 9.5 | 2B | 0 | 0 | 1191 | 0 | 1160 | N/A | N/A | N/A | N/A | 36419280 | 708 | 155.2632 | 0% | 0% | 100% | 0% | 100% | 0% | 8155188 | 0 | 1.11 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 154 | 33701398 | 6161 | 147.864 | 6.161 | 9.1 | 9.1 | 3B+1S | 0 | 1110 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36420608 | 1328 | 215.5494 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 154 | 33707748 | 6350 | 152.4 | 6.35 | 8.5 | 8.5 | 3B+1S | 0 | 1156 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36421996 | 1388 | 218.5827 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 160 | 33714107 | 6359 | 152.616 | 6.359 | 7.9 | 7.9 | 3B+1S | 0 | 1170 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36423392 | 1396 | 219.5314 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 152 | 33720319 | 6212 | 149.088 | 6.212 | 7 | 7 | 3B+1S | 0 | 1170 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36424792 | 1400 | 225.3703 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 157 | 33726840 | 6521 | 156.504 | 6.521 | 6.3 | 6.3 | 3B+1S | 0 | 1142 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36426240 | 1448 | 222.0518 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 150 | 33732927 | 6087 | 146.088 | 6.087 | 5.6 | 5.6 | 3B+1S | 0 | 1137 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36427612 | 1372 | 225.3984 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 145 | 33738927 | 6000 | 144 | 6 | 5.1 | 5.1 | 3B+1S | 0 | 1089 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36428940 | 1328 | 221.3333 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 33744968 | 6041 | 144.984 | 6.041 | 4.6 | 4.6 | 3B+1S | 0 | 1086 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36430244 | 1304 | 215.8583 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 33750645 | 5677 | 136.248 | 5.677 | 4.1 | 4.1 | 3B+1S | 0 | 990 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36431552 | 1308 | 230.4034 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 137 | 33756559 | 5914 | 141.936 | 5.914 | 4 | 4 | 3B+1S | 0 | 988 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36432916 | 1364 | 230.6392 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 33762278 | 5719 | 137.256 | 5.719 | 3.4 | 3.4 | 3B+1S | 0 | 980 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36434248 | 1332 | 232.9079 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 33768075 | 5797 | 139.128 | 5.797 | 3.1 | 3.1 | 3B+1S | 0 | 987 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36435584 | 1336 | 230.464 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 33773691 | 5616 | 134.784 | 5.616 | 3 | 3 | 3B+1S | 0 | 987 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36436940 | 1356 | 241.453 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 138 | 33779337 | 5646 | 135.504 | 5.646 | 2.9 | 2.9 | 3B+1S | 0 | 954 | 1155 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36438284 | 1344 | 238.0446 | 0% | 100% | 100% | 100% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 132 | 33784655 | 5318 | 127.632 | 5.318 | 2.2 | 2.2 | 2B+1S | 0 | 1062 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36439364 | 1080 | 203.0839 | 0% | 100% | 100% | 0% | 100% | 0% | 8155188 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 130 | 33789699 | 5044 | 121.056 | 5.044 | 1.8 | 1.8 | 2B+1S | 0 | 1024 | 1196 | 0 | 119 | N/A | N/A | N/A | N/A | 36440372 | 1008 | 199.8414 | 0% | 100% | 100% | 0% | 100% | 0% | 8155188 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 102 | 33793935 | 4236 | 101.664 | 4.236 | 2.9 | 2.9 | 2B | 0 | 0 | 1165 | 0 | 1109 | N/A | N/A | N/A | N/A | 36441188 | 816 | 192.6346 | 0% | 0% | 100% | 0% | 100% | 45% | 8156313 | 1125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 89 | 33798002 | 4067 | 97.608 | 4.067 | 4.4 | 4.4 | 2B | 0 | 0 | 1080 | 0 | 1110 | N/A | N/A | N/A | N/A | 36441916 | 728 | 179.0017 | 0% | 0% | 100% | 0% | 100% | 45% | 8157687 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 125966 | 125966 | 125.966 | 125.966 | [12 empty] | 26492 | 26492 | 210.3107 | [6 empty] | 7987 | 7987 | 1.0167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:27 AM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT @ 7:20 AM RESUME @ 9:18 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 AM , NORMAL OPERATION
SIR. ARTURO TRINIDAD CONDUCTED INSPECTION & MONITORING ARRIVED @9:31 AM
KBT TRADING PERSONEL MR. KUNIMORI CHIKAZAWA, JOSE SAYSON, MANUEL MAPALO. CONDUCTED INSTALLATION FOR PUMP & MOTOR ARRIVED @ 10:07 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12 AM , NORMAL OPERATION
IMM PERSONELL CONDUCTED UPDATING OF TOTALIZER ARRIVED @11:22 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
SIR. GERRY BAUTISTA CONDUCTED MONITORING & INSPECTION ARRIVED @ 1:57 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:40 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:12 PM , NORMAL OPERATION
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26160 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33798002 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36441916 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8157687 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 89 | 33801591 | 3589 | 86.136 | 3.589 | 6.9 | 6.9 | 2B | 0 | 0 | 1028 | 0 | 1109 | N/A | N/A | N/A | N/A | 36442551 | 635 | 176.9295 | 0% | 0% | 100% | 0% | 100% | 55% | 8159240 | 1553 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 90 | 33805180 | 3589 | 86.136 | 3.589 | 8.8 | 8.8 | 2B | 0 | 0 | 1011 | 0 | 1110 | N/A | N/A | N/A | N/A | 36443186 | 635 | 176.9295 | 0% | 0% | 100% | 0% | 100% | 55% | 8160803 | 1563 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 85 | 33808770 | 3590 | 86.16 | 3.59 | 9.4 | 9.4 | 2B | 0 | 0 | 993 | 0 | 1088 | N/A | N/A | N/A | N/A | 36443836 | 650 | 181.0585 | 0% | 0% | 100% | 0% | 100% | 55% | 8162347 | 1544 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 103 | 91 | 33812413 | 3643 | 87.432 | 3.643 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1088 | N/A | N/A | N/A | N/A | 36444384 | 548 | 150.4255 | 0% | 0% | 100% | 0% | 100% | 55% | 8162508 | 161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 96 | 33816055 | 3642 | 87.408 | 3.642 | 9.5 | 9.5 | 2B | 0 | 0 | 918 | 0 | 1089 | N/A | N/A | N/A | N/A | 36444932 | 548 | 150.4668 | 0% | 0% | 100% | 0% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 118 | 33820721 | 4666 | 111.984 | 4.666 | 9.5 | 9.5 | 2B | 0 | 0 | 1171 | 0 | 1191 | N/A | N/A | N/A | N/A | 36445684 | 752 | 161.1659 | 0% | 0% | 100% | 0% | 100% | 0% | 8162508 | 0 | 0.92 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 150 | 33826991 | 6270 | 150.48 | 6.27 | 8.8 | 8.8 | 3B+1S | 0 | 1151 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36447068 | 1384 | 220.7337 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 155 | 33833280 | 6289 | 150.936 | 6.289 | 8.1 | 8.1 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36448452 | 1384 | 220.0668 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 153 | 33839525 | 6245 | 149.88 | 6.245 | 7.3 | 7.3 | 3B+1S | 0 | 1113 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36449880 | 1428 | 228.6629 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 33845753 | 6228 | 149.472 | 6.228 | 6.5 | 6.5 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36451268 | 1388 | 222.8645 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 | 1.03 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 33852042 | 6289 | 150.936 | 6.289 | 5.9 | 5.9 | 3B+1S | 0 | 1046 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36452688 | 1420 | 225.7911 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 151 | 33858263 | 6221 | 149.304 | 6.221 | 5.5 | 5.5 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36454020 | 1332 | 214.1135 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 145 | 33864360 | 6097 | 146.328 | 6.097 | 5.2 | 5.2 | 3B+1S | 0 | 1028 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36455280 | 1260 | 206.659 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 145 | 33869920 | 5560 | 133.44 | 5.56 | 5.1 | 5.1 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36456559 | 1279 | 230.036 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 33875804 | 5884 | 141.216 | 5.884 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36458029 | 1470 | 249.83 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 33881345 | 5541 | 132.984 | 5.541 | 4.7 | 4.7 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1190 | N/A | N/A | N/A | N/A | 36459316 | 1287 | 232.2685 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 123 | 141 | 33887012 | 5667 | 136.008 | 5.667 | 4.2 | 4.2 | 3B+1S | 0 | 1072 | 1196 | 1185 | 1189 | N/A | N/A | N/A | N/A | 36460644 | 1328 | 234.3392 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 140 | 33892815 | 5803 | 139.272 | 5.803 | 3.8 | 3.8 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36461972 | 1328 | 228.8471 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 136 | 33898497 | 5682 | 136.368 | 5.682 | 3.4 | 3.4 | 3B+1S | 0 | 997 | 1196 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36463268 | 1296 | 228.0887 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 103 | 120 | 33904185 | 5688 | 136.512 | 5.688 | 3.3 | 3.3 | 3B+1S | 0 | 1090 | 1005 | 1185 | 1030 | N/A | N/A | N/A | N/A | 36464520 | 1252 | 220.1125 | 0% | 100% | 100% | 100% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 124 | 33909320 | 5135 | 123.24 | 5.135 | 2.4 | 2.4 | 2B+1S | 0 | 1110 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36465588 | 1068 | 207.9844 | 0% | 100% | 100% | 0% | 100% | 0% | 8162508 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 118 | 33914443 | 5123 | 122.952 | 5.123 | 1.9 | 1.9 | 2B+1S | 0 | 1065 | 1186 | 0 | 1170 | N/A | N/A | N/A | N/A | 36466620 | 1032 | 201.4445 | 0% | 100% | 100% | 0% | 100% | 0% | 8162508 | 0 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 99 | 33918637 | 4194 | 100.656 | 4.194 | 2.5 | 2.5 | 2B | 0 | 0 | 1123 | 0 | 1109 | N/A | N/A | N/A | N/A | 36467388 | 768 | 183.1187 | 0% | 0% | 100% | 0% | 100% | 30% | 8163270 | 762 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 92 | 33922592 | 3955 | 94.92 | 3.955 | 3.4 | 3.4 | 2B | 0 | 0 | 1029 | 0 | 1109 | N/A | N/A | N/A | N/A | 36468076 | 688 | 173.957 | 0% | 0% | 100% | 0% | 100% | 30% | 8164135 | 865 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5417 | 124590 | 124590 | 124.59 | 124.59 | [12 empty] | 26160 | 26160 | 209.9687 | [6 empty] | 6448 | 6448 | 0.90833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (55%) @ 12:01 AM
XCV1 CLOSED @ 3:06 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25 AM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT @ 8:23 AM RESUME @ 8:36 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:36 AM , NORMAL OPERATION
KBT TRADING PERSONEL CONTINUE WORKING ON BP4 ARRIVED 7:15AM
ENGR. A. TRINIDAD AND ENGR. J. BAUTISTA ARRIVED @ 10:20 AM FOR PLANT INSPECTION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:18 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:40 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:27 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26080 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 33922592 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36468076 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8164135 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 86 | 33926377 | 3785 | 90.84 | 3.785 | 5 | 5 | 2B | 0 | 0 | 1033 | 0 | 1109 | N/A | N/A | N/A | N/A | 36468756 | 680 | 179.6565 | 0% | 0% | 100% | 0% | 100% | 46% | 8165641 | 1506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 84 | 33929849 | 3472 | 83.328 | 3.472 | 6.6 | 6.6 | 2B | 0 | 0 | 994 | 0 | 1110 | N/A | N/A | N/A | N/A | 36469364 | 608 | 175.1152 | 0% | 0% | 100% | 0% | 100% | 46% | 8167162 | 1521 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 84 | 33933315 | 3466 | 83.184 | 3.466 | 8.2 | 8.2 | 2B | 0 | 0 | 952 | 0 | 1109 | N/A | N/A | N/A | N/A | 36469964 | 600 | 173.1102 | 0% | 0% | 100% | 0% | 100% | 46% | 8168738 | 1576 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 82 | 33936795 | 3480 | 83.52 | 3.48 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1110 | N/A | N/A | N/A | N/A | 36470532 | 568 | 163.2184 | 0% | 0% | 100% | 0% | 100% | 46% | 8169717 | 979 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 95 | 33940588 | 3793 | 91.032 | 3.793 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1120 | N/A | N/A | N/A | N/A | 36471108 | 576 | 151.8587 | 0% | 0% | 100% | 0% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 126 | 124 | 33945188 | 4600 | 110.4 | 4.6 | 9.5 | 9.5 | 2B | 0 | 0 | 1064 | 0 | 1199 | N/A | N/A | N/A | N/A | 36471848 | 740 | 160.8696 | 0% | 0% | 100% | 0% | 100% | 0% | 8169717 | 0 | 1.16 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 148 | 33951327 | 6139 | 147.336 | 6.139 | 9.2 | 9.2 | 3B+1S | 0 | 1179 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36473156 | 1308 | 213.064 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 156 | 33957523 | 6196 | 148.704 | 6.196 | 8.7 | 8.7 | 3B+1S | 0 | 1164 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36474540 | 1384 | 223.3699 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 158 | 33963892 | 6369 | 152.856 | 6.369 | 8 | 8 | 3B+1S | 0 | 1184 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36475944 | 1404 | 220.4428 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 33970119 | 6227 | 149.448 | 6.227 | 7.3 | 7.3 | 3B+1S | 0 | 1170 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36477324 | 1380 | 221.6155 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 | 1.25 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 144 | 33976395 | 6276 | 150.624 | 6.276 | 6.8 | 6.8 | 3B+1S | 0 | 1091 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36478719 | 1395 | 222.2753 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 33982426 | 6031 | 144.744 | 6.031 | 6.5 | 6.5 | 3B+1S | 0 | 1064 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36480040 | 1321 | 219.035 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 33988466 | 6040 | 144.96 | 6.04 | 6 | 6 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36481396 | 1356 | 224.5033 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 33994627 | 6161 | 147.864 | 6.161 | 5.7 | 5.7 | 3B+1S | 0 | 1045 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36482796 | 1400 | 227.2358 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 34000413 | 5786 | 138.864 | 5.786 | 5.4 | 5.4 | 3B+1S | 0 | 1009 | 1197 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36484132 | 1336 | 230.9022 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 34006059 | 5646 | 135.504 | 5.646 | 5.3 | 5.3 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36485440 | 1308 | 231.6684 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 142 | 34011785 | 5726 | 137.424 | 5.726 | 4.7 | 4.7 | 3B+1S | 0 | 1134 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36486772 | 1332 | 232.6231 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 142 | 34017658 | 5873 | 140.952 | 5.873 | 4.2 | 4.2 | 3B+1S | 0 | 1023 | 1196 | 1185 | 1181 | N/A | N/A | N/A | N/A | 36488096 | 1324 | 225.4384 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 34023159 | 5501 | 132.024 | 5.501 | 3.8 | 3.8 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36489356 | 1260 | 229.0493 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 131 | 34028718 | 5559 | 133.416 | 5.559 | 3.6 | 3.6 | 3B+1S | 0 | 993 | 1164 | 1185 | 1118 | N/A | N/A | N/A | N/A | 36490604 | 1248 | 224.5008 | 0% | 100% | 100% | 100% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 130 | 34033987 | 5269 | 126.456 | 5.269 | 3 | 3 | 2B+1S | 0 | 1059 | 1197 | 0 | 1190 | N/A | N/A | N/A | N/A | 36491668 | 1064 | 201.9359 | 0% | 100% | 100% | 0% | 100% | 0% | 8169717 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 120 | 34039049 | 5062 | 121.488 | 5.062 | 2.6 | 2.6 | 2B+1S | 0 | 993 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 36492676 | 1008 | 199.1308 | 0% | 100% | 100% | 0% | 100% | 0% | 8169717 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 100 | 34043353 | 4304 | 103.296 | 4.304 | 3.6 | 3.6 | 2B | 0 | 0 | 1154 | 0 | 1110 | N/A | N/A | N/A | N/A | 36493476 | 800 | 185.8736 | 0% | 0% | 100% | 0% | 100% | 45% | 8170769 | 1052 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 95 | 34047272 | 3919 | 94.056 | 3.919 | 5 | 5 | 2B | 0 | 0 | 1130 | 0 | 1109 | N/A | N/A | N/A | N/A | 36494156 | 680 | 173.5137 | 0% | 0% | 100% | 0% | 100% | 45% | 8172058 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0833 | 124680 | 124680 | 124.68 | 124.68 | [12 empty] | 26080 | 26080 | 209.1755 | [6 empty] | 7923 | 7923 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:23 AM , NORMAL OPERATION
XCV1 CLOSED @ 3:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT @ 4:35 AM / RESUME @ 6:15 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:21 AM , NORMAL OPERATION
ENGR. ARTURO TRINIDAD ARRIVED @ 8:35 AM FOR PLANT INSPECTION
KBT TRADING PERSONEL CONTINUE WORKING ON BP4 ARRIVED 8:47AM
MAGALLANES IN-LINE FAULT @ 8:37 AM / RESUME @ 9:15 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:20 AM , NORMAL OPERATION
SESI PERSONELL DELIVERED PERSONAL PROTECTIVE EQUIPMENT ARRIVED @10:30 AM
MAGALLANES IN-LINE FAULT @ 10:18 AM / RESUME @ 11:19 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:19 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 25, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
MAINTENANCE TEAM ARRIVED @ 12:09 TO ASSIST KTB TRADING PERSONELL TO TRANSFER KUBOTA MOTOR & PUMP
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:35 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:26 PM , NORMAL OPERATION
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:28 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (45%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | RANDY REGENCIA
[13 empty] | 10pm - 6am | JIMENEZ GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25992 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34047272 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36494156 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8172058 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 85 | 34050891 | 3619 | 86.856 | 3.619 | 6.9 | 6.9 | 2B | 0 | 0 | 981 | 0 | 1109 | N/A | N/A | N/A | N/A | 36494806 | 650 | 179.6076 | 0% | 0% | 100% | 0% | 100% | 45% | 8173384 | 1326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 82 | 34054510 | 3619 | 86.856 | 3.619 | 8 | 8 | 2B | 0 | 0 | 973 | 0 | 1110 | N/A | N/A | N/A | N/A | 36495456 | 650 | 179.6076 | 0% | 0% | 100% | 0% | 100% | 45% | 8174718 | 1334 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 84 | 34057975 | 3465 | 83.16 | 3.465 | 8.9 | 8.9 | 2B | 0 | 0 | 945 | 0 | 1080 | N/A | N/A | N/A | N/A | 36496002 | 546 | 157.5758 | 0% | 0% | 100% | 0% | 100% | 45% | 8175919 | 1201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 86 | 86 | 34061440 | 3465 | 83.16 | 3.465 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 1079 | N/A | N/A | N/A | N/A | 36496548 | 546 | 157.5758 | 0% | 0% | 100% | 0% | 100% | 45% | 8176219 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 92 | 34065214 | 3774 | 90.576 | 3.774 | 9.5 | 9.5 | 2B | 0 | 0 | 942 | 0 | 1079 | N/A | N/A | N/A | N/A | 36497120 | 572 | 151.5633 | 0% | 0% | 100% | 0% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 10 | 7.0423 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 123 | 122 | 34069787 | 4573 | 109.752 | 4.573 | 9.5 | 9.5 | 2B | 0 | 0 | 1147 | 0 | 1170 | N/A | N/A | N/A | N/A | 36497836 | 716 | 156.5712 | 0% | 0% | 100% | 0% | 100% | 0% | 8176219 | 0 | 1.11 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 155 | 34075769 | 5982 | 143.568 | 5.982 | 9.4 | 9.4 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36499100 | 1264 | 211.3006 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 157 | 34081933 | 6164 | 147.936 | 6.164 | 9.1 | 9.1 | 3B+1S | 0 | 1106 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36500445 | 1345 | 218.2025 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 163 | 34088266 | 6333 | 151.992 | 6.333 | 8.4 | 8.4 | 3B+1S | 0 | 1175 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36501836 | 1391 | 219.6431 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 155 | 34094452 | 6186 | 148.464 | 6.186 | 7.8 | 7.8 | 3B+1S | 0 | 1170 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36503192 | 1356 | 219.2047 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 | 1.33 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 162 | 34100743 | 6291 | 150.984 | 6.291 | 7.6 | 7.6 | 3B+1S | 0 | 1059 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36504572 | 1380 | 219.361 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 34106907 | 6164 | 147.936 | 6.164 | 7.2 | 7.2 | 3B+1S | 0 | 1035 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36505932 | 1360 | 220.636 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 149 | 34112970 | 6063 | 145.512 | 6.063 | 6.9 | 6.9 | 3B+1S | 0 | 1081 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36507276 | 1344 | 221.6724 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 143 | 34119103 | 6133 | 147.192 | 6.133 | 6.3 | 6.3 | 3B+1S | 0 | 1032 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36508652 | 1376 | 224.36 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 34124998 | 5895 | 141.48 | 5.895 | 5.9 | 5.9 | 3B+1S | 0 | 1018 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36510016 | 1364 | 231.3825 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 34130702 | 5704 | 136.896 | 5.704 | 5.6 | 5.6 | 3B+1S | 0 | 1011 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36511324 | 1308 | 229.3128 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 34136583 | 5881 | 141.144 | 5.881 | 5.1 | 5.1 | 3B+1S | 0 | 1008 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36512654 | 1330 | 226.152 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 34142451 | 5868 | 140.832 | 5.868 | 4.8 | 4.8 | 3B+1S | 0 | 1002 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36514016 | 1362 | 232.1063 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 34148292 | 5841 | 140.184 | 5.841 | 4.5 | 4.5 | 3B+1S | 0 | 998 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36515356 | 1340 | 229.4128 | 0% | 100% | 100% | 100% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 138 | 34153716 | 5424 | 130.176 | 5.424 | 3.5 | 3.5 | 2B+1S | 0 | 1048 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36516460 | 1104 | 203.5398 | 0% | 100% | 100% | 0% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 131 | 34159134 | 5418 | 130.032 | 5.418 | 2.8 | 2.8 | 2B+1S | 0 | 1012 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36517524 | 1064 | 196.3824 | 0% | 100% | 100% | 0% | 100% | 0% | 8176219 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 121 | 34164376 | 5242 | 125.808 | 5.242 | 2.3 | 2.3 | 2B+1S | 0 | 1031 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36518556 | 1032 | 196.8714 | 0% | 100% | 100% | 0% | 100% | 0% | 8176219 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 104 | 34168769 | 4393 | 105.432 | 4.393 | 3.1 | 3.1 | 2B | 0 | 0 | 1087 | 0 | 1199 | N/A | N/A | N/A | N/A | 36519380 | 824 | 187.5711 | 0% | 0% | 100% | 0% | 100% | 35% | 8177019 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 97 | 34172911 | 4142 | 99.408 | 4.142 | 4.2 | 4.2 | 2B | 0 | 0 | 1028 | 0 | 1199 | N/A | N/A | N/A | N/A | 36520148 | 768 | 185.4177 | 0% | 0% | 100% | 0% | 100% | 35% | 8177990 | 971 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.25 | 125639 | 125639 | 125.639 | 125.639 | [12 empty] | 25992 | 25992 | 206.8784 | [6 empty] | 5932 | 5932 | 1.0467 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT @ 5:43 AM / RESUME @ 6:40 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:43 AM , NORMAL OPERATION
SP2 - STARTED @ 6:45 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:43 AM , NORMAL OPERATION
KBT TRADING PERSONEL CONTINUE WORKING FOR BP4 ARRIVED 8:47AM
MAGALLANES IN-LINE FAULT @ 6:44 AM / RESUME @ 9:12 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:16 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:14 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 26, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:15 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34172911 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36520148 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8177990 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 91 | 34176800 | 3889 | 93.336 | 3.889 | 5.4 | 5.4 | 2B | 0 | 0 | 1043 | 0 | 1160 | N/A | N/A | N/A | N/A | 36520864 | 716 | 184.109 | 0% | 0% | 100% | 0% | 100% | 45% | 8179040 | 1050 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 86 | 34180508 | 3708 | 88.992 | 3.708 | 6.7 | 6.7 | 2B | 0 | 0 | 991 | 0 | 1148 | N/A | N/A | N/A | N/A | 36521548 | 684 | 184.466 | 0% | 0% | 100% | 0% | 100% | 45% | 8180293 | 1253 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 34184134 | 3626 | 87.024 | 3.626 | 7.9 | 7.9 | 2B | 0 | 0 | 981 | 0 | 1110 | N/A | N/A | N/A | N/A | 36522180 | 632 | 174.2967 | 0% | 0% | 100% | 0% | 100% | 45% | 8181619 | 1326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 88 | 83 | 34187713 | 3579 | 85.896 | 3.579 | 9.3 | 9.3 | 2B | 0 | 0 | 947 | 0 | 1100 | N/A | N/A | N/A | N/A | 36522780 | 600 | 167.6446 | 0% | 0% | 100% | 0% | 100% | 45% | 8182953 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 90 | 34191425 | 3712 | 89.088 | 3.712 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 1018 | N/A | N/A | N/A | N/A | 36523284 | 504 | 135.7759 | 0% | 0% | 100% | 0% | 100% | 45% | 8182955 | 2 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 119 | 116 | 34195772 | 4347 | 104.328 | 4.347 | 9.5 | 9.5 | 2B | 0 | 0 | 1106 | 0 | 1118 | N/A | N/A | N/A | N/A | 36523932 | 648 | 149.0683 | 0% | 0% | 100% | 0% | 100% | 0% | 8182955 | 0 | 1.16 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 139 | 34201600 | 5828 | 139.872 | 5.828 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36525144 | 1212 | 207.9616 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 149 | 145 | 34207604 | 6004 | 144.096 | 6.004 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36526440 | 1296 | 215.8561 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 152 | 34213957 | 6353 | 152.472 | 6.353 | 8.9 | 8.9 | 3B+1S | 0 | 1069 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36527812 | 1372 | 215.961 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 152 | 34220189 | 6232 | 149.568 | 6.232 | 8.5 | 8.5 | 3B+1S | 0 | 1129 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36529164 | 1352 | 216.9448 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 153 | 34226363 | 6174 | 148.176 | 6.174 | 8.2 | 8.2 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36530516 | 1352 | 218.9828 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 34232631 | 6268 | 150.432 | 6.268 | 7.8 | 7.8 | 3B+1S | 0 | 1039 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36531914 | 1398 | 223.0377 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 148 | 34238575 | 5944 | 142.656 | 5.944 | 7.6 | 7.6 | 3B+1S | 0 | 980 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36533220 | 1306 | 219.7174 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 142 | 34244613 | 6038 | 144.912 | 6.038 | 7.4 | 7.4 | 3B+1S | 0 | 995 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36534580 | 1360 | 225.2401 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 34250352 | 5739 | 137.736 | 5.739 | 7 | 7 | 3B+1S | 0 | 995 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36535896 | 1316 | 229.3082 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 130 | 34255983 | 5631 | 135.144 | 5.631 | 6.7 | 6.7 | 3B+1S | 0 | 1018 | 1186 | 1185 | 1179 | N/A | N/A | N/A | N/A | 36537176 | 1280 | 227.3131 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 137 | 34261664 | 5681 | 136.344 | 5.681 | 6.2 | 6.2 | 3B+1S | 0 | 1091 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36538492 | 1316 | 231.6494 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 140 | 34267481 | 5817 | 139.608 | 5.817 | 5.7 | 5.7 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36539808 | 1316 | 226.2335 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 34273284 | 5803 | 139.272 | 5.803 | 5.4 | 5.4 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36541112 | 1304 | 224.7114 | 0% | 100% | 100% | 100% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 135 | 34278833 | 5549 | 133.176 | 5.549 | 4.4 | 4.4 | 2B+1S | 0 | 1166 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 36542252 | 1140 | 205.4424 | 0% | 100% | 100% | 0% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 127 | 34284209 | 5376 | 129.024 | 5.376 | 3.4 | 3.4 | 2B+1S | 0 | 1074 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36543328 | 1076 | 200.1488 | 0% | 100% | 100% | 0% | 100% | 0% | 8182955 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 121 | 34289424 | 5215 | 125.16 | 5.215 | 3 | 3 | 2B+1S | 0 | 991 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36544364 | 1036 | 198.6577 | 0% | 100% | 100% | 0% | 100% | 0% | 8182955 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 103 | 34293656 | 4232 | 101.568 | 4.232 | 3.6 | 3.6 | 2B | 0 | 0 | 1110 | 0 | 1129 | N/A | N/A | N/A | N/A | 36545132 | 768 | 181.4745 | 0% | 0% | 100% | 0% | 100% | 30% | 8183610 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 93 | 34297758 | 4102 | 98.448 | 4.102 | 4.5 | 4.5 | 2B | 0 | 0 | 1015 | 0 | 1129 | N/A | N/A | N/A | N/A | 36545844 | 712 | 173.5739 | 0% | 0% | 100% | 0% | 100% | 30% | 8184437 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.75 | 124847 | 124847 | 124.847 | 124.847 | [12 empty] | 25696 | 25696 | 205.8199 | [6 empty] | 6447 | 6447 | 1.0533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 4:03 AM,WATER ELEVATION (9.5M)
FAULT @ 4:49 AM DUE TO HIGH DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
FAULT @ 7:07 AM DUE TO HIGH DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
KBT TRADING PERSONNEL CONTINUE WORKING FOR BP4 ARRIVED @ 8:20 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:07 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 27, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:17 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:17 PM , NORMAL OPERATION
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26328 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34297758 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36545844 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8184437 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 90 | 34301570 | 3812 | 91.488 | 3.812 | 5.7 | 5.7 | 2B | 0 | 0 | 1010 | 0 | 1129 | N/A | N/A | N/A | N/A | 36546516 | 672 | 176.2854 | 0% | 0% | 100% | 0% | 100% | 40% | 8185636 | 1199 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 85 | 34305116 | 3546 | 85.104 | 3.546 | 7.1 | 7.1 | 2B | 0 | 0 | 967 | 0 | 1130 | N/A | N/A | N/A | N/A | 36547140 | 624 | 175.9729 | 0% | 0% | 100% | 0% | 100% | 40% | 8186949 | 1313 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 85 | 34308547 | 3431 | 82.344 | 3.431 | 8.5 | 8.5 | 2B | 0 | 0 | 933 | 0 | 1130 | N/A | N/A | N/A | N/A | 36547724 | 584 | 170.2128 | 0% | 0% | 100% | 0% | 100% | 40% | 8188253 | 1304 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 84 | 85 | 34312078 | 3531 | 84.744 | 3.531 | 9.5 | 9.5 | 2B | 0 | 0 | 932 | 0 | 1129 | N/A | N/A | N/A | N/A | 36548300 | 576 | 163.1266 | 0% | 0% | 100% | 0% | 100% | 40% | 8189090 | 837 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 100 | 34315834 | 3756 | 90.144 | 3.756 | 9.5 | 9.5 | 2B | 0 | 0 | 900 | 0 | 1129 | N/A | N/A | N/A | N/A | 36548876 | 576 | 153.3546 | 0% | 0% | 100% | 0% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 124 | 34320353 | 4519 | 108.456 | 4.519 | 9.5 | 9.5 | 2B | 0 | 0 | 1160 | 0 | 1199 | N/A | N/A | N/A | N/A | 36549596 | 720 | 159.3273 | 0% | 0% | 100% | 0% | 100% | 0% | 8189090 | 0 | 1.12 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 146 | 34326523 | 6170 | 148.08 | 6.17 | 9.1 | 9.1 | 3B+1S | 0 | 1131 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36550940 | 1344 | 217.8282 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 153 | 34332740 | 6217 | 149.208 | 6.217 | 8.7 | 8.7 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36552292 | 1352 | 217.4682 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 156 | 34338957 | 6217 | 149.208 | 6.217 | 8.3 | 8.3 | 3B+1S | 0 | 1167 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36553644 | 1352 | 217.4682 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 34345312 | 6355 | 152.52 | 6.355 | 7.7 | 7.7 | 3B+1S | 0 | 1155 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36555044 | 1400 | 220.299 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 | 1.17 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 151 | 34351533 | 6221 | 149.304 | 6.221 | 7.2 | 7.2 | 3B+1S | 0 | 1107 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36556404 | 1360 | 218.6144 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 34357595 | 6062 | 145.488 | 6.062 | 7 | 7 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36557736 | 1332 | 219.7295 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 154 | 34363771 | 6176 | 148.224 | 6.176 | 6.6 | 6.6 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36559100 | 1364 | 220.8549 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 34369878 | 6107 | 146.568 | 6.107 | 6.2 | 6.2 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36560476 | 1376 | 225.3152 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 34375803 | 5925 | 142.2 | 5.925 | 5.7 | 5.7 | 3B+1S | 0 | 1062 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36561820 | 1344 | 226.8354 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 147 | 34381716 | 5913 | 141.912 | 5.913 | 5.2 | 5.2 | 3B+1S | 0 | 1079 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36563172 | 1352 | 228.6487 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 148 | 34387810 | 6094 | 146.256 | 6.094 | 4.2 | 4.2 | 3B+1S | 0 | 1177 | 1196 | 1185 | 1197 | N/A | N/A | N/A | N/A | 36564620 | 1448 | 237.6108 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 141 | 34393732 | 5922 | 142.128 | 5.922 | 3.6 | 3.6 | 3B+1S | 0 | 1144 | 1176 | 1185 | 1170 | N/A | N/A | N/A | N/A | 36565940 | 1320 | 222.8977 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 143 | 34399473 | 5741 | 137.784 | 5.741 | 3.2 | 3.2 | 3B+1S | 0 | 1141 | 1165 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36567224 | 1284 | 223.6544 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 136 | 34405109 | 5636 | 135.264 | 5.636 | 2.6 | 2.6 | 3B+1S | 0 | 1048 | 1164 | 1185 | 1159 | N/A | N/A | N/A | N/A | 36568476 | 1252 | 222.1434 | 0% | 100% | 100% | 100% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 132 | 34410492 | 5383 | 129.192 | 5.383 | 1.7 | 1.7 | 2B+1S | 0 | 1189 | 1196 | 0 | 1190 | N/A | N/A | N/A | N/A | 36569588 | 1112 | 206.5763 | 0% | 100% | 100% | 0% | 100% | 0% | 8189090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 34415613 | 5121 | 122.904 | 5.121 | 1.3 | 1.3 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36570540 | 952 | 185.9012 | 0% | 0% | 100% | 0% | 100% | 0% | 8189090 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 106 | 34420146 | 4533 | 108.792 | 4.533 | 2.2 | 2.2 | 2B | 0 | 0 | 1177 | 0 | 1139 | N/A | N/A | N/A | N/A | 36571392 | 852 | 187.955 | 0% | 0% | 100% | 0% | 100% | 35% | 8189870 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 97 | 34424373 | 4227 | 101.448 | 4.227 | 3.3 | 3.3 | 2B | 0 | 0 | 1116 | 0 | 1119 | N/A | N/A | N/A | N/A | 36572172 | 780 | 184.528 | 0% | 0% | 100% | 0% | 100% | 35% | 8190982 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.4167 | 126615 | 126615 | 126.615 | 126.615 | [12 empty] | 26328 | 26328 | 207.9374 | [6 empty] | 6545 | 6545 | 1.0133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:33 AM , NORMAL OPERATION
XCV1 CLOSED @ 3:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES IN-LINE FAULT @ 4:15 AM / RESUME @ 6:24 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:27 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:27 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:12 AM , NORMAL OPERATION
MR. E BELTRAN OF CENTRAL LAB. ARRIVED @ 10:15 AM FOR WATER SAMPLING RES.CL2 - 1.17mg/l
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:08 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:10 PM , NORMAL OPERATION
ENGR. A. TRINIDAD AND ENGR.J.DELAROSA ENGR.M.BARAHAN ARRIVED @ 1:42 PM FOR PLANT INSPECTION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:24 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:15 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:23 PM , NORMAL OPERATION
NORMAL OPERATION

## APR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | F. RAMOS / JR. GALINATO
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26440 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34424373 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36572172 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8190982 |  | mg /l |  | Automatic - i2O | AI | F. RAMOS / JR. GALINATO
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 93 | 34428298 | 3925 | 94.2 | 3.925 | 4.9 | 4.9 | 2B | 0 | 0 | 1062 | 0 | 1110 | N/A | N/A | N/A | N/A | 36572880 | 708 | 180.3822 | 0% | 0% | 100% | 0% | 100% | 45% | 8192374 | 1392 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 34432003 | 3705 | 88.92 | 3.705 | 6.5 | 6.5 | 2B | 0 | 0 | 1028 | 0 | 1110 | N/A | N/A | N/A | N/A | 36573532 | 652 | 175.9784 | 0% | 0% | 100% | 0% | 100% | 45% | 8193841 | 1467 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 34435684 | 3681 | 88.344 | 3.681 | 8 | 8 | 2B | 0 | 0 | 988 | 0 | 1110 | N/A | N/A | N/A | N/A | 36574174 | 642 | 174.4091 | 0% | 0% | 100% | 0% | 100% | 45% | 8195284 | 1443 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 91 | 91 | 34439336 | 3652 | 87.648 | 3.652 | 9.5 | 9.5 | 2B | 0 | 0 | 995 | 0 | 1009 | N/A | N/A | N/A | N/A | 36574752 | 578 | 158.2694 | 0% | 0% | 100% | 0% | 100% | 45% | 8196757 | 1473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 101 | 34443249 | 3913 | 93.912 | 3.913 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 1009 | N/A | N/A | N/A | N/A | 36575340 | 588 | 150.2683 | 0% | 0% | 100% | 0% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 129 | 120 | 34448021 | 4772 | 114.528 | 4.772 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1058 | N/A | N/A | N/A | N/A | 36576088 | 748 | 156.7477 | 0% | 0% | 100% | 0% | 100% | 0% | 8196757 | 0 | 1.05 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 152 | 34454120 | 6099 | 146.376 | 6.099 | 8.9 | 8.9 | 3B+1S | 0 | 1187 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36577432 | 1344 | 220.364 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 152 | 34460346 | 6226 | 149.424 | 6.226 | 8.4 | 8.4 | 3B+1S | 0 | 1114 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36578792 | 1360 | 218.4388 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 149 | 34466567 | 6221 | 149.304 | 6.221 | 7.8 | 7.8 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36580140 | 1348 | 216.6854 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 154 | 34472805 | 6238 | 149.712 | 6.238 | 7.4 | 7.4 | 3B+1S | 0 | 1135 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36581556 | 1416 | 226.9958 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 152 | 34478861 | 6056 | 145.344 | 6.056 | 7 | 7 | 3B+1S | 0 | 1115 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36582892 | 1336 | 220.6077 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 153 | 34484991 | 6130 | 147.12 | 6.13 | 6.6 | 6.6 | 3B+1S | 0 | 1124 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36584248 | 1356 | 221.2072 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 149 | 34491069 | 6078 | 145.872 | 6.078 | 6.1 | 6.1 | 3B+1S | 0 | 1120 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36585612 | 1364 | 224.4159 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 147 | 34497108 | 6039 | 144.936 | 6.039 | 5.5 | 5.5 | 3B+1S | 0 | 1125 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36586980 | 1368 | 226.5276 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 34502879 | 5771 | 138.504 | 5.771 | 5.3 | 5.3 | 3B+1S | 0 | 1060 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36588234 | 1254 | 217.2934 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 148 | 34508473 | 5594 | 134.256 | 5.594 | 5.2 | 5.2 | 3B+1S | 0 | 1058 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36589572 | 1338 | 239.1848 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 139 | 34514385 | 5912 | 141.888 | 5.912 | 4.6 | 4.6 | 3B+1S | 0 | 1182 | 1186 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36590936 | 1364 | 230.7172 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 141 | 34520418 | 6033 | 144.792 | 6.033 | 3.7 | 3.7 | 3B+1S | 0 | 1094 | 1175 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36592308 | 1372 | 227.4159 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 140 | 34526224 | 5806 | 139.344 | 5.806 | 3.2 | 3.2 | 3B+1S | 0 | 1173 | 1156 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36593596 | 1288 | 221.8395 | 0% | 100% | 100% | 100% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 135 | 34531824 | 5600 | 134.4 | 5.6 | 2.9 | 2.9 | 3B | 0 | 1101 | 1125 | 0 | 1138 | N/A | N/A | N/A | N/A | 36594820 | 1224 | 218.5714 | 0% | 100% | 100% | 0% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 131 | 34537198 | 5374 | 128.976 | 5.374 | 1.9 | 1.9 | 3B | 0 | 1187 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36595936 | 1116 | 207.6665 | 0% | 100% | 100% | 0% | 100% | 0% | 8196757 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 119 | 34542436 | 5238 | 125.712 | 5.238 | 1.3 | 1.3 | 3B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36596984 | 1048 | 200.0764 | 0% | 0% | 100% | 0% | 100% | 0% | 8196757 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 105 | 34547015 | 4579 | 109.896 | 4.579 | 2.3 | 2.3 | 2B | 0 | 0 | 1155 | 0 | 1159 | N/A | N/A | N/A | N/A | 36597868 | 884 | 193.0553 | 0% | 0% | 100% | 0% | 100% | 40% | 8197724 | 967 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 97 | 34551107 | 4092 | 98.208 | 4.092 | 3.6 | 3.6 | 2B | 0 | 0 | 1102 | 0 | 1109 | N/A | N/A | N/A | N/A | 36598612 | 744 | 181.8182 | 0% | 0% | 100% | 0% | 100% | 40% | 8198922 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.875 | 126734 | 126734 | 126.734 | 126.734 | [12 empty] | 26440 | 26440 | 208.6259 | [6 empty] | 7940 | 7940 | 1.02 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM
XCV1 CLOSED @ 3:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:23 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:15 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:14 AM , NORMAL OPERATION
PUMP INSTALLING BY KBT TRAIDING LOPSIDED @ 9:27 AM BEC. OF LACK OF SUPPORT OTHER FITTINGS NEED TO BEND
FINANCE ACCTG.(GAE MWSS) CONDUCTED INVENTORY FOR 2015 ARRIVED @ 10:50 AM
EGNR A. TRINIDAD, EGNR G. BAUTISTA, & SHEREE GAELA (OJT) CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @ 11:30 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:45 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 29, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:11 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:16 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:11 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:35 PM , NORMAL OPERATION
SP2 - STOPPED @ 9:45 PM DUE TO LOW WATER LEVEL OF RESERVOIR
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | JIMENEZ GALINATO
WATER NETWORK | [12 empty] | 2pm - 10pm | F. A. RAMOS / JR. GALINATO
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34551107 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36598612 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8198922 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 86 | 34554928 | 3821 | 91.704 | 3.821 | 5.2 | 5.2 | 2B | 0 | 0 | 1079 | 0 | 1099 | N/A | N/A | N/A | N/A | 36599316 | 704 | 184.245 | 0% | 0% | 100% | 0% | 100% | 50% | 8200324 | 1402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 87 | 34558668 | 3740 | 89.76 | 3.74 | 6.8 | 6.8 | 2B | 0 | 0 | 1051 | 0 | 1069 | N/A | N/A | N/A | N/A | 36599938 | 622 | 166.3102 | 0% | 0% | 100% | 0% | 100% | 50% | 8201750 | 1426 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 85 | 34562373 | 3705 | 88.92 | 3.705 | 8.4 | 8.4 | 2B | 0 | 0 | 1034 | 0 | 1037 | N/A | N/A | N/A | N/A | 36600536 | 598 | 161.4035 | 0% | 0% | 100% | 0% | 100% | 50% | 8203253 | 1503 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 92 | 34566060 | 3687 | 88.488 | 3.687 | 9.5 | 9.5 | 2B | 0 | 0 | 1021 | 0 | 1038 | N/A | N/A | N/A | N/A | 36601118 | 582 | 157.8519 | 0% | 0% | 100% | 0% | 100% | 50% | 8204436 | 1183 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F. A. RAMOS / JR. GALINATO
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 102 | 34569679 | 3619 | 86.856 | 3.619 | 9.5 | 9.5 | 2B | 0 | 0 | 1005 | 0 | 1009 | N/A | N/A | N/A | N/A | 36601684 | 566 | 156.3968 | 0% | 0% | 100% | 0% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 13.1 | 124 | 121 | 34574383 | 4704 | 112.896 | 4.704 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1151 | N/A | N/A | N/A | N/A | 36602448 | 764 | 162.415 | 0% | 0% | 100% | 0% | 100% | 0% | 8204436 | 0 | 1.5 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 153 | 34580546 | 6163 | 147.912 | 6.163 | 8.9 | 8.9 | 3B+1S | 0 | 1175 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36603808 | 1360 | 220.6718 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 162 | 34586642 | 6096 | 146.304 | 6.096 | 8.5 | 8.5 | 3B+1S | 0 | 1134 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36605148 | 1340 | 219.8163 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 153 | 34592855 | 6213 | 149.112 | 6.213 | 7.9 | 7.9 | 3B+1S | 0 | 1150 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36606524 | 1376 | 221.4711 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 34599055 | 6200 | 148.8 | 6.2 | 7.3 | 7.3 | 3B+1S | 0 | 1163 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36607910 | 1386 | 223.5484 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 34605221 | 6166 | 147.984 | 6.166 | 7 | 7 | 3B+1S | 0 | 1085 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36609256 | 1346 | 218.2939 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 152 | 34611400 | 6179 | 148.296 | 6.179 | 6.7 | 6.7 | 3B+1S | 0 | 1068 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36610616 | 1360 | 220.1003 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 34617408 | 6008 | 144.192 | 6.008 | 6.5 | 6.5 | 3B+1S | 0 | 1050 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36611950 | 1334 | 222.0373 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 34623094 | 5686 | 136.464 | 5.686 | 6.3 | 6.3 | 3B+1S | 0 | 1015 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36613236 | 1286 | 226.1695 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 142 | 34628924 | 5830 | 139.92 | 5.83 | 6.2 | 6.2 | 3B+1S | 0 | 1012 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36614564 | 1328 | 227.7873 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 141 | 34634855 | 5931 | 142.344 | 5.931 | 6 | 6 | 3B+1S | 0 | 1025 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36615928 | 1364 | 229.9781 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 142 | 34640634 | 5779 | 138.696 | 5.779 | 5.5 | 5.5 | 3B+1S | 0 | 1180 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36617264 | 1336 | 231.1819 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 144 | 34646543 | 5909 | 141.816 | 5.909 | 5 | 5 | 3B+1S | 0 | 1029 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36618592 | 1328 | 224.7419 | 0% | 100% | 100% | 100% | 100% | 0% | 8204436 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 132 | 34652073 | 5530 | 132.72 | 5.53 | 4.8 | 4.8 | 3B+1S | 0 | 1040 | 1156 | 0 | 1189 | N/A | N/A | N/A | N/A | 36619840 | 1248 | 225.6781 | 0% | 100% | 100% | 0% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 135 | 34657489 | 5416 | 129.984 | 5.416 | 3.6 | 3.6 | 3B | 0 | 1189 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36620964 | 1124 | 207.5332 | 0% | 100% | 100% | 0% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 107 | 129 | 34662883 | 5394 | 129.456 | 5.394 | 2.6 | 2.6 | 3B | 0 | 1139 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36622072 | 1108 | 205.4134 | 0% | 100% | 100% | 0% | 100% | 0% | 8204436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 130 | 34668179 | 5296 | 127.104 | 5.296 | 2.1 | 2.1 | 3B | 0 | 1094 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36623148 | 1076 | 203.1722 | 0% | 100% | 100% | 0% | 100% | 0% | 8204436 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 103 | 34672621 | 4442 | 106.608 | 4.442 | 2.7 | 2.7 | 2B | 0 | 0 | 1131 | 0 | 1159 | N/A | N/A | N/A | N/A | 36624004 | 856 | 192.706 | 0% | 0% | 100% | 0% | 100% | 35% | 8205093 | 657 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 98 | 34676710 | 4089 | 98.136 | 4.089 | 3.7 | 3.7 | 2B | 0 | 0 | 1084 | 0 | 1099 | N/A | N/A | N/A | N/A | 36624748 | 744 | 181.9516 | 0% | 0% | 100% | 0% | 100% | 35% | 8206046 | 953 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.9583 | 125603 | 125603 | 125.603 | 125.603 | [12 empty] | 26136 | 26136 | 208.0842 | [6 empty] | 7124 | 7124 | 1.1433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM
XCV1 CLOSED @ : AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 68 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:23 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:16 AM
EGNR. A. TRINIDAD & MAINTENANCE TEAM CONDUCTED EXCAVATION @ THE STORAGE ROOM FOR WIRING CONNECTION ARRIVED @ 9:10 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:12 AM , NORMAL OPERATION
MAGALLANES IN-LINE FAULT @ 10:20 AM DUE TO HIGH DISCHARGE PRESSURE.RESUME @ 11:10 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 230, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:40 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:17 PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
Target Discharge Pressure set to 76 psi @ 7:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:22 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:40 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION

## APR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | F.A. RAMOS / JR. GALINATO
[13 empty] | 10pm - 6am | REIVIN M. MALLARI
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-04-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26584 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34676710 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36624748 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8206046 |  | mg /l |  | Automatic - i2O | AI | F.A. RAMOS / JR. GALINATO
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 91 | 34680517 | 3807 | 91.368 | 3.807 | 5.1 | 5.1 | 2B | 0 | 0 | 1066 | 0 | 1079 | N/A | N/A | N/A | N/A | 36625422 | 674 | 177.0423 | 0% | 0% | 100% | 0% | 100% | 40% | 8207226 | 1180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | DENNIS GUANZON
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 85 | 34684352 | 3835 | 92.04 | 3.835 | 6.4 | 6.4 | 2B | 0 | 0 | 1028 | 0 | 1047 | N/A | N/A | N/A | N/A | 36626060 | 638 | 166.3625 | 0% | 0% | 100% | 0% | 100% | 40% | 8208420 | 1194 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 98 | 34688172 | 3820 | 91.68 | 3.82 | 7.9 | 7.9 | 2B | 0 | 0 | 1014 | 0 | 1018 | N/A | N/A | N/A | N/A | 36626662 | 602 | 157.5916 | 0% | 0% | 100% | 0% | 100% | 40% | 8209659 | 1239 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 89 | 34691976 | 3804 | 91.296 | 3.804 | 9.2 | 9.2 | 2B | 0 | 0 | 1057 | 0 | 1068 | N/A | N/A | N/A | N/A | 36627252 | 590 | 155.0999 | 0% | 0% | 100% | 0% | 100% | 40% | 8210861 | 1202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 102 | 34695806 | 3830 | 91.92 | 3.83 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 0 | 1005 | N/A | N/A | N/A | N/A | 36627824 | 572 | 149.3473 | 0% | 0% | 100% | 0% | 100% | 40% | 8211549 | 688 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 123 | 34699881 | 4075 | 97.8 | 4.075 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36628590 | 766 | 187.9755 | 0% | 0% | 100% | 0% | 100% | 0% | 8211549 | 0 | 0.98 | Normal operation schedule | Error - General | E | J. GALINATO / R. MALLARI
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 152 | 34705994 | 6113 | 146.712 | 6.113 | 9.1 | 9.1 | 3B+1S | 0 | 1099 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36629924 | 1334 | 218.2235 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 151 | 34712206 | 6212 | 149.088 | 6.212 | 8.3 | 8.3 | 3B+1S | 0 | 1073 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36631320 | 1396 | 224.7263 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 153 | 34718570 | 6364 | 152.736 | 6.364 | 7.6 | 7.6 | 3B+1S | 0 | 1078 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36632740 | 1420 | 223.1301 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 34724860 | 6290 | 150.96 | 6.29 | 6.8 | 6.8 | 3B+1S | 0 | 1099 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36634140 | 1400 | 222.5755 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 34731145 | 6285 | 150.84 | 6.285 | 6.2 | 6.2 | 3B+1S | 0 | 1056 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36635548 | 1408 | 224.0255 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 149 | 34737418 | 6273 | 150.552 | 6.273 | 5.7 | 5.7 | 3B+1S | 0 | 1087 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36636908 | 1360 | 216.8022 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 148 | 34743509 | 6091 | 146.184 | 6.091 | 5.2 | 5.2 | 3B+1S | 0 | 1030 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36638268 | 1360 | 223.2802 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 145 | 34749551 | 6042 | 145.008 | 6.042 | 4.7 | 4.7 | 3B+1S | 0 | 1120 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36639636 | 1368 | 226.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 34755296 | 5745 | 137.88 | 5.745 | 4.4 | 4.4 | 3B+1S | 0 | 1076 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36640940 | 1304 | 226.98 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 142 | 34761178 | 5882 | 141.168 | 5.882 | 4.3 | 4.3 | 3B+1S | 0 | 1094 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36642276 | 1336 | 227.1336 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 148 | 34767149 | 5971 | 143.304 | 5.971 | 3.4 | 3.4 | 3B+1S | 0 | 1178 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36643656 | 1380 | 231.1171 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 142 | 34773041 | 5892 | 141.408 | 5.892 | 2.8 | 2.8 | 3B+1S | 0 | 1019 | 1176 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36645004 | 1348 | 228.7848 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 136 | 34778823 | 5782 | 138.768 | 5.782 | 2.3 | 2.3 | 3B+1S | 0 | 1076 | 1171 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36646332 | 1328 | 229.6783 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 132 | 34784269 | 5446 | 130.704 | 5.446 | 2.1 | 2.1 | 3B+1S | 0 | 1023 | 1145 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36647580 | 1248 | 229.159 | 0% | 100% | 100% | 100% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 135 | 34789403 | 5134 | 123.216 | 5.134 | 1.7 | 1.7 | 3B | 0 | 1188 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 36648596 | 1016 | 197.8964 | 0% | 100% | 100% | 0% | 100% | 0% | 8211549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 133 | 34794689 | 5286 | 126.864 | 5.286 | 1.4 | 1.4 | 3B | 0 | 1188 | 1192 | 0 | 1199 | N/A | N/A | N/A | N/A | 36649628 | 1032 | 195.2327 | 0% | 100% | 100% | 0% | 100% | 0% | 8211549 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 109 | 34799331 | 4642 | 111.408 | 4.642 | 2 | 2 | 2B | 0 | 0 | 1165 | 0 | 1169 | N/A | N/A | N/A | N/A | 36650528 | 900 | 193.8819 | 0% | 0% | 100% | 0% | 100% | 30% | 8212195 | 646 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 104 | 34803725 | 4394 | 105.456 | 4.394 | 2.8 | 2.8 | 2B | 0 | 0 | 1118 | 0 | 1129 | N/A | N/A | N/A | N/A | 36651332 | 804 | 182.9768 | 0% | 0% | 100% | 0% | 100% | 30% | 8212954 | 759 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.5417 | 127015 | 127015 | 127.015 | 127.015 | [12 empty] | 26584 | 26584 | 209.2981 | [6 empty] | 6908 | 6908 | 0.96167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER REQUEST OF ENGR. FRANCES MORLA (SPM SOUTH)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:31 AM , NORMAL OPERATION
MAGALLANES IN LINE TRIP AT 6:54 AM DUE TO HIGH DISCHARGE PRESSURE.
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:40AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 1, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
MARRIANE PALOMO,ELIZIER TAGUBASE, MARVIN CALMONA, DOMINGO YGONIA. CONDUCTED PREVENTIVE MAINTENANCE OF INSTRUMENT ARRIVED @1:05 PM
EGNR. A. TRINIDAD & TEAM MAINTENANCE CONDUCTED PLANT INSPECTION. ARRIVED @3:25 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:32 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,839
GENSET 1 WARMUP EXERCISED @ 4:19 PM / STOPPED @ 4:29 PM
GENSET 2 WARMUP EXERCISED @ 4:07 PM / STOPPED @ 4:17PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM AS PER SCHEDULE
ENGR.J.BULIGAN ENGR.M.BARAHAN ARRIVED @ 5:04 PM FOR PLANT INSPECTION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:18 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:29 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:50 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
NORMAL OPERATION