## MAY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27384 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34803725 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36651332 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8212954 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 99 | 34808003 | 4278 | 102.672 | 4.278 | 3.9 | 3.9 | 2B | 0 | 0 | 1146 | 0 | 1129 | N/A | N/A | N/A | N/A | 36652134 | 802 | 187.4708 | 0% | 0% | 100% | 0% | 100% | 50% | 8214011 | 1057 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 101 | 34812198 | 4195 | 100.68 | 4.195 | 5.4 | 5.4 | 2B | 0 | 0 | 1112 | 0 | 1079 | N/A | N/A | N/A | N/A | 36652900 | 766 | 182.5983 | 0% | 0% | 100% | 0% | 100% | 50% | 8215170 | 1159 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 97 | 34816325 | 4127 | 99.048 | 4.127 | 6.6 | 6.6 | 2B | 0 | 0 | 1110 | 0 | 1079 | N/A | N/A | N/A | N/A | 36653618 | 718 | 173.9763 | 0% | 0% | 100% | 0% | 100% | 50% | 8216384 | 1214 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 104 | 34820388 | 4063 | 97.512 | 4.063 | 7.8 | 7.8 | 2B | 0 | 0 | 1128 | 0 | 1110 | N/A | N/A | N/A | N/A | 36654286 | 668 | 164.4105 | 0% | 0% | 100% | 0% | 100% | 50% | 8217570 | 1186 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 128 | 107 | 34824665 | 4277 | 102.648 | 4.277 | 8.9 | 8.9 | 2B | 0 | 0 | 1115 | 0 | 1110 | N/A | N/A | N/A | N/A | 36655020 | 734 | 171.6156 | 0% | 0% | 100% | 0% | 100% | 50% | 8218592 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 129 | 34829733 | 5068 | 121.632 | 5.068 | 9.5 | 9.5 | 2B | 0 | 0 | 1197 | 0 | 1199 | N/A | N/A | N/A | N/A | 36655940 | 920 | 181.5312 | 0% | 0% | 100% | 0% | 100% | 50% | 8219167 | 575 | 0.84 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 153 | 34836003 | 6270 | 150.48 | 6.27 | 9 | 9 | 3B+1S | 0 | 1083 | 1147 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36657292 | 1352 | 215.63 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 163 | 34842484 | 6481 | 155.544 | 6.481 | 8.3 | 8.3 | 3B+1S | 0 | 1126 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36658704 | 1412 | 217.8676 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 152 | 34849070 | 6586 | 158.064 | 6.586 | 7.4 | 7.4 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36660172 | 1468 | 222.8971 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 34855635 | 6565 | 157.56 | 6.565 | 6.3 | 6.3 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36661682 | 1510 | 230.0076 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 156 | 34862311 | 6676 | 160.224 | 6.676 | 5.3 | 5.3 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36663156 | 1474 | 220.7909 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 153 | 34868502 | 6191 | 148.584 | 6.191 | 4.4 | 4.4 | 3B+1S | 0 | 1165 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36664556 | 1400 | 226.1347 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 19 | A ONG | 17.5 | 129 | 155 | 34874860 | 6358 | 152.592 | 6.358 | 3.4 | 3.4 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36666012 | 1456 | 229.0028 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 17.3 | 129 | 150 | 34881038 | 6178 | 148.272 | 6.178 | 2.4 | 2.4 | 3B+1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36667444 | 1432 | 231.7902 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 134 | 140 | 34887051 | 6013 | 144.312 | 6.013 | 1.9 | 1.9 | 3B+1S | 0 | 1057 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36668820 | 1376 | 228.8375 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 34892774 | 5723 | 137.352 | 5.723 | 1.7 | 1.7 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36670116 | 1296 | 226.4547 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 144 | 34898647 | 5873 | 140.952 | 5.873 | 1.3 | 1.3 | 3B+1S | 0 | 1112 | 1164 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36671456 | 1340 | 228.1628 | 0% | 100% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 63 | 44.3662 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 18 | A ONG | 16.7 | 123 | 124 | 34903926 | 5279 | 126.696 | 5.279 | 1.3 | 1.3 | 3B | 0 | 0 | 1005 | 1185 | 1058 | N/A | N/A | N/A | N/A | 36672516 | 1060 | 200.7956 | 0% | 0% | 100% | 100% | 100% | 0% | 8219167 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.6 | 130 | 123 | 34909137 | 5211 | 125.064 | 5.211 | 1.3 | 1.3 | 3B | 0 | 0 | 1044 | 1185 | 1128 | N/A | N/A | N/A | N/A | 36673544 | 1028 | 197.275 | 0% | 0% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 69 | 48.5915 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 18 | A ONG | 16.6 | 130 | 131 | 34914272 | 5135 | 123.24 | 5.135 | 1.3 | 1.3 | 3B | 0 | 0 | 1063 | 1185 | 1128 | N/A | N/A | N/A | N/A | 36674572 | 1028 | 200.1947 | 0% | 0% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 137 | 135 | 34919852 | 5580 | 133.92 | 5.58 | 1.3 | 1.3 | 3B | 0 | 0 | 1145 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36675748 | 1176 | 210.7527 | 0% | 0% | 100% | 100% | 100% | 0% | 8219167 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 | 130 | 34925396 | 5544 | 133.056 | 5.544 | 1.3 | 1.3 | 3B | 0 | 0 | 1102 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36676964 | 1216 | 219.3362 | 0% | 0% | 100% | 100% | 100% | 0% | 8219167 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 115 | 34930139 | 4743 | 113.832 | 4.743 | 2.1 | 2.1 | 2B | 0 | 0 | 1195 | 0 | 1169 | N/A | N/A | N/A | N/A | 36677852 | 888 | 187.2233 | 0% | 0% | 100% | 0% | 100% | 35% | 8219958 | 791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 116 | 34934808 | 4669 | 112.056 | 4.669 | 3.2 | 3.2 | 2B | 0 | 0 | 1177 | 0 | 1169 | N/A | N/A | N/A | N/A | 36678716 | 864 | 185.0503 | 0% | 0% | 100% | 0% | 100% | 35% | 8220900 | 942 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 131.9583 | 131083 | 131083 | 131.083 | 131.083 | [12 empty] | 27384 | 27384 | 208.9058 | [6 empty] | 7946 | 7946 | 5.76 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:00 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:00AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 2, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
NOTE: Increase discharge pressure from 81psi to 83psi @ 12pm as per request of spm
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:23 PM , NORMAL OPERATION
NOTE: change discharge pressure from 83psi to 78psi @ 3pm as per request of spm
FAULT @ 4:02 PM DUE TO HIGH DISCHARGE PRESSURE.RESUME @4:23 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25 PM , NORMAL OPERATION
SP2 - STOPPED @ 5:00 PM DUE TO LOW WATER LEVEL OF RESERVOIR
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:14 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18 PM , NORMAL OPERATION

## MAY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | REIVIN M. MALLARI
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27840 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 34934808 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36678716 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8220900 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 105 | 34939320 | 4512 | 108.288 | 4.512 | 4.4 | 4.4 | 2B | 0 | 0 | 1162 | 0 | 1139 | N/A | N/A | N/A | N/A | 36679564 | 848 | 187.9433 | 0% | 0% | 100% | 0% | 100% | 45% | 8221939 | 1039 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 104 | 34943737 | 4417 | 106.008 | 4.417 | 5.6 | 5.6 | 2B | 0 | 0 | 1120 | 0 | 1139 | N/A | N/A | N/A | N/A | 36680360 | 796 | 180.2128 | 0% | 0% | 100% | 0% | 100% | 45% | 8223101 | 1162 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 1010 | 34948081 | 4344 | 104.256 | 4.344 | 6.8 | 6.8 | 2B | 0 | 0 | 1100 | 0 | 1139 | N/A | N/A | N/A | N/A | 36681124 | 764 | 175.8748 | 0% | 0% | 100% | 0% | 100% | 45% | 8224250 | 1149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 134 | 103 | 34952295 | 4214 | 101.136 | 4.214 | 8.1 | 8.1 | 2B | 0 | 0 | 1055 | 0 | 1110 | N/A | N/A | N/A | N/A | 36681828 | 704 | 167.0622 | 0% | 0% | 100% | 0% | 100% | 45% | 8225497 | 1247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 108 | 34956565 | 4270 | 102.48 | 4.27 | 9.5 | 9.5 | 2B | 0 | 0 | 1032 | 0 | 1049 | N/A | N/A | N/A | N/A | 36682512 | 684 | 160.1874 | 0% | 0% | 100% | 0% | 100% | 45% | 8226771 | 1274 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 134 | 34961843 | 5278 | 126.672 | 5.278 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1109 | N/A | N/A | N/A | N/A | 36683480 | 968 | 183.4028 | 0% | 0% | 100% | 100% | 100% | 0% | 8226771 | 0 | 1.12 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 151 | 34968047 | 6204 | 148.896 | 6.204 | 9.1 | 9.1 | 3B+1S | 0 | 1040 | 1170 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36684836 | 1356 | 218.5687 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 152 | 34974417 | 6370 | 152.88 | 6.37 | 8.5 | 8.5 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36686220 | 1384 | 217.2684 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 155 | 34980901 | 6484 | 155.616 | 6.484 | 7.9 | 7.9 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36687644 | 1424 | 219.6175 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 160 | 34987320 | 6419 | 154.056 | 6.419 | 7 | 7 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36689068 | 1424 | 221.8414 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 157 | 34993727 | 6407 | 153.768 | 6.407 | 6 | 6 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36690468 | 1400 | 218.511 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 152 | 150 | 35000134 | 6407 | 153.768 | 6.407 | 5.5 | 5.5 | 3B+1S | 0 | 1030 | 1191 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36691868 | 1400 | 218.511 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 143 | 131 | 35006318 | 6184 | 148.416 | 6.184 | 5.3 | 5.3 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36693212 | 1344 | 217.3351 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 143 | 35012502 | 6184 | 148.416 | 6.184 | 4.9 | 4.9 | 3B+1S | 0 | 1038 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36694556 | 1344 | 217.3351 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 142 | 144 | 35018532 | 6030 | 144.72 | 6.03 | 4.5 | 4.5 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36695912 | 1356 | 224.8756 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 149 | 35024400 | 5868 | 140.832 | 5.868 | 4.2 | 4.2 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36697236 | 1324 | 225.6305 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 35030490 | 6090 | 146.16 | 6.09 | 3.3 | 3.3 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36698650 | 1414 | 232.1839 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 35036570 | 6080 | 145.92 | 6.08 | 2.8 | 2.8 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36700044 | 1394 | 229.2763 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 35042312 | 5742 | 137.808 | 5.742 | 2.4 | 2.4 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36701356 | 1312 | 228.4918 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 137 | 35047982 | 5670 | 136.08 | 5.67 | 1.8 | 1.8 | 3B+1S | 0 | 1025 | 1165 | 1185 | 1169 | N/A | N/A | N/A | N/A | 36702580 | 1224 | 215.873 | 0% | 100% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 136 | 133 | 35053411 | 5429 | 130.296 | 5.429 | 1.5 | 1.5 | 3B | 0 | 0 | 1158 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36703720 | 1140 | 209.9834 | 0% | 0% | 100% | 100% | 100% | 0% | 8226771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 130 | 129 | 35058991 | 5580 | 133.92 | 5.58 | 1.5 | 1.5 | 3B | 0 | 0 | 1162 | 1185 | 1138 | N/A | N/A | N/A | N/A | 36704920 | 1200 | 215.0538 | 0% | 0% | 100% | 100% | 100% | 0% | 8226771 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 103 | 35063487 | 4496 | 107.904 | 4.496 | 2.5 | 2.5 | 2B | 0 | 0 | 1137 | 0 | 1140 | N/A | N/A | N/A | N/A | 36705756 | 836 | 185.9431 | 0% | 0% | 100% | 0% | 100% | 40% | 8227686 | 915 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 101 | 35067822 | 4335 | 104.04 | 4.335 | 3.7 | 3.7 | 2B | 0 | 0 | 1149 | 0 | 1129 | N/A | N/A | N/A | N/A | 36706556 | 800 | 184.5444 | 0% | 0% | 100% | 0% | 100% | 40% | 8228853 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 169.9583 | 133014 | 133014 | 133.014 | 133.014 | [12 empty] | 27840 | 27840 | 209.3013 | [6 empty] | 7953 | 7953 | 6.24 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:54 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:40AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 3, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:00 pM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 pM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM
SP2 - STOPPED @ 8:27 PM DUE TO LOW WATER LEVEL
BP2 - RESTARTED @ 8:28 PM TO MEET 76 PSI TARGET DISCHARGE PRESSURE
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:16 PM , NORMAL OPERATION

## MAY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26280 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35067822 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36706556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8228853 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 94 | 35071891 | 4069 | 97.656 | 4.069 | 5.2 | 5.2 | 2B | 0 | 0 | 1088 | 0 | 1110 | N/A | N/A | N/A | N/A | 36707298 | 742 | 182.3544 | 0% | 0% | 100% | 0% | 100% | 50% | 8229974 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 35075874 | 3983 | 95.592 | 3.983 | 6.3 | 6.3 | 2B | 0 | 0 | 1064 | 0 | 1110 | N/A | N/A | N/A | N/A | 36708020 | 722 | 181.2704 | 0% | 0% | 100% | 0% | 100% | 50% | 8231295 | 1321 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 35079743 | 3869 | 92.856 | 3.869 | 7.6 | 7.6 | 2B | 0 | 0 | 1042 | 0 | 1110 | N/A | N/A | N/A | N/A | 36708692 | 672 | 173.6883 | 0% | 0% | 100% | 0% | 100% | 50% | 8232644 | 1349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 92 | 35083594 | 3851 | 92.424 | 3.851 | 9 | 9 | 2B | 0 | 0 | 1016 | 0 | 1110 | N/A | N/A | N/A | N/A | 36709336 | 644 | 167.2293 | 0% | 0% | 100% | 0% | 100% | 50% | 8234016 | 1372 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 91 | 35087360 | 3766 | 90.384 | 3.766 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1009 | N/A | N/A | N/A | N/A | 36709904 | 568 | 150.8232 | 0% | 0% | 100% | 0% | 100% | 50% | 8234333 | 317 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 35092228 | 4868 | 116.832 | 4.868 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36710748 | 844 | 173.3772 | 0% | 0% | 100% | 0% | 100% | 0% | 8234333 | 0 | 1.09 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 148 | 35098335 | 6107 | 146.568 | 6.107 | 9.3 | 9.3 | 3B+1S | 0 | 989 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36712062 | 1314 | 215.1629 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 150 | 35104442 | 6107 | 146.568 | 6.107 | 9.1 | 9.1 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36713376 | 1314 | 215.1629 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 150 | 35110687 | 6245 | 149.88 | 6.245 | 8.6 | 8.6 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36714736 | 1360 | 217.7742 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 35116978 | 6291 | 150.984 | 6.291 | 7.9 | 7.9 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36716140 | 1404 | 223.176 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 | 0.75 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 150 | 35123353 | 6375 | 153 | 6.375 | 7.3 | 7.3 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36717548 | 1408 | 220.8627 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 150 | 35129695 | 6342 | 152.208 | 6.342 | 6.7 | 6.7 | 3B+1S | 0 | 1020 | 1171 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36718940 | 1392 | 219.4891 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 157 | 131 | 35135381 | 5686 | 136.464 | 5.686 | 6.5 | 6.5 | 3B+1S | 0 | 999 | 1108 | 1185 | 1170 | N/A | N/A | N/A | N/A | 36720156 | 1216 | 213.8586 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 143 | 35141293 | 5912 | 141.888 | 5.912 | 6.3 | 6.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36721468 | 1312 | 221.9215 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 144 | 35147119 | 5826 | 139.824 | 5.826 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1195 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36722786 | 1318 | 226.2273 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 35152980 | 5861 | 140.664 | 5.861 | 5.9 | 5.9 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36724124 | 1338 | 228.2887 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 147 | 35158703 | 5723 | 137.352 | 5.723 | 5.6 | 5.6 | 3B+1S | 0 | 1146 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36725444 | 1320 | 230.6483 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 141 | 35164697 | 5994 | 143.856 | 5.994 | 5.2 | 5.2 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36726804 | 1360 | 226.8936 | 0% | 100% | 100% | 100% | 100% | 0% | 8234333 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 140 | 35170539 | 5842 | 140.208 | 5.842 | 4.9 | 4.9 | 2B+1S | 0 | 990 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36728120 | 1316 | 225.2653 | 0% | 100% | 100% | 0% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 131 | 35175905 | 5366 | 128.784 | 5.366 | 4.2 | 4.2 | 2B+1S | 0 | 1189 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36729188 | 1068 | 199.0309 | 0% | 100% | 100% | 0% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 107 | 130 | 35181119 | 5214 | 125.136 | 5.214 | 3.6 | 3.6 | 2B+1S | 0 | 1160 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36730212 | 1024 | 196.3943 | 0% | 100% | 100% | 0% | 100% | 0% | 8234333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 129 | 35186391 | 5272 | 126.528 | 5.272 | 6.1 | 6.1 | 2B+1S | 0 | 1082 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36731260 | 1048 | 198.786 | 0% | 100% | 100% | 0% | 100% | 0% | 8234333 | 0 | 0.76 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 99 | 35190882 | 4491 | 107.784 | 4.491 | 3.7 | 3.7 | 2B | 0 | 0 | 1137 | 0 | 1139 | N/A | N/A | N/A | N/A | 36732088 | 828 | 184.3687 | 0% | 0% | 100% | 0% | 100% | 35% | 8235012 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 94 | 35195129 | 4247 | 101.928 | 4.247 | 4.8 | 4.8 | 2B | 0 | 0 | 1063 | 0 | 1110 | N/A | N/A | N/A | N/A | 36732836 | 748 | 176.1243 | 0% | 0% | 100% | 0% | 100% | 35% | 8235995 | 983 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.9583 | 127307 | 127307 | 127.307 | 127.307 | [12 empty] | 26280 | 26280 | 206.4301 | [6 empty] | 7142 | 7142 | 5.55 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:00 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 4, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:46 AM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:11 pM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:14 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 8:27 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:17 PM , NORMAL OPERATION

## MAY 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26808 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35195129 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36732836 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8235995 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 92 | 35199041 | 3912 | 93.888 | 3.912 | 5.6 | 5.6 | 2B | 0 | 0 | 1048 | 0 | 1109 | N/A | N/A | N/A | N/A | 36733520 | 684 | 174.8466 | 0% | 0% | 100% | 0% | 100% | 45% | 8237153 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 88 | 35202785 | 3744 | 89.856 | 3.744 | 7.3 | 7.3 | 2B | 0 | 0 | 1017 | 0 | 1109 | N/A | N/A | N/A | N/A | 36734180 | 660 | 176.2821 | 0% | 0% | 100% | 0% | 100% | 45% | 8238451 | 1298 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 88 | 35206503 | 3718 | 89.232 | 3.718 | 8.8 | 8.8 | 2B | 0 | 0 | 1002 | 0 | 1028 | N/A | N/A | N/A | N/A | 36734754 | 574 | 154.3841 | 0% | 0% | 100% | 0% | 100% | 45% | 8239713 | 1262 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 91 | 35210249 | 3746 | 89.904 | 3.746 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1028 | N/A | N/A | N/A | N/A | 36735318 | 564 | 150.5606 | 0% | 0% | 100% | 0% | 100% | 45% | 8240384 | 671 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 97 | 35213954 | 3705 | 88.92 | 3.705 | 9.5 | 9.5 | 2B | 0 | 0 | 970 | 0 | 1008 | N/A | N/A | N/A | N/A | 36735866 | 548 | 147.9082 | 0% | 0% | 100% | 0% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 134 | 35218876 | 4922 | 118.128 | 4.922 | 9.5 | 9.5 | 3B | 0 | 0 | 1023 | 1185 | 1199 | N/A | N/A | N/A | N/A | 36736740 | 874 | 177.5701 | 0% | 0% | 100% | 100% | 100% | 0% | 8240384 | 0 | 0.98 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 151 | 35225163 | 6287 | 150.888 | 6.287 | 8.9 | 8.9 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36738132 | 1392 | 221.4093 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 153 | 35231496 | 6333 | 151.992 | 6.333 | 8.2 | 8.2 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36739528 | 1396 | 220.4327 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 153 | 35237892 | 6396 | 153.504 | 6.396 | 7.2 | 7.2 | 3B+1S | 0 | 1143 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36740956 | 1428 | 223.2645 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 156 | 35244338 | 6446 | 154.704 | 6.446 | 6.4 | 6.4 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36742400 | 1444 | 224.0149 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 133 | 35250726 | 6388 | 153.312 | 6.388 | 5.4 | 5.4 | 3B+1S | 0 | 1153 | 1190 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36743844 | 1444 | 226.0488 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 35256827 | 6101 | 146.424 | 6.101 | 4.8 | 4.8 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36745224 | 1380 | 226.1924 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 146 | 35263111 | 6284 | 150.816 | 6.284 | 4.1 | 4.1 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36746624 | 1400 | 222.788 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 114 | 35269185 | 6074 | 145.776 | 6.074 | 3.3 | 3.3 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36748014 | 1390 | 228.8443 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 148 | 35275002 | 5817 | 139.608 | 5.817 | 3.2 | 3.2 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36749316 | 1302 | 223.8267 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 144 | 35280854 | 5852 | 140.448 | 5.852 | 3.1 | 3.1 | 3B+1S | 0 | 1094 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36750612 | 1296 | 221.4627 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 127 | 35286766 | 5912 | 141.888 | 5.912 | 2.8 | 2.8 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36751956 | 1344 | 227.3342 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 35292679 | 5913 | 141.912 | 5.913 | 2.4 | 2.4 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36753300 | 1344 | 227.2958 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 142 | 35298625 | 5946 | 142.704 | 5.946 | 2 | 2 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36754660 | 1360 | 228.7252 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 140 | 35304306 | 5681 | 136.344 | 5.681 | 1.8 | 1.8 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36755956 | 1296 | 228.1289 | 0% | 100% | 100% | 100% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 131 | 35309400 | 5094 | 122.256 | 5.094 | 1.6 | 1.6 | 2B+1S | 0 | 1189 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36756980 | 1024 | 201.0208 | 0% | 100% | 100% | 0% | 100% | 0% | 8240384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 123 | 35314663 | 5263 | 126.312 | 5.263 | 1.5 | 1.5 | 2B+1S | 0 | 1154 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36758024 | 1044 | 198.366 | 0% | 100% | 100% | 0% | 100% | 0% | 8240384 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 106 | 35319113 | 4450 | 106.8 | 4.45 | 2.1 | 2.1 | 2B | 0 | 0 | 1127 | 0 | 1160 | N/A | N/A | N/A | N/A | 36758852 | 828 | 186.0674 | 0% | 0% | 100% | 0% | 100% | 30% | 8241068 | 684 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 35323474 | 4361 | 104.664 | 4.361 | 2.9 | 2.9 | 2B | 0 | 0 | 1050 | 0 | 1160 | N/A | N/A | N/A | N/A | 36759644 | 792 | 181.6097 | 0% | 0% | 100% | 0% | 100% | 30% | 8241943 | 875 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.6667 | 128345 | 128345 | 128.345 | 128.345 | [12 empty] | 26808 | 26808 | 208.8745 | [6 empty] | 5948 | 5948 | 6.24 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:45AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:17 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 5, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
KBT TRAIDING CONTINUE WORKING FOR BP4 ARRIVED @1:50 PM
ENGR. A TRINIDAD CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @ 2:10 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:26 AM , NORMAL OPERATION
TEAM MAINTENANCE ARRIVED @ 2:42 PM TO FIXED THE CRANE
SIR. MARIANITO BARAHAN CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @ 2:50 PM
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:33 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:25 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:29 PM , NORMAL OPERATION

## MAY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35323474 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36759644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8241943 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 91 | 35327504 | 4030 | 96.72 | 4.03 | 4.4 | 4.4 | 2B | 0 | 0 | 1050 | 0 | 1159 | N/A | N/A | N/A | N/A | 36760396 | 752 | 186.6005 | 0% | 0% | 100% | 0% | 100% | 46% | 8243346 | 1403 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 92 | 35331400 | 3896 | 93.504 | 3.896 | 6.1 | 6.1 | 2B | 0 | 0 | 1020 | 0 | 1128 | N/A | N/A | N/A | N/A | 36761108 | 712 | 182.7515 | 0% | 0% | 100% | 0% | 100% | 46% | 8244890 | 1544 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 86 | 35334951 | 3551 | 85.224 | 3.551 | 7.5 | 7.5 | 2B | 0 | 0 | 994 | 0 | 1129 | N/A | N/A | N/A | N/A | 36761724 | 616 | 173.4723 | 0% | 0% | 100% | 0% | 100% | 46% | 8246276 | 1386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 91 | 35338656 | 3705 | 88.92 | 3.705 | 8.8 | 8.8 | 2B | 0 | 0 | 999 | 0 | 1129 | N/A | N/A | N/A | N/A | 36762356 | 632 | 170.5803 | 0% | 0% | 100% | 0% | 100% | 46% | 8247586 | 1310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 99 | 35342623 | 3967 | 95.208 | 3.967 | 9.5 | 9.5 | 2B | 0 | 0 | 944 | 0 | 1129 | N/A | N/A | N/A | N/A | 36762984 | 628 | 158.306 | 0% | 0% | 100% | 0% | 100% | 46% | 8248068 | 482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 144 | 140 | 35348102 | 5479 | 131.496 | 5.479 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36764108 | 1124 | 205.1469 | 0% | 0% | 100% | 100% | 100% | 0% | 8248068 | 0 | 0.97 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 152 | 35354361 | 6259 | 150.216 | 6.259 | 8.8 | 8.8 | 3B+1S | 0 | 1155 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36765508 | 1400 | 223.6779 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 153 | 35360801 | 6440 | 154.56 | 6.44 | 7.9 | 7.9 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36766940 | 1432 | 222.3602 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 157 | 35367109 | 6308 | 151.392 | 6.308 | 7.1 | 7.1 | 3B+1S | 0 | 1124 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36768352 | 1412 | 223.8427 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 156 | 35373526 | 6417 | 154.008 | 6.417 | 6.2 | 6.2 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36769788 | 1436 | 223.7806 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 35379818 | 6292 | 151.008 | 6.292 | 5.5 | 5.5 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36771204 | 1416 | 225.0477 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 158 | 35385969 | 6151 | 147.624 | 6.151 | 4.8 | 4.8 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36772580 | 1376 | 223.7035 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 35392057 | 6088 | 146.112 | 6.088 | 4.1 | 4.1 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36773980 | 1400 | 229.9606 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 144 | 35397974 | 5917 | 142.008 | 5.917 | 3.4 | 3.4 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36775348 | 1368 | 231.1982 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 146 | 35403535 | 5561 | 133.464 | 5.561 | 3.3 | 3.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36776620 | 1272 | 228.7358 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 35409228 | 5693 | 136.632 | 5.693 | 3.2 | 3.2 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36777924 | 1304 | 229.0532 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 143 | 35414881 | 5653 | 135.672 | 5.653 | 2.9 | 2.9 | 3B+1S | 0 | 1175 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36779220 | 1296 | 229.2588 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 35420665 | 5784 | 138.816 | 5.784 | 2.8 | 2.8 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36780551 | 1331 | 230.1176 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 35426351 | 5686 | 136.464 | 5.686 | 2.6 | 2.6 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36781856 | 1305 | 229.5111 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 134 | 35431977 | 5626 | 135.024 | 5.626 | 2.4 | 2.4 | 3B+1S | 0 | 1006 | 1125 | 1185 | 1181 | N/A | N/A | N/A | N/A | 36783148 | 1292 | 229.6481 | 0% | 100% | 100% | 100% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 131 | 35437364 | 5387 | 129.288 | 5.387 | 2 | 2 | 2B+1S | 0 | 1146 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36784220 | 1072 | 198.9976 | 0% | 100% | 100% | 0% | 100% | 0% | 8248068 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 120 | 35442522 | 5158 | 123.792 | 5.158 | 1.5 | 1.5 | 2B+1S | 0 | 1066 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36785264 | 1044 | 202.404 | 0% | 100% | 100% | 0% | 100% | 0% | 8248068 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 102 | 35447708 | 5186 | 124.464 | 5.186 | 2.4 | 2.4 | 2B | 0 | 0 | 1160 | 0 | 1129 | N/A | N/A | N/A | N/A | 36786124 | 860 | 165.8311 | 0% | 0% | 100% | 0% | 100% | 35% | 8248938 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 96 | 35451278 | 3570 | 85.68 | 3.57 | 3.5 | 3.5 | 2B | 0 | 0 | 1060 | 0 | 1129 | N/A | N/A | N/A | N/A | 36786876 | 752 | 210.6443 | 0% | 0% | 100% | 0% | 100% | 35% | 8250018 | 1080 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129 | 127804 | 127804 | 127.804 | 127.804 | [12 empty] | 27232 | 27232 | 213.0763 | [6 empty] | 8075 | 8075 | 6.18 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:34 AM , NORMAL OPERATION
XCV1 CLOSED @ 4:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:17AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:00AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 6, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
MHE DEMAG REPAIRING THE OVERHEAD CRANE ARRIVED @ 1:00 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:42 PM , NORMAL OPERATION
SIR. JOSEPH DELA ROSA. SIR MARIANITO BARAHAN CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @2:05 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:19 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:10 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20 PM , NORMAL OPERATION

## MAY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | JIMENEZ GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26748 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35451278 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36786876 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8250018 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 91 | 35455035 | 3757 | 90.168 | 3.757 | 5.1 | 5.1 | 2B | 0 | 0 | 1062 | 0 | 1110 | N/A | N/A | N/A | N/A | 36787556 | 680 | 180.9955 | 0% | 0% | 100% | 0% | 100% | 45% | 8251426 | 1408 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 85 | 35458766 | 3731 | 89.544 | 3.731 | 6.6 | 6.6 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 36788204 | 648 | 173.68 | 0% | 0% | 100% | 0% | 100% | 45% | 8252838 | 1412 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 35462362 | 3596 | 86.304 | 3.596 | 8 | 8 | 2B | 0 | 0 | 1032 | 0 | 1048 | N/A | N/A | N/A | N/A | 36788828 | 624 | 173.5261 | 0% | 0% | 100% | 0% | 100% | 45% | 8254290 | 1452 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 93 | 35466059 | 3697 | 88.728 | 3.697 | 9.5 | 9.5 | 2B | 0 | 0 | 981 | 0 | 988 | N/A | N/A | N/A | N/A | 36789408 | 580 | 156.884 | 0% | 0% | 100% | 0% | 100% | 45% | 8255666 | 1376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 102 | 35470090 | 4031 | 96.744 | 4.031 | 9.5 | 9.5 | 2B | 0 | 0 | 1035 | 0 | 1008 | N/A | N/A | N/A | N/A | 36789972 | 564 | 139.9157 | 0% | 0% | 100% | 0% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 1336 | 35475275 | 5185 | 124.44 | 5.185 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1138 | N/A | N/A | N/A | N/A | 36790924 | 952 | 183.6066 | 0% | 0% | 100% | 100% | 100% | 0% | 8255666 | 0 | 1.09 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 149 | 35481467 | 6192 | 148.608 | 6.192 | 8.9 | 8.9 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36792308 | 1384 | 223.5142 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 154 | 35487826 | 6359 | 152.616 | 6.359 | 8.1 | 8.1 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36793708 | 1400 | 220.1604 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 35494142 | 6316 | 151.584 | 6.316 | 7.3 | 7.3 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36795116 | 1408 | 222.9259 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 35500471 | 6329 | 151.896 | 6.329 | 6.5 | 6.5 | 3B+1S | 0 | 1111 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36796532 | 1416 | 223.732 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 153 | 35506841 | 6370 | 152.88 | 6.37 | 5.8 | 5.8 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36797948 | 1416 | 222.292 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 150 | 35513070 | 6229 | 149.496 | 6.229 | 5.2 | 5.2 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36799332 | 1384 | 222.1865 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 141 | 35519113 | 6043 | 145.032 | 6.043 | 4.8 | 4.8 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36800704 | 1372 | 227.0395 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 137 | 35524976 | 5863 | 140.712 | 5.863 | 4.3 | 4.3 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36802036 | 1332 | 227.1874 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 35530685 | 5709 | 137.016 | 5.709 | 4.1 | 4.1 | 3B+1S | 0 | 1044 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36803340 | 1304 | 228.4113 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 145 | 35536376 | 5691 | 136.584 | 5.691 | 3.9 | 3.9 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36804628 | 1288 | 226.3223 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 149 | 35542404 | 6028 | 144.672 | 6.028 | 3.4 | 3.4 | 3B+1S | 0 | 1170 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36806012 | 1384 | 229.5952 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 142 | 35548329 | 5925 | 142.2 | 5.925 | 2.9 | 2.9 | 3B+1S | 0 | 1153 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36807368 | 1356 | 228.8608 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 134 | 35554041 | 5712 | 137.088 | 5.712 | 2.6 | 2.6 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36808692 | 1324 | 231.7927 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 132 | 35559659 | 5618 | 134.832 | 5.618 | 2.3 | 2.3 | 3B+1S | 0 | 1016 | 1156 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36809976 | 1284 | 228.5511 | 0% | 100% | 100% | 100% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 131 | 35564911 | 5252 | 126.048 | 5.252 | 1.8 | 1.8 | 2B+1S | 0 | 1189 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36811028 | 1052 | 200.3046 | 0% | 100% | 100% | 0% | 100% | 0% | 8255666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 126 | 35569994 | 5083 | 121.992 | 5.083 | 1.6 | 1.6 | 2B+1S | 0 | 1082 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36812028 | 1000 | 196.7342 | 0% | 100% | 100% | 0% | 100% | 0% | 8255666 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 102 | 35574431 | 4437 | 106.488 | 4.437 | 2.4 | 2.4 | 2B | 0 | 0 | 1184 | 0 | 1109 | N/A | N/A | N/A | N/A | 36812864 | 836 | 188.4156 | 0% | 0% | 100% | 0% | 100% | 35% | 8256553 | 887 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 102 | 35578638 | 4207 | 100.968 | 4.207 | 3.6 | 3.6 | 2B | 0 | 0 | 1092 | 0 | 1109 | N/A | N/A | N/A | N/A | 36813624 | 760 | 180.6513 | 0% | 0% | 100% | 0% | 100% | 35% | 8257627 | 1074 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 178.5 | 127360 | 127360 | 127.36 | 127.36 | [12 empty] | 26748 | 26748 | 210.0188 | [6 empty] | 7609 | 7609 | 6 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:37AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:00AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:16 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 7, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:32 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:10 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:14 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18 PM , NORMAL OPERATION
NORMAL OPERATION

## MAY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | JIMENEZ GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26868 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35578638 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36813624 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8257627 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 104 | 35582995 | 4357 | 104.568 | 4.357 | 4.9 | 4.9 | 2B | 0 | 0 | 1116 | 0 | 1139 | N/A | N/A | N/A | N/A | 36814428 | 804 | 184.5306 | 0% | 0% | 100% | 0% | 100% | 46% | 8258750 | 1123 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 101 | 35587228 | 4233 | 101.592 | 4.233 | 6.1 | 6.1 | 2B | 0 | 0 | 1101 | 0 | 1109 | N/A | N/A | N/A | N/A | 36815180 | 752 | 177.6518 | 0% | 0% | 100% | 0% | 100% | 46% | 8260005 | 1255 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 35591363 | 4135 | 99.24 | 4.135 | 7.6 | 7.6 | 2B | 0 | 0 | 1074 | 0 | 1100 | N/A | N/A | N/A | N/A | 36815876 | 696 | 168.3192 | 0% | 0% | 100% | 0% | 100% | 46% | 8261325 | 1320 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 100 | 35595586 | 4223 | 101.352 | 4.223 | 9 | 9 | 2B | 0 | 0 | 1071 | 0 | 1088 | N/A | N/A | N/A | N/A | 36816556 | 680 | 161.023 | 0% | 0% | 100% | 0% | 100% | 46% | 8262730 | 1405 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 111 | 35599975 | 4389 | 105.336 | 4.389 | 9.5 | 9.5 | 2B | 0 | 0 | 1068 | 0 | 1025 | N/A | N/A | N/A | N/A | 36817248 | 692 | 157.6669 | 0% | 0% | 100% | 0% | 100% | 46% | 8263215 | 485 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 35605209 | 5234 | 125.616 | 5.234 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 36818188 | 940 | 179.595 | 0% | 0% | 100% | 0% | 100% | 0% | 8263215 | 0 | 1.31 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 152 | 35611581 | 6372 | 152.928 | 6.372 | 8.8 | 8.8 | 3B+1S | 0 | 1189 | 1185 | 1185 | 1180 | N/A | N/A | N/A | N/A | 36819564 | 1376 | 215.9448 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 157 | 35617708 | 6127 | 147.048 | 6.127 | 8 | 8 | 3B+1S | 0 | 1188 | 1185 | 1185 | 1190 | N/A | N/A | N/A | N/A | 36820896 | 1332 | 217.3984 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 153 | 35623896 | 6188 | 148.512 | 6.188 | 7.4 | 7.4 | 3B+1S | 0 | 1190 | 1195 | 1185 | 1189 | N/A | N/A | N/A | N/A | 36822252 | 1356 | 219.1338 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 154 | 35630650 | 6754 | 162.096 | 6.754 | 6.3 | 6.3 | 3B+1S | 0 | 1189 | 1187 | 1185 | 1190 | N/A | N/A | N/A | N/A | 36823748 | 1496 | 221.4984 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 152 | 35636304 | 5654 | 135.696 | 5.654 | 5.9 | 5.9 | 3B+1S | 0 | 1148 | 1164 | 1185 | 1170 | N/A | N/A | N/A | N/A | 36824955 | 1207 | 213.4772 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Normal operation schedule
59:00 | 12:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 124 | 146 | 35642693 | 6389 | 153.336 | 6.389 | 5.6 | 5.6 | 3B+1S | 0 | 1108 | 1165 | 1185 | 1170 | N/A | N/A | N/A | N/A | 36826340 | 1385 | 216.7788 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 122 | 140 | 35649213 | 6520 | 156.48 | 6.52 | 5.1 | 5.1 | 3B+1S | 0 | 1189 | 1164 | 1185 | 1170 | N/A | N/A | N/A | N/A | 36827800 | 1460 | 223.9264 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 123 | 141 | 35654336 | 5123 | 122.952 | 5.123 | 4.8 | 4.8 | 3B+1S | 0 | 1145 | 1165 | 1185 | 1168 | N/A | N/A | N/A | N/A | 36828940 | 1140 | 222.5259 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 35659795 | 5459 | 131.016 | 5.459 | 4.6 | 4.6 | 3B+1S | 0 | 1102 | 1165 | 1185 | 1168 | N/A | N/A | N/A | N/A | 36830172 | 1232 | 225.6824 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 35665459 | 5664 | 135.936 | 5.664 | 4.5 | 4.5 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36831472 | 1300 | 229.5198 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 142 | 35671147 | 5688 | 136.512 | 5.688 | 4.2 | 4.2 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36832788 | 1316 | 231.3643 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 35676911 | 5764 | 138.336 | 5.764 | 3.9 | 3.9 | 3B+1S | 0 | 1023 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36834116 | 1328 | 230.3956 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 | 0.74 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 35682607 | 5696 | 136.704 | 5.696 | 3.7 | 3.7 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36835428 | 1312 | 230.3371 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 35688398 | 5791 | 138.984 | 5.791 | 3.4 | 3.4 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36836722 | 1294 | 223.4502 | 0% | 100% | 100% | 100% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 106 | 131 | 35693568 | 5170 | 124.08 | 5.17 | 2.8 | 2.8 | 2B+1S | 0 | 1156 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36837844 | 1122 | 217.0213 | 0% | 100% | 100% | 0% | 100% | 0% | 8263215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 125 | 35698738 | 5170 | 124.08 | 5.17 | 2 | 2 | 2B+1S | 0 | 1085 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36838904 | 1060 | 205.029 | 0% | 100% | 100% | 0% | 100% | 0% | 8263215 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 105 | 35703237 | 4499 | 107.976 | 4.499 | 2.8 | 2.8 | 2B | 0 | 0 | 1128 | 0 | 1150 | N/A | N/A | N/A | N/A | 36839748 | 844 | 187.5972 | 0% | 0% | 100% | 0% | 100% | 35% | 8264006 | 791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 95 | 35707438 | 4201 | 100.824 | 4.201 | 3.9 | 3.9 | 2B | 0 | 0 | 1077 | 0 | 1100 | N/A | N/A | N/A | N/A | 36840492 | 744 | 177.1007 | 0% | 0% | 100% | 0% | 100% | 35% | 8265072 | 1066 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 130 | 128800 | 128800 | 128.8 | 128.8 | [12 empty] | 26868 | 26868 | 208.6025 | [6 empty] | 7445 | 7445 | 5.98 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:31 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8:15AM
SIR MARIANITO BARAHAN CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @8:15 AM
TEAM MAINTENANCE ARRIVED @ 9:05 AM TO FIXED THE CRANE AND REPAIR THE CRANE LIFT SIDE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:28 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 7, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55 AM , NORMAL OPERATION
MR. ARIEL MULA OF KBT TRAIDING DELIVER 16 PCS. UMBRELLA & 50 PCS. CALENDAR ARRIVED @2:20 PM
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,787
GENSET 1 WARMUP EXERCISED @ 4:21 PM / STOPPED @ 4:31 PM
GENSET 2 WARMUP EXERCISED @ 4:10 PM / STOPPED @ 4:20PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:42 pM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
SIR MARIANITO BARAHAN CONDUCTED PLANT INSPECTION & MONITORING ARRIVED @5:33 PM
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:28 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:28 PM , NORMAL OPERATION
NORMAL OPERATION

## MAY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | JIMENEZ GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26848 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks |  | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35707438 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36840492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8265072 |  | mg /l |  |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 90 | 35711288 | 3850 | 92.4 | 3.85 | 5.5 | 5.5 | 2B | 0 | 0 | 1053 | 0 | 1109 | N/A | N/A | N/A | N/A | 36841180 | 688 | 178.7013 | 0% | 0% | 100% | 0% | 100% | 45% | 8266406 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 87 | 35714939 | 3651 | 87.624 | 3.651 | 7 | 7 | 2B | 0 | 0 | 1010 | 0 | 1109 | N/A | N/A | N/A | N/A | 36841820 | 640 | 175.2944 | 0% | 0% | 100% | 0% | 100% | 45% | 8267854 | 1448 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 83 | 35718535 | 3596 | 86.304 | 3.596 | 8.5 | 8.5 | 2B | 0 | 0 | 1002 | 0 | 1059 | N/A | N/A | N/A | N/A | 36842428 | 608 | 169.0768 | 0% | 0% | 100% | 0% | 100% | 45% | 8269316 | 1462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 88 | 35722214 | 3679 | 88.296 | 3.679 | 9.5 | 9.5 | 2B | 0 | 0 | 872 | 0 | 1009 | N/A | N/A | N/A | N/A | 36842980 | 552 | 150.0408 | 0% | 0% | 100% | 0% | 100% | 45% | 8270333 | 1017 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 100 | 35726160 | 3946 | 94.704 | 3.946 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 1028 | N/A | N/A | N/A | N/A | 36843508 | 528 | 133.8064 | 0% | 0% | 100% | 0% | 100% | 45% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 8269 | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 35731019 | 4859 | 116.616 | 4.859 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36844372 | 864 | 177.8144 | 0% | 0% | 100% | 0% | 100% | 0% | 8270333 | 0 | 1.1 | Normal operation schedule |  | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 155 | 35737212 | 6193 | 148.632 | 6.193 | 9 | 9 | 3B+1S | 0 | 1103 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36845736 | 1364 | 220.2487 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Normal operation schedule |  | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 152 | 35743601 | 6389 | 153.336 | 6.389 | 8.3 | 8.3 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36847148 | 1412 | 221.0049 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Normal operation schedule |  | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 35749981 | 6380 | 153.12 | 6.38 | 7.6 | 7.6 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36848564 | 1416 | 221.9436 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Normal operation schedule |  | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 152 | 35756247 | 6266 | 150.384 | 6.266 | 6.8 | 6.8 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36849980 | 1416 | 225.9815 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 35762514 | 6267 | 150.408 | 6.267 | 5.9 | 5.9 | 3B+1S | 0 | 1162 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36851396 | 1416 | 225.9454 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 35768768 | 6254 | 150.096 | 6.254 | 5.1 | 5.1 | 3B+1S | 0 | 1140 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36852820 | 1424 | 227.6943 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Normal operation schedule |  | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 149 | 35775055 | 6287 | 150.888 | 6.287 | 4.4 | 4.4 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36854228 | 1408 | 223.9542 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 143 | 35781004 | 5949 | 142.776 | 5.949 | 3.5 | 3.5 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36855572 | 1344 | 225.9203 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 144 | 35787039 | 6035 | 144.84 | 6.035 | 3.5 | 3.5 | 3B+1S | 0 | 1066 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36856932 | 1360 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 147 | 35792895 | 5856 | 140.544 | 5.856 | 3.4 | 3.4 | 3B+1S | 0 | 1084 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36858252 | 1320 | 225.4098 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 146 | 35798791 | 5896 | 141.504 | 5.896 | 3.1 | 3.1 | 3B+1S | 0 | 1140 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36859591 | 1339 | 227.1031 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 143 | 35804592 | 5801 | 139.224 | 5.801 | 2.8 | 2.8 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36860928 | 1337 | 230.4775 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 141 | 35810385 | 5793 | 139.032 | 5.793 | 2.6 | 2.6 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36862244 | 1316 | 227.1707 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 136 | 35816052 | 5667 | 136.008 | 5.667 | 2.4 | 2.4 | 3B+1S | 0 | 966 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36863548 | 1304 | 230.1041 | 0% | 100% | 100% | 100% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 129 | 35821441 | 5389 | 129.336 | 5.389 | 2 | 2 | 2B+1S | 0 | 118 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36864628 | 1080 | 200.4082 | 0% | 100% | 100% | 0% | 100% | 0% | 8270333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 127 | 35826681 | 5240 | 125.76 | 5.24 | 1.5 | 1.5 | 2B+1S | 0 | 1167 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36865656 | 1028 | 196.1832 | 0% | 100% | 100% | 0% | 100% | 0% | 8270333 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 106 | 35831272 | 4591 | 110.184 | 4.591 | 2.2 | 2.2 | 2B | 0 | 0 | 1143 | 0 | 1170 | N/A | N/A | N/A | N/A | 36866532 | 876 | 190.8081 | 0% | 0% | 100% | 0% | 100% | 35% | 8271114 | 781 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 99 | 35835668 | 4396 | 105.504 | 4.396 | 3.3 | 3.3 | 2B | 0 | 0 | 1097 | 0 | 1109 | N/A | N/A | N/A | N/A | 36867340 | 808 | 183.8035 | 0% | 0% | 100% | 0% | 100% | 35% | 8272117 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.7917 | 128230 | 128230 | 128.23 | 128.23 | [12 empty] | 26848 | 26848 | 209.3738 | [6 empty] | 7045 | 7045 | 6.07 |  |  | MLD | 1
[45 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [44 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 9, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12pM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:10 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:40 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:10 PM , NORMAL OPERATION
NORMAL OPERATION

## MAY 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26488 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35835668 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36867340 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8272117 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 94 | 35839725 | 4057 | 97.368 | 4.057 | 4.7 | 4.7 | 2B | 0 | 0 | 1090 | 0 | 1109 | N/A | N/A | N/A | N/A | 36868080 | 740 | 182.4008 | 0% | 0% | 100% | 0% | 100% | 45% | 8273388 | 1271 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 99 | 35843732 | 4007 | 96.168 | 4.007 | 6.1 | 6.1 | 2B | 0 | 0 | 1077 | 0 | 1110 | N/A | N/A | N/A | N/A | 36868788 | 708 | 176.6908 | 0% | 0% | 100% | 0% | 100% | 45% | 8274678 | 1290 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 94 | 35847693 | 3961 | 95.064 | 3.961 | 7.4 | 7.4 | 2B | 0 | 0 | 1048 | 0 | 1109 | N/A | N/A | N/A | N/A | 36869468 | 680 | 171.6738 | 0% | 0% | 100% | 0% | 100% | 45% | 8275907 | 1229 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 95 | 35851586 | 3893 | 93.432 | 3.893 | 8.6 | 8.6 | 2B | 0 | 0 | 1017 | 0 | 1139 | N/A | N/A | N/A | N/A | 36870120 | 652 | 167.4801 | 0% | 0% | 100% | 0% | 100% | 45% | 8277043 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 32 | 22.5352 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 96 | 35855632 | 4046 | 97.104 | 4.046 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 1110 | N/A | N/A | N/A | N/A | 36870784 | 664 | 164.1127 | 0% | 0% | 100% | 0% | 100% | 45% | 8277892 | 849 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 123 | 35860559 | 4927 | 118.248 | 4.927 | 9.5 | 9.5 | 2B | 0 | 0 | 1190 | 0 | 1199 | N/A | N/A | N/A | N/A | 36871660 | 876 | 177.7958 | 0% | 0% | 100% | 0% | 100% | 0% | 8277892 | 0 | 1.12 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 150 | 35866692 | 6133 | 147.192 | 6.133 | 9.1 | 9.1 | 3B+1S | 0 | 1026 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36873020 | 1360 | 221.7512 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 155 | 35872963 | 6271 | 150.504 | 6.271 | 8.5 | 8.5 | 3B+1S | 0 | 1091 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36874396 | 1376 | 219.4227 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 155 | 35879475 | 6512 | 156.288 | 6.512 | 7.6 | 7.6 | 3B+1S | 0 | 1160 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36875844 | 1448 | 222.3587 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 159 | 35886022 | 6547 | 157.128 | 6.547 | 6.5 | 6.5 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36877332 | 1488 | 227.2797 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 153 | 35892580 | 6558 | 157.392 | 6.558 | 5.6 | 5.6 | 3B+1S | 0 | 1172 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36878812 | 1480 | 225.6786 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 155 | 35898943 | 6363 | 152.712 | 6.363 | 4.7 | 4.7 | 3B+1S | 0 | 1138 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36880252 | 1440 | 226.3083 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 146 | 35905233 | 6290 | 150.96 | 6.29 | 3.5 | 3.5 | 3B+1S | 0 | 1134 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36881662 | 1410 | 224.1653 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 144 | 35911313 | 6080 | 145.92 | 6.08 | 2.9 | 2.9 | 3B+1S | 0 | 1132 | 1196 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36883108 | 1446 | 237.8289 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 121 | 143 | 35916983 | 5670 | 136.08 | 5.67 | 2.6 | 2.6 | 3B+1S | 0 | 1189 | 1145 | 1185 | 1140 | N/A | N/A | N/A | N/A | 36884348 | 1240 | 218.6949 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 121 | 143 | 35922747 | 5764 | 138.336 | 5.764 | 2.2 | 2.2 | 3B+1S | 0 | 1188 | 1146 | 1185 | 1138 | N/A | N/A | N/A | N/A | 36885608 | 1260 | 218.5982 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 142 | 35928532 | 5785 | 138.84 | 5.785 | 1.4 | 1.4 | 3B+1S | 0 | 1189 | 1145 | 1185 | 1139 | N/A | N/A | N/A | N/A | 36886908 | 1300 | 224.7191 | 0% | 100% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 35933946 | 5414 | 129.936 | 5.414 | 1.3 | 1.3 | 3B | 0 | 0 | 1157 | 1185 | 1148 | N/A | N/A | N/A | N/A | 36888084 | 1176 | 217.2146 | 0% | 0% | 100% | 100% | 100% | 0% | 8277892 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 130 | 35939301 | 5355 | 128.52 | 5.355 | 1.3 | 1.3 | 3B | 0 | 0 | 1126 | 1185 | 1128 | N/A | N/A | N/A | N/A | 36889228 | 1144 | 213.6321 | 0% | 0% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 137 | 35944801 | 5500 | 132 | 5.5 | 1.3 | 1.3 | 3B | 0 | 0 | 1185 | 1185 | 1168 | N/A | N/A | N/A | N/A | 36890364 | 1136 | 206.5455 | 0% | 0% | 100% | 100% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 123 | 117 | 35949923 | 5122 | 122.928 | 5.122 | 1.3 | 1.3 | 2B | 0 | 0 | 1186 | 0 | 1190 | N/A | N/A | N/A | N/A | 36891308 | 944 | 184.303 | 0% | 0% | 100% | 0% | 100% | 0% | 8277892 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 122 | 35954853 | 4930 | 118.32 | 4.93 | 1.3 | 1.3 | 2B | 0 | 0 | 1196 | 0 | 1199 | N/A | N/A | N/A | N/A | 36892212 | 904 | 183.3671 | 0% | 0% | 100% | 0% | 100% | 0% | 8277892 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 103 | 35959312 | 4459 | 107.016 | 4.459 | 2.2 | 2.2 | 2B | 0 | 0 | 1184 | 0 | 1129 | N/A | N/A | N/A | N/A | 36893052 | 840 | 188.383 | 0% | 0% | 100% | 0% | 100% | 30% | 8278515 | 623 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 101 | 35963703 | 4391 | 105.384 | 4.391 | 3.1 | 3.1 | 2B | 0 | 0 | 1081 | 0 | 1129 | N/A | N/A | N/A | N/A | 36893828 | 776 | 176.7251 | 0% | 0% | 100% | 0% | 100% | 30% | 8279343 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.8333 | 128035 | 128035 | 128.035 | 128.035 | [12 empty] | 26488 | 26488 | 206.8809 | [6 empty] | 7226 | 7226 | 5.79 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 10, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:28PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:20PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 5:02 PM DUE TO WATER LEVEL LOW 1.4M
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:23PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:20PM , NORMAL OPERATION
NORMAL OPERATION

## MAY 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26080 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 35963703 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36893828 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8279343 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 96 | 35967816 | 4113 | 98.712 | 4.113 | 4.3 | 4.3 | 2B | 0 | 0 | 1110 | 0 | 1129 | N/A | N/A | N/A | N/A | 36894588 | 760 | 184.78 | 0% | 0% | 100% | 0% | 100% | 46% | 8280479 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 92 | 35971683 | 3867 | 92.808 | 3.867 | 5.6 | 5.6 | 2B | 0 | 0 | 1049 | 0 | 1129 | N/A | N/A | N/A | N/A | 36895288 | 700 | 181.0189 | 0% | 0% | 100% | 0% | 100% | 46% | 8281776 | 1297 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 35975512 | 3829 | 91.896 | 3.829 | 7.1 | 7.1 | 2B | 0 | 0 | 1018 | 0 | 1129 | N/A | N/A | N/A | N/A | 36895964 | 676 | 176.5474 | 0% | 0% | 100% | 0% | 100% | 46% | 8283161 | 1385 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 88 | 35979293 | 3781 | 90.744 | 3.781 | 8.8 | 8.8 | 2B | 0 | 0 | 983 | 0 | 1119 | N/A | N/A | N/A | N/A | 36896620 | 656 | 173.4991 | 0% | 0% | 100% | 0% | 100% | 46% | 8284826 | 1665 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 94 | 35982932 | 3639 | 87.336 | 3.639 | 9.5 | 9.5 | 2B | 0 | 0 | 920 | 0 | 1119 | N/A | N/A | N/A | N/A | 36897172 | 552 | 151.69 | 0% | 0% | 100% | 0% | 100% | 46% | 8285282 | 456 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 122 | 35987859 | 4927 | 118.248 | 4.927 | 9.5 | 9.5 | 2B | 0 | 0 | 1196 | 0 | 1149 | N/A | N/A | N/A | N/A | 36898020 | 848 | 172.1128 | 0% | 0% | 100% | 0% | 100% | 0% | 8285282 | 0 | 0.97 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 142 | 35993642 | 5783 | 138.792 | 5.783 | 9.5 | 9.5 | 3B | 0 | 0 | 1138 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36899220 | 1200 | 207.5048 | 0% | 0% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 149 | 145 | 35999712 | 6070 | 145.68 | 6.07 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36900500 | 1280 | 210.8731 | 0% | 0% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 152 | 36006014 | 6302 | 151.248 | 6.302 | 8.9 | 8.9 | 3B+1S | 0 | 1067 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36901888 | 1388 | 220.2475 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 36012319 | 6305 | 151.32 | 6.305 | 8.2 | 8.2 | 3B+1S | 0 | 1093 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36903292 | 1404 | 222.6804 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 | 0.84 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 36018612 | 6293 | 151.032 | 6.293 | 7.5 | 7.5 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36904696 | 1404 | 223.105 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Normal operation schedule
59:00 | 12:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 139 | 36024713 | 6101 | 146.424 | 6.101 | 7.1 | 7.1 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36906058 | 1362 | 223.2421 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 148 | 36030814 | 6101 | 146.424 | 6.101 | 7 | 7 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36907420 | 1362 | 223.2421 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 36036690 | 5876 | 141.024 | 5.876 | 6.7 | 6.7 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36908748 | 1328 | 226.0041 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 22 | 15.493 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 36042496 | 5806 | 139.344 | 5.806 | 6.4 | 6.4 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36910092 | 1344 | 231.4847 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 36048181 | 5685 | 136.44 | 5.685 | 6.1 | 6.1 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36911412 | 1320 | 232.19 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 36053909 | 5728 | 137.472 | 5.728 | 5.8 | 5.8 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36912748 | 1336 | 233.2402 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 36059565 | 5656 | 135.744 | 5.656 | 5.6 | 5.6 | 3B+1S | 0 | 971 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36914052 | 1304 | 230.5516 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 130 | 36065182 | 5617 | 134.808 | 5.617 | 5.5 | 5.5 | 3B+1S | 0 | 986 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36915324 | 1272 | 226.4554 | 0% | 100% | 100% | 100% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 127 | 36070558 | 5376 | 129.024 | 5.376 | 5 | 5 | 2B+1S | 0 | 1039 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36916396 | 1072 | 199.4048 | 0% | 100% | 100% | 0% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 36075761 | 5203 | 124.872 | 5.203 | 4.3 | 4.3 | 2B+1S | 0 | 1039 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36917432 | 1036 | 199.1159 | 0% | 100% | 100% | 0% | 100% | 0% | 8285282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 120 | 36080779 | 5018 | 120.432 | 5.018 | 4 | 4 | 2B+1S | 0 | 1014 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36918420 | 988 | 196.8912 | 0% | 100% | 100% | 0% | 100% | 0% | 8285282 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 98 | 36085943 | 5164 | 123.936 | 5.164 | 4.7 | 4.7 | 2B | 0 | 0 | 1091 | 0 | 1110 | N/A | N/A | N/A | N/A | 36919204 | 784 | 151.8203 | 0% | 0% | 100% | 0% | 100% | 30% | 8285943 | 661 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 97 | 36089301 | 3358 | 80.592 | 3.358 | 5.5 | 5.5 | 2B | 0 | 0 | 1030 | 0 | 1110 | N/A | N/A | N/A | N/A | 36919908 | 704 | 209.6486 | 0% | 0% | 100% | 0% | 100% | 30% | 8286714 | 771 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.625 | 125598 | 125598 | 125.598 | 125.598 | [12 empty] | 26080 | 26080 | 207.6466 | [6 empty] | 7371 | 7371 | 6.13 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:35AM , NORMAL OPERATION
XCV1 CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 11, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:40 PM , NORMAL OPERATION

## MAY 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26536 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36089301 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36919908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8286714 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 92 | 36093069 | 3768 | 90.432 | 3.768 | 6.5 | 6.5 | 2B | 0 | 0 | 1020 | 0 | 1110 | N/A | N/A | N/A | N/A | 36920564 | 656 | 174.0977 | 0% | 0% | 100% | 0% | 100% | 35% | 8287689 | 975 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 90 | 36096800 | 3731 | 89.544 | 3.731 | 7.6 | 7.6 | 2B | 0 | 0 | 1024 | 0 | 1048 | N/A | N/A | N/A | N/A | 36921188 | 624 | 167.2474 | 0% | 0% | 100% | 0% | 100% | 35% | 8288788 | 1099 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 87 | 36100399 | 3599 | 86.376 | 3.599 | 8.8 | 8.8 | 2B | 0 | 0 | 1005 | 0 | 1028 | N/A | N/A | N/A | N/A | 36921756 | 568 | 157.8216 | 0% | 0% | 100% | 0% | 100% | 35% | 8289798 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 90 | 36104172 | 3773 | 90.552 | 3.773 | 9.5 | 9.5 | 2B | 0 | 0 | 901 | 0 | 1008 | N/A | N/A | N/A | N/A | 36922300 | 544 | 144.1823 | 0% | 0% | 100% | 0% | 100% | 35% | 8290539 | 741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 99 | 36107999 | 3827 | 91.848 | 3.827 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 1008 | N/A | N/A | N/A | N/A | 36922804 | 504 | 131.6958 | 0% | 0% | 100% | 0% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 125 | 36112776 | 4777 | 114.648 | 4.777 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 |  | 1198 | N/A | N/A | N/A | N/A | 36923656 | 852 | 178.3546 | 0% | 0% | 100% | 0% | 100% | 0% | 8290539 | 0 | 1.02 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 152 | 36118996 | 6220 | 149.28 | 6.22 | 9.1 | 9.1 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36925020 | 1364 | 219.2926 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 155 | 36125419 | 6423 | 154.152 | 6.423 | 8.4 | 8.4 | 3B+1S | 0 | 1093 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36926428 | 1408 | 219.2122 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 155 | 36131743 | 6324 | 151.776 | 6.324 | 7.5 | 7.5 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36927844 | 1416 | 223.9089 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 36138068 | 6325 | 151.8 | 6.325 | 6.8 | 6.8 | 3B+1S | 0 | 1132 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36929260 | 1416 | 223.8735 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 36144502 | 6434 | 154.416 | 6.434 | 5.9 | 5.9 | 3B+1S | 0 | 1108 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36930708 | 1448 | 225.0544 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 36150767 | 6265 | 150.36 | 6.265 | 5.3 | 5.3 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36932124 | 1416 | 226.0176 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 36156655 | 5888 | 141.312 | 5.888 | 4.8 | 4.8 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36933468 | 1344 | 228.2609 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 36162516 | 5861 | 140.664 | 5.861 | 4.3 | 4.3 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36934828 | 1360 | 232.0423 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 36168282 | 5766 | 138.384 | 5.766 | 3.8 | 3.8 | 3B+1S | 0 | 1041 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36936164 | 1336 | 231.7031 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 36173929 | 5647 | 135.528 | 5.647 | 3.6 | 3.6 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36937496 | 1332 | 235.8775 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 141 | 36179531 | 5602 | 134.448 | 5.602 | 3.3 | 3.3 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36938800 | 1304 | 232.774 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 139 | 36185325 | 5794 | 139.056 | 5.794 | 3 | 3 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36940128 | 1328 | 229.2026 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 36191075 | 5750 | 138 | 5.75 | 2.7 | 2.7 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36941460 | 1332 | 231.6522 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 133 | 36196726 | 5651 | 135.624 | 5.651 | 2.5 | 2.5 | 3B+1S | 0 | 997 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36942736 | 1276 | 225.8007 | 0% | 100% | 100% | 100% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 121 | 36202110 | 5384 | 129.216 | 5.384 | 1.6 | 1.6 | 2B+1S | 0 | 1019 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36943860 | 1124 | 208.7667 | 0% | 100% | 100% | 0% | 100% | 0% | 8290539 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 120 | 36207271 | 5161 | 123.864 | 5.161 | 1.3 | 1.3 | 2B+1S | 0 | 960 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36944868 | 1008 | 195.311 | 0% | 100% | 100% | 0% | 100% | 0% | 8290539 | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 103 | 36211604 | 4333 | 103.992 | 4.333 | 2.3 | 2.3 | 2B | 0 | 0 | 1170 | 0 | 1119 | N/A | N/A | N/A | N/A | 36945676 | 808 | 186.4759 | 0% | 0% | 100% | 0% | 100% | 37% | 8291507 | 968 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 94 | 36215843 | 4239 | 101.736 | 4.239 | 3.4 | 3.4 | 2B | 0 | 0 | 1059 | 0 | 1119 | N/A | N/A | N/A | N/A | 36946444 | 768 | 181.1748 | 0% | 0% | 100% | 0% | 100% | 37% | 8292660 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.4583 | 126542 | 126542 | 126.542 | 126.542 | [12 empty] | 26536 | 26536 | 209.7011 | [6 empty] | 5946 | 5946 | 6.09 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (35%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
EXPONENT CONTINUE WORKING THE PIPE LINE AND FOR WIRING
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 12, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:36PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (37%) @ 10:01 PM FOR REFILLING

## MAY 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27016 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36215843 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36946444 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8292660 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 90 | 36219734 | 3891 | 93.384 | 3.891 | 5 | 5 | 2B | 0 | 0 | 1051 | 0 | 1119 | N/A | N/A | N/A | N/A | 36947156 | 712 | 182.9864 | 0% | 0% | 100% | 0% | 100% | 46% | 8294034 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 85 | 36223267 | 3533 | 84.792 | 3.533 | 6.4 | 6.4 | 2B | 0 | 0 | 1006 | 0 | 1118 | N/A | N/A | N/A | N/A | 36947776 | 620 | 175.4883 | 0% | 0% | 100% | 0% | 100% | 46% | 8295487 | 1453 | 0.68 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 86 | 36226865 | 3598 | 86.352 | 3.598 | 7.9 | 7.9 | 2B | 0 | 0 | 980 | 0 | 1119 | N/A | N/A | N/A | N/A | 36948404 | 628 | 174.5414 | 0% | 0% | 100% | 0% | 100% | 46% | 8296969 | 1482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 89 | 88 | 36230403 | 3538 | 84.912 | 3.538 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 1119 | N/A | N/A | N/A | N/A | 36948996 | 592 | 167.3262 | 0% | 0% | 100% | 0% | 100% | 46% | 8298220 | 1251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 98 | 36234282 | 3879 | 93.096 | 3.879 | 9.5 | 9.5 | 2B | 0 | 0 | 907 | 0 | 1120 | N/A | N/A | N/A | N/A | 36949580 | 584 | 150.5543 | 0% | 0% | 100% | 0% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 144 | 142 | 36239563 | 5281 | 126.744 | 5.281 | 9.5 | 9.5 | 3B | 0 | 0 | 1196 | 1185 | 11981 | N/A | N/A | N/A | N/A | 36950608 | 1028 | 194.6601 | 0% | 0% | 100% | 100% | 100% | 0% | 8298220 | 0 | 0.97 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 154 | 36245740 | 6177 | 148.248 | 6.177 | 9 | 9 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36951976 | 1368 | 221.4667 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 136 | 36252078 | 6338 | 152.112 | 6.338 | 8.1 | 8.1 | 3B+1S | 0 | 1133 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36953380 | 1404 | 221.521 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 152 | 36258618 | 6540 | 156.96 | 6.54 | 7.3 | 7.3 | 3B+1S | 0 | 1123 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36954852 | 1472 | 225.0765 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 36264918 | 6300 | 151.2 | 6.3 | 6.4 | 6.4 | 3B+1S | 0 | 1142 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36956268 | 1416 | 224.7619 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 | 0.83 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 154 | 36271224 | 6306 | 151.344 | 6.306 | 5.4 | 5.4 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36957684 | 1416 | 224.548 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 36277531 | 6307 | 151.368 | 6.307 | 4.9 | 4.9 | 3B+1S | 0 | 1050 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36959100 | 1416 | 224.5124 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 150 | 36282596 | 5065 | 121.56 | 5.065 | 4.2 | 4.2 | 3B+1S | 0 | 1081 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36960496 | 1396 | 275.617 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 36289531 | 6935 | 166.44 | 6.935 | 3.6 | 3.6 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36961852 | 1356 | 195.5299 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 36295272 | 5741 | 137.784 | 5.741 | 3.5 | 3.5 | 3B+1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36963196 | 1344 | 234.1056 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 136 | 36300955 | 5683 | 136.392 | 5.683 | 3.4 | 3.4 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36964510 | 1314 | 231.2159 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 142 | 36306704 | 5749 | 137.976 | 5.749 | 3 | 3 | 3B+1S | 0 | 1185 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36965836 | 1326 | 230.6488 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 143 | 36312585 | 5881 | 141.144 | 5.881 | 2.6 | 2.6 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36967180 | 1344 | 228.5326 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 148 | 36318413 | 5828 | 139.872 | 5.828 | 2.3 | 2.3 | 3B+1S | 0 | 1098 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36968496 | 1316 | 225.8065 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 137 | 36324249 | 5836 | 140.064 | 5.836 | 2 | 2 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36969844 | 1348 | 230.9801 | 0% | 100% | 100% | 100% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 130 | 36329352 | 5103 | 122.472 | 5.103 | 1.8 | 1.8 | 2B+1S | 0 | 1159 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36970860 | 1016 | 199.0986 | 0% | 100% | 100% | 0% | 100% | 0% | 8298220 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 124 | 36334426 | 5074 | 121.776 | 5.074 | 1.4 | 1.4 | 2B+1S | 0 | 1110 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36971880 | 1020 | 201.0248 | 0% | 100% | 100% | 0% | 100% | 0% | 8298220 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 102 | 36338908 | 4482 | 107.568 | 4.482 | 2.3 | 2.3 | 2B | 0 | 0 | 1138 | 0 | 1139 | N/A | N/A | N/A | N/A | 36972720 | 840 | 187.4163 | 0% | 0% | 100% | 0% | 100% | 38% | 8299084 | 864 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 95 | 36342976 | 4068 | 97.632 | 4.068 | 3.5 | 3.5 | 2B | 0 | 0 | 1053 | 0 | 1139 | N/A | N/A | N/A | N/A | 36973460 | 740 | 181.9076 | 0% | 0% | 100% | 0% | 100% | 38% | 8300266 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.9167 | 127133 | 127133 | 127.133 | 127.133 | [12 empty] | 27016 | 27016 | 212.5019 | [6 empty] | 7606 | 7606 | 5.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:25AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:22AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
TEAM MAINTENANCE ARRIVED @ 1;00 PM TO REPAIR THE OVERHEAD CRANE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 13, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:33 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:31 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
EXPONENT PERSONELL ARRIVED @ 5:05 PM FOR INSTALLATION OF FLOW METER FOR GENSET
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:16PM , NORMAL OPERATION
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:20PM , NORMAL OPERATION

## MAY 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26776 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36342976 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 36973460 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8300266 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 91 | 36346902 | 3926 | 94.224 | 3.926 | 5.2 | 5.2 | 2B | 0 | 0 | 1056 | 0 | 1110 | N/A | N/A | N/A | N/A | 36974172 | 712 | 181.3551 | 0% | 0% | 100% | 0% | 100% | 48% | 8301697 | 1431 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 89 | 36350616 | 3714 | 89.136 | 3.714 | 6.7 | 6.7 | 2B | 0 | 0 | 1025 | 0 | 1110 | N/A | N/A | N/A | N/A | 36974828 | 656 | 176.629 | 0% | 0% | 100% | 0% | 100% | 48% | 8303229 | 1532 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 88 | 36354247 | 3631 | 87.144 | 3.631 | 8.3 | 8.3 | 2B | 0 | 0 | 1027 | 0 | 1048 | N/A | N/A | N/A | N/A | 36975408 | 580 | 159.7356 | 0% | 0% | 100% | 0% | 100% | 48% | 8304743 | 1514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 92 | 36357940 | 3693 | 88.632 | 3.693 | 9.5 | 9.5 | 2B | 0 | 0 | 965 | 0 | 1008 | N/A | N/A | N/A | N/A | 36976016 | 608 | 164.6358 | 0% | 0% | 100% | 0% | 100% | 48% | 8305826 | 1083 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 105 | 36362304 | 4364 | 104.736 | 4.364 | 9.5 | 9.5 | 2B | 0 | 0 | 1035 | 0 | 1008 | N/A | N/A | N/A | N/A | 36976620 | 604 | 138.4051 | 0% | 0% | 100% | 0% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 137 | 36367058 | 4754 | 114.096 | 4.754 | 9.5 | 9.5 | 3B | 0 | 0 | 1054 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36977492 | 872 | 183.4245 | 0% | 0% | 100% | 100% | 100% | 0% | 8305826 | 0 | 0.87 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 153 | 36373137 | 6079 | 145.896 | 6.079 | 8.9 | 8.9 | 3B+1S | 0 | 1031 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36978836 | 1344 | 221.089 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 153 | 36379516 | 6379 | 153.096 | 6.379 | 8.4 | 8.4 | 3B+1S | 0 | 1073 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36980232 | 1396 | 218.8431 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 36385766 | 6250 | 150 | 6.25 | 7.7 | 7.7 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36981632 | 1400 | 224 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 36392060 | 6294 | 151.056 | 6.294 | 7 | 7 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36983024 | 1392 | 221.163 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 36398356 | 6296 | 151.104 | 6.296 | 6.3 | 6.3 | 3B+1S | 0 | 1053 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36984428 | 1404 | 222.9987 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 36404610 | 6254 | 150.096 | 6.254 | 5.9 | 5.9 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36985820 | 1392 | 222.5776 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 145 | 36410628 | 6018 | 144.432 | 6.018 | 5.4 | 5.4 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36987188 | 1368 | 227.318 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 36416542 | 5914 | 141.936 | 5.914 | 5.1 | 5.1 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36988540 | 1352 | 228.6101 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 145 | 36422069 | 5527 | 132.648 | 5.527 | 5 | 5 | 3B+1S | 0 | 1014 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36989820 | 1280 | 231.5904 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 141 | 36427767 | 5698 | 136.752 | 5.698 | 4.9 | 4.9 | 3B+1S | 0 | 1034 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36991124 | 1304 | 228.8522 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 141 | 36433539 | 5772 | 138.528 | 5.772 | 4.6 | 4.6 | 3B+1S | 0 | 1149 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36992456 | 1332 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 148 | 36439442 | 5903 | 141.672 | 5.903 | 4 | 4 | 3B+1S | 0 | 1052 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36993808 | 1352 | 229.0361 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 150 | 36445422 | 5980 | 143.52 | 5.98 | 3.5 | 3.5 | 3B+1S | 0 | 1189 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36995180 | 1372 | 229.4314 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 141 | 36451203 | 5781 | 138.744 | 5.781 | 3.1 | 3.1 | 3B+1S | 0 | 1006 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 36996472 | 1292 | 223.4907 | 0% | 100% | 100% | 100% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 132 | 36456561 | 5358 | 128.592 | 5.358 | 2.5 | 2.5 | 2B+1S | 0 | 1189 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36997532 | 1060 | 197.835 | 0% | 100% | 100% | 0% | 100% | 0% | 8305826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 127 | 36461941 | 5380 | 129.12 | 5.38 | 2 | 2 | 2B+1S | 0 | 1181 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 36998592 | 1060 | 197.026 | 0% | 100% | 100% | 0% | 100% | 0% | 8305826 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 106 | 36466514 | 4573 | 109.752 | 4.573 | 2.7 | 2.7 | 2B | 0 | 0 | 1177 | 0 | 1160 | N/A | N/A | N/A | N/A | 36999444 | 852 | 186.311 | 0% | 0% | 100% | 0% | 100% | 35% | 8306526 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 102 | 36470819 | 4305 | 103.32 | 4.305 | 3.6 | 3.6 | 2B | 0 | 0 | 1108 | 0 | 1128 | N/A | N/A | N/A | N/A | 37000236 | 792 | 183.9721 | 0% | 0% | 100% | 0% | 100% | 35% | 8307462 | 936 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.8333 | 127843 | 127843 | 127.843 | 127.843 | [12 empty] | 26776 | 26776 | 209.4444 | [6 empty] | 7196 | 7196 | 6.08 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:45AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 14, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:21 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:18PM , NORMAL OPERATION

## MAY 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26800 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36470819 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37000236 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8307462 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 95 | 36474990 | 4171 | 100.104 | 4.171 | 5 | 5 | 2B | 0 | 0 | 1100 | 0 | 1110 | N/A | N/A | N/A | N/A | 37000992 | 756 | 181.2515 | 0% | 0% | 100% | 0% | 100% | 45% | 8308661 | 1199 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 36478902 | 3912 | 93.888 | 3.912 | 6.3 | 6.3 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 37001668 | 676 | 172.8016 | 0% | 0% | 100% | 0% | 100% | 45% | 8309972 | 1311 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 93 | 36482633 | 3731 | 89.544 | 3.731 | 7.7 | 7.7 | 2B | 0 | 0 | 1016 | 0 | 1110 | N/A | N/A | N/A | N/A | 37002312 | 644 | 172.6079 | 0% | 0% | 100% | 0% | 100% | 45% | 8311293 | 1321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 92 | 36486467 | 3834 | 92.016 | 3.834 | 9 | 9 | 2B | 0 | 0 | 1042 | 0 | 1059 | N/A | N/A | N/A | N/A | 37002932 | 620 | 161.711 | 0% | 0% | 100% | 0% | 100% | 45% | 8312588 | 1295 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 36490495 | 4028 | 96.672 | 4.028 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1008 | N/A | N/A | N/A | N/A | 37003524 | 592 | 146.9712 | 0% | 0% | 100% | 0% | 100% | 45% | 8312995 | 407 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 | 131 | 36495595 | 5100 | 122.4 | 5.1 | 9.5 | 9.5 | 3B | 0 | 0 | 1108 | 1185 | 1109 | N/A | N/A | N/A | N/A | 37004469 | 945 | 185.2941 | 0% | 0% | 100% | 100% | 100% | 0% | 8312995 | 0 | 0.88 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 151 | 36501815 | 6220 | 149.28 | 6.22 | 9 | 9 | 3B + 1S | 0 | 1019 | 1196 | 1185 | 1199 | N/A | N/A | N/A | N/A | 37005832 | 1363 | 219.1318 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 149 | 36508267 | 6452 | 154.848 | 6.452 | 8.5 | 8.5 | 3B + 1S | 0 | 1130 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37007218 | 1386 | 214.8171 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 151 | 36514413 | 6146 | 147.504 | 6.146 | 7.7 | 7.7 | 3B + 1S | 0 | 1187 | 1176 | 1185 | 1180 | N/A | N/A | N/A | N/A | 37008572 | 1354 | 220.3059 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 154 | 36520398 | 5985 | 143.64 | 5.985 | 6.9 | 6.9 | 3B + 1S | 0 | 1190 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37009888 | 1316 | 219.883 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 36526793 | 6395 | 153.48 | 6.395 | 6.1 | 6.1 | 3B + 1S | 0 | 1141 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37011300 | 1412 | 220.7975 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 36532924 | 6131 | 147.144 | 6.131 | 5.7 | 5.7 | 3B + 1S | 0 | 1121 | 1186 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37012644 | 1344 | 219.2138 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 123 | 143 | 36538982 | 6058 | 145.392 | 6.058 | 5.1 | 5.1 | 3B + 1S | 0 | 1148 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37014036 | 1392 | 229.7788 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 145 | 36544848 | 5866 | 140.784 | 5.866 | 4.4 | 4.4 | 3B + 1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37015356 | 1320 | 225.0256 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 139 | 36550591 | 5743 | 137.832 | 5.743 | 4.3 | 4.3 | 3B + 1S | 0 | 1075 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37016658 | 1302 | 226.7108 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 140 | 36556231 | 5640 | 135.36 | 5.64 | 4.1 | 4.1 | 3B + 1S | 0 | 1076 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37017972 | 1314 | 232.9787 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 1253 | 36562063 | 5832 | 139.968 | 5.832 | 3.5 | 3.5 | 3B + 1S | 0 | 1188 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37019316 | 1344 | 230.4527 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 141 | 36568069 | 6006 | 144.144 | 6.006 | 2.8 | 2.8 | 3B + 1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37020700 | 1384 | 230.4362 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 142 | 36573786 | 5717 | 137.208 | 5.717 | 2.4 | 2.4 | 3B + 1S | 0 | 1064 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37022020 | 1320 | 230.8903 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 36579517 | 5731 | 137.544 | 5.731 | 2.1 | 2.1 | 3B + 1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37023332 | 1312 | 228.9304 | 0% | 100% | 100% | 100% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 131 | 36584805 | 5288 | 126.912 | 5.288 | 1.7 | 1.7 | 2B + 1S | 0 | 1189 | 1196 | 0 | 1198 | N/A | N/A | N/A | N/A | 37024372 | 1040 | 196.6717 | 0% | 100% | 100% | 0% | 100% | 0% | 8312995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 129 | 36590030 | 5225 | 125.4 | 5.225 | 1.3 | 1.3 | 2B + 1S | 0 | 1164 | 1186 | 0 | 1198 | N/A | N/A | N/A | N/A | 37025404 | 1032 | 197.512 | 0% | 100% | 100% | 0% | 100% | 0% | 8312995 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 106 | 36594562 | 4532 | 108.768 | 4.532 | 2.1 | 2.1 | 2B | 0 | 0 | 1196 | 0 | 1130 | N/A | N/A | N/A | N/A | 37026236 | 832 | 183.5834 | 0% | 0% | 100% | 0% | 100% | 38% | 8313739 | 744 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 99 | 36598924 | 4362 | 104.688 | 4.362 | 3.2 | 3.2 | 2B | 0 | 0 | 1107 | 0 | 1130 | N/A | N/A | N/A | N/A | 37027036 | 800 | 183.4021 | 0% | 0% | 100% | 0% | 100% | 38% | 8314866 | 1127 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 175.2917 | 128105 | 128105 | 128.105 | 128.105 | [12 empty] | 26800 | 26800 | 209.2034 | [6 empty] | 7404 | 7404 | 5.71 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:45AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:57AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:29AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:21AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 14, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12:35PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:55PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,774
GENSET 1 WARMUP EXERCISED @ 4:20 PM / STOPPED @ 4:30 PM
GENSET 2 WARMUP EXERCISED @ 4:09 PM / STOPPED @ 4:19PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:38PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:18 PM , NORMAL OPERATION
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:43PM , NORMAL OPERATION

## MAY 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27192 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36598924 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37027036 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8314866 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 97 | 36602968 | 4044 | 97.056 | 4.044 | 4.9 | 4.9 | 2B | 0 | 0 | 1088 | 0 | 1110 | N/A | N/A | N/A | N/A | 37027780 | 744 | 183.9763 | 0% | 0% | 100% | 0% | 100% | 45% | 8316298 | 1432 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 94 | 36606884 | 3916 | 93.984 | 3.916 | 6.1 | 6.1 | 2B | 0 | 0 | 1035 | 0 | 1110 | N/A | N/A | N/A | N/A | 37028474 | 694 | 177.2217 | 0% | 0% | 100% | 0% | 100% | 45% | 8317846 | 1548 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 92 | 36610729 | 3845 | 92.28 | 3.845 | 8.2 | 8.2 | 2B | 0 | 0 | 1008 | 0 | 1110 | N/A | N/A | N/A | N/A | 37029116 | 642 | 166.9701 | 0% | 0% | 100% | 0% | 100% | 45% | 8319426 | 1580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 94 | 36614477 | 3748 | 89.952 | 3.748 | 9.5 | 9.5 | 2B | 0 | 0 | 1008 | 0 | 1008 | N/A | N/A | N/A | N/A | 37029708 | 592 | 157.9509 | 0% | 0% | 100% | 0% | 100% | 45% | 8320748 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 36618450 | 3973 | 95.352 | 3.973 | 9.5 | 9.5 | 2B | 0 | 0 | 976 | 0 | 1008 | N/A | N/A | N/A | N/A | 37030244 | 536 | 134.9106 | 0% | 0% | 100% | 0% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 140 | 139 | 36623588 | 5138 | 123.312 | 5.138 | 9.5 | 9.5 | 3B | 0 | 0 | 1120 | 1185 | 1148 | N/A | N/A | N/A | N/A | 37031188 | 944 | 183.7291 | 0% | 0% | 100% | 100% | 100% | 0% | 8320748 | 0 | 1.1 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 153 | 36629743 | 6155 | 147.72 | 6.155 | 9 | 9 | 3B+1S | 0 | 1093 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37032544 | 1356 | 220.3087 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 151 | 36636090 | 6347 | 152.328 | 6.347 | 8.3 | 8.3 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37033948 | 1404 | 221.2069 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 36642537 | 6447 | 154.728 | 6.447 | 7.6 | 7.6 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37035380 | 1432 | 222.1188 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 36648536 | 5999 | 143.976 | 5.999 | 6.9 | 6.9 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37036728 | 1348 | 224.7041 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 23 | 16.1972 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 36654745 | 6209 | 149.016 | 6.209 | 6.2 | 6.2 | 3B+1S | 0 | 1071 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37038108 | 1380 | 222.258 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Normal operation schedule
59:00 | 12:00 | 27 | 19.0141 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 36660897 | 6152 | 147.648 | 6.152 | 5.6 | 5.6 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37039480 | 1372 | 223.0169 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 36666869 | 5972 | 143.328 | 5.972 | 5 | 5 | 3B+1S | 0 | 1101 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37040842 | 1362 | 228.0643 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 143 | 36672842 | 5973 | 143.352 | 5.973 | 4.5 | 4.5 | 3B+1S | 0 | 1102 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37042204 | 1362 | 228.0261 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 23 | 16.1972 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 138 | 36678770 | 5928 | 142.272 | 5.928 | 4.2 | 4.2 | 3B+1S | 0 | 1056 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37043560 | 1356 | 228.7449 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 142 | 36684363 | 5593 | 134.232 | 5.593 | 4.1 | 4.1 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37044852 | 1292 | 231.003 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 125 | 147 | 36690140 | 5777 | 138.648 | 5.777 | 3.6 | 3.6 | 3B+1S | 0 | 1172 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37046167 | 1315 | 227.6268 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 144 | 36696067 | 5927 | 142.248 | 5.927 | 3.1 | 3.1 | 3B+1S | 0 | 1063 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37047532 | 1365 | 230.302 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 36702054 | 5987 | 143.688 | 5.987 | 2.7 | 2.7 | 3B+1S | 0 | 1080 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37048892 | 1360 | 227.1588 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 135 | 36707652 | 5598 | 134.352 | 5.598 | 2.4 | 2.4 | 3B+1S | 0 | 1013 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37050180 | 1288 | 230.0822 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 141 | 36713320 | 5668 | 136.032 | 5.668 | 2.1 | 2.1 | 3B+1S | 0 | 1031 | 1145 | 1185 | 1149 | N/A | N/A | N/A | N/A | 37051460 | 1280 | 225.8292 | 0% | 100% | 100% | 100% | 100% | 0% | 8320748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 114 | 36718803 | 5483 | 131.592 | 5.483 | 1.5 | 1.5 | 2B+1S | 0 | 954 | 115 | 1185 | 1106 | N/A | N/A | N/A | N/A | 37052636 | 1176 | 214.4811 | 0% | 100% | 100% | 0% | 100% | 0% | 8320748 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  | 0
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 103 | 36723217 | 4414 | 105.936 | 4.414 | 2.4 | 2.4 | 2B | 0 | 0 | 1150 | 0 | 1139 | N/A | N/A | N/A | N/A | 37053460 | 824 | 186.6787 | 0% | 0% | 100% | 0% | 100% | 35% | 8321635 | 887 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 99 | 36727438 | 4221 | 101.304 | 4.221 | 3.6 | 3.6 | 2B | 0 | 0 | 1105 | 0 | 1110 | N/A | N/A | N/A | N/A | 37054228 | 768 | 181.9474 | 0% | 0% | 100% | 0% | 100% | 35% | 8322781 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.2083 | 128514 | 128514 | 128.514 | 128.514 | [12 empty] | 27192 | 27192 | 211.5878 | [6 empty] | 7915 | 7915 | 5.79 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:42AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
MR. PAUL CRUZ (SERVICE ENGINEER) INSTALLING THE POWER SWITCH OF SOFT STARTER (BP2) IN THE PLC
EXPONENT INSTALLING THE FLOWMETER
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11AM , NORMAL OPERATION
BP2 - STOP @ 11:45 AM DUE TO INSTALLING THE POWER SWITCH OF SOFT STARTED BP2 IN THE PLC
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 16, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:53 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:34 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:18 PM , NORMAL OPERATION
BP2 - STOPPED @ 9:09 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:14PM , NORMAL OPERATION

## MAY 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27048 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36727438 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37054228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8322781 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 36731485 | 4047 | 97.128 | 4.047 | 5 | 5 | 2B | 0 | 0 | 1096 | 0 | 1110 | N/A | N/A | N/A | N/A | 37054948 | 720 | 177.9096 | 0% | 0% | 100% | 0% | 100% | 45% | 8324018 | 1237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 36735422 | 3937 | 94.488 | 3.937 | 6.4 | 6.4 | 2B | 0 | 0 | 1045 | 0 | 1110 | N/A | N/A | N/A | N/A | 37055677 | 729 | 185.1664 | 0% | 0% | 100% | 0% | 100% | 45% | 8325448 | 1430 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 93 | 36739209 | 3787 | 90.888 | 3.787 | 8 | 8 | 2B | 0 | 0 | 1005 | 0 | 1110 | N/A | N/A | N/A | N/A | 37056298 | 621 | 163.982 | 0% | 0% | 100% | 0% | 100% | 45% | 8326874 | 1426 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 90 | 36743044 | 3835 | 92.04 | 3.835 | 9.2 | 9.2 | 2B | 0 | 0 | 983 | 0 | 1059 | N/A | N/A | N/A | N/A | 37056908 | 610 | 159.0613 | 0% | 0% | 100% | 0% | 100% | 45% | 8328080 | 1206 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 36746865 | 3821 | 91.704 | 3.821 | 9.5 | 9.5 | 2B | 0 | 0 | 975 | 0 | 1059 | N/A | N/A | N/A | N/A | 37057448 | 540 | 141.3243 | 0% | 0% | 100% | 0% | 100% | 45% | 8328302 | 222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 136 | 36751798 | 4933 | 118.392 | 4.933 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37058316 | 868 | 175.9578 | 0% | 0% | 100% | 0% | 100% | 0% | 8328302 | 0 | 0.89 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 145 | 36757780 | 5982 | 143.568 | 5.982 | 9.3 | 9.3 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37059631 | 1315 | 219.8261 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 151 | 36764013 | 6233 | 149.592 | 6.233 | 8.9 | 8.9 | 3B+1S | 0 | 1032 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37060980 | 1349 | 216.4287 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 156 | 36770456 | 6443 | 154.632 | 6.443 | 8.3 | 8.3 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37062396 | 1416 | 219.7734 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 156 | 36776799 | 6343 | 152.232 | 6.343 | 7.4 | 7.4 | 3B+1S | 0 | 1112 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37063796 | 1400 | 220.7157 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 161 | 36783279 | 6480 | 155.52 | 6.48 | 6.7 | 6.7 | 3B+1S | 0 | 1092 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37065224 | 1428 | 220.3704 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 36789579 | 6300 | 151.2 | 6.3 | 6 | 6 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37066628 | 1404 | 222.8571 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 36795658 | 6079 | 145.896 | 6.079 | 5.5 | 5.5 | 3B+1S | 0 | 1062 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37068004 | 1376 | 226.353 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 36801517 | 5859 | 140.616 | 5.859 | 4.8 | 4.8 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37069352 | 1348 | 230.0734 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 36807435 | 5918 | 142.032 | 5.918 | 4.4 | 4.4 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37070718 | 1366 | 230.8212 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 36813204 | 5769 | 138.456 | 5.769 | 3.7 | 3.7 | 3B+1S | 0 | 1014 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 37072028 | 1310 | 227.0757 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 36819066 | 5862 | 140.688 | 5.862 | 3.1 | 3.1 | 3B+1S | 0 | 1082 | 1185 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37073380 | 1352 | 230.638 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 144 | 36825001 | 5935 | 142.44 | 5.935 | 2.5 | 2.5 | 3B+1S | 0 | 1081 | 1185 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37074736 | 1356 | 228.4751 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 141 | 36830855 | 5854 | 140.496 | 5.854 | 1.9 | 1.9 | 3B+1S | 0 | 1081 | 1185 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37076080 | 1344 | 229.5866 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 132 | 36836485 | 5630 | 135.12 | 5.63 | 1.6 | 1.6 | 3B+1S | 0 | 1019 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37077372 | 1292 | 229.4849 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 134 | 137 | 36842017 | 5532 | 132.768 | 5.532 | 1.5 | 1.5 | 3B+1S | 0 | 1008 | 1185 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37078644 | 1272 | 229.9349 | 0% | 100% | 100% | 100% | 100% | 0% | 8328302 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 100 | 36847382 | 5365 | 128.76 | 5.365 | 1.3 | 1.3 | 3B+1S | 0 | 0 | 1185 | 0 | 1188 | N/A | N/A | N/A | N/A | 37079732 | 1088 | 202.7959 | 0% | 0% | 100% | 0% | 100% | 0% | 8328302 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 101 | 36851342 | 3960 | 95.04 | 3.96 | 2.1 | 2.1 | 2B | 0 | 0 | 1185 | 0 | 1188 | N/A | N/A | N/A | N/A | 37080468 | 736 | 185.8586 | 0% | 0% | 100% | 0% | 100% | 36% | 8329132 | 830 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 99 | 36855801 | 4459 | 107.016 | 4.459 | 3.4 | 3.4 | 2B | 0 | 0 | 1186 | 0 | 1189 | N/A | N/A | N/A | N/A | 37081276 | 808 | 181.2065 | 0% | 0% | 100% | 0% | 100% | 36% | 8330324 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.4167 | 128363 | 128363 | 128.363 | 128.363 | [12 empty] | 27048 | 27048 | 210.7149 | [6 empty] | 7543 | 7543 | 5.5 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:13 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @8AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 17, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:15PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:26PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:26PM , NORMAL OPERATION
BP2 - STOPPED @ 9:09 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:38 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (36%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12PM , NORMAL OPERATION

## MAY 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JR. GALINATO / A. CABREROS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26104 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36855801 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37081276 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8330324 |  | mg /l |  | Automatic - i2O | AI | JR. GALINATO / A. CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 97 | 36859841 | 4040 | 96.96 | 4.04 | 4.9 | 4.9 | 2B | 0 | 0 | 1115 | 0 | 1107 | N/A | N/A | N/A | N/A | 37082004 | 728 | 180.198 | 0% | 0% | 100% | 0% | 100% | 45% | 8331695 | 1371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 94 | 36863700 | 3859 | 92.616 | 3.859 | 6.3 | 6.3 | 2B | 0 | 0 | 1013 | 0 | 1067 | N/A | N/A | N/A | N/A | 37082688 | 684 | 177.248 | 0% | 0% | 100% | 0% | 100% | 45% | 8333118 | 1423 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 90 | 36867444 | 3744 | 89.856 | 3.744 | 8.1 | 8.1 | 2B | 0 | 0 | 1013 | 0 | 1067 | N/A | N/A | N/A | N/A | 37083308 | 620 | 165.5983 | 0% | 0% | 100% | 0% | 100% | 45% | 8334715 | 1597 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 94 | 36871022 | 3578 | 85.872 | 3.578 | 9.5 | 9.5 | 2B | 0 | 0 | 953 | 0 | 1037 | N/A | N/A | N/A | N/A | 37083884 | 576 | 160.9838 | 0% | 0% | 100% | 0% | 100% | 45% | 8336135 | 1420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 36875034 | 4012 | 96.288 | 4.012 | 9.5 | 9.5 | 2B | 0 | 0 | 923 | 0 | 1017 | N/A | N/A | N/A | N/A | 37084444 | 560 | 139.5813 | 0% | 0% | 100% | 0% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 128 | 36879561 | 4527 | 108.648 | 4.527 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37085204 | 760 | 167.8816 | 0% | 0% | 100% | 0% | 100% | 0% | 8336135 | 0 | 0.89 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 143 | 36885520 | 5959 | 143.016 | 5.959 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37086440 | 1236 | 207.4174 | 0% | 0% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 157 | 36891765 | 6245 | 149.88 | 6.245 | 9.4 | 9.4 | 3B+1S | 0 | 100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37087768 | 1328 | 212.6501 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 36897734 | 5969 | 143.256 | 5.969 | 9 | 9 | 3B+1S | 0 | 1051 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37089084 | 1316 | 220.4724 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 36904146 | 6412 | 153.888 | 6.412 | 8.3 | 8.3 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37090508 | 1424 | 222.0836 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 | 0.78 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 36910346 | 6200 | 148.8 | 6.2 | 7.6 | 7.6 | 3B+1S | 0 | 1082 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37091884 | 1376 | 221.9355 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 36916568 | 6222 | 149.328 | 6.222 | 7 | 7 | 3B+1S | 0 | 1030 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37093284 | 1400 | 225.008 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 36922530 | 5962 | 143.088 | 5.962 | 6.6 | 6.6 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37094632 | 1348 | 226.0986 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 36928508 | 5978 | 143.472 | 5.978 | 6.1 | 6.1 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37095992 | 1360 | 227.5008 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 36934436 | 5928 | 142.272 | 5.928 | 5.7 | 5.7 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37097376 | 1384 | 233.4683 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 36939877 | 5441 | 130.584 | 5.441 | 5.6 | 5.6 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37098636 | 1260 | 231.5751 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 141 | 36945486 | 5609 | 134.616 | 5.609 | 5.3 | 5.3 | 3B+1S | 0 | 1060 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37099948 | 1312 | 233.9098 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 144 | 36951258 | 5772 | 138.528 | 5.772 | 5 | 5 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37101284 | 1336 | 231.4622 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 36956995 | 5737 | 137.688 | 5.737 | 4.6 | 4.6 | 3B+1S | 0 | 1018 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37102596 | 1312 | 228.691 | 0% | 100% | 100% | 100% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 133 | 36962407 | 5412 | 129.888 | 5.412 | 3.7 | 3.7 | 2B+1S | 0 | 1140 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37103680 | 1084 | 200.2956 | 0% | 100% | 100% | 0% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 132 | 36967797 | 5390 | 129.36 | 5.39 | 3 | 3 | 2B+1S | 0 | 1111 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37104744 | 1064 | 197.4026 | 0% | 100% | 100% | 0% | 100% | 0% | 8336135 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 129 | 36973072 | 5275 | 126.6 | 5.275 | 2.4 | 2.4 | 2B+1S | 0 | 1059 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37105796 | 1052 | 199.4313 | 0% | 100% | 100% | 0% | 100% | 0% | 8336135 | 0 | 0.853 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 107 | 36977675 | 4603 | 110.472 | 4.603 | 2.9 | 2.9 | 2B | 0 | 0 | 1148 | 0 | 1128 | N/A | N/A | N/A | N/A | 37106620 | 824 | 179.0137 | 0% | 0% | 100% | 0% | 100% | 25% | 8336705 | 570 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 99 | 36981960 | 4285 | 102.84 | 4.285 | 3.7 | 3.7 | 2B | 0 | 0 | 1108 | 0 | 1086 | N/A | N/A | N/A | N/A | 37107380 | 760 | 177.3629 | 0% | 0% | 100% | 0% | 100% | 25% | 8337380 | 675 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.9583 | 126159 | 126159 | 126.159 | 126.159 | [12 empty] | 26104 | 26104 | 206.9135 | [6 empty] | 7056 | 7056 | 5.433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:46 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:16 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:36 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:40 PM , NORMAL OPERATION
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (25%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:43PM , NORMAL OPERATION

## MAY 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | A.CABREROS / R.REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | JR. GALINATO / A. CABREROS
[13 empty] | 10pm - 6am | JIMENEZ GALINATO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27056 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 36981960 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37107380 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8337380 |  | mg /l |  | Automatic - i2O | AI | JR. GALINATO / A. CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 90 | 36985929 | 3969 | 95.256 | 3.969 | 4.9 | 4.9 | 2B | 0 | 0 | 1096 | 0 | 1100 | N/A | N/A | N/A | N/A | 37108068 | 688 | 173.3434 | 0% | 0% | 100% | 0% | 100% | 38% | 8338535 | 1155 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 88 | 36989784 | 3855 | 92.52 | 3.855 | 6.2 | 6.2 | 2B | 0 | 0 | 1067 | 0 | 1066 | N/A | N/A | N/A | N/A | 37108712 | 644 | 167.0558 | 0% | 0% | 100% | 0% | 100% | 38% | 8339805 | 1270 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 90 | 36993478 | 3694 | 88.656 | 3.694 | 7.7 | 7.7 | 2B | 0 | 0 | 1016 | 0 | 1047 | N/A | N/A | N/A | N/A | 37109340 | 628 | 170.0054 | 0% | 0% | 100% | 0% | 100% | 38% | 8341130 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 91 | 36997219 | 3741 | 89.784 | 3.741 | 9.1 | 9.1 | 2B | 0 | 0 | 1017 | 0 | 1046 | N/A | N/A | N/A | N/A | 37109916 | 576 | 153.9695 | 0% | 0% | 100% | 0% | 100% | 38% | 8342396 | 1266 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 98 | 37001190 | 3971 | 95.304 | 3.971 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 0 | 1006 | N/A | N/A | N/A | N/A | 37110444 | 528 | 132.964 | 0% | 0% | 100% | 0% | 100% | 38% | 8342832 | 436 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 136 | 37006198 | 5008 | 120.192 | 5.008 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 1185 | 1137 | N/A | N/A | N/A | N/A | 37111356 | 912 | 182.1086 | 0% | 0% | 100% | 100% | 100% | 0% | 8342832 | 0 | 1.19 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 150 | 37012367 | 6169 | 148.056 | 6.169 | 8.89 | 8.89 | 3B | 0 | 1050 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37112704 | 1348 | 218.5119 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Normal operation schedule | Power Interruption | PI | A.CABREROS / R.REGENCIA
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 153 | 37018720 | 6353 | 152.472 | 6.353 | 8.4 | 8.4 | 3B+1S | 0 | 1101 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37114092 | 1388 | 218.4795 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 37025009 | 6289 | 150.936 | 6.289 | 7.8 | 7.8 | 3B+1S | 0 | 1131 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37115468 | 1376 | 218.7947 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 154 | 37030201 | 5192 | 124.608 | 5.192 | 7.3 | 7.3 | 3B+1S | 0 | 1131 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37116840 | 1372 | 264.2527 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 37035599 | 5398 | 129.552 | 5.398 | 6.8 | 6.8 | 3B+1S | 0 | 1130 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37118228 | 1388 | 257.1323 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 37040849 | 5250 | 126 | 5.25 | 6.5 | 6.5 | 3B+1S | 0 | 1130 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37119528 | 1300 | 247.619 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 37046189 | 5340 | 128.16 | 5.34 | 6.2 | 6.2 | 3B+1S | 0 | 1123 | 1198 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37120850 | 1322 | 247.5655 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 37051649 | 5460 | 131.04 | 5.46 | 6 | 6 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37122276 | 1426 | 261.1722 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 37056779 | 5130 | 123.12 | 5.13 | 5.2 | 5.2 | 3B+1S | 0 | 1072 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37123612 | 1336 | 260.4288 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 37062080 | 5301 | 127.224 | 5.301 | 4.7 | 4.7 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37124988 | 1376 | 259.5737 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 37068062 | 5982 | 143.568 | 5.982 | 3.8 | 3.8 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37126368 | 1380 | 230.6921 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 143 | 37073944 | 5882 | 141.168 | 5.882 | 3.4 | 3.4 | 3B+1S | 0 | 1042 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37127708 | 1340 | 227.8137 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 148 | 37079735 | 5791 | 138.984 | 5.791 | 3.2 | 3.2 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37129028 | 1320 | 227.9399 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 37085449 | 5714 | 137.136 | 5.714 | 2.9 | 2.9 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37130332 | 1304 | 228.2114 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 136 | 129 | 37091250 | 5801 | 139.224 | 5.801 | 2.7 | 2.7 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37131668 | 1336 | 230.3051 | 0% | 100% | 100% | 100% | 100% | 0% | 8342832 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 12.6 | 109 | 122 | 37096617 | 5367 | 128.808 | 5.367 | 1.9 | 1.9 | 2B+1S | 0 | 1131 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37132764 | 1096 | 204.2109 | 0% | 100% | 100% | 0% | 100% | 0% | 8342832 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 112 | 37101332 | 4715 | 113.16 | 4.715 | 2.7 | 2.7 | 2B | 0 | 0 | 1159 | 0 | 1148 | N/A | N/A | N/A | N/A | 37133656 | 892 | 189.1835 | 0% | 0% | 100% | 0% | 100% | 39% | 8343725 | 893 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 98 | 37105545 | 4213 | 101.112 | 4.213 | 3.8 | 3.8 | 2B | 0 | 0 | 1150 | 0 | 1148 | N/A | N/A | N/A | N/A | 37134436 | 780 | 185.1412 | 0% | 0% | 100% | 0% | 100% | 39% | 8344769 | 1044 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.5 | 123585 | 123585 | 123.585 | 123.585 | [12 empty] | 27056 | 27056 | 218.9262 | [6 empty] | 7389 | 7389 | 6.28 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (38%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:21 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:37 AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:07 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAGALLANES ON-LINE BOOSTER FAULT @ 7:14 / RESUME @ 7:22 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
KBT TRAIDING PERSONELL CONTINUE WORKING FOR BP4 ARRIVED @ 8:16 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:10 AM , NORMAL OPERATION
MR. E BELTRAN OF CENTRAL LAB. ARRIVED @ 10:01 AM FOR WATER SAMPLING RES.CL2 - 1.12mg/l
EXPONENT PERSONELL ARRIVED @ 10:02 AM FOR HMI INSTALLATION AND PANEL CUT OUT
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:15 AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 19, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
EGNR.A.TRINIDAD & TEAM MAINTENANCE CONDUCTED PREVENTIVE MAINTENANCE FOR ALL MOTORS ARRIVED @ 12:01 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:16 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:50 PM , NORMAL OPERATION
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (39%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:30PM , NORMAL OPERATION

## MAY 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27376 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37105545 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37134436 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8344769 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 93 | 37109584 | 4039 | 96.936 | 4.039 | 5.3 | 5.3 | 2B | 0 | 0 | 1128 | 0 | 1108 | N/A | N/A | N/A | N/A | 37135172 | 736 | 182.2233 | 0% | 0% | 100% | 0% | 100% | 45% | 8346017 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 89 | 37113537 | 3953 | 94.872 | 3.953 | 6.8 | 6.8 | 2B | 0 | 0 | 1069 | 0 | 1096 | N/A | N/A | N/A | N/A | 37135862 | 690 | 174.551 | 0% | 0% | 100% | 0% | 100% | 45% | 8347441 | 1424 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 96 | 37117490 | 3953 | 94.872 | 3.953 | 8.4 | 8.4 | 2B | 0 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 37136552 | 690 | 174.551 | 0% | 0% | 100% | 0% | 100% | 45% | 8348866 | 1425 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 90 | 37120829 | 3339 | 80.136 | 3.339 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 37137124 | 572 | 171.3088 | 0% | 0% | 100% | 0% | 100% | 45% | 8350014 | 1148 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 98 | 37125249 | 4420 | 106.08 | 4.42 | 9.5 | 9.5 | 2B | 0 | 0 | 1016 | 0 | 1017 | N/A | N/A | N/A | N/A | 37137740 | 616 | 139.3665 | 0% | 0% | 100% | 0% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 140 | 138 | 37130588 | 5339 | 128.136 | 5.339 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1117 | N/A | N/A | N/A | N/A | 37138740 | 1000 | 187.301 | 0% | 0% | 100% | 100% | 100% | 0% | 8350014 | 0 | 1.02 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 149 | 37136740 | 6152 | 147.648 | 6.152 | 8.9 | 8.9 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37140100 | 1360 | 221.0663 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 152 | 37143208 | 6468 | 155.232 | 6.468 | 7.9 | 7.9 | 3B+1S | 0 | 1120 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37141544 | 1444 | 223.2529 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 37149633 | 6425 | 154.2 | 6.425 | 7.2 | 7.2 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37142972 | 1428 | 222.2568 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 37155961 | 6328 | 151.872 | 6.328 | 6.3 | 6.3 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37144396 | 1424 | 225.0316 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 37162153 | 6192 | 148.608 | 6.192 | 5.6 | 5.6 | 3B+1S | 0 | 1119 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37145784 | 1388 | 224.1602 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 37168492 | 6339 | 152.136 | 6.339 | 4.8 | 4.8 | 3B+1S | 0 | 1068 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37147208 | 1424 | 224.6411 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 37174428 | 5936 | 142.464 | 5.936 | 4.4 | 4.4 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37148556 | 1348 | 227.0889 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 37180367 | 5939 | 142.536 | 5.939 | 3.9 | 3.9 | 3B+1S | 0 | 1048 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37149928 | 1372 | 231.0153 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 37185920 | 5553 | 133.272 | 5.553 | 3.7 | 3.7 | 3B+1S | 0 | 1022 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37151228 | 1300 | 234.1077 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 135 | 37191547 | 5627 | 135.048 | 5.627 | 3.6 | 3.6 | 3B+1S | 0 | 1025 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37152536 | 1308 | 232.4507 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 140 | 37197136 | 5589 | 134.136 | 5.589 | 3.2 | 3.2 | 3B+1S | 0 | 1020 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37153840 | 1304 | 233.3154 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 144 | 37203112 | 5976 | 143.424 | 5.976 | 2.9 | 2.9 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37155220 | 1380 | 230.9237 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 136 | 37208817 | 5705 | 136.92 | 5.705 | 2.5 | 2.5 | 3B+1S | 0 | 1083 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37156540 | 1320 | 231.376 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 133 | 37214459 | 5642 | 135.408 | 5.642 | 2.2 | 2.2 | 3B+1S | 0 | 1036 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37157852 | 1312 | 232.5417 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 135 | 132 | 37220012 | 5553 | 133.272 | 5.553 | 2.1 | 2.1 | 2B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37159146 | 1294 | 233.0272 | 0% | 100% | 100% | 100% | 100% | 0% | 8350014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 123 | 37225145 | 5133 | 123.192 | 5.133 | 1.5 | 1.5 | 2B+1S | 0 | 1058 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37160212 | 1066 | 207.6758 | 0% | 100% | 100% | 0% | 100% | 0% | 8350014 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 101 | 37229540 | 4395 | 105.48 | 4.395 | 2.4 | 2.4 | 2B | 0 | 0 | 1136 | 0 | 1138 | N/A | N/A | N/A | N/A | 37161028 | 816 | 185.6655 | 0% | 0% | 100% | 0% | 100% | 35% | 8350907 | 893 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 99 | 37233672 | 4132 | 99.168 | 4.132 | 3.5 | 3.5 | 2B | 0 | 0 | 1118 | 0 | 1108 | N/A | N/A | N/A | N/A | 37161812 | 784 | 189.7386 | 0% | 0% | 100% | 0% | 100% | 35% | 8351869 | 962 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.5833 | 128127 | 128127 | 128.127 | 128.127 | [12 empty] | 27376 | 27376 | 213.663 | [6 empty] | 7100 | 7100 | 5.92 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:52 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 5:27 AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10AM , NORMAL OPERATION
EXPONENT PERSONELL ARRIVED @ 10:02 AM FOR HMI INSTALLATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 20, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
MAGALLANES IN-LINE BOOSTER FAULT @1:39 PM/ RESUME @5:35 PM. DUE TO OVER/UNDER VOLTAGE
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:20 PM , NORMAL OPERATION
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:23PM , NORMAL OPERATION

## MAY 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26688 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37233672 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37161812 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8351869 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 95 | 37237549 | 3877 | 93.048 | 3.877 | 5.1 | 5.1 | 2B | 0 | 0 | 1046 | 0 | 1108 | N/A | N/A | N/A | N/A | 37162456 | 644 | 166.1078 | 0% | 0% | 100% | 0% | 100% | 45% | 8353299 | 1430 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 93 | 37241220 | 3671 | 88.104 | 3.671 | 6.3 | 6.3 | 2B | 0 | 0 | 1046 | 0 | 1108 | N/A | N/A | N/A | N/A | 37163104 | 648 | 176.5187 | 0% | 0% | 100% | 0% | 100% | 45% | 8354839 | 1540 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 90 | 37244767 | 3547 | 85.128 | 3.547 | 8.2 | 8.2 | 2B | 0 | 0 | 1025 | 0 | 1108 | N/A | N/A | N/A | N/A | 37163726 | 622 | 175.3595 | 0% | 0% | 100% | 0% | 100% | 45% | 8356361 | 1522 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 93 | 37248499 | 3732 | 89.568 | 3.732 | 9.5 | 9.5 | 2B | 0 | 0 | 955 | 0 | 986 | N/A | N/A | N/A | N/A | 37164264 | 538 | 144.1586 | 0% | 0% | 100% | 0% | 100% | 45% | 8357777 | 1416 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 104 | 37252503 | 4004 | 96.096 | 4.004 | 9.5 | 9.5 | 2B | 0 | 0 | 1006 | 0 | 1016 | N/A | N/A | N/A | N/A | 37164788 | 524 | 130.8691 | 0% | 0% | 100% | 0% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 120 | 37257388 | 4885 | 117.24 | 4.885 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37165548 | 760 | 155.5783 | 0% | 0% | 100% | 0% | 100% | 0% | 8357777 | 0 | 1.08 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 136 | 37263744 | 6356 | 152.544 | 6.356 | 9.2 | 9.2 | 3B+1S | 0 | 1121 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37167068 | 1520 | 239.1441 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 37270012 | 6268 | 150.432 | 6.268 | 8.2 | 8.2 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37168468 | 1400 | 223.3567 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 37276441 | 6429 | 154.296 | 6.429 | 7.2 | 7.2 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37169908 | 1440 | 223.9851 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 37282952 | 6511 | 156.264 | 6.511 | 6.5 | 6.5 | 3B+1S | 0 | 1130 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37171368 | 1460 | 224.2359 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 37289216 | 6264 | 150.336 | 6.264 | 5.6 | 5.6 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37172788 | 1420 | 226.6922 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 150 | 37295345 | 6129 | 147.096 | 6.129 | 5 | 5 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37174172 | 1384 | 225.8117 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 37301423 | 6078 | 145.872 | 6.078 | 4.5 | 4.5 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37175548 | 1376 | 226.3903 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 37307290 | 5867 | 140.808 | 5.867 | 4.1 | 4.1 | 3B+1S | 0 | 1040 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37176892 | 1344 | 229.0779 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 37312964 | 5674 | 136.176 | 5.674 | 3.9 | 3.9 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37178196 | 1304 | 229.8202 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 37318565 | 5601 | 134.424 | 5.601 | 3.7 | 3.7 | 3B+1S | 0 | 1055 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37179510 | 1314 | 234.601 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 141 | 37324276 | 5711 | 137.064 | 5.711 | 3.4 | 3.4 | 3B+1S | 0 | 1150 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37180820 | 1310 | 229.3819 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 143 | 37330133 | 5857 | 140.568 | 5.857 | 3.1 | 3.1 | 3B+1S | 0 | 1045 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37182164 | 1344 | 229.469 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 142 | 37335885 | 5752 | 138.048 | 5.752 | 2.8 | 2.8 | 3B+1S | 0 | 1047 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37183496 | 1332 | 231.5716 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 138 | 37341565 | 5680 | 136.32 | 5.68 | 1.6 | 1.6 | 3B+1S | 0 | 1021 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37184684 | 1188 | 209.1549 | 0% | 100% | 100% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 18 | A ONG | 16.1 | 124 | 137 | 37346914 | 5349 | 128.376 | 5.349 | 1.4 | 1.4 | 2B+1S | 0 | 980 | 0 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37185792 | 1108 | 207.1415 | 0% | 100% | 0% | 100% | 100% | 0% | 8357777 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 68 | 47.8873 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 12.6 | 120 | 135 | 37351823 | 4909 | 117.816 | 4.909 | 1.3 | 1.3 | 2B | 0 | 0 | 0 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37186836 | 1044 | 212.6706 | 0% | 0% | 0% | 100% | 100% | 0% | 8357777 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 103 | 37356399 | 4576 | 109.824 | 4.576 | 2.2 | 2.2 | 2B | 0 | 0 | 0 | 1185 | 1117 | N/A | N/A | N/A | N/A | 37187708 | 872 | 190.5594 | 0% | 0% | 0% | 100% | 100% | 38% | 8358547 | 770 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 98 | 37360635 | 4236 | 101.664 | 4.236 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1056 | N/A | N/A | N/A | N/A | 37188500 | 792 | 186.9688 | 0% | 0% | 0% | 100% | 100% | 38% | 8359687 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.6667 | 126963 | 126963 | 126.963 | 126.963 | [12 empty] | 26688 | 26688 | 210.203 | [6 empty] | 7818 | 7818 | 6.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30AM , NORMAL OPERATION
EXPONENT PERSONELL ARRIVED @ 10:02 AM FOR HMI INSTALLATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:12 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:30 PM , NORMAL OPERATION
BP1 TRIP @ 8:05 PM DUE TO DEFECTIVE VFD, FAULT SINE FILTERCAP + LINK AB LOST
SP2 - STOPPED @ 9:20 PM DUE TO LOW WATER LEVEL OF RESERVIOUR
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:36PM , NORMAL OPERATION

## MAY 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | JIMENEZ GALINATO
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25296 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37360635 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37188500 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8359687 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 97 | 37364581 | 3946 | 94.704 | 3.946 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 1005 | N/A | N/A | N/A | N/A | 37189244 | 744 | 188.5454 | 0% | 0% | 0% | 100% | 100% | 50% | 8361173 | 1486 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 94 | 37368365 | 3784 | 90.816 | 3.784 | 6.6 | 6.6 | 2B | 0 | 0 | 0 | 1185 | 1005 | N/A | N/A | N/A | N/A | 37189944 | 700 | 184.9894 | 0% | 0% | 0% | 100% | 100% | 50% | 8362787 | 1614 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 37372134 | 3769 | 90.456 | 3.769 | 8.2 | 8.2 | 2B | 0 | 0 | 0 | 1185 | 965 | N/A | N/A | N/A | N/A | 37190652 | 708 | 187.8482 | 0% | 0% | 0% | 100% | 100% | 50% | 8364312 | 1525 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 98 | 37375916 | 3782 | 90.768 | 3.782 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 965 | N/A | N/A | N/A | N/A | 37191340 | 688 | 181.9143 | 0% | 0% | 0% | 100% | 100% | 50% | 8365557 | 1245 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 106 | 37380108 | 4192 | 100.608 | 4.192 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 965 | N/A | N/A | N/A | N/A | 37192036 | 696 | 166.0305 | 0% | 0% | 0% | 100% | 100% | 50% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 136 | 37385076 | 4968 | 119.232 | 4.968 | 9.5 | 9.5 | 2B+1S | 0 | 0 | 0 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37192932 | 896 | 180.3543 | 0% | 0% | 0% | 100% | 100% | 0% | 8365557 | 0 | 1.03 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 16.7 | 117 | 141 | 37390843 | 5767 | 138.408 | 5.767 | 8.5 | 8.5 | 2B+1S | 0 | 1159 | 0 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37194052 | 1120 | 194.2084 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 17.3 | 118 | 139 | 37396863 | 6020 | 144.48 | 6.02 | 7.5 | 7.5 | 2B+1S | 0 | 1159 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37195208 | 1156 | 192.0266 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 72 | 50.7042 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 52.1242 | 19 | A ONG | 18.4 | 118 | 140 | 37402592 | 5729 | 137.496 | 5.729 | 6.5 | 6.5 | 2B+1S | 0 | 1159 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37196312 | 1104 | 192.7038 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 17.7 | 118 | 135 | 37408620 | 6028 | 144.672 | 6.028 | 5.5 | 5.5 | 2B+1S | 0 | 1159 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37197488 | 1176 | 195.0896 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 74 | 52.1127 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.7 | 119 | 136 | 37414088 | 5468 | 131.232 | 5.468 | 4.4 | 4.4 | 2B+1S | 0 | 1159 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37198548 | 1060 | 193.8552 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 71 | 50 | Automatic - Pressure Setting | 48.5915 | 50 | 51.42 | 19 | A ONG | 17.3 | 116 | 134 | 37419814 | 5726 | 137.424 | 5.726 | 3.5 | 3.5 | 2B+1S | 0 | 1047 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37199624 | 1076 | 187.9148 | 0% | 100% | 0% | 100% | 100% | 0% | 8365557 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 132 | 137 | 37425384 | 5570 | 133.68 | 5.57 | 2.7 | 2.7 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37200772 | 1148 | 206.1041 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 133 | 136 | 37430914 | 5530 | 132.72 | 5.53 | 2.3 | 2.3 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37202028 | 1256 | 227.1248 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 138 | 37436901 | 5987 | 143.688 | 5.987 | 2 | 2 | 3B+1S | 0 | 1096 | 1199 | 1185 | 1199 | N/A | N/A | N/A | N/A | 37203412 | 1384 | 231.1675 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 37442644 | 5743 | 137.832 | 5.743 | 1.7 | 1.7 | 3B+1S | 0 | 1001 | 1199 | 1185 | 1199 | N/A | N/A | N/A | N/A | 37204748 | 1336 | 232.631 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 137 | 130 | 37447993 | 5349 | 128.376 | 5.349 | 1.5 | 1.5 | 3B+1S | 0 | 995 | 1199 | 1185 | 1199 | N/A | N/A | N/A | N/A | 37206065 | 1317 | 246.2142 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 138 | 131 | 37453816 | 5823 | 139.752 | 5.823 | 1.4 | 1.4 | 3B+1S | 0 | 997 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37207384 | 1319 | 226.5155 | 0% | 100% | 100% | 100% | 100% | 0% | 8365557 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 131 | 135 | 37459316 | 5500 | 132 | 5.5 | 1.3 | 1.3 | 3B+1S | 0 | 0 | 1169 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37208632 | 1248 | 226.9091 | 0% | 0% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 135 | 137 | 37464700 | 5384 | 129.216 | 5.384 | 1.3 | 1.3 | 3B | 0 | 0 | 1179 | 1185 | 1179 | N/A | N/A | N/A | N/A | 37209824 | 1192 | 221.3967 | 0% | 0% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 132 | 127 | 37470250 | 5550 | 133.2 | 5.55 | 1.3 | 1.3 | 3B | 0 | 0 | 1159 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37211044 | 1220 | 219.8198 | 0% | 0% | 100% | 100% | 100% | 0% | 8365557 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 130 | 37475602 | 5352 | 128.448 | 5.352 | 1.3 | 1.3 | 3B | 0 | 0 | 1119 | 1185 | 1110 | N/A | N/A | N/A | N/A | 37212236 | 1192 | 222.7205 | 0% | 0% | 100% | 100% | 100% | 0% | 8365557 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 101 | 37479966 | 4364 | 104.736 | 4.364 | 2 | 2 | 2B | 0 | 0 | 1119 | 0 | 1149 | N/A | N/A | N/A | N/A | 37213032 | 796 | 182.4015 | 0% | 0% | 100% | 0% | 100% | 38% | 8366340 | 783 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 97 | 37484143 | 4177 | 100.248 | 4.177 | 3.3 | 3.3 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 37213796 | 764 | 182.9064 | 0% | 0% | 100% | 0% | 100% | 38% | 8367478 | 1138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.4167 | 123508 | 123508 | 123.508 | 123.508 | [12 empty] | 25296 | 25296 | 204.8126 | [6 empty] | 7791 | 7791 | 6.17 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:52AM , NORMAL OPERATION
EXPONENT PERSONELL ARRIVED @ 8:40 AM FOR HMI INSTALLATION
EGNR.A.TRINIDAD & TEAM MAINTENANCE TO REPAIR THE DEFECTIVE VFD OF BP1 @ 9:07 AM
CONDUCTED SITE INSPECTION SIR JOSEPHUS DELA ROSA AND SIR MICHAEL BULIGAN AND ERNESTO PASCUA ARRIVED @ 9:22AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:33AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
BP1 RESUMED THE OPERATION STARTED AT 12:40PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:50 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:15 PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL OF RESERVIOUR
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:26 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
Mr. Wilfredo De Jesus of ABB arrived @ 10:10 PM and conduct Inspection on BP1 VFD by Uploading and Monitoring Critical Parameters

## MAY 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27592 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37484143 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37213796 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8367478 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 98 | 37488091 | 3948 | 94.752 | 3.948 | 4.9 | 4.9 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 37214528 | 732 | 185.4103 | 0% | 0% | 100% | 0% | 100% | 48% | 8368825 | 1347 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 37492045 | 3954 | 94.896 | 3.954 | 6.3 | 6.3 | 2B | 0 | 0 | 1059 | 0 | 1109 | N/A | N/A | N/A | N/A | 37215248 | 720 | 182.0941 | 0% | 0% | 100% | 0% | 100% | 48% | 8370213 | 1388 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 95 | 37495823 | 3778 | 90.672 | 3.778 | 8 | 8 | 2B | 0 | 0 | 1019 | 0 | 1109 | N/A | N/A | N/A | N/A | 37215920 | 672 | 177.8719 | 0% | 0% | 100% | 0% | 100% | 48% | 8371764 | 1551 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 100 | 37499703 | 3880 | 93.12 | 3.88 | 9.5 | 9.5 | 2B | 0 | 0 | 940 | 0 | 1009 | N/A | N/A | N/A | N/A | 37216532 | 612 | 157.732 | 0% | 0% | 100% | 0% | 100% | 48% | 8373389 | 1625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 104 | 37503592 | 3889 | 93.336 | 3.889 | 9.5 | 9.5 | 2B | 0 | 0 | 1009 | 0 | 1029 | N/A | N/A | N/A | N/A | 37217064 | 532 | 136.7961 | 0% | 0% | 100% | 0% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 138 | 37508513 | 4921 | 118.104 | 4.921 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1195 | N/A | N/A | N/A | N/A | 37217924 | 860 | 174.7612 | 0% | 0% | 100% | 0% | 100% | 0% | 8373389 | 0 | 1.02 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 142 | 37514823 | 6310 | 151.44 | 6.31 | 8.7 | 8.7 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37219340 | 1416 | 224.4057 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 37521134 | 6311 | 151.464 | 6.311 | 7.5 | 7.5 | 3B+1S | 0 | 1149 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37220756 | 1416 | 224.3701 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 37527629 | 6495 | 155.88 | 6.495 | 6.3 | 6.3 | 3B+1S | 0 | 1149 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37222220 | 1464 | 225.4042 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 37534199 | 6570 | 157.68 | 6.57 | 5.8 | 5.8 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37223646 | 1426 | 217.0472 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 37540372 | 6173 | 148.152 | 6.173 | 5.1 | 5.1 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37225088 | 1442 | 233.5979 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 37546651 | 6279 | 150.696 | 6.279 | 4.4 | 4.4 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37226500 | 1412 | 224.8766 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 37552535 | 5884 | 141.216 | 5.884 | 3.9 | 3.9 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37227828 | 1328 | 225.6968 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 140 | 37558630 | 6095 | 146.28 | 6.095 | 3.1 | 3.1 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37229256 | 1428 | 234.2904 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 142 | 37564497 | 5867 | 140.808 | 5.867 | 2.5 | 2.5 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37230644 | 1388 | 236.5775 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 37570256 | 5759 | 138.216 | 5.759 | 2.1 | 2.1 | 3B+1S | 0 | 1039 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37231972 | 1328 | 230.5956 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 141 | 37575982 | 5726 | 137.424 | 5.726 | 1.8 | 1.8 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37233304 | 1332 | 232.6231 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 146 | 37581908 | 5926 | 142.224 | 5.926 | 1.3 | 1.3 | 3B+1S | 0 | 969 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37234680 | 1376 | 232.1971 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 149 | 37587496 | 5588 | 134.112 | 5.588 | 1.3 | 1.3 | 3B+1S | 0 | 969 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37235968 | 1288 | 230.4939 | 0% | 100% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 2 | 1.4085 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 149 | 37593150 | 5654 | 135.696 | 5.654 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37237228 | 1260 | 222.8511 | 0% | 0% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 136 | 143 | 37598838 | 5688 | 136.512 | 5.688 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1195 | N/A | N/A | N/A | N/A | 37238476 | 1248 | 219.4093 | 0% | 0% | 100% | 100% | 100% | 0% | 8373389 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 132 | 140 | 37604417 | 5579 | 133.896 | 5.579 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37239724 | 1248 | 223.696 | 0% | 0% | 100% | 100% | 100% | 0% | 8373389 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 104 | 37609063 | 4646 | 111.504 | 4.646 | 2 | 2 | 2B | 0 | 0 | 1139 | 0 | 1139 | N/A | N/A | N/A | N/A | 37240636 | 912 | 196.2979 | 0% | 0% | 100% | 0% | 100% | 35% | 8374121 | 732 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 99 | 37613208 | 4145 | 99.48 | 4.145 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1039 | N/A | N/A | N/A | N/A | 37241388 | 752 | 181.4234 | 0% | 0% | 0% | 100% | 100% | 35% | 8375180 | 1059 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 131.2083 | 129065 | 129065 | 129.065 | 129.065 | [12 empty] | 27592 | 27592 | 213.7838 | [6 empty] | 7702 | 7702 | 5.43 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (48%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:30 PM , NORMAL OPERATION
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,761
GENSET 2 WARMUP EXERCISED @ 4:16 PM / STOPPED @ 4:26PM
GENSET 1 WARMUP EXERCISED @ 4:27 PM / STOPPED @ 4:37 PM
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 7:01 PM DUE TO low water level
PREVENTIVE MAINTENANCE OF ALL UNITS sp2,bp1,bp2bp3
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30 PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
BP1 - STOPPED @ 11:20 PM
BP2 - STARTED @ 11:21 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:35 PM , NORMAL OPERATION

## MAY 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27104 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37613208 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37241388 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8375180 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 97 | 37617102 | 3894 | 93.456 | 3.894 | 4.7 | 4.7 | 2B | 0 | 0 | 1039 | 1185 | 0 | N/A | N/A | N/A | N/A | 37242124 | 736 | 189.0087 | 0% | 0% | 100% | 0% | 100% | 50% | 8376516 | 1336 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 37621146 | 4044 | 97.056 | 4.044 | 6.3 | 6.3 | 2B | 0 | 0 | 1009 | 1185 | 0 | N/A | N/A | N/A | N/A | 37242860 | 736 | 181.998 | 0% | 0% | 100% | 0% | 100% | 50% | 8377813 | 1297 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 91 | 37624842 | 3696 | 88.704 | 3.696 | 7.6 | 7.6 | 2B | 0 | 0 | 1019 | 0 | 1109 | N/A | N/A | N/A | N/A | 37243508 | 648 | 175.3247 | 0% | 0% | 100% | 0% | 100% | 50% | 8379300 | 1487 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 90 | 37628620 | 3778 | 90.672 | 3.778 | 9 | 9 | 2B | 0 | 0 | 1019 | 0 | 1109 | N/A | N/A | N/A | N/A | 37244160 | 652 | 172.5781 | 0% | 0% | 100% | 0% | 100% | 50% | 8381242 | 1942 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 101 | 37632626 | 4006 | 96.144 | 4.006 | 9.5 | 9.5 | 2B | 0 | 0 | 979 | 0 | 999 | N/A | N/A | N/A | N/A | 37244804 | 644 | 160.7589 | 0% | 0% | 100% | 0% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 102 | 130 | 37637263 | 4637 | 111.288 | 4.637 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37245580 | 776 | 167.3496 | 0% | 0% | 100% | 0% | 100% | 0% | 8381242 | 0 | 1.02 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 127 | 139 | 37643508 | 6245 | 149.88 | 6.245 | 9.1 | 9.1 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37246950 | 1370 | 219.3755 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 37649754 | 6246 | 149.904 | 6.246 | 8.6 | 8.6 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37248320 | 1370 | 219.3404 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 37656113 | 6359 | 152.616 | 6.359 | 7.9 | 7.9 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37249728 | 1408 | 221.4185 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 37662472 | 6359 | 152.616 | 6.359 | 7.2 | 7.2 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37251136 | 1408 | 221.4185 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 | 1.07 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 37668963 | 6491 | 155.784 | 6.491 | 6.4 | 6.4 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37252580 | 1444 | 222.4619 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 152 | 37675312 | 6349 | 152.376 | 6.349 | 5.2 | 5.2 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37253988 | 1408 | 221.7672 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 37681816 | 6504 | 156.096 | 6.504 | 4.7 | 4.7 | 3B+1S | 0 | 1100 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37255436 | 1448 | 222.6322 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 37687684 | 5868 | 140.832 | 5.868 | 4 | 4 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37256808 | 1372 | 233.8105 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 137 | 37693843 | 6159 | 147.816 | 6.159 | 3.2 | 3.2 | 3B+1S | 0 | 1109 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37258224 | 1416 | 229.9075 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 135 | 37699695 | 5852 | 140.448 | 5.852 | 2.5 | 2.5 | 3B+1S | 0 | 1109 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37259556 | 1332 | 227.6145 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 77 | 54.2254 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 126 | 133 | 37705406 | 5711 | 137.064 | 5.711 | 1.8 | 1.8 | 3B+1S | 0 | 1109 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37260864 | 1308 | 229.0317 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 77 | 54.2254 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 128 | 135 | 37711482 | 6076 | 145.824 | 6.076 | 1.3 | 1.3 | 3B+1S | 0 | 1109 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37262252 | 1388 | 228.4398 | 0% | 100% | 100% | 100% | 100% | 0% | 8381242 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 138 | 149 | 37716981 | 5499 | 131.976 | 5.499 | 1.3 | 1.3 | 3B | 0 | 0 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37263436 | 1184 | 215.3119 | 0% | 0% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 136 | 146 | 37722580 | 5599 | 134.376 | 5.599 | 1.3 | 1.3 | 3B | 0 | 0 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37264636 | 1200 | 214.324 | 0% | 0% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 137 | 147 | 37728179 | 5599 | 134.376 | 5.599 | 1.3 | 1.3 | 3B | 0 | 0 | 1169 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37265828 | 1192 | 212.8952 | 0% | 0% | 100% | 100% | 100% | 0% | 8381242 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 68 | 47.8873 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 12.6 | 119 | 123 | 37733039 | 4860 | 116.64 | 4.86 | 1.3 | 1.3 | 2B | 0 | 0 | 1169 | 0 | 1159 | N/A | N/A | N/A | N/A | 37266716 | 888 | 182.716 | 0% | 0% | 100% | 0% | 100% | 0% | 8381242 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 139 | 37737691 | 4652 | 111.648 | 4.652 | 1.8 | 1.8 | 2B | 0 | 0 | 1169 | 0 | 1159 | N/A | N/A | N/A | N/A | 37267596 | 880 | 189.166 | 0% | 0% | 100% | 0% | 100% | 35% | 8382030 | 788 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 71 | 50 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | 135 | 142 | 37742245 | 4554 | 109.296 | 4.554 | 2.7 | 2.7 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37268492 | 896 | 196.7501 | 0% | 0% | 100% | 0% | 100% | 35% | 8382953 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 131.7083 | 129037 | 129037 | 129.037 | 129.037 | [12 empty] | 27104 | 27104 | 210.0483 | [6 empty] | 7773 | 7773 | 5.89 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
BP3 - STOPPED @ 12:45 AM
BP1 - STARTED @ 12:46 AM
BP2 - STOPPED @ 2:01 AM
BP3 - STARTED @ 2:02 AM
XCV1 CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9AM , NORMAL OPERATION
Exponent install the level sensor of fuel storage tank
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 24, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:43PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:23PM , NORMAL OPERATION
XCV4 - OPENED (10%) @ 5:40PM DUE TO LOW WATER LEVEL
XCV4 CLOSED @ 5:50 PM
SP2 - STOPPED @ 6:01 PM DUE TO low water level
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:35PM , NORMAL OPERATION
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
MAINTENANCE GROUP REPAIR THE LEAK OF ALL UNITS BP1/BP2/BP3 ARRIVED @ 10:50PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:30PM , NORMAL OPERATION

## MAY 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | ALEX CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28530 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37742245 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37268492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8382953 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 6 | 4.2254 | 72 | 50.7042 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 130 | 138 | 37746753 | 4508 | 108.192 | 4.508 | 3.6 | 3.6 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37269400 | 908 | 201.4197 | 0% | 0% | 100% | 0% | 100% | 50% | 8383838 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 7 | 4.9296 | 74 | 52.1127 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 134 | 139 | 37750963 | 4210 | 101.04 | 4.21 | 4.8 | 4.8 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37270272 | 872 | 207.1259 | 0% | 0% | 100% | 0% | 100% | 50% | 8384926 | 1088 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 137 | 37755522 | 4559 | 109.416 | 4.559 | 6 | 6 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37271148 | 876 | 192.1474 | 0% | 0% | 100% | 0% | 100% | 50% | 8386084 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 139 | 147 | 37759613 | 4091 | 98.184 | 4.091 | 7.1 | 7.1 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37272044 | 896 | 219.0174 | 0% | 0% | 100% | 0% | 100% | 50% | 8387135 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A.ONG | 13.1 | 152 | 150 | 37764153 | 4540 | 108.96 | 4.54 | 8.3 | 8.3 | 2B | 0 | 0 | 1189 | 0 | 1179 | N/A | N/A | N/A | N/A | 37272948 | 904 | 199.1189 | 0% | 0% | 100% | 0% | 100% | 50% | 8388338 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 130 | 37768884 | 4731 | 113.544 | 4.731 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37273828 | 880 | 186.0072 | 0% | 0% | 100% | 0% | 100% | 50% | 8389033 | 695 | 1.08 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 0 | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 37774914 | 6030 | 144.72 | 6.03 | 9.5 | 9.5 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37275116 | 1288 | 213.5987 | 0% | 0% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 1 | 0.70423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 152 | 37780944 | 6030 | 144.72 | 6.03 | 9.3 | 9.3 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37276404 | 1288 | 213.5987 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 150 | 37787290 | 6346 | 152.304 | 6.346 | 8.8 | 8.8 | 3B+1S | 0 | 1008 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37277796 | 1392 | 219.3508 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 37793421 | 6131 | 147.144 | 6.131 | 8.3 | 8.3 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37279148 | 1352 | 220.5187 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 | 0.89 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 37799827 | 6406 | 153.744 | 6.406 | 7.5 | 7.5 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37280564 | 1416 | 221.0428 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 37806098 | 6271 | 150.504 | 6.271 | 6.9 | 6.9 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37281956 | 1392 | 221.9742 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 149 | 37812154 | 6056 | 145.344 | 6.056 | 6.5 | 6.5 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37283308 | 1352 | 223.2497 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 37818328 | 6174 | 148.176 | 6.174 | 5.9 | 5.9 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37284708 | 1400 | 226.7574 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 139 | 37824070 | 5742 | 137.808 | 5.742 | 5.4 | 5.4 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37286056 | 1348 | 234.7614 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 134 | 37830056 | 5986 | 143.664 | 5.986 | 4.8 | 4.8 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37287432 | 1376 | 229.8697 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 142 | 37836067 | 6011 | 144.264 | 6.011 | 4 | 4 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37288828 | 1396 | 232.2409 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 37842059 | 5992 | 143.808 | 5.992 | 3.3 | 3.3 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37290208 | 1380 | 230.3071 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 | 0.69 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 37847851 | 5792 | 139.008 | 5.792 | 2.8 | 2.8 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37291548 | 1340 | 231.3536 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 143 | 37853537 | 5686 | 136.464 | 5.686 | 2.7 | 2.7 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37292860 | 1312 | 230.7422 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 139 | 149 | 37859199 | 5662 | 135.888 | 5.662 | 2.5 | 2.5 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37294180 | 1320 | 233.1332 | 0% | 100% | 100% | 100% | 100% | 0% | 8389033 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 129 | 37864426 | 5227 | 125.448 | 5.227 | 2.2 | 2.2 | 2B+1S | 0 | 1059 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37295244 | 1064 | 203.5584 | 0% | 100% | 100% | 0% | 100% | 0% | 8389033 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 126 | 37869180 | 4754 | 114.096 | 4.754 | 3.1 | 3.1 | 2B | 0 | 0 | 1189 | 0 | 1178 | N/A | N/A | N/A | N/A | 37296136 | 892 | 187.6315 | 0% | 0% | 100% | 0% | 100% | 40% | 8390029 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 129 | 37873935 | 4755 | 114.12 | 4.755 | 4.3 | 4.3 | 2B | 0 | 0 | 1189 | 0 | 1178 | N/A | N/A | N/A | N/A | 37297022 | 886 | 186.3302 | 0% | 0% | 100% | 0% | 100% | 40% | 8391035 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 140.75 | 131690 | 131690 | 131.69 | 131.69 | [12 empty] | 28530 | 28530 | 216.6452 | [6 empty] | 8082 | 8082 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2:20AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
XCV1 CLOSED @ 5:40 AM,WATER ELEVATION (9.5M)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:25AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:02AM , NORMAL OPERATION
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:33 AM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:40AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 25, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:25 PM , NORMAL OPERATION
CITI PEST ARRIVED VILLAMOR PS FOR PEST CONTROL
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Joyjl Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING

## MAY 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | GLITTERS. SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28474 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 37873935 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37297022 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8391035 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 126 | 37878097 | 4162 | 99.888 | 4.162 | 5.3 | 5.3 | 2B | 0 | 0 | 1189 | 0 | 1178 | N/A | N/A | N/A | N/A | 37297912 | 890 | 213.8395 | 0% | 0% | 100% | 0% | 100% | 50% | 8392057 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEX CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 119 | 37882529 | 4432 | 106.368 | 4.432 | 6.5 | 6.5 | 2B | 0 | 0 | 1189 | 0 | 1178 | N/A | N/A | N/A | N/A | 37298780 | 868 | 195.8484 | 0% | 0% | 100% | 0% | 100% | 50% | 8393367 | 1310 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | REIVIN M. MALLARI
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 123 | 37886962 | 4433 | 106.392 | 4.433 | 7.8 | 7.8 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 37299648 | 868 | 195.8042 | 0% | 0% | 100% | 0% | 100% | 50% | 8394676 | 1309 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | RANDY REGENCIA
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 136 | 120 | 37890413 | 3451 | 82.824 | 3.451 | 9.5 | 9.5 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 37300288 | 640 | 185.4535 | 0% | 0% | 100% | 0% | 100% | 50% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | GLITTERS. SY
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 122 | 37895051 | 4638 | 111.312 | 4.638 | 9.5 | 9.5 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 37301176 | 888 | 191.4618 | 0% | 0% | 100% | 0% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | FIDEL A. RAMOS
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 136 | 37899763 | 4712 | 113.088 | 4.712 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37301884 | 708 | 150.2547 | 0% | 0% | 100% | 0% | 100% | 0% | 8394676 | 0 | 0.91 | Normal operation schedule | Error - General | E | JIMENEZ GALINATO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 148 | 37905931 | 6168 | 148.032 | 6.168 | 8.9 | 8.9 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37303240 | 1356 | 219.8444 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 37912202 | 6271 | 150.504 | 6.271 | 8.2 | 8.2 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37304634 | 1394 | 222.2931 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 37918474 | 6272 | 150.528 | 6.272 | 7.6 | 7.6 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37306028 | 1394 | 222.2577 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 139 | 37924873 | 6399 | 153.576 | 6.399 | 6.89 | 6.89 | 3B+1S | 0 | 1139 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37307460 | 1432 | 223.785 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 | 1.07 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 37931206 | 6333 | 151.992 | 6.333 | 5.9 | 5.9 | 3B+1S | 0 | 1159 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37308894 | 1434 | 226.433 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 37937539 | 6333 | 151.992 | 6.333 | 5 | 5 | 3B+1S | 0 | 1129 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37310328 | 1434 | 226.433 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 139 | 37943619 | 6080 | 145.92 | 6.08 | 4.2 | 4.2 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37311716 | 1388 | 228.2895 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 37949515 | 5896 | 141.504 | 5.896 | 3.4 | 3.4 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37313092 | 1376 | 233.3786 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 37955466 | 5951 | 142.824 | 5.951 | 2.8 | 2.8 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37314468 | 1376 | 231.2216 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 37961442 | 5976 | 143.424 | 5.976 | 2.3 | 2.3 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37315844 | 1376 | 230.2544 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 37967412 | 5970 | 143.28 | 5.97 | 1.7 | 1.7 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37317220 | 1376 | 230.4858 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 148 | 37973231 | 5819 | 139.656 | 5.819 | 1.3 | 1.3 | 3B+1S | 0 | 1019 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37318540 | 1320 | 226.8431 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 149 | 37979015 | 5784 | 138.816 | 5.784 | 1.3 | 1.3 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37319884 | 1344 | 232.3651 | 0% | 100% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 137 | 37984692 | 5677 | 136.248 | 5.677 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37321140 | 1256 | 221.2436 | 0% | 0% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 135 | 37990370 | 5678 | 136.272 | 5.678 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37322396 | 1256 | 221.2046 | 0% | 0% | 100% | 100% | 100% | 0% | 8394676 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 134 | 37996048 | 5678 | 136.272 | 5.678 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37323652 | 1256 | 221.2046 | 0% | 0% | 100% | 100% | 100% | 0% | 8394676 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 137 | 38000758 | 4710 | 113.04 | 4.71 | 2.3 | 2.3 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37324612 | 960 | 203.8217 | 0% | 0% | 100% | 0% | 100% | 40% | 8396808 | 2132 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 142 | 38005209 | 4451 | 106.824 | 4.451 | 3.2 | 3.2 | 2B | 0 | 0 | 1159 | 0 | 1159 | N/A | N/A | N/A | N/A | 37325496 | 884 | 198.6071 | 0% | 0% | 100% | 0% | 100% | 40% | 8397858 | 1050 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 137.875 | 131274 | 131274 | 131.274 | 131.274 | [12 empty] | 28474 | 28474 | 216.9051 | [6 empty] | 6823 | 6823 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6AM , NORMAL OPERATION
MAINTENANCE TEAM CEMENT THE FLOORING OF CHEMICAL & HAZARD WAREHOUSE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 26, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:25 PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:30PM , NORMAL OPERATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (40%) @ 10:01 PM FOR REFILLING

## MAY 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28116 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38005209 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37325496 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8397858 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 125 | 38009390 | 4181 | 100.344 | 4.181 | 4.5 | 4.5 | 2B | 0 | 0 | 1159 | 0 | 1139 | N/A | N/A | N/A | N/A | 37326312 | 816 | 195.1686 | 0% | 0% | 100% | 0% | 100% | 50% | 8399077 | 1219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 123 | 38013488 | 4098 | 98.352 | 4.098 | 6.3 | 6.3 | 2B | 0 | 0 | 1159 | 0 | 1139 | N/A | N/A | N/A | N/A | 37327093 | 781 | 190.5808 | 0% | 0% | 100% | 0% | 100% | 50% | 8400491 | 1414 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 137 | 124 | 38017589 | 4101 | 98.424 | 4.101 | 7.8 | 7.8 | 2B | 0 | 0 | 1159 | 0 | 1139 | N/A | N/A | N/A | N/A | 37327870 | 777 | 189.466 | 0% | 0% | 100% | 0% | 100% | 50% | 8401951 | 1460 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 139 | 120 | 38021685 | 4096 | 98.304 | 4.096 | 9 | 9 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 37328648 | 778 | 189.9414 | 0% | 0% | 100% | 0% | 100% | 50% | 8403420 | 1469 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 121 | 38025912 | 4227 | 101.448 | 4.227 | 9.5 | 9.5 | 2B | 0 | 0 | 1099 | 0 | 1099 | N/A | N/A | N/A | N/A | 37329340 | 692 | 163.7095 | 0% | 0% | 100% | 0% | 100% | 50% | 8403927 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 133 | 38030972 | 5060 | 121.44 | 5.06 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37330228 | 888 | 175.4941 | 0% | 0% | 100% | 0% | 100% | 0% | 8403927 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 153 | 38037086 | 6114 | 146.736 | 6.114 | 9.2 | 9.2 | 3B+1S | 0 | 1000 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37331556 | 1328 | 217.2064 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 38043336 | 6250 | 150 | 6.25 | 8.7 | 8.7 | 3B+1S | 0 | 1049 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37332928 | 1372 | 219.52 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 142 | 38049740 | 6404 | 153.696 | 6.404 | 7.9 | 7.9 | 3B+1S | 0 | 1079 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37334376 | 1448 | 226.1087 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 38055868 | 6128 | 147.072 | 6.128 | 7.3 | 7.3 | 3B+1S | 0 | 1119 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37335748 | 1372 | 223.8903 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 | 0.72 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 140 | 38062111 | 6243 | 149.832 | 6.243 | 6.4 | 6.4 | 3B+1S | 0 | 1119 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37337152 | 1404 | 224.8919 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 38068354 | 6243 | 149.832 | 6.243 | 5.8 | 5.8 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37338556 | 1404 | 224.8919 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 38074520 | 6166 | 147.984 | 6.166 | 5.1 | 5.1 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37339948 | 1392 | 225.7541 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 138 | 38080530 | 6010 | 144.24 | 6.01 | 4.4 | 4.4 | 3B+1S | 0 | 1169 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37341332 | 1384 | 230.2829 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 38086605 | 6075 | 145.8 | 6.075 | 3.4 | 3.4 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37342728 | 1396 | 229.7942 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 38092680 | 6075 | 145.8 | 6.075 | 3 | 3 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37344124 | 1396 | 229.7942 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 38098591 | 5911 | 141.864 | 5.911 | 2.3 | 2.3 | 3B+1S | 0 | 1109 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37345492 | 1368 | 231.4329 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 145 | 38104452 | 5861 | 140.664 | 5.861 | 1.9 | 1.9 | 3B+1S | 0 | 1059 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37346810 | 1318 | 224.8763 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 149 | 38110314 | 5862 | 140.688 | 5.862 | 1.4 | 1.4 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37348188 | 1378 | 235.0734 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 140 | 38116039 | 5725 | 137.4 | 5.725 | 1.4 | 1.4 | 3B+1S | 0 | 999 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37349510 | 1322 | 230.917 | 0% | 100% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 138 | 143 | 38121764 | 5725 | 137.4 | 5.725 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37350832 | 1322 | 230.917 | 0% | 0% | 100% | 100% | 100% | 0% | 8403927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 131 | 140 | 38127380 | 5616 | 134.784 | 5.616 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37352020 | 1188 | 211.5385 | 0% | 0% | 100% | 100% | 100% | 0% | 8403927 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 102 | 38132018 | 4638 | 111.312 | 4.638 | 2 | 2 | 2B | 0 | 0 | 1139 | 0 | 1149 | N/A | N/A | N/A | N/A | 37352860 | 840 | 181.1125 | 0% | 0% | 100% | 0% | 100% | 38% | 8404606 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 97 | 38136220 | 4202 | 100.848 | 4.202 | 3.2 | 3.2 | 2B | 0 | 0 | 1019 | 0 | 1119 | N/A | N/A | N/A | N/A | 37353612 | 752 | 178.9624 | 0% | 0% | 100% | 0% | 100% | 38% | 8405327 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 134 | 131011 | 131011 | 131.011 | 131.011 | [12 empty] | 28116 | 28116 | 214.6079 | [6 empty] | 7469 | 7469 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:20AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 27, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2AM , NORMAL OPERATION
Engr. Michael joseph buligan & accelence (IEMS) arrived 2pm
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6AM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
EXPONENT PERSONELL ARRIVED @ 7PM FOR TESTING HMI INSTALLATION
SP2 - STOPPED @ 8:30 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (38%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:25 PM
PUMP1 AND PUMP2 TRIP @ 7:59PM TO 11:20PM. ALARM: ALL PUMPS ARE NOT HEALTHY

## MAY 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26824 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38136220 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37353612 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8405327 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 99 | 38140219 | 3999 | 95.976 | 3.999 | 4.7 | 4.7 | 2B | 0 | 0 | 1109 | 0 | 1119 | N/A | N/A | N/A | N/A | 37354352 | 740 | 185.0463 | 0% | 0% | 100% | 0% | 100% | 50% | 8406800 | 1473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 95 | 38144095 | 3876 | 93.024 | 3.876 | 6.1 | 6.1 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37355044 | 692 | 178.5346 | 0% | 0% | 100% | 0% | 100% | 50% | 8408365 | 1565 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 93 | 38147915 | 3820 | 91.68 | 3.82 | 7.9 | 7.9 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37355716 | 672 | 175.9162 | 0% | 0% | 100% | 0% | 100% | 50% | 8409925 | 1560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 99 | 38151719 | 3804 | 91.296 | 3.804 | 9.5 | 9.5 | 2B | 0 | 0 | 1039 | 0 | 1049 | N/A | N/A | N/A | N/A | 37356356 | 640 | 168.244 | 0% | 0% | 100% | 0% | 100% | 50% | 8411611 | 1686 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 101 | 38155959 | 4240 | 101.76 | 4.24 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 1009 | N/A | N/A | N/A | N/A | 37356992 | 636 | 150 | 0% | 0% | 100% | 0% | 100% | 50% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 139 | 38160679 | 4720 | 113.28 | 4.72 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37357844 | 852 | 180.5085 | 0% | 0% | 100% | 0% | 100% | 0% | 8411611 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 143 | 38166621 | 5942 | 142.608 | 5.942 | 9.2 | 9.2 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37359172 | 1328 | 223.4938 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 38173041 | 6420 | 154.08 | 6.42 | 8.6 | 8.6 | 3B+1S | 0 | 1069 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37360600 | 1428 | 222.4299 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 38179462 | 6421 | 154.104 | 6.421 | 7.6 | 7.6 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37362028 | 1428 | 222.3953 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 143 | 38185634 | 6172 | 148.128 | 6.172 | 6.9 | 6.9 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37363412 | 1384 | 224.2385 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 | 0.87 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 38191808 | 6174 | 148.176 | 6.174 | 6.3 | 6.3 | 3B+1S | 0 | 1089 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37364788 | 1376 | 222.8701 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 38198025 | 6217 | 149.208 | 6.217 | 5.7 | 5.7 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37366180 | 1392 | 223.9022 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 38203954 | 5929 | 142.296 | 5.929 | 5.2 | 5.2 | 3B+1S | 0 | 1029 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37367532 | 1352 | 228.0317 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 38209747 | 5793 | 139.032 | 5.793 | 4.8 | 4.8 | 3B+1S | 0 | 139 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37368872 | 1340 | 231.3137 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 38215541 | 5794 | 139.056 | 5.794 | 4.4 | 4.4 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37370212 | 1340 | 231.2737 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 38221114 | 5573 | 133.752 | 5.573 | 4.3 | 4.3 | 3B+1S | 0 | 1099 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37371512 | 1300 | 233.2675 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 38226788 | 5674 | 136.176 | 5.674 | 4 | 4 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37372836 | 1324 | 233.3451 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 38232475 | 5687 | 136.488 | 5.687 | 3.4 | 3.4 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37374164 | 1328 | 233.515 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 38237957 | 5482 | 131.568 | 5.482 | 3.6 | 3.6 | 3B+1S | 0 | 1009 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37375452 | 1288 | 234.9507 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 143 | 38243639 | 5682 | 136.368 | 5.682 | 3.5 | 3.5 | 3B+1S | 0 | 979 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37376796 | 1344 | 236.5364 | 0% | 100% | 100% | 100% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 38248752 | 5113 | 122.712 | 5.113 | 3 | 3 | 2B+1S | 0 | 1059 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37377828 | 1032 | 201.8385 | 0% | 100% | 100% | 0% | 100% | 0% | 8411611 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 122 | 38254085 | 5333 | 127.992 | 5.333 | 2.4 | 2.4 | 2B+1S | 0 | 1039 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37378876 | 1048 | 196.5123 | 0% | 100% | 100% | 0% | 100% | 0% | 8411611 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 99 | 38258471 | 4386 | 105.264 | 4.386 | 3 | 3 | 2B | 0 | 0 | 1139 | 0 | 1139 | N/A | N/A | N/A | N/A | 37379704 | 828 | 188.7825 | 0% | 0% | 100% | 0% | 100% | 30% | 8412173 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 97 | 38262662 | 4191 | 100.584 | 4.191 | 4.1 | 4.1 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37380436 | 732 | 174.66 | 0% | 0% | 100% | 0% | 100% | 30% | 8413057 | 884 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.6667 | 126442 | 126442 | 126.442 | 126.442 | [12 empty] | 26824 | 26824 | 212.1447 | [6 empty] | 7730 | 7730 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
EXPONENT PERSONNEL WENT TO MAGALLANES IN LINE AND CHECK UP THE PROBLEM
MAGALLANES IN LINE BACK TO NORMAL OPERATION @ 12:35AM
XCV1 CLOSED @ 3:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:25AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30PM , NORMAL OPERATION
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12PM , NORMAL OPERATION

## MAY 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25920 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38262662 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37380436 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8413057 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 96 | 38266482 | 3820 | 91.68 | 3.82 | 5.5 | 5.5 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37381108 | 672 | 175.9162 | 0% | 0% | 100% | 0% | 100% | 40% | 8414475 | 1418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 94 | 38270266 | 3784 | 90.816 | 3.784 | 7 | 7 | 2B | 0 | 0 | 1019 | 0 | 1049 | N/A | N/A | N/A | N/A | 37381776 | 668 | 176.5328 | 0% | 0% | 100% | 0% | 100% | 40% | 8415990 | 1515 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 91 | 38273822 | 3556 | 85.344 | 3.556 | 8.3 | 8.3 | 2B | 0 | 0 | 1019 | 0 | 1049 | N/A | N/A | N/A | N/A | 37382386 | 610 | 171.5411 | 0% | 0% | 100% | 0% | 100% | 40% | 8417282 | 1292 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 93 | 38277586 | 3764 | 90.336 | 3.764 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 999 | N/A | N/A | N/A | N/A | 37382956 | 570 | 151.4346 | 0% | 0% | 100% | 0% | 100% | 40% | 8418331 | 1049 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 38281483 | 3897 | 93.528 | 3.897 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 999 | N/A | N/A | N/A | N/A | 37383460 | 504 | 129.3303 | 0% | 0% | 100% | 0% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 107 | 38286406 | 4923 | 118.152 | 4.923 | 9.5 | 9.5 | 2B | 0 | 0 | 1179 | 0 | 1189 | N/A | N/A | N/A | N/A | 37384312 | 852 | 173.0652 | 0% | 0% | 100% | 0% | 100% | 0% | 8418331 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 138 | 38292563 | 6157 | 147.768 | 6.157 | 8.8 | 8.8 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37385704 | 1392 | 226.0841 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 137 | 38298982 | 6419 | 154.056 | 6.419 | 7.8 | 7.8 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37387148 | 1444 | 224.9572 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 135 | 38305514 | 6532 | 156.768 | 6.532 | 6.7 | 6.7 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37388620 | 1472 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 135 | 38311805 | 6291 | 150.984 | 6.291 | 5.8 | 5.8 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37390048 | 1428 | 226.9909 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 137 | 38318471 | 6666 | 159.984 | 6.666 | 4.9 | 4.9 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37391564 | 1516 | 227.4227 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 136 | 38324447 | 5976 | 143.424 | 5.976 | 3.9 | 3.9 | 3B+1S | 0 | 1179 | 1179 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37392924 | 1360 | 227.577 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 110 | 38330548 | 6101 | 146.424 | 6.101 | 2.9 | 2.9 | 3B+1S | 0 | 1179 | 1159 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37394332 | 1408 | 230.7818 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 38336249 | 5701 | 136.824 | 5.701 | 2.3 | 2.3 | 3B+1S | 0 | 1059 | 1159 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37395612 | 1280 | 224.522 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 108 | 38341970 | 5721 | 137.304 | 5.721 | 1.8 | 1.8 | 3B+1S | 0 | 1059 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37396848 | 1236 | 216.0461 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 115 | 38347671 | 5701 | 136.824 | 5.701 | 1.4 | 1.4 | 3B+1S | 0 | 1059 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37398076 | 1228 | 215.4008 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 118 | 38353270 | 5599 | 134.376 | 5.599 | 1.3 | 1.3 | 3B+1S | 0 | 1059 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37399308 | 1232 | 220.0393 | 0% | 100% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 123 | 38358694 | 5424 | 130.176 | 5.424 | 1.3 | 1.3 | 3B | 0 | 0 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37400452 | 1144 | 210.9145 | 0% | 0% | 100% | 100% | 100% | 0% | 8418331 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 121 | 38363852 | 5158 | 123.792 | 5.158 | 1.3 | 1.3 | 3B | 0 | 0 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37401522 | 1070 | 207.4447 | 0% | 0% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 119 | 38369081 | 5229 | 125.496 | 5.229 | 1.3 | 1.3 | 3B | 0 | 0 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37402660 | 1138 | 217.6324 | 0% | 0% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 124 | 38374513 | 5432 | 130.368 | 5.432 | 1.3 | 1.3 | 3B | 0 | 0 | 1129 | 1185 | 1119 | N/A | N/A | N/A | N/A | 37403812 | 1152 | 212.0766 | 0% | 0% | 100% | 100% | 100% | 0% | 8418331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 100 | 38379104 | 4591 | 110.184 | 4.591 | 1.3 | 1.3 | 2B | 0 | 0 | 1179 | 0 | 1159 | N/A | N/A | N/A | N/A | 37404676 | 864 | 188.1943 | 0% | 0% | 100% | 0% | 100% | 0% | 8418331 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 104 | 38383608 | 4504 | 108.096 | 4.504 | 2.1 | 2.1 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 37405548 | 872 | 193.6057 | 0% | 0% | 100% | 0% | 100% | 35% | 8419205 | 874 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 99 | 38387963 | 4355 | 104.52 | 4.355 | 3.9 | 3.9 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 37406356 | 808 | 185.5339 | 0% | 0% | 100% | 0% | 100% | 35% | 8420684 | 1479 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 115.5417 | 125301 | 125301 | 125.301 | 125.301 | [12 empty] | 25920 | 25920 | 206.8619 | [6 empty] | 7627 | 7627 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 9:29AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:26AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:28PM , NORMAL OPERATION
SP2 - STOPPED @ 5:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:35PM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
EXPONENT PERSONELL ARRIVED @ 9:22 PM FOR CONTINUES HMI INSTALLATION
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (30%) @ 10:01 PM FOR REFILLING
BP1 - STOPPED @ 10:15 PM DUE TO POWER CYCLE FROM PLC TO VFD
BP2 - STARTED @ 10:16 PM
BP3 - STOPPED @ 10:25 PM DUE TO POWER CYCLE FROM PLC TO VFD
BP1 - RESTARTED @ 10:26 PM
BP2 - STOPPED @ 10:35 PM
BP3 - RESTARTED @ 10:36 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:12PM , NORMAL OPERATION

## MAY 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27464 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38387963 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37406356 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8420684 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 96 | 38391791 | 3828 | 91.872 | 3.828 | 5 | 5 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37407076 | 720 | 188.0878 | 0% | 0% | 100% | 0% | 100% | 45% | 8422159 | 1475 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 98 | 38395497 | 3706 | 88.944 | 3.706 | 6.4 | 6.4 | 2B | 0 | 0 | 1019 | 0 | 1109 | N/A | N/A | N/A | N/A | 37407740 | 664 | 179.1689 | 0% | 0% | 100% | 0% | 100% | 45% | 8423655 | 1496 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 38399222 | 3725 | 89.4 | 3.725 | 8 | 8 | 2B | 0 | 0 | 1009 | 0 | 1049 | N/A | N/A | N/A | N/A | 37408388 | 648 | 173.9597 | 0% | 0% | 100% | 0% | 100% | 45% | 8425109 | 1454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 91 | 38402868 | 3646 | 87.504 | 3.646 | 9.5 | 9.5 | 2B | 0 | 0 | 929 | 0 | 969 | N/A | N/A | N/A | N/A | 37408980 | 592 | 162.3697 | 0% | 0% | 100% | 0% | 100% | 45% | 8426582 | 1473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 105 | 38406709 | 3841 | 92.184 | 3.841 | 9.5 | 9.5 | 2B | 0 | 0 | 1009 | 0 | 1039 | N/A | N/A | N/A | N/A | 37409484 | 504 | 131.2158 | 0% | 0% | 100% | 0% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 130 | 38411712 | 5003 | 120.072 | 5.003 | 9.5 | 9.5 | 2B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37410356 | 872 | 174.2954 | 0% | 0% | 100% | 0% | 100% | 0% | 8426582 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 38417750 | 6038 | 144.912 | 6.038 | 8.6 | 8.6 | 3B+1S | 0 | 1149 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37411772 | 1416 | 234.5147 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 38423986 | 6236 | 149.664 | 6.236 | 7.8 | 7.8 | 3B+1S | 0 | 1097 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37413172 | 1400 | 224.5029 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 156 | 38430303 | 6317 | 151.608 | 6.317 | 7.1 | 7.1 | 3B+1S | 0 | 1128 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37414588 | 1416 | 224.157 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 152 | 38436846 | 6543 | 157.032 | 6.543 | 6.1 | 6.1 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37416060 | 1472 | 224.9733 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 | 1.01 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 38442896 | 6050 | 145.2 | 6.05 | 5.3 | 5.3 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37417444 | 1384 | 228.7603 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 38449188 | 6292 | 151.008 | 6.292 | 4.6 | 4.6 | 3B+1S | 0 | 1127 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37418876 | 1432 | 227.5906 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 147 | 38455306 | 6118 | 146.832 | 6.118 | 3.3 | 3.3 | 3B+1S | 0 | 1086 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37420268 | 1392 | 227.5253 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 38461316 | 6010 | 144.24 | 6.01 | 3 | 3 | 3B+1S | 0 | 1033 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37421644 | 1376 | 228.9517 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 38467326 | 6010 | 144.24 | 6.01 | 2.6 | 2.6 | 3B+1S | 0 | 1035 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37423020 | 1376 | 228.9517 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 38472994 | 5668 | 136.032 | 5.668 | 2.4 | 2.4 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37424332 | 1312 | 231.4749 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 38478818 | 5824 | 139.776 | 5.824 | 2 | 2 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37425668 | 1336 | 229.3956 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 38484552 | 5734 | 137.616 | 5.734 | 1.7 | 1.7 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37427008 | 1340 | 233.6938 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 143 | 38490455 | 5903 | 141.672 | 5.903 | 1.4 | 1.4 | 3B+1S | 0 | 1037 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37428372 | 1364 | 231.0689 | 0% | 100% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 138 | 38495934 | 5479 | 131.496 | 5.479 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37429600 | 1228 | 224.1285 | 0% | 0% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 138 | 136 | 38501611 | 5677 | 136.248 | 5.677 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37430868 | 1268 | 223.3574 | 0% | 0% | 100% | 100% | 100% | 0% | 8426582 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 135 | 137 | 38507413 | 5802 | 139.248 | 5.802 | 1.3 | 1.3 | 3B | 0 | 0 | 1195 | 0 | 1198 | N/A | N/A | N/A | N/A | 37432124 | 1256 | 216.4771 | 0% | 0% | 100% | 0% | 100% | 0% | 8426582 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 108 | 38511941 | 4528 | 108.672 | 4.528 | 2.2 | 2.2 | 2B | 0 | 0 | 1139 | 0 | 1139 | N/A | N/A | N/A | N/A | 37433008 | 884 | 195.2297 | 0% | 0% | 100% | 0% | 100% | 35% | 8427426 | 844 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 105 | 38516268 | 4327 | 103.848 | 4.327 | 3.2 | 3.2 | 2B | 0 | 0 | 1139 | 0 | 1139 | N/A | N/A | N/A | N/A | 37433820 | 812 | 187.6589 | 0% | 0% | 100% | 0% | 100% | 35% | 8428390 | 964 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 130.0417 | 128305 | 128305 | 128.305 | 128.305 | [12 empty] | 27464 | 27464 | 214.0525 | [6 empty] | 7706 | 7706 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:39AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 7:30AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:48AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 30, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 3:30PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6PM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING

## MAY 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27480 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38516268 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37433820 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8428390 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 38520443 | 4175 | 100.2 | 4.175 | 4.5 | 4.5 | 2B | 0 | 0 | 1099 | 0 | 1109 | N/A | N/A | N/A | N/A | 37434612 | 792 | 189.7006 | 0% | 0% | 100% | 0% | 100% | 45% | 8429519 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 96 | 38524505 | 4062 | 97.488 | 4.062 | 5.7 | 5.7 | 2B | 0 | 0 | 1099 | 0 | 1109 | N/A | N/A | N/A | N/A | 37435340 | 728 | 179.2221 | 0% | 0% | 100% | 0% | 100% | 45% | 8430710 | 1191 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 93 | 38528537 | 4032 | 96.768 | 4.032 | 7.1 | 7.1 | 2B | 0 | 0 | 1049 | 0 | 1049 | N/A | N/A | N/A | N/A | 37436060 | 720 | 178.5714 | 0% | 0% | 100% | 0% | 100% | 45% | 8431885 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 90 | 38532397 | 3860 | 92.64 | 3.86 | 8.4 | 8.4 | 2B | 0 | 0 | 1049 | 0 | 1049 | N/A | N/A | N/A | N/A | 37436742 | 682 | 176.6839 | 0% | 0% | 100% | 0% | 100% | 45% | 8433079 | 1194 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 38536390 | 3993 | 95.832 | 3.993 | 9.5 | 9.5 | 2B | 0 | 0 | 1019 | 0 | 1049 | N/A | N/A | N/A | N/A | 37437340 | 598 | 149.7621 | 0% | 0% | 100% | 0% | 100% | 45% | 8434263 | 1184 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 38541134 | 4744 | 113.856 | 4.744 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37438192 | 852 | 179.5953 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 | 0.91 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 149 | 38547087 | 5953 | 142.872 | 5.953 | 9.5 | 9.5 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37439456 | 1264 | 212.3299 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 150 | 38553344 | 6257 | 150.168 | 6.257 | 9 | 9 | 3B+1S | 0 | 1010 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37440824 | 1368 | 218.6351 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 153 | 38559622 | 6278 | 150.672 | 6.278 | 8.6 | 8.6 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37442192 | 1368 | 217.9038 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 38566090 | 6468 | 155.232 | 6.468 | 7.9 | 7.9 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37443620 | 1428 | 220.7792 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 38572341 | 6251 | 150.024 | 6.251 | 7.2 | 7.2 | 3B+1S | 0 | 1070 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37444992 | 1372 | 219.4849 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 38578515 | 6174 | 148.176 | 6.174 | 6.6 | 6.6 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37446360 | 1368 | 221.5743 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 38584842 | 6327 | 151.848 | 6.327 | 5.9 | 5.9 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37447804 | 1444 | 228.2282 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 149 | 38590878 | 6036 | 144.864 | 6.036 | 5.1 | 5.1 | 3B+1S | 0 | 1090 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37449176 | 1372 | 227.3028 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 38596814 | 5936 | 142.464 | 5.936 | 4.2 | 4.2 | 3B+1S | 0 | 1099 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37450580 | 1404 | 236.5229 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 38602910 | 6096 | 146.304 | 6.096 | 3.5 | 3.5 | 3B+1S | 0 | 1099 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37451840 | 1260 | 206.6929 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 38608889 | 5979 | 143.496 | 5.979 | 2.9 | 2.9 | 3B+1S | 0 | 1099 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37453328 | 1488 | 248.871 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 137 | 38614628 | 5739 | 137.736 | 5.739 | 2.2 | 2.2 | 3B+1S | 0 | 1099 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37454652 | 1324 | 230.7022 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 135 | 38620566 | 5938 | 142.512 | 5.938 | 1.7 | 1.7 | 3B+1S | 0 | 1079 | 1179 | 1185 | 1179 | N/A | N/A | N/A | N/A | 37456036 | 1384 | 233.0751 | 0% | 100% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 38626428 | 5862 | 140.688 | 5.862 | 1.3 | 1.3 | 3B | 0 | 0 | 1179 | 1185 | 1179 | N/A | N/A | N/A | N/A | 37457396 | 1360 | 232.0027 | 0% | 0% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 140 | 148 | 38632069 | 5641 | 135.384 | 5.641 | 1.3 | 1.3 | 3B | 0 | 0 | 1179 | 1185 | 1179 | N/A | N/A | N/A | N/A | 37458628 | 1232 | 218.401 | 0% | 0% | 100% | 100% | 100% | 0% | 8434263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 135 | 38637138 | 5069 | 121.656 | 5.069 | 1.3 | 1.3 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37459600 | 972 | 191.7538 | 0% | 0% | 100% | 0% | 100% | 0% | 8434263 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 106 | 38641887 | 4749 | 113.976 | 4.749 | 2.4 | 2.4 | 2B | 0 | 0 | 1139 | 0 | 1109 | N/A | N/A | N/A | N/A | 37460520 | 920 | 193.725 | 0% | 0% | 100% | 0% | 100% | 40% | 8435331 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 99 | 38646186 | 4299 | 103.176 | 4.299 | 3.5 | 3.5 | 2B | 0 | 0 | 1139 | 0 | 1109 | N/A | N/A | N/A | N/A | 37461300 | 780 | 181.4375 | 0% | 0% | 100% | 0% | 100% | 40% | 8436570 | 1239 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.875 | 129918 | 129918 | 129.918 | 129.918 | [12 empty] | 27480 | 27480 | 211.518 | [6 empty] | 8180 | 8180 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:40AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 7:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:15AM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 30, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
Mr . Mark Froilan Pavia AND TEAM OF EXPONENT ARRIVE @ MAY 30, 2015 @ 11AM TO INSTALL DATA CABINET AND FINISH @ 12:30PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 1:45PM , NORMAL OPERATION
POWER FLUCTUATION 3:28PM BP3 FAULT
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:26PM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:18PM , NORMAL OPERATION
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 11:19PM , NORMAL OPERATION

## MAY 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEX CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | RANDY REGENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-05-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38646186 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 37461300 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8436570 |  | mg /l |  | Automatic - i2O | AI | ALEX CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 98 | 38650361 | 4175 | 100.2 | 4.175 | 4.9 | 4.9 | 2B | 0 | 0 | 1089 | 0 | 1109 | N/A | N/A | N/A | N/A | 37462068 | 768 | 183.9521 | 0% | 0% | 100% | 0% | 100% | 50% | 8437634 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | REIVIN M. MALLARI
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 38654297 | 3936 | 94.464 | 3.936 | 6 | 6 | 2B | 0 | 0 | 1039 | 0 | 1109 | N/A | N/A | N/A | N/A | 37462780 | 712 | 180.8943 | 0% | 0% | 100% | 0% | 100% | 50% | 8438849 | 1215 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | RANDY REGENCIA
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 93 | 38658181 | 3884 | 93.216 | 3.884 | 7.5 | 7.5 | 2B | 0 | 0 | 1039 | 0 | 1049 | N/A | N/A | N/A | N/A | 37463452 | 672 | 173.0175 | 0% | 0% | 100% | 0% | 100% | 50% | 8440125 | 1276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | GLITTERS. SY
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 92 | 38661973 | 3792 | 91.008 | 3.792 | 8.9 | 8.9 | 2B | 0 | 0 | 1039 | 0 | 1049 | N/A | N/A | N/A | N/A | 37464068 | 616 | 162.4473 | 0% | 0% | 100% | 0% | 100% | 50% | 8441494 | 1369 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 96 | 38665842 | 3869 | 92.856 | 3.869 | 9.5 | 9.5 | 2B | 0 | 0 | 949 | 0 | 949 | N/A | N/A | N/A | N/A | 37464660 | 592 | 153.0111 | 0% | 0% | 100% | 0% | 100% | 50% | 8442195 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | JIMENEZ GALINATO
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 38670433 | 4591 | 110.184 | 4.591 | 9.5 | 9.5 | 2B | 0 | 0 | 1159 | 0 | 1159 | N/A | N/A | N/A | N/A | 37465436 | 776 | 169.0264 | 0% | 0% | 100% | 0% | 100% | 0% | 8442195 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 139 | 38676087 | 5654 | 135.696 | 5.654 | 9.5 | 9.5 | 3B | 0 | 0 | 1159 | 1185 | 1159 | N/A | N/A | N/A | N/A | 37466608 | 1172 | 207.2869 | 0% | 0% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 151 | 143 | 38682111 | 6024 | 144.576 | 6.024 | 9.3 | 9.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37467844 | 1236 | 205.1793 | 0% | 0% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 153 | 38688506 | 6395 | 153.48 | 6.395 | 9.2 | 9.2 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37469240 | 1396 | 218.2955 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 152 | 38697452 | 8946 | 214.704 | 8.946 | 9.4 | 9.4 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37470604 | 1364 | 152.4704 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 38701102 | 3650 | 87.6 | 3.65 | 7.8 | 7.8 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37472012 | 1408 | 385.7534 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 150 | 38707395 | 6293 | 151.032 | 6.293 | 7.2 | 7.2 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37473420 | 1408 | 223.7407 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 38713422 | 6027 | 144.648 | 6.027 | 6.7 | 6.7 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37474764 | 1344 | 222.9965 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 38719597 | 6175 | 148.2 | 6.175 | 6.1 | 6.1 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37476172 | 1408 | 228.0162 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 38725362 | 5765 | 138.36 | 5.765 | 5.6 | 5.6 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37477500 | 1328 | 230.3556 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 38731414 | 6052 | 145.248 | 6.052 | 5 | 5 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37478896 | 1396 | 230.6675 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 38737201 | 5787 | 138.888 | 5.787 | 4.5 | 4.5 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37480244 | 1348 | 232.9359 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 155 | 38743204 | 6003 | 144.072 | 6.003 | 4 | 4 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37481628 | 1384 | 230.5514 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 38748802 | 5598 | 134.352 | 5.598 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37482920 | 1292 | 230.7967 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 132 | 38754370 | 5568 | 133.632 | 5.568 | 3.7 | 3.7 | 3B+1S | 0 | 954 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37484208 | 1288 | 231.3218 | 0% | 100% | 100% | 100% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 38759830 | 5460 | 131.04 | 5.46 | 3.2 | 3.2 | 2B+1S | 0 | 1067 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37485276 | 1068 | 195.6044 | 0% | 100% | 100% | 0% | 100% | 0% | 8442195 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 125 | 38765277 | 5447 | 130.728 | 5.447 | 2.6 | 2.6 | 2B+1S | 0 | 1047 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37486344 | 1068 | 196.0712 | 0% | 100% | 100% | 0% | 100% | 0% | 8442195 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 105 | 38769754 | 4477 | 107.448 | 4.477 | 3.5 | 3.5 | 2B | 0 | 0 | 1129 | 0 | 1109 | N/A | N/A | N/A | N/A | 37487140 | 796 | 177.7976 | 0% | 0% | 100% | 0% | 100% | 35% | 8443101 | 906 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 96 | 38774027 | 4273 | 102.552 | 4.273 | 4.7 | 4.7 | 2B | 0 | 0 | 1049 | 0 | 1109 | N/A | N/A | N/A | N/A | 37487900 | 760 | 177.861 | 0% | 0% | 100% | 0% | 100% | 35% | 8444122 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.5 | 127841 | 127841 | 127.841 | 127.841 | [12 empty] | 26600 | 26600 | 208.071 | [6 empty] | 7552 | 7552 |  |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:23AM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 8:30AM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 12PM , NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 1, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 81psi @ 12:01 pm as per request of Engr. Frances Morla (SPM-South)
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 2PM , NORMAL OPERATION
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 4:30PM , NORMAL OPERATION
Target Discharge Pressure set to 78psi @ 5:01 pm as per request of Engr. Frances Morla (SPM-South)
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,748
GENSET 2 WARMUP EXERCISED @ 5:16 PM / STOPPED @ 5:26PM
GENSET 1 WARMUP EXERCISED @ 5:27 PM / STOPPED @ 5:37 PM
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:22PM , NORMAL OPERATION
Target Discharge Pressure set to 76psi @ 7:01 pm as per request of Engr. Frances Morla (SPM-South)
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
Target Discharge Pressure set to 66 psi @ 10:01 pm as per request of Engr. Frances Morla (SPM-South)
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 - OPENED (35%) @ 10:01 PM FOR REFILLING
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 10:19PM , NORMAL OPERATION