## JUNE 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEX CABREROS
[13 empty] | 10pm - 6am | ALEX CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26856 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38774027 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37487900 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8444122 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 97 | 38777910 | 3883 | 93.192 | 3.883 | 5.8 | 5.8 | 2B | 0 | 0 | 1049 | 0 | 1109 | N/A | N/A | N/A | N/A | 37488580 | 680 | 175.1223 | 0% | 0% | 100% | 0% | 100% | 45% | 8445247 | 1125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 94 | 38781797 | 3887 | 93.288 | 3.887 | 7 | 7 | 2B | 0 | 0 | 999 | 0 | 1059 | N/A | N/A | N/A | N/A | 37489268 | 688 | 177.0003 | 0% | 0% | 100% | 0% | 100% | 45% | 8446459 | 1212 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 92 | 38785424 | 3627 | 87.048 | 3.627 | 8.5 | 8.5 | 2B | 0 | 0 | 999 | 0 | 1059 | N/A | N/A | N/A | N/A | 37489864 | 596 | 164.3231 | 0% | 0% | 100% | 0% | 100% | 45% | 8447737 | 1278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | JIMENEZ GALINATO
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 94 | 38789188 | 3764 | 90.336 | 3.764 | 9.5 | 9.5 | 2B | 0 | 0 | 939 | 0 | 979 | N/A | N/A | N/A | N/A | 37490456 | 592 | 157.2795 | 0% | 0% | 100% | 0% | 100% | 45% | 8448739 | 1002 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 38793066 | 3878 | 93.072 | 3.878 | 9.5 | 9.5 | 2B | 0 | 0 | 1049 | 0 | 1049 | N/A | N/A | N/A | N/A | 37490980 | 524 | 135.1212 | 0% | 0% | 100% | 0% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 38798031 | 4965 | 119.16 | 4.965 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37491828 | 848 | 170.7956 | 0% | 0% | 100% | 0% | 100% | 0% | 8448739 | 0 | 0.9 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 151 | 38804065 | 6034 | 144.816 | 6.034 | 9.2 | 9.2 | 3B+1S | 0 | 1059 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37493132 | 1304 | 216.1087 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 151 | 38810405 | 6340 | 152.16 | 6.34 | 8.7 | 8.7 | 3B+1S | 0 | 1049 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37494516 | 1384 | 218.2965 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 149 | 38816725 | 6320 | 151.68 | 6.32 | 8.3 | 8.3 | 3B+1S | 0 | 1049 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37495896 | 1380 | 218.3544 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 149 | 38823040 | 6315 | 151.56 | 6.315 | 7.8 | 7.8 | 3B+1S | 0 | 1049 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37497272 | 1376 | 217.8939 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 139 | 38829336 | 6296 | 151.104 | 6.296 | 7.4 | 7.4 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37498636 | 1364 | 216.6455 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 148 | 38835441 | 6105 | 146.52 | 6.105 | 7.1 | 7.1 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37499992 | 1356 | 222.113 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 144 | 148 | 38841554 | 6113 | 146.712 | 6.113 | 6.8 | 6.8 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37501336 | 1344 | 219.8593 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 141 | 38847460 | 5906 | 141.744 | 5.906 | 6.5 | 6.5 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37502644 | 1308 | 221.4697 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 38853324 | 5864 | 140.736 | 5.864 | 6.1 | 6.1 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37504020 | 1376 | 234.6521 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 38859189 | 5865 | 140.76 | 5.865 | 5.9 | 5.9 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37505396 | 1376 | 234.6121 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 38864822 | 5633 | 135.192 | 5.633 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37506692 | 1296 | 230.0728 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 146 | 38870871 | 6049 | 145.176 | 6.049 | 5 | 5 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37508060 | 1368 | 226.1531 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 142 | 38876705 | 5834 | 140.016 | 5.834 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37509396 | 1336 | 229.0024 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 141 | 38882498 | 5793 | 139.032 | 5.793 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37510720 | 1324 | 228.5517 | 0% | 100% | 100% | 100% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 122 | 38887975 | 5477 | 131.448 | 5.477 | 3.4 | 3.4 | 2B+1S | 0 | 1178 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37511852 | 1132 | 206.6825 | 0% | 100% | 100% | 0% | 100% | 0% | 8448739 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 120 | 38893444 | 5469 | 131.256 | 5.469 | 2.4 | 2.4 | 2B+1S | 0 | 1139 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37512968 | 1116 | 204.0592 | 0% | 100% | 100% | 0% | 100% | 0% | 8448739 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 144 | 111 | 38898324 | 4880 | 117.12 | 4.88 | 3.3 | 3.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37513928 | 960 | 196.7213 | 0% | 0% | 100% | 0% | 100% | 40% | 8449776 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 129 | 38902788 | 4464 | 107.136 | 4.464 | 4.6 | 4.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37514756 | 828 | 185.4839 | 0% | 0% | 100% | 0% | 100% | 40% | 8450928 | 1152 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.5833 | 128761 | 128761 | 128.761 | 128.761 | [12 empty] | 26856 | 26856 | 208.5725 | [6 empty] | 6806 | 6806 | 5.61 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (45%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:22 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 2, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (40%)

## JUNE 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27200 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 38902788 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37514756 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8450928 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 95 | 38906640 | 3852 | 92.448 | 3.852 | 5.8 | 5.8 | 2B | 0 | 0 | 1066 | 0 | 1077 | N/A | N/A | N/A | N/A | 37515432 | 676 | 175.4933 | 0% | 0% | 100% | 0% | 100% | 50% | 8452085 | 1157 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 93 | 38910593 | 3953 | 94.872 | 3.953 | 7.3 | 7.3 | 2B | 0 | 0 | 1066 | 0 | 1077 | N/A | N/A | N/A | N/A | 37516116 | 684 | 173.0331 | 0% | 0% | 100% | 0% | 100% | 50% | 8453252 | 1167 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 106 | 95 | 38914539 | 3946 | 94.704 | 3.946 | 8.9 | 8.9 | 2B | 0 | 0 | 1066 | 0 | 1077 | N/A | N/A | N/A | N/A | 37516784 | 668 | 169.2854 | 0% | 0% | 100% | 0% | 100% | 50% | 8454420 | 1168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 103 | 102 | 38918489 | 3950 | 94.8 | 3.95 | 9.5 | 9.5 | 2B | 0 | 0 | 1066 | 0 | 1077 | N/A | N/A | N/A | N/A | 37517460 | 676 | 171.1392 | 0% | 0% | 100% | 0% | 100% | 50% | 8455588 | 1168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 106 | 38922884 | 4395 | 105.48 | 4.395 | 9.5 | 9.5 | 2B | 0 | 0 | 1066 | 0 | 1077 | N/A | N/A | N/A | N/A | 37518152 | 692 | 157.4516 | 0% | 0% | 100% | 0% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 119 | 38927780 | 4896 | 117.504 | 4.896 | 9.5 | 9.5 | 2B | 0 | 0 | 1066 | 0 | 1066 | N/A | N/A | N/A | N/A | 37518940 | 788 | 160.9477 | 0% | 0% | 100% | 0% | 100% | 0% | 8455588 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 149 | 38933873 | 6093 | 146.232 | 6.093 | 9.2 | 9.2 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37520284 | 1344 | 220.581 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 149 | 38940051 | 6178 | 148.272 | 6.178 | 8.8 | 8.8 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37521656 | 1372 | 222.0783 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 145 | 38946180 | 6129 | 147.096 | 6.129 | 8.4 | 8.4 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37523014 | 1358 | 221.5696 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 146 | 38952460 | 6280 | 150.72 | 6.28 | 8 | 8 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37524341 | 1327 | 211.3057 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 | 1.01 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 162 | 38958612 | 6152 | 147.648 | 6.152 | 7.6 | 7.6 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37525716 | 1375 | 223.5046 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 147 | 38964796 | 6184 | 148.416 | 6.184 | 7.2 | 7.2 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37527044 | 1328 | 214.7477 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 148 | 38970941 | 6145 | 147.48 | 6.145 | 6.9 | 6.9 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37528452 | 1408 | 229.1294 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 145 | 38976839 | 5898 | 141.552 | 5.898 | 6.5 | 6.5 | 3B+1S | 0 | 1002 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37529802 | 1350 | 228.8911 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 142 | 38982738 | 5899 | 141.576 | 5.899 | 6.2 | 6.2 | 3B+1S | 0 | 1002 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37531152 | 1350 | 228.8523 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 38988645 | 5907 | 141.768 | 5.907 | 6 | 6 | 3B+1S | 0 | 1043 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37532484 | 1332 | 225.4952 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 38994533 | 5888 | 141.312 | 5.888 | 5.5 | 5.5 | 3B+1S | 0 | 1043 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37533834 | 1350 | 229.2799 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 145 | 39000422 | 5889 | 141.336 | 5.889 | 5 | 5 | 3B+1S | 0 | 1043 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37535184 | 1350 | 229.241 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 39006273 | 5851 | 140.424 | 5.851 | 4.4 | 4.4 | 3B+1S | 0 | 1043 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37536544 | 1360 | 232.4389 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 142 | 39012152 | 5879 | 141.096 | 5.879 | 3.9 | 3.9 | 3B+1S | 0 | 1043 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37537904 | 1360 | 231.3319 | 0% | 100% | 100% | 100% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 | 113 | 39017579 | 5427 | 130.248 | 5.427 | 3 | 3 | 2B+1S | 0 | 1124 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37539012 | 1108 | 204.1644 | 0% | 100% | 100% | 0% | 100% | 0% | 8455588 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 114 | 39023037 | 5458 | 130.992 | 5.458 | 2.2 | 2.2 | 2B+1S | 0 | 1126 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37540088 | 1076 | 197.1418 | 0% | 100% | 100% | 0% | 100% | 0% | 8455588 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 110 | 39027804 | 4767 | 114.408 | 4.767 | 2.6 | 2.6 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37541012 | 924 | 193.8326 | 0% | 0% | 100% | 0% | 100% | 35% | 8456205 | 617 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 120 | 39032568 | 4764 | 114.336 | 4.764 | 3.5 | 3.5 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37541956 | 944 | 198.1528 | 0% | 0% | 100% | 0% | 100% | 35% | 8457078 | 873 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.4167 | 129780 | 129780 | 129.78 | 129.78 | [12 empty] | 27200 | 27200 | 209.5855 | [6 empty] | 6150 | 6150 | 5.93 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 3, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (35%)

## JUNE 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27192 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39032568 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37541956 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8457078 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 105 | 39037206 | 4638 | 111.312 | 4.638 | 4.7 | 4.7 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37542876 | 920 | 198.3614 | 0% | 0% | 100% | 0% | 100% | 46% | 8458081 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 100 | 39041060 | 3854 | 92.496 | 3.854 | 5.9 | 5.9 | 2B | 0 | 0 | 1069 | 0 | 1069 | N/A | N/A | N/A | N/A | 37543568 | 692 | 179.5537 | 0% | 0% | 100% | 0% | 100% | 46% | 8459329 | 1248 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 113 | 39044911 | 3851 | 92.424 | 3.851 | 7.3 | 7.3 | 2B | 0 | 0 | 1069 | 0 | 1069 | N/A | N/A | N/A | N/A | 37544236 | 668 | 173.4614 | 0% | 0% | 100% | 0% | 100% | 46% | 8460628 | 1299 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 130 | 117 | 39048755 | 3844 | 92.256 | 3.844 | 8.4 | 8.4 | 2B | 0 | 0 | 1069 | 0 | 1069 | N/A | N/A | N/A | N/A | 37544888 | 652 | 169.615 | 0% | 0% | 100% | 0% | 100% | 46% | 8461761 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 129 | 115 | 39052643 | 3888 | 93.312 | 3.888 | 9.5 | 9.5 | 2B | 0 | 0 | 1069 | 0 | 1069 | N/A | N/A | N/A | N/A | 37545532 | 644 | 165.6379 | 0% | 0% | 100% | 0% | 100% | 46% | 8462323 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 122 | 39057710 | 5067 | 121.608 | 5.067 | 9.5 | 9.5 | 2B | 0 | 0 | 1066 | 0 | 1066 | N/A | N/A | N/A | N/A | 37546348 | 816 | 161.042 | 0% | 0% | 100% | 0% | 100% |  | 8462323 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 152 | 39063827 | 6117 | 146.808 | 6.117 | 9.1 | 9.1 | 3B+1S | 0 | 1012 | 1195 | 1185 | 1198 | N/A | N/A | N/A | N/A | 37547696 | 1348 | 220.3695 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 147 | 39070122 | 6295 | 151.08 | 6.295 | 8.7 | 8.7 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37549054 | 1358 | 215.7268 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 140 | 39076394 | 6272 | 150.528 | 6.272 | 8.2 | 8.2 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37550494 | 1440 | 229.5918 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 150 | 39082605 | 6211 | 149.064 | 6.211 | 7.7 | 7.7 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37551944 | 1450 | 233.4568 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 | 0.99 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 150 | 39088617 | 6012 | 144.288 | 6.012 | 7.3 | 7.3 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37553124 | 1180 | 196.2741 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 143 | 39095044 | 6427 | 154.248 | 6.427 | 6.9 | 6.9 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37554544 | 1420 | 220.9429 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 143 | 39100964 | 5920 | 142.08 | 5.92 | 6.6 | 6.6 | 3B+1S | 0 | 1006 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37555876 | 1332 | 225 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 39106898 | 5934 | 142.416 | 5.934 | 6.1 | 6.1 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37557220 | 1344 | 226.4914 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 142 | 39112728 | 5830 | 139.92 | 5.83 | 5.8 | 5.8 | 3B+1S | 0 | 1012 | 1190 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37558540 | 1320 | 226.4151 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 39118621 | 5893 | 141.432 | 5.893 | 5.6 | 5.6 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37559891 | 1351 | 229.255 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 144 | 39124377 | 5756 | 138.144 | 5.756 | 5.2 | 5.2 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37561204 | 1313 | 228.1098 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 142 | 39130325 | 5948 | 142.752 | 5.948 | 4.9 | 4.9 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37562556 | 1352 | 227.3033 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 141 | 39136203 | 5878 | 141.072 | 5.878 | 4.6 | 4.6 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37563892 | 1336 | 227.2882 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 140 | 39141995 | 5792 | 139.008 | 5.792 | 4.2 | 4.2 | 3B+1S | 0 | 1022 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37565236 | 1344 | 232.0442 | 0% | 100% | 100% | 100% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 129 | 39147335 | 5340 | 128.16 | 5.34 | 3.4 | 3.4 | 2B+1S | 0 | 1062 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37566300 | 1064 | 199.2509 | 0% | 100% | 100% | 0% | 100% |  | 8462323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 128 | 39152714 | 5379 | 129.096 | 5.379 | 2.8 | 2.8 | 2B+1S | 0 | 1062 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37567342 | 1042 | 193.7163 | 0% | 100% | 100% | 0% | 100% |  | 8462323 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 140 | 39157403 | 4689 | 112.536 | 4.689 | 3.4 | 3.4 | 2B | 0 | 0 | 1159 | 0 | 1179 | N/A | N/A | N/A | N/A | 37568288 | 946 | 201.7488 | 0% | 0% | 100% | 0% | 100% | 40% | 8463453 | 1130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 138 | 39161865 | 4462 | 107.088 | 4.462 | 4.6 | 4.6 | 2B | 0 | 0 | 1159 | 0 | 1179 | N/A | N/A | N/A | N/A | 37569148 | 860 | 192.7387 | 0% | 0% | 100% | 0% | 100% | 40% | 8464504 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 134.0833 | 129297 | 129297 | 129.297 | 129.297 | [12 empty] | 27192 | 27192 | 210.3065 | [6 empty] | 7426 | 7426 | 5.8 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (46%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
WATER SAMPLING / CENTRAL LAB. Res. Chl. 1.03 mg/l BY MR.ED BELTRAN
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 4, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JUNE 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | F.A.RAMSO / R.DIGNUN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS
[13 empty] | 10pm - 6am | F.A.RAMSO / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39161865 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37569148 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8464504 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 115 | 39165877 | 4012 | 96.288 | 4.012 | 5.9 | 5.9 | 2B | 0 | 0 | 1059 | 0 | 1129 | N/A | N/A | N/A | N/A | 37569876 | 728 | 181.4556 | 0% | 0% | 100% | 0% | 100% | 50% | 8465764 | 1260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 117 | 39169614 | 3737 | 89.688 | 3.737 | 7.2 | 7.2 | 2B | 0 | 0 | 1059 | 0 | 1129 | N/A | N/A | N/A | N/A | 37570548 | 672 | 179.8234 | 0% | 0% | 100% | 0% | 100% | 50% | 8466977 | 1213 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 112 | 39173618 | 4004 | 96.096 | 4.004 | 8.5 | 8.5 | 2B | 0 | 0 | 1059 | 0 | 1079 | N/A | N/A | N/A | N/A | 37571236 | 688 | 171.8282 | 0% | 0% | 100% | 0% | 100% | 50% | 8468312 | 1335 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 98 | 39177441 | 3823 | 91.752 | 3.823 | 9.5 | 9.5 | 2B | 0 | 0 | 1059 | 0 | 1079 | N/A | N/A | N/A | N/A | 37571904 | 668 | 174.7319 | 0% | 0% | 100% | 0% | 100% | 50% | 8469330 | 1018 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 100 | 39181913 | 4472 | 107.328 | 4.472 | 9.5 | 9.5 | 2B | 0 | 0 | 1059 | 0 | 1079 | N/A | N/A | N/A | N/A | 37572616 | 712 | 159.2129 | 0% | 0% | 100% | 0% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 118 | 39186825 | 4912 | 117.888 | 4.912 | 9.5 | 9.5 | 2B | 0 | 0 | 1059 | 0 | 1079 | N/A | N/A | N/A | N/A | 37573508 | 892 | 181.5961 | 0% | 0% | 100% | 0% | 100% |  | 8469330 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 148 | 39193465 | 6640 | 159.36 | 6.64 | 9 | 9 | 3B+1S | 0 | 1182 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37574996 | 1488 | 224.0964 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 39199319 | 5854 | 140.496 | 5.854 | 8.5 | 8.5 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37576292 | 1296 | 221.3871 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 149 | 39205388 | 6069 | 145.656 | 6.069 | 8 | 8 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37577620 | 1328 | 218.8169 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 148 | 39211846 | 6458 | 154.992 | 6.458 | 7.6 | 7.6 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37579044 | 1424 | 220.5017 | 0% | 100% | 100% | 100% | 1000% |  | 8469330 | 0 | 1.22 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 146 | 39218028 | 6182 | 148.368 | 6.182 | 7.2 | 7.2 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37580396 | 1352 | 218.6995 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 149 | 39224309 | 6281 | 150.744 | 6.281 | 6.8 | 6.8 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37581772 | 1376 | 219.0734 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 143 | 147 | 39230246 | 5937 | 142.488 | 5.937 | 6.4 | 6.4 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37583072 | 1300 | 218.9658 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 39236768 | 6522 | 156.528 | 6.522 | 6 | 6 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37584548 | 1476 | 226.3109 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 39242459 | 5691 | 136.584 | 5.691 | 5.7 | 5.7 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37585844 | 1296 | 227.728 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 39248418 | 5959 | 143.016 | 5.959 | 5.3 | 5.3 | 3B+1S | 0 | 1052 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37587200 | 1356 | 227.555 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 39253956 | 5538 | 132.912 | 5.538 | 4.8 | 4.8 | 3B+1S | 0 | 1052 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37588492 | 1292 | 233.2972 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 39260078 | 6122 | 146.928 | 6.122 | 4.2 | 4.2 | 3B+1S | 0 | 1052 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37589900 | 1408 | 229.9902 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 39265763 | 5685 | 136.44 | 5.685 | 3.6 | 3.6 | 3B+1S | 0 | 1052 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37591212 | 1312 | 230.7828 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 141 | 39271368 | 5605 | 134.52 | 5.605 | 3.3 | 3.3 | 3B+1S | 0 | 1052 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37592490 | 1278 | 228.0107 | 0% | 100% | 100% | 100% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 39276872 | 5504 | 132.096 | 5.504 | 2.7 | 2.7 | 2B+1S | 0 | 1052 | 1179 | 0 | 1179 | N/A | N/A | N/A | N/A | 37593604 | 1114 | 202.3983 | 0% | 100% | 100% | 0% | 100% |  | 8469330 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 125 | 39282084 | 5212 | 125.088 | 5.212 | 2.1 | 2.1 | 2B+1S | 0 | 1052 | 1179 | 0 | 1179 | N/A | N/A | N/A | N/A | 37594632 | 1028 | 197.2371 | 0% | 100% | 100% | 0% | 100% |  | 8469330 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 139 | 39286754 | 4670 | 112.08 | 4.67 | 2.8 | 2.8 | 2B | 0 | 0 | 1159 | 0 | 1169 | N/A | N/A | N/A | N/A | 37595528 | 896 | 191.863 | 0% | 0% | 100% | 0% | 100% | 35% | 8470129 | 799 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 138 | 39291225 | 4471 | 107.304 | 4.471 | 3.7 | 3.7 | 2B | 0 | 0 | 1159 | 0 | 1169 | N/A | N/A | N/A | N/A | 37596380 | 852 | 190.5614 | 0% | 0% | 100% | 0% | 100% | 35% | 8471033 | 904 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 133.125 | 129360 | 129360 | 129.36 | 129.36 | [12 empty] | 27232 | 27232 | 210.5133 | [6 empty] | 6529 | 6529 | 6.6 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CONDUCTED SITE INSPECTION AND DELIVERED THE OFFICE SUPPLIES SIR ERNESTO PASCUA AND SIR ARTURO TRINIDAD ARRIVED @ 4:05PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## JUNE 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27236 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39291225 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37596380 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8471033 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 110 | 39295733 | 4508 | 108.192 | 4.508 | 5 | 5 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 37597260 | 880 | 195.2085 | 0% | 0% | 100% | 0% | 100% | 50% | 8472179 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 111 | 39299663 | 3930 | 94.32 | 3.93 | 6.2 | 6.2 | 2B | 0 | 0 | 1029 | 0 | 1149 | N/A | N/A | N/A | N/A | 37597996 | 736 | 187.2774 | 0% | 0% | 100% | 0% | 100% | 50% | 8473472 | 1293 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 112 | 39303562 | 3899 | 93.576 | 3.899 | 7.9 | 7.9 | 2B | 0 | 0 | 1029 | 0 | 1149 | N/A | N/A | N/A | N/A | 37598769 | 773 | 198.256 | 0% | 0% | 100% | 0% | 100% | 50% | 8474755 | 1283 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 115 | 39307290 | 3728 | 89.472 | 3.728 | 8.8 | 8.8 | 2B | 0 | 0 | 1029 | 0 | 1149 | N/A | N/A | N/A | N/A | 37599410 | 641 | 171.9421 | 0% | 0% | 100% | 0% | 100% | 50% | 8475750 | 995 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 133 | 120 | 39311318 | 4028 | 96.672 | 4.028 | 9.5 | 9.5 | 2B | 0 | 0 | 1029 | 0 | 1149 | N/A | N/A | N/A | N/A | 37600124 | 714 | 177.2592 | 0% | 0% | 100% | 0% | 100% | 50% | 8476136 | 386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 112 | 39316140 | 4822 | 115.728 | 4.822 | 9.5 | 9.5 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37601004 | 880 | 182.4969 | 0% | 0% | 100% | 0% | 100% |  | 8476136 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 152 | 39322248 | 6108 | 146.592 | 6.108 | 9 | 9 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37602348 | 1344 | 220.0393 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 150 | 39328450 | 6202 | 148.848 | 6.202 | 8.5 | 8.5 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37603712 | 1364 | 219.9291 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 148 | 39334599 | 6149 | 147.576 | 6.149 | 8.1 | 8.1 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37605044 | 1332 | 216.6206 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 143 | 39340779 | 6180 | 148.32 | 6.18 | 7.6 | 7.6 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37606444 | 1400 | 226.5372 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 149 | 39346901 | 6122 | 146.928 | 6.122 | 7.3 | 7.3 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37607900 | 1456 | 237.8308 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 133 | 39353022 | 6121 | 146.904 | 6.121 | 6.9 | 6.9 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37609156 | 1256 | 205.1952 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 144 | 39358924 | 5902 | 141.648 | 5.902 | 6.5 | 6.5 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37610511 | 1355 | 229.5832 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 117 | 39364813 | 5889 | 141.336 | 5.889 | 6.2 | 6.2 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37611852 | 1341 | 227.7127 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 145 | 39370529 | 5716 | 137.184 | 5.716 | 5.9 | 5.9 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37613176 | 1324 | 231.6305 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 39376345 | 5816 | 139.584 | 5.816 | 5.6 | 5.6 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37614516 | 1340 | 230.3989 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 39382095 | 5750 | 138 | 5.75 | 5.2 | 5.2 | 3B+1S | 0 | 1032 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37615852 | 1336 | 232.3478 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 143 | 39387911 | 5816 | 139.584 | 5.816 | 4.7 | 4.7 | 3B+1S | 0 | 1032 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37617196 | 1344 | 231.0867 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 129 | 39393646 | 5735 | 137.64 | 5.735 | 4.3 | 4.3 | 3B+1S | 0 | 1032 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37618520 | 1324 | 230.8631 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 139 | 39399484 | 5838 | 140.112 | 5.838 | 3.8 | 3.8 | 3B+1S | 0 | 1032 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37619880 | 1360 | 232.9565 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 134 | 39404797 | 5313 | 127.512 | 5.313 | 3.2 | 3.2 | 2B+1S | 0 | 1072 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37620948 | 1068 | 201.0164 | 0% | 100% | 100% | 100% | 100% |  | 8476136 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 130 | 39410066 | 5269 | 126.456 | 5.269 | 2.5 | 2.5 | 2B+1S | 0 | 1072 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37622008 | 1060 | 201.1767 | 0% | 100% | 100% | 0% | 100% |  | 8476136 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 134 | 39414528 | 4462 | 107.088 | 4.462 | 3.3 | 3.3 | 2B | 0 | 0 | 1079 | 0 | 1189 | N/A | N/A | N/A | N/A | 37622852 | 844 | 189.1528 | 0% | 0% | 100% | 0% | 100% | 40% | 8477110 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 132 | 39418546 | 4018 | 96.432 | 4.018 | 4.3 | 4.3 | 2B | 0 | 0 | 1079 | 0 | 1189 | N/A | N/A | N/A | N/A | 37623616 | 764 | 190.1444 | 0% | 0% | 100% | 0% | 100% | 40% | 8478061 | 951 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 132.7917 | 127321 | 127321 | 127.321 | 127.321 | [12 empty] | 27236 | 27236 | 213.916 | [6 empty] | 7028 | 7028 | 6.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 6, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JUNE 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27400 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39418546 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37623616 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8478061 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 116 | 39422796 | 4250 | 102 | 4.25 | 5.4 | 5.4 | 2B | 0 | 0 | 1039 | 0 | 1189 | N/A | N/A | N/A | N/A | 37624452 | 836 | 196.7059 | 0% | 0% | 100% | 0% | 100% | 50% | 8479061 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 119 | 39426347 | 3551 | 85.224 | 3.551 | 6.5 | 6.5 | 2B | 0 | 0 | 1039 | 0 | 1189 | N/A | N/A | N/A | N/A | 37625156 | 704 | 198.254 | 0% | 0% | 100% | 0% | 100% | 50% | 8480066 | 1005 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 121 | 39430157 | 3810 | 91.44 | 3.81 | 7.6 | 7.6 | 2B | 0 | 0 | 1029 | 0 | 1129 | N/A | N/A | N/A | N/A | 37625876 | 720 | 188.9764 | 0% | 0% | 100% | 0% | 100% | 50% | 8481262 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 126 | 39434019 | 3862 | 92.688 | 3.862 | 8.7 | 8.7 | 2B | 0 | 0 | 1029 | 0 | 1129 | N/A | N/A | N/A | N/A | 37626580 | 704 | 182.289 | 0% | 0% | 100% | 0% | 100% | 50% | 8482328 | 1066 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 137 | 39437710 | 3691 | 88.584 | 3.691 | 9.5 | 9.5 | 2B | 0 | 0 | 1029 | 0 | 1129 | N/A | N/A | N/A | N/A | 37627252 | 672 | 182.0645 | 0% | 0% | 100% | 0% | 100% | 50% | 8483114 | 786 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 124 | 39442720 | 5010 | 120.24 | 5.01 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37628076 | 824 | 164.4711 | 0% | 0% | 100% | 0% | 100% | 0% | 8483114 | 0 | 0.91 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 149 | 146 | 39448700 | 5980 | 143.52 | 5.98 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37629360 | 1284 | 214.7157 | 0% | 0% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 140 | 39454872 | 6172 | 148.128 | 6.172 | 9.4 | 9.4 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37630708 | 1348 | 218.4057 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 146 | 146 | 39461091 | 6219 | 149.256 | 6.219 | 8.9 | 8.9 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37632054 | 1346 | 216.4335 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 146 | 154 | 39467511 | 6420 | 154.08 | 6.42 | 8.4 | 8.4 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37633460 | 1406 | 219.0031 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 149 | 151 | 39473806 | 6295 | 151.08 | 6.295 | 7.9 | 7.9 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37634852 | 1392 | 221.1279 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 150 | 39480130 | 6324 | 151.776 | 6.324 | 7.4 | 7.4 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37636236 | 1384 | 218.8488 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 143 | 39486195 | 6065 | 145.56 | 6.065 | 6.8 | 6.8 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37637592 | 1356 | 223.5779 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 144 | 39492305 | 6110 | 146.64 | 6.11 | 6.2 | 6.2 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37638972 | 1380 | 225.8592 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 145 | 39498418 | 6113 | 146.712 | 6.113 | 5.7 | 5.7 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37640344 | 1372 | 224.4397 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 148 | 39504434 | 6016 | 144.384 | 6.016 | 5.2 | 5.2 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37641716 | 1372 | 228.0585 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 39510282 | 5848 | 140.352 | 5.848 | 4.7 | 4.7 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37643052 | 1336 | 228.4542 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 143 | 39516293 | 6011 | 144.264 | 6.011 | 4.1 | 4.1 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37644412 | 1360 | 226.2519 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 129 | 39522166 | 5873 | 140.952 | 5.873 | 3.6 | 3.6 | 3B+1S | 0 | 1042 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37645772 | 1360 | 231.5682 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 130 | 39527675 | 5509 | 132.216 | 5.509 | 3.3 | 3.3 | 3B+1S | 0 | 1022 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37647068 | 1296 | 235.2514 | 0% | 100% | 100% | 100% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 130 | 39533014 | 5339 | 128.136 | 5.339 | 2.8 | 2.8 | 2B+1S | 0 | 1022 | 1189 | 0 | 1190 | N/A | N/A | N/A | N/A | 37648132 | 1064 | 199.2883 | 0% | 100% | 100% | 0% | 100% | 0% | 8483114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 39538301 | 5287 | 126.888 | 5.287 | 2.3 | 2.3 | 2B+1S | 0 | 1022 | 1189 | 0 | 1190 | N/A | N/A | N/A | N/A | 37649192 | 1060 | 200.4918 | 0% | 100% | 100% | 0% | 100% | 0% | 8483114 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 117 | 39542846 | 4545 | 109.08 | 4.545 | 2.8 | 2.8 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37650092 | 900 | 198.0198 | 0% | 0% | 100% | 0% | 100% | 40% | 8483704 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 112 | 39547568 | 4722 | 113.328 | 4.722 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37651016 | 924 | 195.6798 | 0% | 0% | 100% | 0% | 0% | 40% | 8484324 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 134.8333 | 129022 | 129022 | 129.022 | 129.022 | [12 empty] | 27400 | 27400 | 212.3669 | [6 empty] | 6263 | 6263 | 6.03 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MR. MARK PAVIA, PAUL CRUZ, DENNIS,ALFREDD, RAYMOND OF EXPONENT (ICONTROL TECH, ELECTRICAL AND INDUSTRIAL SERVICES) REPLACE CPU AND MONITOR OF SCADA PC./ INSTALATION OF SCADA
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 7, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JUNE 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27884 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39547568 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37651016 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8484324 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 95 | 39551656 | 4088 | 98.112 | 4.088 | 4.5 | 4.5 | 2B | 0 | 0 | 1026 | 0 | 1189 | N/A | N/A | N/A | N/A | 37651780 | 764 | 186.8885 | 0% | 0% | 100% | 0% | 100% | 50% | 8485233 | 909 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 96 | 39555639 | 3983 | 95.592 | 3.983 | 5.4 | 5.4 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 37652520 | 740 | 185.7896 | 0% | 0% | 100% | 0% | 100% | 50% | 8486282 | 1049 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 98 | 39559765 | 4126 | 99.024 | 4.126 | 6.7 | 6.7 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 37653304 | 784 | 190.0145 | 0% | 0% | 100% | 0% | 100% | 50% | 8487337 | 1055 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 96 | 39563708 | 3943 | 94.632 | 3.943 | 7.3 | 7.3 | 2B | 0 | 0 | 1026 | 0 | 1187 | N/A | N/A | N/A | N/A | 37654048 | 744 | 188.6888 | 0% | 0% | 100% | 0% | 100% | 50% | 8487843 | 506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 139 | 98 | 39567748 | 4040 | 96.96 | 4.04 | 8.3 | 8.3 | 2B | 0 | 0 | 1027 | 0 | 1187 | N/A | N/A | N/A | N/A | 37654812 | 764 | 189.1089 | 0% | 0% | 100% | 0% | 100% | 50% | 8488995 | 1152 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 123 | 39572525 | 4777 | 114.648 | 4.777 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37655696 | 884 | 185.0534 | 0% | 0% | 100% | 0% | 100% | 50% | 8489733 | 738 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 126 | 39578323 | 5798 | 139.152 | 5.798 | 9.4 | 9.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 37656924 | 1228 | 211.7972 | 0% | 0% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 152 | 39584282 | 5959 | 143.016 | 5.959 | 9.1 | 9.1 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37658272 | 1348 | 226.2125 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 155 | 39590246 | 5964 | 143.136 | 5.964 | 8.6 | 8.6 | 3B+1S | 0 | 1069 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37659604 | 1332 | 223.34 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 153 | 39596610 | 6364 | 152.736 | 6.364 | 7.8 | 7.8 | 3B+1S | 0 | 1100 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 37661024 | 1420 | 223.1301 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 | 0.82 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 39603030 | 6420 | 154.08 | 6.42 | 7.1 | 7.1 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 37662468 | 1444 | 224.9221 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 151 | 39609334 | 6304 | 151.296 | 6.304 | 6.4 | 6.4 | 3B+1S | 0 | 1099 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37663872 | 1404 | 222.7157 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 145 | 39615455 | 6121 | 146.904 | 6.121 | 5.8 | 5.8 | 3B+1S | 0 | 1099 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37665274 | 1402 | 229.0475 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 146 | 39621577 | 6122 | 146.928 | 6.122 | 4.9 | 4.9 | 3B+1S | 0 | 1099 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37666676 | 1402 | 229.0101 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 145 | 39627596 | 6019 | 144.456 | 6.019 | 4.1 | 4.1 | 3B+1S | 0 | 1099 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37668076 | 1400 | 232.5968 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 145 | 39633454 | 5858 | 140.592 | 5.858 | 3.3 | 3.3 | 3B+1S | 0 | 1049 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37669436 | 1360 | 232.1611 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 146 | 39639389 | 5935 | 142.44 | 5.935 | 2.9 | 2.9 | 3B+1S | 0 | 1049 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37670804 | 1368 | 230.4971 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 39645287 | 5898 | 141.552 | 5.898 | 2.5 | 2.5 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37672164 | 1360 | 230.5866 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 142 | 133 | 39651147 | 5860 | 140.64 | 5.86 | 2.2 | 2.2 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37673500 | 1336 | 227.9863 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 137 | 39656754 | 5607 | 134.568 | 5.607 | 2.1 | 2.1 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37674804 | 1304 | 232.5664 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 141 | 140 | 39662479 | 5725 | 137.4 | 5.725 | 2 | 2 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37676132 | 1328 | 231.9651 | 0% | 100% | 100% | 100% | 100% | 0% | 8489733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 120 | 39667639 | 5160 | 123.84 | 5.16 | 1.9 | 1.9 | 2B+1S | 0 | 997 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37677152 | 1020 | 197.6744 | 0% | 100% | 100% | 0% | 100% | 0% | 8489733 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 105 | 39672211 | 4572 | 109.728 | 4.572 | 3 | 3 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 37678026 | 874 | 191.1636 | 0% | 0% | 100% | 0% | 100% | 45% | 8490729 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 102 | 39676783 | 4572 | 109.728 | 4.572 | 3.7 | 3.7 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 37678900 | 874 | 191.1636 | 0% | 0% | 100% | 0% | 100% | 45% | 8491726 | 997 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.0833 | 129215 | 129215 | 129.215 | 129.215 | [12 empty] | 27884 | 27884 | 215.7954 | [6 empty] | 7402 | 7402 | 5.55 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (50%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:23 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 8, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
GENSET 1&2 WARM UP EXERCISE W/O LOAD FOR 10MINS ONLY, FUEL CONSUMPTION = 13LITERS / FUEL STOCKS = 10,735 LITERS
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (45%)

## JUNE 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27520 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39676783 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37678900 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8491726 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 98 | 39680900 | 4117 | 98.808 | 4.117 | 5.1 | 5.1 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 37679692 | 792 | 192.3731 | 0% | 0% | 100% | 0% | 100% | 55% | 8492929 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 99 | 39685021 | 4121 | 98.904 | 4.121 | 6.7 | 6.7 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 37680478 | 786 | 190.7304 | 0% | 0% | 100% | 0% | 100% | 55% | 8494124 | 1195 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 39689136 | 4115 | 98.76 | 4.115 | 7.8 | 7.8 | 2B | 0 | 0 | 1097 | 0 | 1107 | N/A | N/A | N/A | N/A | 37681276 | 798 | 193.9247 | 0% | 0% | 100% | 0% | 100% | 55% | 8495336 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 129 | 97 | 39693215 | 4079 | 97.896 | 4.079 | 8.9 | 8.9 | 2B | 0 | 0 | 1097 | 0 | 1107 | N/A | N/A | N/A | N/A | 37682036 | 760 | 186.3202 | 0% | 0% | 100% | 0% | 100% | 55% | 8496595 | 1259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 121 | 120 | 39697693 | 4478 | 107.472 | 4.478 | 9.5 | 9.5 | 2B | 0 | 0 | 1147 | 0 | 1157 | N/A | N/A | N/A | N/A | 37682824 | 788 | 175.9714 | 0% | 0% | 100% | 0% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 121 | 39702640 | 4947 | 118.728 | 4.947 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 0 | 1158 | N/A | N/A | N/A | N/A | 37683664 | 840 | 169.7999 | 0% | 0% | 100% | 0% | 100% | 0% | 8496595 | 0 | 0.91 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 151 | 39708689 | 6049 | 145.176 | 6.049 | 8.9 | 8.9 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37684988 | 1324 | 218.8792 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 139 | 39714931 | 6242 | 149.808 | 6.242 | 8.4 | 8.4 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37686360 | 1372 | 219.8013 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 149 | 39721243 | 6312 | 151.488 | 6.312 | 8 | 8 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37687732 | 1372 | 217.3638 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 149 | 39727452 | 6209 | 149.016 | 6.209 | 7.6 | 7.6 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37689092 | 1360 | 219.0369 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 145 | 39733699 | 6247 | 149.928 | 6.247 | 7.2 | 7.2 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37690456 | 1364 | 218.3448 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 149 | 39739889 | 6190 | 148.56 | 6.19 | 6.9 | 6.9 | 3B+1S | 0 | 1012 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37691820 | 1364 | 220.3554 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 39745899 | 6010 | 144.24 | 6.01 | 6.5 | 6.5 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37693164 | 1344 | 223.6273 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 141 | 39751713 | 5814 | 139.536 | 5.814 | 6.2 | 6.2 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37694532 | 1368 | 235.2941 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 138 | 39757489 | 5776 | 138.624 | 5.776 | 5.8 | 5.8 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37695852 | 1320 | 228.5319 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 147 | 39763354 | 5865 | 140.76 | 5.865 | 5.6 | 5.6 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37697204 | 1352 | 230.52 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 39769161 | 5807 | 139.368 | 5.807 | 5.4 | 5.4 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37698524 | 1320 | 227.3119 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 149 | 39774931 | 5770 | 138.48 | 5.77 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37699852 | 1328 | 230.156 | 0% | 100% | 100% | 100% | 100% | 0% | 8496595 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 143 | 39780545 | 5614 | 134.736 | 5.614 | 4.9 | 4.9 | 3B+1S | 0 | 985 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 37701160 | 1308 | 232.989 | 0% | 100% | 100% | 0% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 137 | 39786159 | 5614 | 134.736 | 5.614 | 4.7 | 4.7 | 2B+1S | 0 | 985 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 37702468 | 1308 | 232.989 | 0% | 100% | 100% | 0% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 133 | 39791643 | 5484 | 131.616 | 5.484 | 3.6 | 3.6 | 2B+1S | 0 | 1127 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37703604 | 1136 | 207.1481 | 0% | 100% | 100% | 0% | 100% | 0% | 8496595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 130 | 39796812 | 5169 | 124.056 | 5.169 | 3 | 3 | 2B+1S | 0 | 1128 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37704688 | 1084 | 209.7117 | 0% | 100% | 100% | 0% | 100% | 0% | 8496595 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 110 | 39801577 | 4765 | 114.36 | 4.765 | 3.9 | 3.9 | 2B | 0 | 0 | 1148 | 0 | 1107 | N/A | N/A | N/A | N/A | 37705684 | 996 | 209.0241 | 0% | 0% | 100% | 0% | 100% | 50% | 8497335 | 740 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 101 | 39805451 | 3874 | 92.976 | 3.874 | 4.9 | 4.9 | 2B | 0 | 0 | 1148 | 0 | 1107 | N/A | N/A | N/A | N/A | 37706420 | 736 | 189.9845 | 0% | 0% | 100% | 0% | 100% | 50% | 8498331 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 128668 | 128668 | 128.668 | 128.668 | [12 empty] | 27520 | 27520 | 213.8838 | [6 empty] | 6605 | 6605 | 5.54 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (55%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:13 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
WATER SAMPLING / CENTRAL LAB. Res. Chl. 1.12 mg/l BY MR.ED BELTRAN
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 9, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (45%)
ALEX VILLACORTE AND HER TEAM MAINTENANCE INSPECTION THE CHECK VALVE OF BP3
BP3 - STOPPED @ 10:28 PM / BP3 - RESTART @ 10:50 PM
BP2 - STARTED @ 10:30 PM / BP2 - STOPPED @ 11:55 PM

## JUNE 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS. SY
[13 empty] | 10pm - 6am | F.A.RAMSO / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27461 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39805451 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37706420 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8498331 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 105 | 39809565 | 4114 | 98.736 | 4.114 | 5.5 | 5.5 | 2B | 0 | 0 | 1147 | 0 | 1107 | N/A | N/A | N/A | N/A | 37707196 | 776 | 188.6242 | 0% | 0% | 100% | 0% | 100% | 55% | 8499391 | 1060 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 101 | 39813687 | 4122 | 98.928 | 4.122 | 7 | 7 | 2B | 0 | 0 | 1147 | 0 | 1107 | N/A | N/A | N/A | N/A | 37707984 | 788 | 191.1693 | 0% | 0% | 100% | 0% | 100% | 55% | 8500460 | 1069 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 99 | 39817807 | 4120 | 98.88 | 4.12 | 8.1 | 8.1 | 2B | 0 | 0 | 1147 | 0 | 1107 | N/A | N/A | N/A | N/A | 37708766 | 782 | 189.8058 | 0% | 0% | 100% | 0% | 100% | 55% | 8501513 | 1053 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / R.DIGNUN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 102 | 39821927 | 4120 | 98.88 | 4.12 | 9.1 | 9.1 | 2B | 0 | 0 | 1147 | 0 | 1107 | N/A | N/A | N/A | N/A | 37709548 | 782 | 189.8058 | 0% | 0% | 100% | 0% | 100% | 55% | 8502572 | 1059 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 124 | 39827289 | 5362 | 128.688 | 5.362 | 9.5 | 9.5 | 2B | 0 | 0 | 1147 | 0 | 1107 | N/A | N/A | N/A | N/A | 37710508 | 960 | 179.0377 | 0% | 0% | 100% | 0% | 100% | 55% | 8502718 | 146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 121 | 39831042 | 3753 | 90.072 | 3.753 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37711136 | 628 | 167.3328 | 0% | 0% | 100% | 0% | 100% |  | 8502718 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 153 | 39837158 | 6116 | 146.784 | 6.116 | 9 | 9 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37712496 | 1360 | 222.3676 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 39843220 | 6062 | 145.488 | 6.062 | 8.5 | 8.5 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37713832 | 1336 | 220.3893 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 150 | 39849528 | 6308 | 151.392 | 6.308 | 8.1 | 8.1 | 3B+1S | 0 | 1050 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37715216 | 1384 | 219.4039 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 152 | 39855803 | 6275 | 150.6 | 6.275 | 7.5 | 7.5 | 3B+1S | 0 | 1050 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37716614 | 1398 | 222.7888 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 127 | 39862027 | 6224 | 149.376 | 6.224 | 7.1 | 7.1 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37717941 | 1327 | 213.2069 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 39867983 | 5956 | 142.944 | 5.956 | 6.7 | 6.7 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37719316 | 1375 | 230.8596 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 146 | 39874017 | 6034 | 144.816 | 6.034 | 6.3 | 6.3 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37720644 | 1328 | 220.0862 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 121 | 39879845 | 5828 | 139.872 | 5.828 | 6 | 6 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37722016 | 1372 | 235.4152 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 144 | 39885600 | 5755 | 138.12 | 5.755 | 5.7 | 5.7 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37723320 | 1304 | 226.5856 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 39891397 | 5797 | 139.128 | 5.797 | 5.5 | 5.5 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37724680 | 1360 | 234.6041 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 39897115 | 5718 | 137.232 | 5.718 | 5.3 | 5.3 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37726004 | 1324 | 231.5495 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 140 | 39902869 | 5754 | 138.096 | 5.754 | 4.9 | 4.9 | 3B+1S | 0 | 1039 | 1166 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37727316 | 1312 | 228.0153 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 39908515 | 5646 | 135.504 | 5.646 | 4.4 | 4.4 | 3B+1S | 0 | 1039 | 1166 | 1185 | 1169 | N/A | N/A | N/A | N/A | 37728620 | 1304 | 230.96 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 2 | 1.4085 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 127 | 39914049 | 5534 | 132.816 | 5.534 | 4 | 4 | 3B+1S | 0 | 1012 | 1137 | 1185 | 1167 | N/A | N/A | N/A | N/A | 37729916 | 1296 | 234.1887 | 0% | 100% | 100% | 100% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 138 | 128 | 39919318 | 5269 | 126.456 | 5.269 | 3.3 | 3.3 | 2B+1S | 0 | 1072 | 1189 | 0 | 1190 | N/A | N/A | N/A | N/A | 37730988 | 1072 | 203.4542 | 0% | 100% | 100% | 0% | 100% |  | 8502718 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 120 | 39924928 | 5610 | 134.64 | 5.61 | 2.4 | 2.4 | 2B+1S | 0 | 1069 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 37732144 | 1156 | 206.0606 | 0% | 100% | 100% | 0% | 100% |  | 8502718 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 112 | 39929069 | 4141 | 99.384 | 4.141 | 3 | 3 | 2B | 0 | 0 | 1147 | 0 | 1188 | N/A | N/A | N/A | N/A | 37732976 | 832 | 200.9177 | 0% | 0% | 100% | 0% | 100% | 51% | 8503333 | 615 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 108 | 39933158 | 4089 | 98.136 | 4.089 | 3.9 | 3.9 | 2B | 0 | 0 | 1147 | 0 | 1188 | N/A | N/A | N/A | N/A | 37733881 | 905 | 221.3255 | 0% | 0% | 100% | 0% | 100% | 51% | 8504165 | 832 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 127707 | 127707 | 127.707 | 127.707 | [12 empty] | 27461 | 27461 | 215.0313 | [6 empty] | 5834 | 5834 | 5.57 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (55%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MR. ARTURO TRINIDAD AND MAINTENANCE TEAM ARRIVE @ 9:00AM INSPECT AND CHEACK THE LEAK FROM GENSET FLOWMETERS
MR. RUDY, ALAN, QUAMAO ALBERT OF MAKATI FOUNDARY ARRIVE @ 9:20AM TO MEASURE THE ADAPTER REJUCER OF BP4(NEW BOOSTER)
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 10, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. SAMUEL AND ACOSTA OF MAINTENANCE TEAM ARRIVE @ 12:30PM TO PICK UP THE WOOD
MR. RUDY, ANDREW AND ANG GONZALO, OF MAKATI FOUNDARY ARRIVE @ 3:50PM TO MEASURE THE ADAPTER REJUCER OF BP4(NEW BOOSTER)
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (51%)

## JUNE 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMSO / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27395 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 39933158 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37733881 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8504165 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 81 | 39937498 | 4340 | 104.16 | 4.34 | 4.9 | 4.9 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 37734703 | 822 | 189.4009 | 0% | 0% | 100% | 0% | 100% | 65% | 8505049 | 884 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 96 | 39941229 | 3731 | 89.544 | 3.731 | 6 | 6 | 2B | 0 | 0 | 1037 | 0 | 1189 | N/A | N/A | N/A | N/A | 37735449 | 746 | 199.9464 | 0% | 0% | 100% | 0% | 100% | 65% | 8506116 | 1067 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 96 | 39945136 | 3907 | 93.768 | 3.907 | 7.1 | 7.1 | 2B | 0 | 0 | 1037 | 0 | 1189 | N/A | N/A | N/A | N/A | 37736216 | 767 | 196.3143 | 0% | 0% | 100% | 0% | 100% | 65% | 8507180 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 136 | 98 | 39948918 | 3782 | 90.768 | 3.782 | 8.1 | 8.1 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 37736940 | 724 | 191.4331 | 0% | 0% | 100% | 0% | 100% | 65% | 8508121 | 941 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 129 | 101 | 39953436 | 4518 | 108.432 | 4.518 | 9.5 | 9.5 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 37737776 | 836 | 185.0376 | 0% | 0% | 100% | 0% | 100% | 65% | 8508725 | 604 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 103 | 39958038 | 4602 | 110.448 | 4.602 | 9.5 | 9.5 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 37738572 | 796 | 172.9683 | 0% | 0% | 100% | 0% | 100% |  | 8508725 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 156 | 39964091 | 6053 | 145.272 | 6.053 | 8.5 | 8.5 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37739916 | 1344 | 222.0387 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 145 | 39970142 | 6051 | 145.224 | 6.051 | 8 | 8 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37741251 | 1335 | 220.6247 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 137 | 39976527 | 6385 | 153.24 | 6.385 | 7.6 | 7.6 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37742660 | 1409 | 220.6735 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 128 | 39982586 | 6059 | 145.416 | 6.059 | 7.2 | 7.2 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37744016 | 1356 | 223.7993 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 148 | 39988777 | 6191 | 148.584 | 6.191 | 6.8 | 6.8 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37745392 | 1376 | 222.2581 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 143 | 39994730 | 5953 | 142.872 | 5.953 | 6.5 | 6.5 | 3B+1S | 0 | 1010 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37746724 | 1332 | 223.7527 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 149 | 40000770 | 6040 | 144.96 | 6.04 | 6.1 | 6.1 | 3B+1S | 0 | 1032 | 1189 | 1185 | 1190 | N/A | N/A | N/A | N/A | 37748112 | 1388 | 229.8013 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 146 | 40006809 | 6039 | 144.936 | 6.039 | 5.6 | 5.6 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37749516 | 1404 | 232.4888 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 144 | 40012544 | 5735 | 137.64 | 5.735 | 5.2 | 5.2 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37750836 | 1320 | 230.1656 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 40018714 | 6170 | 148.08 | 6.17 | 4.9 | 4.9 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37752244 | 1408 | 228.201 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 40024194 | 5480 | 131.52 | 5.48 | 4.6 | 4.6 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37753528 | 1284 | 234.3066 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 138 | 40029750 | 5556 | 133.344 | 5.556 | 4.5 | 4.5 | 3B+1S | 0 | 976 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37754852 | 1324 | 238.3009 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 134 | 40035294 | 5544 | 133.056 | 5.544 | 4.3 | 4.3 | 3B+1S | 0 | 975 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37756188 | 1336 | 240.9812 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 133 | 40040587 | 5293 | 127.032 | 5.293 | 4 | 4 | 3B+1S | 0 | 975 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37757480 | 1292 | 244.096 | 0% | 100% | 100% | 100% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 131 | 40045660 | 5073 | 121.752 | 5.073 | 3.7 | 3.7 | 2B+1S | 0 | 1110 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37758556 | 1076 | 212.1033 | 0% | 100% | 100% | 0% | 100% |  | 8508725 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 129 | 40050882 | 5222 | 125.328 | 5.222 | 3 | 3 | 2B+1S | 0 | 1109 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37759628 | 1072 | 205.2853 | 0% | 100% | 100% | 0% | 100% |  | 8508725 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 88 | 40054777 | 3895 | 93.48 | 3.895 | 3.5 | 3.5 | 2B | 0 | 0 | 1117 | 0 | 1188 | N/A | N/A | N/A | N/A | 37760436 | 808 | 207.4454 | 0% | 0% | 100% | 0% | 100% | 55% | 8509425 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 102 | 40058928 | 4151 | 99.624 | 4.151 | 4.6 | 4.6 | 2B | 0 | 0 | 1117 | 0 | 1188 | N/A | N/A | N/A | N/A | 37761276 | 840 | 202.3609 | 0% | 0% | 100% | 0% | 100% | 55% | 8510348 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 125770 | 125770 | 125.77 | 125.77 | [12 empty] | 27395 | 27395 | 217.8182 | [6 empty] | 6183 | 6183 | 5.87 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (65%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 11, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (55%)

## JUNE 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMSO / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27392 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40058928 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37761276 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8510348 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 96 | 40063159 | 4231 | 101.544 | 4.231 | 5.6 | 5.6 | 2B | 0 | 0 | 1056 | 0 | 1187 | N/A | N/A | N/A | N/A | 37762136 | 860 | 203.2616 | 0% | 0% | 100% | 0% | 100% | 70% | 8511305 | 957 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 40066728 | 3569 | 85.656 | 3.569 | 6.6 | 6.6 | 2B | 0 | 0 | 1056 | 0 | 1188 | N/A | N/A | N/A | N/A | 37762860 | 724 | 202.8579 | 0% | 0% | 100% | 0% | 100% | 70% | 8512337 | 1032 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 40070589 | 3861 | 92.664 | 3.861 | 7.7 | 7.7 | 2B | 0 | 0 | 1056 | 0 | 1187 | N/A | N/A | N/A | N/A | 37763629 | 769 | 199.1712 | 0% | 0% | 100% | 0% | 100% | 70% | 8513374 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 131 | 97 | 40074358 | 3769 | 90.456 | 3.769 | 8.7 | 8.7 | 2B | 0 | 0 | 1016 | 0 | 1158 | N/A | N/A | N/A | N/A | 37764356 | 727 | 192.8894 | 0% | 0% | 100% | 0% | 100% | 70% | 8514360 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 120 | 106 | 40078226 | 3868 | 92.832 | 3.868 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1158 | N/A | N/A | N/A | N/A | 37765060 | 704 | 182.0062 | 0% | 0% | 100% | 0% | 100% | 70% | 8514968 | 608 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 126 | 40082914 | 4688 | 112.512 | 4.688 | 9.5 | 9.5 | 2B | 0 | 0 | 1189 | 0 | 1188 | N/A | N/A | N/A | N/A | 37765876 | 816 | 174.0614 | 0% | 0% | 100% | 0% | 100% |  | 8514968 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 150 | 40089071 | 6157 | 147.768 | 6.157 | 9.1 | 9.1 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37767244 | 1368 | 222.1861 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 165 | 40095413 | 6342 | 152.208 | 6.342 | 8.6 | 8.6 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37768628 | 1384 | 218.2277 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 159 | 40101574 | 6161 | 147.864 | 6.161 | 8.2 | 8.2 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37770014 | 1386 | 224.9635 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 40107703 | 6129 | 147.096 | 6.129 | 7.7 | 7.7 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37771372 | 1358 | 221.5696 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 152 | 40113907 | 6204 | 148.896 | 6.204 | 7.2 | 7.2 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37772748 | 1376 | 221.7924 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 150 | 40119940 | 6033 | 144.792 | 6.033 | 6.8 | 6.8 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37774104 | 1356 | 224.7638 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 40125827 | 5887 | 141.288 | 5.887 | 6.4 | 6.4 | 3B+1S | 0 | 1018 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37775456 | 1352 | 229.6586 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 165 | 40131592 | 5765 | 138.36 | 5.765 | 6 | 6 | 3B+1S | 0 | 1016 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37776810 | 1354 | 234.8656 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 40137357 | 5765 | 138.36 | 5.765 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37778164 | 1354 | 234.8656 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 40143039 | 5682 | 136.368 | 5.682 | 5.5 | 5.5 | 3B+1S | 0 | 1016 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37779496 | 1332 | 234.4245 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 40148721 | 5682 | 136.368 | 5.682 | 5.1 | 5.1 | 3B+1S | 0 | 1017 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37780828 | 1332 | 234.4245 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 138 | 40154366 | 5645 | 135.48 | 5.645 | 4.8 | 4.8 | 3B+1S | 0 | 984 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37782144 | 1316 | 233.1267 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 138 | 40159933 | 5567 | 133.608 | 5.567 | 4.7 | 4.7 | 3B+1S | 0 | 986 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37783468 | 1324 | 237.8301 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 135 | 40165538 | 5605 | 134.52 | 5.605 | 4.6 | 4.6 | 3B+1S | 0 | 986 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37784812 | 1344 | 239.7859 | 0% | 100% | 100% | 100% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 136 | 40170834 | 5296 | 127.104 | 5.296 | 3.7 | 3.7 | 2B+1S | 0 | 1119 | 1189 | 0 | 1188 | N/A | N/A | N/A | N/A | 37785920 | 1108 | 209.2145 | 0% | 100% | 100% | 0% | 100% |  | 8514968 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 149 | 40175986 | 5152 | 123.648 | 5.152 | 2.9 | 2.9 | 2B+1S | 0 | 1119 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37786968 | 1048 | 203.4161 | 0% | 100% | 0% | 100% | 100% |  | 8514968 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 104 | 40180300 | 4314 | 103.536 | 4.314 | 3.4 | 3.4 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 37787895 | 927 | 214.8818 | 0% | 0% | 100% | 100% | 0% | 55% | 8515620 | 652 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 104 | 40184264 | 3964 | 95.136 | 3.964 | 4.3 | 4.3 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 37788668 | 773 | 195.005 | 0% | 0% | 100% | 100% | 0% | 55% | 8516414 | 794 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 125336 | 125336 | 125.336 | 125.336 | [12 empty] | 27392 | 27392 | 218.5485 | [6 empty] | 6066 | 6066 | 5.89 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 12, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
monthly preventive maintenance of all units.
TARGET DISCHARGE PRESSURE SET TO 66 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)
BP1 - STARTED @ 9:29 PM / BP1 - STOPPED @ 10:56 PM
BP2 - STARTED @ 9:28 PM / STOPPED @ 2:10AM
BP3 - STOPPED @ 11:01 PM / RE-STARTED @ 2:11AM

## JUNE 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28236 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40184264 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37788668 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8516414 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 96 | 40188438 | 4174 | 100.176 | 4.174 | 5 | 5 | 2B | 0 | 0 | 1118 | 1185 | 0 | N/A | N/A | N/A | N/A | 37789492 | 824 | 197.4126 | 0% | 0% | 100% | 100% | 0% | 70% | 8517159 | 745 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 105 | 40192552 | 4114 | 98.736 | 4.114 | 5.9 | 5.9 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 37790320 | 828 | 201.264 | 0% | 0% | 100% | 100% | 0% | 70% | 8518030 | 871 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 96 | 40196525 | 3973 | 95.352 | 3.973 | 6.9 | 6.9 | 2B | 0 | 0 | 1117 | 0 | 1188 | N/A | N/A | N/A | N/A | 37791156 | 836 | 210.4203 | 0% | 0% | 100% | 0% | 100% | 70% | 8518972 | 942 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMSO / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 135 | 86 | 40200165 | 3640 | 87.36 | 3.64 | 8.1 | 8.1 | 2B | 0 | 0 | 996 | 0 | 1188 | N/A | N/A | N/A | N/A | 37791892 | 736 | 202.1978 | 0% | 0% | 100% | 0% | 100% | 70% | 8520153 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 144 | 91 | 40203869 | 3704 | 88.896 | 3.704 | 9.5 | 9.5 | 2B | 0 | 0 | 996 | 0 | 1188 | N/A | N/A | N/A | N/A | 37792628 | 736 | 198.7041 | 0% | 0% | 100% | 0% | 100% | 70% | 8521263 | 1110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 127 | 40208319 | 4450 | 106.8 | 4.45 | 9.5 | 9.5 | 2B | 0 | 0 | 1189 | 0 | 1188 | N/A | N/A | N/A | N/A | 37793444 | 816 | 183.3708 | 0% | 0% | 100% | 0% | 100% |  | 8521263 | 0 | 0.81 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 143 | 40214225 | 5906 | 141.744 | 5.906 | 9.5 | 9.5 | 3B+1S | 0 | 1020 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37794756 | 1312 | 222.147 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 151 | 40220437 | 6212 | 149.088 | 6.212 | 9.2 | 9.2 | 3B+1S | 0 | 1020 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37796140 | 1384 | 222.7946 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 156 | 40226633 | 6196 | 148.704 | 6.196 | 8.7 | 8.7 | 3B+1S | 0 | 1020 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37797516 | 1376 | 222.0788 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 153 | 40233007 | 6374 | 152.976 | 6.374 | 8 | 8 | 3B+1S | 0 | 1060 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37798932 | 1416 | 222.1525 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 129 | 40239218 | 6211 | 149.064 | 6.211 | 7.3 | 7.3 | 3B+1S | 0 | 1060 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37800320 | 1388 | 223.4745 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 148 | 40245422 | 6204 | 148.896 | 6.204 | 6.8 | 6.8 | 3B+1S | 0 | 1030 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37801720 | 1400 | 225.6609 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 158 | 40251402 | 5980 | 143.52 | 5.98 | 6.2 | 6.2 | 3B+1S | 0 | 1050 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37803044 | 1324 | 221.4047 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 146 | 40257312 | 5910 | 141.84 | 5.91 | 5.7 | 5.7 | 3B+1S | 0 | 1060 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37804466 | 1422 | 240.6091 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 144 | 40263222 | 5910 | 141.84 | 5.91 | 4.9 | 4.9 | 3B+1S | 0 | 1129 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37805888 | 1422 | 240.6091 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 40269062 | 5840 | 140.16 | 5.84 | 3.9 | 3.9 | 3B+1S | 0 | 1068 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37807300 | 1412 | 241.7808 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 40274771 | 5709 | 137.016 | 5.709 | 3.3 | 3.3 | 3B+1S | 0 | 1068 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37808668 | 1368 | 239.6217 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 140 | 40280592 | 5821 | 139.704 | 5.821 | 2.8 | 2.8 | 3B+1S | 0 | 1069 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37810060 | 1392 | 239.1342 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 144 | 40286415 | 5823 | 139.752 | 5.823 | 2.4 | 2.4 | 3B+1S | 0 | 1069 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37811432 | 1372 | 235.6174 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 130 | 40291857 | 5442 | 130.608 | 5.442 | 2.2 | 2.2 | 3B+1S | 0 | 1005 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37812740 | 1308 | 240.3528 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 141 | 132 | 40297120 | 5263 | 126.312 | 5.263 | 2.1 | 2.1 | 3B+1S | 0 | 1005 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37814063 | 1323 | 251.3775 | 0% | 100% | 100% | 100% | 100% |  | 8521263 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 123 | 40302315 | 5195 | 124.68 | 5.195 | 1.5 | 1.5 | 2B+1S | 0 | 1098 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37815084 | 1021 | 196.5351 | 0% | 100% | 100% | 0% | 100% |  | 8521263 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 147 | 113 | 40306683 | 4368 | 104.832 | 4.368 | 2.3 | 2.3 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37815988 | 904 | 206.9597 | 0% | 0% | 100% | 0% | 100% | 55% | 8522549 | 1286 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 148 | 102 | 40311214 | 4531 | 108.744 | 4.531 | 3.6 | 3.6 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37816904 | 916 | 202.1629 | 0% | 0% | 100% | 0% | 100% | 55% | 8523783 | 1234 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 126950 | 126950 | 126.95 | 126.95 | [12 empty] | 28236 | 28236 | 222.4183 | [6 empty] | 7369 | 7369 | 5.68 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:37 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 13, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (55%)

## JUNE 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28564 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40311214 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37816904 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8523783 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 133 | 105 | 40315564 | 4350 | 104.4 | 4.35 | 4.6 | 4.6 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37817816 | 912 | 209.6552 | 0% | 0% | 100% | 0% | 100% | 70% | 8524544 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 135 | 106 | 40319872 | 4308 | 103.392 | 4.308 | 5.6 | 5.6 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37818732 | 916 | 212.6277 | 0% | 0% | 100% | 0% | 100% | 70% | 8525525 | 981 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 131 | 104 | 40324284 | 4412 | 105.888 | 4.412 | 7.4 | 7.4 | 2B | 0 | 0 | 1107 | 0 | 1187 | N/A | N/A | N/A | N/A | 37819676 | 944 | 213.9619 | 0% | 0% | 100% | 0% | 100% | 70% | 8526818 | 1293 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 118 | 95 | 40327827 | 3543 | 85.032 | 3.543 | 7.7 | 7.7 | 2B | 0 | 0 | 1108 | 0 | 1187 | N/A | N/A | N/A | N/A | 37820388 | 712 | 200.9596 | 0% | 0% | 100% | 0% | 100% | 70% | 8527703 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 144 | 82 | 40331786 | 3959 | 95.016 | 3.959 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1187 | N/A | N/A | N/A | N/A | 37821188 | 800 | 202.0712 | 0% | 0% | 100% | 0% | 100% | 70% | 8528260 | 557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 113 | 40336104 | 4318 | 103.632 | 4.318 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1187 | N/A | N/A | N/A | N/A | 37822012 | 824 | 190.8291 | 0% | 0% | 100% | 0% | 100% |  | 8528260 | 0 | 0.87 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 152 | 40342134 | 6030 | 144.72 | 6.03 | 8.6 | 8.6 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37823372 | 1360 | 225.539 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 148 | 40348351 | 6217 | 149.208 | 6.217 | 8.2 | 8.2 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37824748 | 1376 | 221.3286 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 140 | 40354436 | 6085 | 146.04 | 6.085 | 7.8 | 7.8 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37826112 | 1364 | 224.1578 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 153 | 40360656 | 6220 | 149.28 | 6.22 | 7.3 | 7.3 | 3B+1S | 0 | 1040 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37827511 | 1399 | 224.9196 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 148 | 146 | 40366800 | 6144 | 147.456 | 6.144 | 6.8 | 6.8 | 3B+1S | 0 | 1040 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37828992 | 1481 | 241.0482 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 158 | 40373020 | 6220 | 149.28 | 6.22 | 6.3 | 6.3 | 3B+1S | 0 | 1040 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37830292 | 1300 | 209.0032 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 150 | 40379030 | 6010 | 144.24 | 6.01 | 5.7 | 5.7 | 3B+1S | 0 | 1060 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37831654 | 1362 | 226.6223 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 149 | 40385094 | 6064 | 145.536 | 6.064 | 4.9 | 4.9 | 3B+1S | 0 | 1059 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37833116 | 1462 | 241.095 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 40390825 | 5731 | 137.544 | 5.731 | 4.4 | 4.4 | 3B+1S | 0 | 1059 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37834444 | 1328 | 231.7222 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 40396623 | 5798 | 139.152 | 5.798 | 3.7 | 3.7 | 3B+1S | 0 | 1059 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37835824 | 1380 | 238.0131 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 40402422 | 5799 | 139.176 | 5.799 | 3 | 3 | 3B+1S | 0 | 1109 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37837204 | 1380 | 237.9721 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 133 | 40408177 | 5755 | 138.12 | 5.755 | 2.6 | 2.6 | 3B+1S | 0 | 1037 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37838580 | 1376 | 239.0964 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 40413794 | 5617 | 134.808 | 5.617 | 2.3 | 2.3 | 3B+1S | 0 | 1037 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37839920 | 1340 | 238.5615 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 135 | 40419411 | 5617 | 134.808 | 5.617 | 2 | 2 | 3B+1S | 0 | 1038 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37841260 | 1340 | 238.5615 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 140 | 130 | 40424740 | 5329 | 127.896 | 5.329 | 1.9 | 1.9 | 3B+1S | 0 | 1039 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37842564 | 1304 | 244.6988 | 0% | 100% | 100% | 100% | 100% |  | 8528260 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 138 | 115 | 40429911 | 5171 | 124.104 | 5.171 | 1.3 | 1.3 | 2B+1S | 0 | 996 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37843684 | 1120 | 216.5925 | 0% | 100% | 100% | 0% | 100% |  | 8528260 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 145 | 123 | 40433976 | 4065 | 97.56 | 4.065 | 2.1 | 2.1 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37844556 | 872 | 214.5141 | 0% | 0% | 100% | 0% | 100% | 50% | 8529714 | 1454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 141 | 112 | 40438251 | 4275 | 102.6 | 4.275 | 31 | 31 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 37845468 | 912 | 213.3333 | 0% | 0% | 100% | 0% | 100% | 50% | 8530736 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 127037 | 127037 | 127.037 | 127.037 | [12 empty] | 28564 | 28564 | 224.8479 | [6 empty] | 6953 | 6953 | 5.73 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 14, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JUNE 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / A.DELOS ANGELES
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40438251 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37845468 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8530736 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 137 | 103 | 40442565 | 4314 | 103.536 | 4.314 | 4.2 | 4.2 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37846380 | 912 | 211.4047 | 0% | 0% | 100% | 0% | 100% | 70% | 8531656 | 920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 137 | 105 | 40446877 | 4312 | 103.488 | 4.312 | 5.4 | 5.4 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37847280 | 900 | 208.7199 | 0% | 0% | 100% | 0% | 100% | 70% | 8532798 | 1142 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 137 | 87 | 40451085 | 4208 | 100.992 | 4.208 | 6.5 | 6.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37848184 | 904 | 214.8289 | 0% | 0% | 100% | 0% | 100% | 70% | 8533878 | 1080 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 130 | 96 | 40454941 | 3856 | 92.544 | 3.856 | 7.9 | 7.9 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 37848969 | 785 | 203.5788 | 0% | 0% | 100% | 0% | 100% | 70% | 8535120 | 1242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 12 | 8.4507 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 141 | 100 | 40458655 | 3714 | 89.136 | 3.714 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 37849756 | 787 | 211.9009 | 0% | 0% | 100% | 0% | 100% | 70% | 8536087 | 967 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 117 | 40463202 | 4547 | 109.128 | 4.547 | 9.5 | 9.5 | 2B | 0 | 0 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37850600 | 844 | 185.6169 | 0% | 0% | 100% | 100% | 100% |  | 8536087 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 139 | 40468838 | 5636 | 135.264 | 5.636 | 9.5 | 9.5 | 3B | 0 | 0 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37851860 | 1260 | 223.5628 | 0% | 0% | 100% | 100% | 100% |  | 8536087 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 145 | 40474834 | 5996 | 143.904 | 5.996 | 9.4 | 9.4 | 3B+1S | 0 | 1020 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37853224 | 1364 | 227.485 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 155 | 40480715 | 5881 | 141.144 | 5.881 | 8.8 | 8.8 | 3B+1S | 0 | 1040 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37854592 | 1368 | 232.6135 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 40486683 | 5968 | 143.232 | 5.968 | 8.2 | 8.2 | 3B+1S | 0 | 1040 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37855972 | 1380 | 231.2332 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 117 | 40492744 | 6061 | 145.464 | 6.061 | 7.7 | 7.7 | 3B+1S | 0 | 1040 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37857354 | 1382 | 228.0152 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 141 | 40498830 | 6086 | 146.064 | 6.086 | 7.2 | 7.2 | 3B+1S | 0 | 1030 | 1189 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37858740 | 1386 | 227.7358 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 40504666 | 5836 | 140.064 | 5.836 | 6.8 | 6.8 | 3B+1S | 0 | 1050 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37860114 | 1374 | 235.4352 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 40510490 | 5824 | 139.776 | 5.824 | 6.1 | 6.1 | 3B+1S | 0 | 1048 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37861576 | 1462 | 251.0302 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 142 | 40516229 | 5739 | 137.736 | 5.739 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37862904 | 1328 | 231.3992 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 40521968 | 5739 | 137.736 | 5.739 | 5.1 | 5.1 | 3B+1S | 0 | 1047 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37864232 | 1328 | 231.3992 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 144 | 40527567 | 5599 | 134.376 | 5.599 | 4.6 | 4.6 | 3B+1S | 0 | 1047 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37865566 | 1334 | 238.2568 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 134 | 40533166 | 5599 | 134.376 | 5.599 | 4.4 | 4.4 | 3B+1S | 0 | 996 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37866900 | 1334 | 238.2568 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 120 | 40538742 | 5576 | 133.824 | 5.576 | 4.2 | 4.2 | 3B+1S | 0 | 996 | 1189 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37868232 | 1332 | 238.8809 | 0% | 100% | 100% | 100% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 120 | 40544061 | 5319 | 127.656 | 5.319 | 3.3 | 3.3 | 2B+1S | 0 | 1131 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37869348 | 1116 | 209.8139 | 0% | 100% | 100% | 0% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 135 | 40549360 | 5299 | 127.176 | 5.299 | 2.4 | 2.4 | 2B+1S | 0 | 1071 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 37870460 | 1112 | 209.8509 | 0% | 100% | 100% | 0% | 100% |  | 8536087 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 117 | 40554378 | 5018 | 120.432 | 5.018 | 1.8 | 1.8 | 2B+1S | 0 | 1078 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37871496 | 1036 | 206.4568 | 0% | 100% | 100% | 0% | 100% |  | 8536087 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 142 | 111 | 40558286 | 3908 | 93.792 | 3.908 | 2.5 | 2.5 | 2B | 0 | 0 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 37872428 | 932 | 238.4852 | 0% | 0% | 100% | 0% | 100% | 55% | 8537630 | 1543 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 143 | 83 | 40562218 | 3932 | 94.368 | 3.932 | 3.7 | 3.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37873328 | 900 | 228.8911 | 0% | 0% | 100% | 0% | 100% | 55% | 8538759 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 123967 | 123967 | 123.967 | 123.967 | [12 empty] | 27860 | 27860 | 224.7372 | [6 empty] | 8023 | 8023 | 5.7 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:16 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 15, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (55%)

## JUNE 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28128 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40562218 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37873328 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8538759 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 139 | 93 | 40566508 | 4290 | 102.96 | 4.29 | 5 | 5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37874264 | 936 | 218.1818 | 0% | 0% | 100% | 0% | 100% | 70% | 8539896 | 1137 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 137 | 96 | 40570409 | 3901 | 93.624 | 3.901 | 6.4 | 6.4 | 2B | 0 | 0 | 1086 | 0 | 1188 | N/A | N/A | N/A | N/A | 37875080 | 816 | 209.1771 | 0% | 0% | 100% | 0% | 100% | 70% | 8541296 | 1400 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 135 | 98 | 40574218 | 3809 | 91.416 | 3.809 | 7.8 | 7.8 | 2B | 0 | 0 | 1087 | 0 | 1188 | N/A | N/A | N/A | N/A | 37875884 | 804 | 211.079 | 0% | 0% | 100% | 0% | 100% | 70% | 8542597 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 134 | 136 | 40578107 | 3889 | 93.336 | 3.889 | 9.1 | 9.1 | 2B | 0 | 0 | 1086 | 0 | 1188 | N/A | N/A | N/A | N/A | 37876676 | 792 | 203.6513 | 0% | 0% | 100% | 0% | 100% | 70% | 8543771 | 1174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 12 | 8.4507 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 116 | 83 | 40582246 | 4139 | 99.336 | 4.139 | 9.5 | 9.5 | 2B | 0 | 0 | 1088 | 0 | 1188 | N/A | N/A | N/A | N/A | 37877484 | 808 | 195.2162 | 0% | 0% | 100% | 0% | 100% | 70% | 8544207 | 436 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 117 | 40587027 | 4781 | 114.744 | 4.781 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37878368 | 884 | 184.8986 | 0% | 0% | 100% | 0% | 100% | 0% | 8544207 | 0 | 0.9 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 151 | 40593105 | 6078 | 145.872 | 6.078 | 9 | 9 | 3B+1S | 0 | 1070 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37879760 | 1392 | 229.0227 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 133 | 40599104 | 5999 | 143.976 | 5.999 | 8.4 | 8.4 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37881156 | 1396 | 232.7055 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 148 | 40605125 | 6021 | 144.504 | 6.021 | 7.9 | 7.9 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37882552 | 1396 | 231.8552 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 153 | 40611095 | 5970 | 143.28 | 5.97 | 7.4 | 7.4 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37883916 | 1364 | 228.4757 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 144 | 40617030 | 5935 | 142.44 | 5.935 | 6.9 | 6.9 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37885268 | 1352 | 227.8012 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 138 | 40623221 | 6191 | 148.584 | 6.191 | 6.5 | 6.5 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37886688 | 1420 | 229.3652 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 135 | 40628920 | 5699 | 136.776 | 5.699 | 6.1 | 6.1 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37888020 | 1332 | 233.7252 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 135 | 40634401 | 5481 | 131.544 | 5.481 | 5.6 | 5.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37889364 | 1344 | 245.2107 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 143 | 40640105 | 5704 | 136.896 | 5.704 | 5.2 | 5.2 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37890716 | 1352 | 237.0266 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 40645695 | 5590 | 134.16 | 5.59 | 4.9 | 4.9 | 3B+1S | 0 | 1029 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37892052 | 1336 | 238.9982 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 40651271 | 5576 | 133.824 | 5.576 | 4.5 | 4.5 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37893402 | 1350 | 242.109 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 137 | 40656847 | 5576 | 133.824 | 5.576 | 4.1 | 4.1 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37894752 | 1350 | 242.109 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 143 | 40662399 | 5552 | 133.248 | 5.552 | 3.6 | 3.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37896092 | 1340 | 241.3545 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 142 | 40668003 | 5604 | 134.496 | 5.604 | 3.3 | 3.3 | 2B+1S | 0 | 1027 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37897444 | 1352 | 241.2562 | 0% | 100% | 100% | 100% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 133 | 40673131 | 5128 | 123.072 | 5.128 | 3.2 | 3.2 | 2B+1S | 0 | 1117 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37898540 | 1096 | 213.7285 | 0% | 100% | 100% | 0% | 100% | 0% | 8544207 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 128 | 40678260 | 5129 | 123.096 | 5.129 | 1.7 | 1.7 | 2B+1S | 0 | 1119 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37899636 | 1096 | 213.6869 | 0% | 100% | 100% | 0% | 100% | 0% | 8544207 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 140 | 110 | 40682361 | 4101 | 98.424 | 4.101 | 2.4 | 2.4 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37900552 | 916 | 223.3602 | 0% | 0% | 100% | 0% | 100% | 50% | 8545133 | 926 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 146 | 120 | 40686130 | 3769 | 90.456 | 3.769 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1189 | N/A | N/A | N/A | N/A | 37901456 | 904 | 239.8514 | 0% | 0% | 100% | 0% | 100% | 50% | 8546059 | 926 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 123912 | 123912 | 123.912 | 123.912 | [12 empty] | 28128 | 28128 | 226.9998 | [6 empty] | 7300 | 7300 | 5.82 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 16, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
GENSET 1&2 WARM UP EXERCISE W/O LOAD FOR 10MINS ONLY, FUEL CONSUMPTION = 13LITERS / FUEL STOCKS = 10,721 LITERS
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JUNE 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28628 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40686130 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37901456 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8546059 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 130 | 104 | 40690029 | 3899 | 93.576 | 3.899 | 5.1 | 5.1 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 37902293 | 837 | 214.6704 | 0% | 0% | 100% | 0% | 100% | 65% | 8547213 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 129 | 95 | 40693930 | 3901 | 93.624 | 3.901 | 6.3 | 6.3 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 37903149 | 856 | 219.4309 | 0% | 0% | 100% | 0% | 100% | 65% | 8548368 | 1155 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 126 | 90 | 40697826 | 3896 | 93.504 | 3.896 | 7.8 | 7.8 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 37903970 | 821 | 210.729 | 0% | 0% | 100% | 0% | 100% | 65% | 8549504 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 124 | 98 | 40701729 | 3903 | 93.672 | 3.903 | 8 | 8 | 2B | 0 | 0 | 1128 | 0 | 1107 | N/A | N/A | N/A | N/A | 37904804 | 834 | 213.6818 | 0% | 0% | 100% | 0% | 100% | 75% | 8550678 | 1174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 133 | 108 | 40705699 | 3970 | 95.28 | 3.97 | 8.8 | 8.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37905636 | 832 | 209.5718 | 0% | 0% | 100% | 0% | 100% | 75% | 8550816 | 138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 145 | 114 | 40710887 | 5188 | 124.512 | 5.188 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37906892 | 1256 | 242.0971 | 0% | 0% | 100% | 100% | 100% | 0% | 8550816 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 148 | 40716649 | 5762 | 138.288 | 5.762 | 8.8 | 8.8 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37908260 | 1368 | 237.4176 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 40722451 | 5802 | 139.248 | 5.802 | 8.2 | 8.2 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37909652 | 1392 | 239.9173 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 138 | 40728135 | 5684 | 136.416 | 5.684 | 7.7 | 7.7 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37911024 | 1372 | 241.3793 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 139 | 40733981 | 5846 | 140.304 | 5.846 | 7.2 | 7.2 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37912424 | 1400 | 239.48 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 120 | 40739798 | 5817 | 139.608 | 5.817 | 6.7 | 6.7 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37913796 | 1372 | 235.8604 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 130 | 40745455 | 5657 | 135.768 | 5.657 | 6.3 | 6.3 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 37915160 | 1364 | 241.1172 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 118 | 40751204 | 5749 | 137.976 | 5.749 | 6 | 6 | 3B+1S | 0 | 1030 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37916520 | 1360 | 236.5629 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 141 | 40756826 | 5622 | 134.928 | 5.622 | 5.5 | 5.5 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37917896 | 1376 | 244.7528 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 142 | 40762493 | 5667 | 136.008 | 5.667 | 5.2 | 5.2 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37919244 | 1348 | 237.8684 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 147 | 40768007 | 5514 | 132.336 | 5.514 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37920576 | 1332 | 241.5669 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 40773561 | 5554 | 133.296 | 5.554 | 4.6 | 4.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37921924 | 1348 | 242.708 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 134 | 40779116 | 5555 | 133.32 | 5.555 | 4.1 | 4.1 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37923272 | 1348 | 242.6643 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 141 | 130 | 40784897 | 5781 | 138.744 | 5.781 | 3.7 | 3.7 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37924620 | 1348 | 233.1777 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 135 | 40790123 | 5226 | 125.424 | 5.226 | 3.6 | 3.6 | 3B+1S | 0 | 977 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37925932 | 1312 | 251.0524 | 0% | 100% | 100% | 100% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 144 | 40795404 | 5281 | 126.744 | 5.281 | 2.8 | 2.8 | 2B+1S | 0 | 1129 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37927060 | 1128 | 213.5959 | 0% | 100% | 100% | 0% | 100% | 0% | 8550816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 121 | 40800484 | 5080 | 121.92 | 5.08 | 2 | 2 | 2B+1S | 0 | 1129 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37928172 | 1112 | 218.8976 | 0% | 100% | 100% | 0% | 100% | 0% | 8550816 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 104 | 40804254 | 3770 | 90.48 | 3.77 | 2.6 | 2.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37929096 | 924 | 245.0928 | 0% | 0% | 100% | 0% | 100% | 50% | 8551721 | 905 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 96 | 40808728 | 4474 | 107.376 | 4.474 | 3.8 | 3.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37930084 | 988 | 220.8315 | 0% | 0% | 100% | 0% | 100% | 50% | 8552627 | 906 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 122598 | 122598 | 122.598 | 122.598 | [12 empty] | 28628 | 28628 | 233.5112 | [6 empty] | 6568 | 6568 | 5.87 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (65%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:39 AM,WATER ELEVATION (8.5M)
XCV4 -OPENED @ 4:40AM / CLOSED @ 5:40 AM (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 5:01AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 17, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JUNE 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28656 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40808728 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37930084 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8552627 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 131 | 98 | 40812906 | 4178 | 100.272 | 4.178 | 4.6 | 4.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37930985 | 901 | 215.6534 | 0% | 0% | 100% | 0% | 100% | 65% | 8553426 | 799 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 130 | 100 | 40817091 | 4185 | 100.44 | 4.185 | 5.5 | 5.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37931905 | 920 | 219.8327 | 0% | 0% | 100% | 0% | 100% | 65% | 8554228 | 802 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 132 | 111 | 40821263 | 4172 | 100.128 | 4.172 | 6.4 | 6.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37932788 | 883 | 211.6491 | 0% | 0% | 100% | 0% | 100% | 75% | 8555024 | 796 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 114 | 104 | 40825371 | 4108 | 98.592 | 4.108 | 7 | 7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37933644 | 856 | 208.3739 | 0% | 0% | 100% | 0% | 100% | 75% | 8555604 | 580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 137 | 104 | 40829323 | 3952 | 94.848 | 3.952 | 7.9 | 7.9 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37934600 | 956 | 241.9028 | 0% | 0% | 100% | 0% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 146 | 121 | 40834277 | 4954 | 118.896 | 4.954 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37935900 | 1300 | 262.4142 | 0% | 0% | 100% | 100% | 100% | 0% | 8555604 | 0 | 0.92 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 131 | 40840049 | 5772 | 138.528 | 5.772 | 9 | 9 | 3B+1S | 0 | 1020 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37937260 | 1360 | 235.6202 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 131 | 40846133 | 6084 | 146.016 | 6.084 | 8.1 | 8.1 | 3B+1S | 0 | 1020 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37938636 | 1376 | 226.167 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 140 | 40852127 | 5994 | 143.856 | 5.994 | 7.5 | 7.5 | 3B+1S | 0 | 1020 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37940012 | 1376 | 229.5629 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 40858077 | 5950 | 142.8 | 5.95 | 7.1 | 7.1 | 3B+1S | 0 | 1020 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37941341 | 1329 | 223.3613 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 147 | 152 | 40863951 | 5874 | 140.976 | 5.874 | 6.7 | 6.7 | 3B+1S | 0 | 1020 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37942740 | 1399 | 238.1682 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 146 | 40869868 | 5917 | 142.008 | 5.917 | 6.3 | 6.3 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37944116 | 1376 | 232.5503 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 136 | 40875620 | 5752 | 138.048 | 5.752 | 5.9 | 5.9 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37945456 | 1340 | 232.9624 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 142 | 40881281 | 5661 | 135.864 | 5.661 | 5.5 | 5.5 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37946804 | 1348 | 238.1205 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 139 | 40886919 | 5638 | 135.312 | 5.638 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37948132 | 1328 | 235.5445 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 126 | 40892475 | 5556 | 133.344 | 5.556 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37949460 | 1328 | 239.0209 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 40897996 | 5521 | 132.504 | 5.521 | 4.7 | 4.7 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37950792 | 1332 | 241.2606 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 135 | 40903405 | 5409 | 129.816 | 5.409 | 4.5 | 4.5 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37952134 | 1342 | 248.105 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 40908639 | 5234 | 125.616 | 5.234 | 4.2 | 4.2 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37953444 | 1310 | 250.2866 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 133 | 40914033 | 5394 | 129.456 | 5.394 | 4 | 4 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37954764 | 1320 | 244.7164 | 0% | 100% | 100% | 100% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 156 | 40919193 | 5160 | 123.84 | 5.16 | 3.2 | 3.2 | 2B+1S | 0 | 1099 | 1197 | 0 | 1188 | N/A | N/A | N/A | N/A | 37955860 | 1096 | 212.4031 | 0% | 100% | 100% | 0% | 100% | 0% | 8555604 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 124 | 40924178 | 4985 | 119.64 | 4.985 | 2.5 | 2.5 | 2B+1S | 0 | 1098 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37956908 | 1048 | 210.2307 | 0% | 100% | 100% | 0% | 100% | 0% | 8555604 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 143 | 111 | 40928319 | 4141 | 99.384 | 4.141 | 2.9 | 2.9 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37957844 | 936 | 226.0324 | 0% | 0% | 100% | 0% | 100% | 65% | 8556187 | 583 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 146 | 110 | 40932653 | 4334 | 104.016 | 4.334 | 4.2 | 4.2 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37958740 | 896 | 206.7374 | 0% | 0% | 100% | 0% | 100% | 65% | 8557283 | 1096 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 123925 | 123925 | 123.925 | 123.925 | [12 empty] | 28656 | 28656 | 231.2366 | [6 empty] | 4656 | 4656 | 5.89 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (65%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:56 AM,WATER ELEVATION (7.5M)
XCV4 -OPENED @ 4:00AM / CLOSED @ 5:40 AM (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 5:01AM TO MEET 75 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27760 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 40932653 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37958740 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8557283 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 139 | 131 | 40937208 | 4555 | 109.32 | 4.555 | 5.2 | 5.2 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37959692 | 952 | 209.0011 | 0% | 0% | 100% | 0% | 100% | 75% | 8558294 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 139 | 109 | 40941318 | 4110 | 98.64 | 4.11 | 6.3 | 6.3 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 37960564 | 872 | 212.1655 | 0% | 0% | 100% | 0% | 100% | 75% | 8559308 | 1014 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 134 | 98 | 40945176 | 3858 | 92.592 | 3.858 | 7.6 | 7.6 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 37961376 | 812 | 210.4717 | 0% | 0% | 100% | 0% | 100% | 75% | 8560627 | 1319 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 122 | 107 | 40948925 | 3749 | 89.976 | 3.749 | 8.7 | 8.7 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 37962132 | 756 | 201.6538 | 0% | 0% | 100% | 0% | 100% | 75% | 8561515 | 888 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 116 | 111 | 40952773 | 3848 | 92.352 | 3.848 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 37962932 | 800 | 207.9002 | 0% | 0% | 100% | 0% | 100% | 75% | 8561815 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 110 | 40957163 | 4390 | 105.36 | 4.39 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37963868 | 936 | 213.2118 | 0% | 0% | 100% | 0% | 100% | 0% | 8561815 | 0 | 1.06 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 40963031 | 5868 | 140.832 | 5.868 | 8.3 | 8.3 | 3B+1S | 0 | 1099 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37965260 | 1392 | 237.2188 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 131 | 40969032 | 6001 | 144.024 | 6.001 | 7.7 | 7.7 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37966660 | 1400 | 233.2945 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 150 | 40975026 | 5994 | 143.856 | 5.994 | 7.1 | 7.1 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37968032 | 1372 | 228.8956 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 149 | 40981021 | 5995 | 143.88 | 5.995 | 6.6 | 6.6 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37969404 | 1372 | 228.8574 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 145 | 40986830 | 5809 | 139.416 | 5.809 | 6.3 | 6.3 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37970728 | 1324 | 227.9222 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 145 | 40992762 | 5932 | 142.368 | 5.932 | 6.1 | 6.1 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37972108 | 1380 | 232.6365 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 147 | 40998508 | 5746 | 137.904 | 5.746 | 6 | 6 | 3B+1S | 0 | 975 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37973412 | 1304 | 226.9405 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 130 | 41004063 | 5555 | 133.32 | 5.555 | 5.8 | 5.8 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37974780 | 1368 | 246.2646 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 133 | 41009473 | 5410 | 129.84 | 5.41 | 5.5 | 5.5 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37976092 | 1312 | 242.5139 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 41014870 | 5397 | 129.528 | 5.397 | 5.3 | 5.3 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37977393 | 1301 | 241.0598 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 129 | 41020156 | 5286 | 126.864 | 5.286 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37978776 | 1383 | 261.6345 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 130 | 41025573 | 5417 | 130.008 | 5.417 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37980102 | 1326 | 244.7849 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 135 | 41030990 | 5417 | 130.008 | 5.417 | 4.2 | 4.2 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37981428 | 1326 | 244.7849 | 0% | 100% | 100% | 100% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 120 | 41036070 | 5080 | 121.92 | 5.08 | 3.2 | 3.2 | 2B+1S | 0 | 1139 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37982524 | 1096 | 215.748 | 0% | 100% | 100% | 0% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 41041150 | 5080 | 121.92 | 5.08 | 2.3 | 2.3 | 2B+1S | 0 | 1139 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37983620 | 1096 | 215.748 | 0% | 100% | 100% | 0% | 100% | 0% | 8561815 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 133 | 41046100 | 4950 | 118.8 | 4.95 | 1.6 | 1.6 | 2B+1S | 0 | 1139 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 37984680 | 1060 | 214.1414 | 0% | 100% | 100% | 0% | 100% | 0% | 8561815 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 149 | 106 | 41050148 | 4048 | 97.152 | 4.048 | 2.4 | 2.4 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 37985588 | 908 | 224.3083 | 0% | 0% | 100% | 0% | 100% | 65% | 8562875 | 1060 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 145 | 104 | 41054256 | 4108 | 98.592 | 4.108 | 3.7 | 3.7 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 37986500 | 912 | 222.0058 | 0% | 0% | 100% | 0% | 100% | 65% | 8564093 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 121603 | 121603 | 121.603 | 121.603 | [12 empty] | 27760 | 27760 | 228.2838 | [6 empty] | 6810 | 6810 | 6.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 19, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41054256 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 37986500 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8564093 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 123 | 97 | 41058307 | 4051 | 97.224 | 4.051 | 4.9 | 4.9 | 2B | 0 | 0 | 1087 | 0 | 1187 | N/A | N/A | N/A | N/A | 37987400 | 900 | 222.1674 | 0% | 0% | 100% | 0% | 100% | 75% | 8565178 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 135 | 103 | 41062058 | 3751 | 90.024 | 3.751 | 6.1 | 6.1 | 2B | 0 | 0 | 1087 | 0 | 1187 | N/A | N/A | N/A | N/A | 37988196 | 796 | 212.2101 | 0% | 0% | 100% | 0% | 100% | 75% | 8566378 | 1200 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 133 | 98 | 41066314 | 4256 | 102.144 | 4.256 | 7.5 | 7.5 | 2B | 0 | 0 | 1087 | 0 | 1188 | N/A | N/A | N/A | N/A | 37989068 | 872 | 204.8872 | 0% | 0% | 100% | 0% | 100% | 75% | 8567703 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 113 | 100 | 41070169 | 3855 | 92.52 | 3.855 | 8.5 | 8.5 | 2B | 0 | 0 | 1086 | 0 | 1187 | N/A | N/A | N/A | N/A | 37989860 | 792 | 205.4475 | 0% | 0% | 100% | 0% | 100% | 75% | 8568585 | 882 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A.ONG | 13.1 | 124 | 112 | 41074330 | 4161 | 99.864 | 4.161 | 8.6 | 8.6 | 2B | 0 | 0 | 1087 | 0 | 1188 | N/A | N/A | N/A | N/A | 37990660 | 800 | 192.2615 | 0% | 0% | 100% | 0% | 100% | 75% | 8568782 | 197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 126 | 41078846 | 4516 | 108.384 | 4.516 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 37991508 | 848 | 187.7768 | 0% | 0% | 100% | 0% | 100% | 75% | 8568962 | 180 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 145 | 41084970 | 6124 | 146.976 | 6.124 | 8.4 | 8.4 | 3B+1S | 0 | 1010 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37992912 | 1404 | 229.2619 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 150 | 41091001 | 6031 | 144.744 | 6.031 | 8 | 8 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37994276 | 1364 | 226.1648 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 147 | 41096986 | 5985 | 143.64 | 5.985 | 7.5 | 7.5 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37995636 | 1360 | 227.2348 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 146 | 150 | 41103140 | 6154 | 147.696 | 6.154 | 7.5 | 7.5 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37997036 | 1400 | 227.4943 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 148 | 41109077 | 5937 | 142.488 | 5.937 | 6.8 | 6.8 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37998386 | 1350 | 227.3876 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 149 | 41114954 | 5877 | 141.048 | 5.877 | 6.5 | 6.5 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 37999708 | 1322 | 224.9447 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 135 | 41120901 | 5947 | 142.728 | 5.947 | 6.2 | 6.2 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38001084 | 1376 | 231.3772 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 119 | 41126424 | 5523 | 132.552 | 5.523 | 5.8 | 5.8 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38002392 | 1308 | 236.8278 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 134 | 41132017 | 5593 | 134.232 | 5.593 | 5.5 | 5.5 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38003732 | 1340 | 239.5852 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 41137527 | 5510 | 132.24 | 5.51 | 5.3 | 5.3 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38005052 | 1320 | 239.5644 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 41143048 | 5521 | 132.504 | 5.521 | 5 | 5 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38006432 | 1380 | 249.9547 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 144 | 41148580 | 5532 | 132.768 | 5.532 | 4.7 | 4.7 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38007748 | 1316 | 237.8886 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 127 | 41154008 | 5428 | 130.272 | 5.428 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38009076 | 1328 | 244.6573 | 0% | 100% | 100% | 100% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 138 | 41159194 | 5186 | 124.464 | 5.186 | 3.5 | 3.5 | 2B+1S | 0 | 1150 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38010196 | 1120 | 215.9661 | 0% | 100% | 100% | 0% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 132 | 41164387 | 5193 | 124.632 | 5.193 | 2.6 | 2.6 | 2B+1S | 0 | 1150 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38011320 | 1124 | 216.4452 | 0% | 100% | 100% | 0% | 100% | 0% | 8568962 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 106 | 41169218 | 4831 | 115.944 | 4.831 | 1.7 | 1.7 | 2B+1S | 0 | 1148 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38012340 | 1020 | 211.1364 | 0% | 100% | 100% | 0% | 100% | 0% | 8568962 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 142 | 98 | 41173482 | 4264 | 102.336 | 4.264 | 2.7 | 2.7 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38013308 | 968 | 227.0169 | 0% | 0% | 100% | 0% | 100% | 70% | 8569994 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 146 | 100 | 41177378 | 3896 | 93.504 | 3.896 | 3.9 | 3.9 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38014200 | 892 | 228.9528 | 0% | 0% | 100% | 0% | 100% | 70% | 8571242 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 123122 | 123122 | 123.122 | 123.122 | [12 empty] | 27700 | 27700 | 224.9801 | [6 empty] | 7149 | 7149 | 6.15 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 20, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (70%)

## JUNE 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27956 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41177378 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38014200 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8571242 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 98 | 41181203 | 3825 | 91.8 | 3.825 | 5.1 | 5.1 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38015092 | 892 | 233.2026 | 0% | 0% | 100% | 0% | 100% | 75% | 8572269 | 1027 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 105 | 41184608 | 3405 | 81.72 | 3.405 | 6.4 | 6.4 | 2B | 0 | 0 | 1086 | 0 | 1188 | N/A | N/A | N/A | N/A | 38015892 | 800 | 234.9486 | 0% | 0% | 100% | 0% | 100% | 75% | 8573530 | 1261 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 96 | 41188231 | 3623 | 86.952 | 3.623 | 7.6 | 7.6 | 2B | 0 | 0 | 1087 | 0 | 1188 | N/A | N/A | N/A | N/A | 38016692 | 800 | 220.8115 | 0% | 0% | 100% | 0% | 100% | 75% | 8574648 | 1118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 100 | 41191867 | 3636 | 87.264 | 3.636 | 8.5 | 8.5 | 2B | 0 | 0 | 1086 | 0 | 1188 | N/A | N/A | N/A | N/A | 38017500 | 808 | 222.2222 | 0% | 0% | 100% | 0% | 100% | 75% | 8575651 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 105 | 41195624 | 3757 | 90.168 | 3.757 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1188 | N/A | N/A | N/A | N/A | 38018316 | 816 | 217.1946 | 0% | 0% | 100% | 0% | 100% | 75% | 8576559 | 908 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 113 | 41200225 | 4601 | 110.424 | 4.601 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38019228 | 912 | 198.2178 | 0% | 0% | 100% | 0% | 100% | 0% | 8576559 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 122 | 41205922 | 5697 | 136.728 | 5.697 | 9.5 | 9.5 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38020532 | 1304 | 228.8924 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 147 | 41211999 | 6077 | 145.848 | 6.077 | 9.1 | 9.1 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38021904 | 1372 | 225.7693 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 131 | 41218092 | 6093 | 146.232 | 6.093 | 8.7 | 8.7 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38023268 | 1364 | 223.8634 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 151 | 41224187 | 6095 | 146.28 | 6.095 | 8 | 8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38024661 | 1393 | 228.548 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 41230394 | 6207 | 148.968 | 6.207 | 7.5 | 7.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38026076 | 1415 | 227.9684 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 41236312 | 5918 | 142.032 | 5.918 | 6.9 | 6.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38027444 | 1368 | 231.1592 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 121 | 41241927 | 5615 | 134.76 | 5.615 | 6.3 | 6.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38028816 | 1372 | 244.3455 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 147 | 41247548 | 5621 | 134.904 | 5.621 | 5.7 | 5.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38030144 | 1328 | 236.2569 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 133 | 41252839 | 5291 | 126.984 | 5.291 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38031528 | 1384 | 261.5763 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 41258492 | 5653 | 135.672 | 5.653 | 4.7 | 4.7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38032892 | 1364 | 241.2878 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 41263938 | 5446 | 130.704 | 5.446 | 4.2 | 4.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38034236 | 1344 | 246.7866 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 113 | 41269187 | 5249 | 125.976 | 5.249 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38035568 | 1332 | 253.7626 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 114 | 41274638 | 5451 | 130.824 | 5.451 | 3.5 | 3.5 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38036900 | 1332 | 244.3588 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 134 | 41279892 | 5254 | 126.096 | 5.254 | 3.3 | 3.3 | 2B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38038220 | 1320 | 251.2372 | 0% | 100% | 100% | 100% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 112 | 41284670 | 4778 | 114.672 | 4.778 | 2.9 | 2.9 | 2B+1S | 0 | 1008 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 38039284 | 1064 | 222.6873 | 0% | 100% | 100% | 0% | 100% | 0% | 8576559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 124 | 41289509 | 4839 | 116.136 | 4.839 | 2.3 | 2.3 | 2B+1S | 0 | 1048 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38040292 | 1008 | 208.3075 | 0% | 100% | 100% | 0% | 100% | 0% | 8576559 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 149 | 112 | 41293903 | 4394 | 105.456 | 4.394 | 3.3 | 3.3 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38041252 | 960 | 218.4797 | 0% | 0% | 100% | 0% | 100% | 70% | 8577781 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 113 | 41298177 | 4274 | 102.576 | 4.274 | 4.8 | 4.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38042156 | 904 | 211.5115 | 0% | 0% | 100% | 0% | 100% | 75% | 8579099 | 1318 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 120799 | 120799 | 120.799 | 120.799 | [12 empty] | 27956 | 27956 | 231.4258 | [6 empty] | 7857 | 7857 | 5.97 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:34 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (70%)

## JUNE 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / A.DELOS ANGELES
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27176 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41298177 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38042156 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8579099 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 100 | 41302325 | 4148 | 99.552 | 4.148 | 5.9 | 5.9 | 2B | 0 | 0 | 1056 | 0 | 1187 | N/A | N/A | N/A | N/A | 38043052 | 896 | 216.0077 | 0% | 0% | 100% | 0% | 100% | 75% | 8580154 | 1055 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 104 | 41306441 | 4116 | 98.784 | 4.116 | 6.8 | 6.8 | 2B | 0 | 0 | 1056 | 0 | 1188 | N/A | N/A | N/A | N/A | 38043898 | 846 | 205.5394 | 0% | 0% | 100% | 0% | 100% | 75% | 8581195 | 1041 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 103 | 41310562 | 4121 | 98.904 | 4.121 | 8.3 | 8.3 | 2B | 0 | 0 | 1056 | 0 | 1187 | N/A | N/A | N/A | N/A | 38044800 | 902 | 218.8789 | 0% | 0% | 100% | 0% | 100% | 75% | 8582256 | 1061 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 101 | 41313994 | 3432 | 82.368 | 3.432 | 8.9 | 8.9 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 38045470 | 670 | 195.2214 | 0% | 0% | 100% | 0% | 100% | 75% | 8582897 | 641 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 103 | 41317305 | 3311 | 79.464 | 3.311 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1188 | N/A | N/A | N/A | N/A | 38046132 | 662 | 199.9396 | 0% | 0% | 100% | 0% | 100% | 75% | 8583530 | 633 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 114 | 41321825 | 4520 | 108.48 | 4.52 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 118 | N/A | N/A | N/A | N/A | 38046968 | 836 | 184.9558 | 0% | 0% | 100% | 0% | 100% | 0% | 8583530 | 0 | 0.9 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 143 | 41327551 | 5726 | 137.424 | 5.726 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38048224 | 1256 | 219.3503 | 0% | 0% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 149 | 139 | 41333260 | 5709 | 137.016 | 5.709 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38049434 | 1210 | 211.9461 | 0% | 0% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 151 | 41339275 | 6015 | 144.36 | 6.015 | 9.1 | 9.1 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38050804 | 1370 | 227.7639 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 182 | 41345323 | 6048 | 145.152 | 6.048 | 8.5 | 8.5 | 3B+1S | 0 | 1061 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38052188 | 1384 | 228.836 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 41351530 | 6207 | 148.968 | 6.207 | 7.7 | 7.7 | 3B+1S | 0 | 1101 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38053620 | 1432 | 230.7073 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 149 | 41357484 | 5954 | 142.896 | 5.954 | 7 | 7 | 3B+1S | 0 | 1101 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38055044 | 1424 | 239.1669 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 148 | 41363364 | 5880 | 141.12 | 5.88 | 6.5 | 6.5 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38056412 | 1368 | 232.6531 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 41369305 | 5941 | 142.584 | 5.941 | 5.9 | 5.9 | 3B+1S | 0 | 1070 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38057796 | 1384 | 232.9574 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 159 | 41375078 | 5773 | 138.552 | 5.773 | 5.3 | 5.3 | 3B+1S | 0 | 1070 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38059196 | 1400 | 242.5082 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 143 | 41380850 | 5772 | 138.528 | 5.772 | 4.8 | 4.8 | 3B+1S | 0 | 1069 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38060596 | 1400 | 242.5502 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 136 | 41385994 | 5144 | 123.456 | 5.144 | 4.5 | 4.5 | 3B+1S | 0 | 958 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38061920 | 1324 | 257.3872 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 130 | 41391243 | 5249 | 125.976 | 5.249 | 4.4 | 4.4 | 3B+1S | 0 | 957 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38063232 | 1312 | 249.9524 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 145 | 41396298 | 5055 | 121.32 | 5.055 | 4.2 | 4.2 | 3B+1S | 0 | 958 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38064460 | 1228 | 242.9278 | 0% | 100% | 100% | 100% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 41401333 | 5035 | 120.84 | 5.035 | 3.6 | 3.6 | 2B+1S | 0 | 1131 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38065556 | 1096 | 217.6763 | 0% | 100% | 100% | 0% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 124 | 41406355 | 5022 | 120.528 | 5.022 | 2.8 | 2.8 | 2B+1S | 0 | 1131 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38066660 | 1104 | 219.8327 | 0% | 100% | 100% | 0% | 100% | 0% | 8583530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 129 | 41411326 | 4971 | 119.304 | 4.971 | 2 | 2 | 2B+1S | 0 | 1131 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38067692 | 1032 | 207.6041 | 0% | 100% | 100% | 0% | 100% | 0% | 8583530 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 144 | 100 | 41415040 | 3714 | 89.136 | 3.714 | 3.1 | 3.1 | 2B | 0 | 0 | 1076 | 0 | 1187 | N/A | N/A | N/A | N/A | 38068556 | 864 | 232.6333 | 0% | 0% | 100% | 0% | 100% | 65% | 8585015 | 1485 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 105 | 41418603 | 3563 | 85.512 | 3.563 | 4.9 | 4.9 | 2B | 0 | 0 | 1076 | 0 | 1188 | N/A | N/A | N/A | N/A | 38069332 | 776 | 217.794 | 0% | 0% | 100% | 0% | 100% | 65% | 8586447 | 1432 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 120426 | 120426 | 120.426 | 120.426 | [12 empty] | 27176 | 27176 | 225.6656 | [6 empty] | 7348 | 7348 | 5.28 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 22, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27400 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41418603 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38069332 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8586447 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 91 | 41422378 | 3775 | 90.6 | 3.775 | 6.3 | 6.3 | 2B | 0 | 0 | 1076 | 0 | 1187 | N/A | N/A | N/A | N/A | 38070132 | 800 | 211.9205 | 0% | 0% | 100% | 0% | 100% | 75% | 8587745 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 98 | 41425984 | 3606 | 86.544 | 3.606 | 7.5 | 7.5 | 2B | 0 | 0 | 1027 | 0 | 1188 | N/A | N/A | N/A | N/A | 38070872 | 740 | 205.2135 | 0% | 0% | 100% | 0% | 100% | 75% | 8588983 | 1238 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 41429638 | 3654 | 87.696 | 3.654 | 8.8 | 8.8 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38071604 | 732 | 200.3284 | 0% | 0% | 100% | 0% | 100% | 75% | 8590121 | 1138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 100 | 41433459 | 3821 | 91.704 | 3.821 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 0 | 1188 | N/A | N/A | N/A | N/A | 38072356 | 752 | 196.8071 | 0% | 0% | 100% | 0% | 100% | 75% | 8590896 | 775 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 100 | 41437387 | 3928 | 94.272 | 3.928 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 0 | 1188 | N/A | N/A | N/A | N/A | 38073116 | 760 | 193.4827 | 0% | 0% | 100% | 0% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 142 | 135 | 41442378 | 4991 | 119.784 | 4.991 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 1108 | N/A | N/A | N/A | N/A | 38074124 | 1008 | 201.9635 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 149 | 41448313 | 5935 | 142.44 | 5.935 | 9.2 | 9.2 | 3B+1S | 0 | 1022 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38075496 | 1372 | 231.171 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 149 | 41454174 | 5861 | 140.664 | 5.861 | 8.8 | 8.8 | 3B+1S | 0 | 1108 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38076836 | 1340 | 228.6299 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 149 | 41460125 | 5951 | 142.824 | 5.951 | 8.3 | 8.3 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38078196 | 1360 | 228.533 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 153 | 41466309 | 6184 | 148.416 | 6.184 | 7.9 | 7.9 | 3B+1S | 0 | 1009 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38079580 | 1384 | 223.8034 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 150 | 41472153 | 5844 | 140.256 | 5.844 | 7.5 | 7.5 | 3B+1S | 0 | 1009 | 1187 | 1185 | 1189 | N/A | N/A | N/A | N/A | 38080908 | 1328 | 227.2416 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 140 | 41478229 | 6076 | 145.824 | 6.076 | 7.2 | 7.2 | 3B+1S | 0 | 1009 | 1187 | 1185 | 1189 | N/A | N/A | N/A | N/A | 38082300 | 1392 | 229.0981 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 41483907 | 5678 | 136.272 | 5.678 | 6.9 | 6.9 | 3B+1S | 0 | 1008 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38083632 | 1332 | 234.5896 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 41489411 | 5504 | 132.096 | 5.504 | 6.5 | 6.5 | 3B+1S | 0 | 1029 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38084998 | 1366 | 248.1831 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 131 | 41494916 | 5505 | 132.12 | 5.505 | 6.1 | 6.1 | 3B+1S | 0 | 1028 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38086364 | 1366 | 248.1381 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 41500429 | 5513 | 132.312 | 5.513 | 5.8 | 5.8 | 3B+1S | 0 | 1008 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38087684 | 1320 | 239.4341 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 41505895 | 5466 | 131.184 | 5.466 | 5.6 | 5.6 | 3B+1S | 0 | 1008 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38089004 | 1320 | 241.4929 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 41511494 | 5599 | 134.376 | 5.599 | 5.3 | 5.3 | 3B+1S | 0 | 1008 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38090328 | 1324 | 236.4708 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 131 | 41516902 | 5408 | 129.792 | 5.408 | 5 | 5 | 3B+1S | 0 | 1008 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38091660 | 1332 | 246.3018 | 0% | 100% | 100% | 100% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 113 | 41522105 | 5203 | 124.872 | 5.203 | 4 | 4 | 2B+1S | 0 | 1152 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 38092772 | 1112 | 213.7229 | 0% | 100% | 100% | 0% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 132 | 41527577 | 5472 | 131.328 | 5.472 | 3 | 3 | 2B+1S | 0 | 1150 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 38093900 | 1128 | 206.1404 | 0% | 100% | 100% | 0% | 100% | 0% | 8590896 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 120 | 41532874 | 5297 | 127.128 | 5.297 | 2.1 | 2.1 | 2B+1S | 0 | 1067 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 38095020 | 1120 | 211.4404 | 0% | 100% | 100% | 0% | 100% | 0% | 8590896 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 97 | 41536948 | 4074 | 97.776 | 4.074 | 3 | 3 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 38095900 | 880 | 216.0039 | 0% | 0% | 100% | 0% | 100% | 50% | 8591804 | 908 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 90 | 41540865 | 3917 | 94.008 | 3.917 | 4.3 | 4.3 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 38096732 | 832 | 212.4075 | 0% | 0% | 100% | 0% | 100% | 50% | 8592975 | 1171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 122262 | 122262 | 122.262 | 122.262 | [12 empty] | 27400 | 27400 | 224.1089 | [6 empty] | 6528 | 6528 | 5.44 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 5:58AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JUNE 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27052 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41540865 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38096732 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8592975 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 95 | 41544542 | 3677 | 88.248 | 3.677 | 6 | 6 | 2B | 0 | 0 | 1159 | 0 | 1159 | N/A | N/A | N/A | N/A | 38097476 | 744 | 202.3389 | 0% | 0% | 100% | 0% | 100% | 70% | 8593993 | 1018 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 91 | 41548212 | 3670 | 88.08 | 3.67 | 7.3 | 7.3 | 2B | 0 | 0 | 1159 | 0 | 1159 | N/A | N/A | N/A | N/A | 38098251 | 775 | 211.1717 | 0% | 0% | 100% | 0% | 100% | 70% | 8595012 | 1019 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 41551896 | 3684 | 88.416 | 3.684 | 8.7 | 8.7 | 2B | 0 | 0 | 1078 | 0 | 1087 | N/A | N/A | N/A | N/A | 38099025 | 774 | 210.0977 | 0% | 0% | 100% | 0% | 100% | 70% | 8596030 | 1018 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 96 | 41555573 | 3677 | 88.248 | 3.677 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1087 | N/A | N/A | N/A | N/A | 38099800 | 775 | 210.7696 | 0% | 0% | 100% | 0% | 100% | 70% | 8597049 | 1019 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 80 | 41559250 | 3677 | 88.248 | 3.677 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1087 | N/A | N/A | N/A | N/A | 38100456 | 656 | 178.4063 | 0% | 0% | 100% | 0% | 100% | 70% | 8598069 | 1020 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 124 | 41563907 | 4657 | 111.768 | 4.657 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38101348 | 892 | 191.5396 | 0% | 0% | 100% | 0% | 100% | 0% | 8598069 | 0 | 1.01 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 138 | 41569746 | 5839 | 140.136 | 5.839 | 9.3 | 9.3 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38102676 | 1328 | 227.4362 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 128 | 41575887 | 6141 | 147.384 | 6.141 | 9.3 | 9.3 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38104060 | 1384 | 225.3705 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 144 | 41581729 | 5842 | 140.208 | 5.842 | 8.5 | 8.5 | 3B+1S | 0 | 1020 | 1887 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38105400 | 1340 | 229.3735 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 147 | 41587809 | 6080 | 145.92 | 6.08 | 8.1 | 8.1 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38106780 | 1380 | 226.9737 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 | 1.49 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 138 | 41593857 | 6048 | 145.152 | 6.048 | 7.7 | 7.7 | 3B+1S | 0 | 1019 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38108156 | 1376 | 227.5132 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 121 | 41599680 | 5823 | 139.752 | 5.823 | 7.3 | 7.3 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38109508 | 1352 | 232.1827 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 135 | 41605306 | 5626 | 135.024 | 5.626 | 7 | 7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38110856 | 1348 | 239.6018 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 135 | 41610822 | 5516 | 132.384 | 5.516 | 6.6 | 6.6 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38112222 | 1366 | 247.6432 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 41616338 | 5516 | 132.384 | 5.516 | 6.3 | 6.3 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38113588 | 1366 | 247.6432 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 41621423 | 5085 | 122.04 | 5.085 | 6.1 | 6.1 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38114852 | 1264 | 248.5742 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 41626495 | 5072 | 121.728 | 5.072 | 5.8 | 5.8 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38116156 | 1304 | 257.0978 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 41631568 | 5073 | 121.752 | 5.073 | 5.6 | 5.6 | 3B+1S | 0 | 1018 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38117460 | 1304 | 257.0471 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 41636589 | 5021 | 120.504 | 5.021 | 5.3 | 5.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38118820 | 1360 | 270.8624 | 0% | 100% | 100% | 100% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 125 | 41641045 | 4456 | 106.944 | 4.456 | 4.4 | 4.4 | 2B+1S | 0 | 1120 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38119924 | 1104 | 247.7558 | 0% | 100% | 100% | 0% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 126 | 41645661 | 4616 | 110.784 | 4.616 | 3.5 | 3.5 | 2B+1S | 0 | 1121 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38121020 | 1096 | 237.435 | 0% | 100% | 100% | 0% | 100% | 0% | 8598069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 113 | 41650147 | 4486 | 107.664 | 4.486 | 2.8 | 2.8 | 2B+1S | 0 | 947 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38122076 | 1056 | 235.399 | 0% | 100% | 100% | 0% | 100% | 0% | 8598069 | 0 | 0.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 97 | 41653775 | 3628 | 87.072 | 3.628 | 3.9 | 3.9 | 2B | 0 | 0 | 1148 | 0 | 1158 | N/A | N/A | N/A | N/A | 38122940 | 864 | 238.1477 | 0% | 0% | 100% | 0% | 100% | 55% | 8599070 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 94 | 41657429 | 3654 | 87.696 | 3.654 | 5.4 | 5.4 | 2B | 0 | 0 | 1148 | 0 | 1158 | N/A | N/A | N/A | N/A | 38123784 | 844 | 230.9797 | 0% | 0% | 100% | 0% | 100% | 55% | 8600251 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 116564 | 116564 | 116.564 | 116.564 | [12 empty] | 27052 | 27052 | 232.0785 | [6 empty] | 7276 | 7276 | 6.08 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:11 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 24, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JUNE 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27260 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41657429 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38123784 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8600251 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 98 | 41661039 | 3610 | 86.64 | 3.61 | 6.2 | 6.2 | 2B | 0 | 0 | 1012 | 0 | 1012 | N/A | N/A | N/A | N/A | 38124544 | 760 | 210.5263 | 0% | 0% | 100% | 0% | 100% | 70% | 8601305 | 1054 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 41664660 | 3621 | 86.904 | 3.621 | 7.6 | 7.6 | 2B | 0 | 0 | 1012 | 0 | 1012 | N/A | N/A | N/A | N/A | 38125304 | 760 | 209.8868 | 0% | 0% | 100% | 0% | 100% | 70% | 8602363 | 1058 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 90 | 41668252 | 3592 | 86.208 | 3.592 | 8.9 | 8.9 | 2B | 0 | 0 | 1012 | 0 | 1012 | N/A | N/A | N/A | N/A | 38126073 | 769 | 214.0869 | 0% | 0% | 100% | 0% | 100% | 70% | 8603417 | 1054 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 93 | 41671862 | 3610 | 86.64 | 3.61 | 9.5 | 9.5 | 2B | 0 | 0 | 1100 | 0 | 1100 | N/A | N/A | N/A | N/A | 38126824 | 751 | 208.0332 | 0% | 0% | 100% | 0% | 100% | 70% | 8604419 | 1002 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 106 | 41675476 | 3614 | 86.736 | 3.614 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38127584 | 760 | 210.2933 | 0% | 0% | 100% | 0% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 132 | 114 | 41679544 | 4068 | 97.632 | 4.068 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38128412 | 828 | 203.5398 | 0% | 0% | 100% | 0% | 100% | 0% | 8604419 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 142 | 41685352 | 5808 | 139.392 | 5.808 | 9.2 | 9.2 | 3B+1S | 0 | 1029 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38129776 | 1364 | 234.8485 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 41691200 | 5848 | 140.352 | 5.848 | 8.7 | 8.7 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38131120 | 1344 | 229.8222 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 112 | 41697161 | 5961 | 143.064 | 5.961 | 8.2 | 8.2 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38132532 | 1412 | 236.873 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 151 | 41702939 | 5778 | 138.672 | 5.778 | 7.6 | 7.6 | 3B+1S | 0 | 1029 | 1188 | 1185 | 1189 | N/A | N/A | N/A | N/A | 38133916 | 1384 | 239.5292 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 154 | 41708747 | 5808 | 139.392 | 5.808 | 7.2 | 7.2 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38135276 | 1360 | 234.1598 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 139 | 41714494 | 5747 | 137.928 | 5.747 | 6.8 | 6.8 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38136672 | 1396 | 242.9093 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 148 | 41719662 | 5168 | 124.032 | 5.168 | 6.4 | 6.4 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38138004 | 1332 | 257.7399 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 41724882 | 5220 | 125.28 | 5.22 | 6 | 6 | 3B+1S | 0 | 1029 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38139340 | 1336 | 255.9387 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 131 | 41729923 | 5041 | 120.984 | 5.041 | 5.6 | 5.6 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38140708 | 1368 | 271.3747 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 148 | 41735206 | 5283 | 126.792 | 5.283 | 5.2 | 5.2 | 3B+1S | 0 | 1028 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38142028 | 1320 | 249.858 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 41740243 | 5037 | 120.888 | 5.037 | 4.9 | 4.9 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38143380 | 1352 | 268.4137 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 138 | 41744734 | 4491 | 107.784 | 4.491 | 4.7 | 4.7 | 3B+1S | 0 | 988 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38144708 | 1328 | 295.7025 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 130 | 41749655 | 4921 | 118.104 | 4.921 | 4.6 | 4.6 | 3B+1S | 0 | 988 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38145996 | 1288 | 261.7354 | 0% | 100% | 100% | 100% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 127 | 41754399 | 4744 | 113.856 | 4.744 | 3.6 | 3.6 | 2B+1S | 0 | 1130 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38147108 | 1112 | 234.4013 | 0% | 100% | 100% | 0% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 133 | 41758939 | 4540 | 108.96 | 4.54 | 2.7 | 2.7 | 2B+1S | 0 | 1130 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38148216 | 1108 | 244.0529 | 0% | 100% | 100% | 0% | 100% | 0% | 8604419 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 122 | 41763259 | 4320 | 103.68 | 4.32 | 1.9 | 1.9 | 2B+1S | 0 | 1131 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38149284 | 1068 | 247.2222 | 0% | 100% | 100% | 0% | 100% | 0% | 8604419 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 141 | 111 | 41766812 | 3553 | 85.272 | 3.553 | 2.8 | 2.8 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38150204 | 920 | 258.9361 | 0% | 0% | 100% | 0% | 100% | 60% | 8605408 | 989 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 96 | 41770033 | 3221 | 77.304 | 3.221 | 4.3 | 4.3 | 2B | 0 | 0 | 1127 | 0 | 1188 | N/A | N/A | N/A | N/A | 38151044 | 840 | 260.7886 | 0% | 0% | 100% | 0% | 100% | 60% | 8606720 | 1312 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 112604 | 112604 | 112.604 | 112.604 | [12 empty] | 27260 | 27260 | 242.0873 | [6 empty] | 6469 | 6469 | 5.92 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:05 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 25, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (60%)

## JUNE 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27632 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41770033 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38151044 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8606720 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 84 | 41772520 | 2487 | 59.688 | 2.487 | 5.5 | 5.5 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38151788 | 744 | 299.1556 | 0% | 0% | 100% | 0% | 100% | 75% | 8607989 | 1269 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 88 | 41775567 | 3047 | 73.128 | 3.047 | 6.8 | 6.8 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38152556 | 768 | 252.0512 | 0% | 0% | 100% | 0% | 100% | 75% | 8609276 | 1287 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 41778889 | 3322 | 79.728 | 3.322 | 8.1 | 8.1 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38153316 | 760 | 228.7778 | 0% | 0% | 100% | 0% | 100% | 75% | 8610473 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 107 | 100 | 41782111 | 3222 | 77.328 | 3.222 | 8.8 | 8.8 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38154044 | 728 | 225.9466 | 0% | 0% | 100% | 0% | 100% | 75% | 8611033 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 121 | 100 | 41785734 | 3623 | 86.952 | 3.623 | 9.1 | 9.1 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38154808 | 764 | 210.875 | 0% | 0% | 100% | 0% | 100% | 75% | 8611336 | 303 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 147 | 137 | 41790272 | 4538 | 108.912 | 4.538 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38155860 | 1052 | 231.8202 | 0% | 0% | 100% | 100% | 100% | 0% | 8611336 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 140 | 41796022 | 5750 | 138 | 5.75 | 8.7 | 8.7 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38157204 | 1344 | 233.7391 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 150 | 41801644 | 5622 | 134.928 | 5.622 | 8.2 | 8.2 | 3B+1S | 0 | 1029 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38158580 | 1376 | 244.7528 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 120 | 41807076 | 5432 | 130.368 | 5.432 | 7.6 | 7.6 | 3B+1S | 0 | 1029 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38159972 | 1392 | 256.2592 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 142 | 41812690 | 5614 | 134.736 | 5.614 | 7.2 | 7.2 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38161340 | 1368 | 243.6765 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 156 | 41818331 | 5641 | 135.384 | 5.641 | 6.8 | 6.8 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38162680 | 1340 | 237.5465 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 105 | 41823625 | 5294 | 127.056 | 5.294 | 6.4 | 6.4 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38164068 | 1388 | 262.1836 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 118 | 41828907 | 5282 | 126.768 | 5.282 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38165428 | 1360 | 257.4782 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 141 | 41833926 | 5019 | 120.456 | 5.019 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38166748 | 1320 | 263.0006 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 142 | 41838691 | 4765 | 114.36 | 4.765 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38168132 | 1384 | 290.4512 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 131 | 41843457 | 4766 | 114.384 | 4.766 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38169444 | 1312 | 275.2833 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 121 | 41848409 | 4952 | 118.848 | 4.952 | 5 | 5 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38170776 | 1332 | 268.9822 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 141 | 41852909 | 4500 | 108 | 4.5 | 4.8 | 4.8 | 3B+1S | 0 | 986 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38172080 | 1304 | 289.7778 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 142 | 41857383 | 4474 | 107.376 | 4.474 | 4.7 | 4.7 | 3B+1S | 0 | 985 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38173408 | 1328 | 296.8261 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 134 | 41862238 | 4855 | 116.52 | 4.855 | 4.6 | 4.6 | 2B+1S | 0 | 985 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 38174740 | 1332 | 274.3563 | 0% | 100% | 100% | 100% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 41866849 | 4611 | 110.664 | 4.611 | 3.8 | 3.8 | 2B+1S | 0 | 1119 | 1188 | 0 | 1185 | N/A | N/A | N/A | N/A | 38175852 | 1112 | 241.1624 | 0% | 100% | 100% | 0% | 100% | 0% | 8611336 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 108 | 41871378 | 4529 | 108.696 | 4.529 | 2.9 | 2.9 | 2B+1S | 0 | 1117 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38176940 | 1088 | 240.2296 | 0% | 100% | 100% | 0% | 100% | 0% | 8611336 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 110 | 41874430 | 3052 | 73.248 | 3.052 | 3.5 | 3.5 | 2B | 0 | 0 | 1157 | 0 | 1189 | N/A | N/A | N/A | N/A | 38177895 | 955 | 312.9096 | 0% | 0% | 100% | 0% | 100% | 65% | 8612042 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 99 | 41878024 | 3594 | 86.256 | 3.594 | 4.6 | 4.6 | 2B | 0 | 0 | 1157 | 0 | 1187 | N/A | N/A | N/A | N/A | 38178676 | 781 | 217.3066 | 0% | 0% | 100% | 0% | 100% | 65% | 8613111 | 1069 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 107991 | 107991 | 107.991 | 107.991 | [12 empty] | 27632 | 27632 | 255.8732 | [6 empty] | 6391 | 6391 | 5.6 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (65%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 3:56 AM,WATER ELEVATION (7.5M)
XCV4 -OPENED @ 5:01AM (7%) / CLOSED @ 5:46 AM (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 5:30AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 26, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41878024 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38178676 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8613111 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 105 | 41881425 | 3401 | 81.624 | 3.401 | 5.8 | 5.8 | 2B | 0 | 0 | 1157 | 0 | 1187 | N/A | N/A | N/A | N/A | 38179544 | 868 | 255.2191 | 0% | 0% | 100% | 0% | 100% | 75% | 8614203 | 1092 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 98 | 41883919 | 2494 | 59.856 | 2.494 | 7 | 7 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38180300 | 756 | 303.1275 | 0% | 0% | 100% | 0% | 100% | 75% | 8615401 | 1198 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 92 | 41886790 | 2871 | 68.904 | 2.871 | 8.2 | 8.2 | 2B | 0 | 0 | 1026 | 0 | 1187 | N/A | N/A | N/A | N/A | 38181036 | 736 | 256.3567 | 0% | 0% | 100% | 0% | 100% | 75% | 8616616 | 1215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 100 | 41890094 | 3304 | 79.296 | 3.304 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 0 | 1187 | N/A | N/A | N/A | N/A | 38181788 | 752 | 227.6029 | 0% | 0% | 100% | 0% | 100% | 75% | 8617684 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 107 | 41894103 | 4009 | 96.216 | 4.009 | 9.5 | 9.5 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38182592 | 804 | 200.5488 | 0% | 0% | 100% | 0% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 109 | 41898023 | 3920 | 94.08 | 3.92 | 9.6 | 9.6 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38183420 | 828 | 211.2245 | 0% | 0% | 100% | 0% | 100% | 0% | 8617684 | 0 | 0.9 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 41903643 | 5620 | 134.88 | 5.62 | 9.1 | 9.1 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38184798 | 1378 | 245.1957 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 41909170 | 5527 | 132.648 | 5.527 | 8.7 | 8.7 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38186156 | 1358 | 245.7029 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 154 | 41914625 | 5455 | 130.92 | 5.455 | 8.2 | 8.2 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38187532 | 1376 | 252.2456 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 152 | 41920002 | 5377 | 129.048 | 5.377 | 7.7 | 7.7 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38188914 | 1382 | 257.0206 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 | 1.03 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 143 | 41925424 | 5422 | 130.128 | 5.422 | 7.2 | 7.2 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38190311 | 1397 | 257.654 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 110 | 41930734 | 5310 | 127.44 | 5.31 | 6.8 | 6.8 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38191668 | 1357 | 255.5556 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 133 | 41935617 | 4883 | 117.192 | 4.883 | 6.4 | 6.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38192956 | 1288 | 263.7723 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 130 | 41940484 | 4867 | 116.808 | 4.867 | 5.9 | 5.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38194348 | 1392 | 286.0078 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 134 | 41945574 | 5090 | 122.16 | 5.09 | 5.6 | 5.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38195692 | 1344 | 264.0472 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 149 | 41950144 | 4570 | 109.68 | 4.57 | 5.3 | 5.3 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38197024 | 1332 | 291.4661 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 41955005 | 4861 | 116.664 | 4.861 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38198356 | 1332 | 274.0177 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 139 | 41959422 | 4417 | 106.008 | 4.417 | 4.7 | 4.7 | 3B+1S | 0 | 985 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38199692 | 1336 | 302.4677 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 140 | 128 | 41963816 | 4394 | 105.456 | 4.394 | 4.6 | 4.6 | 3B+1S | 0 | 985 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38200996 | 1304 | 296.7683 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 128 | 41968503 | 4687 | 112.488 | 4.687 | 4.5 | 4.5 | 3B+1S | 0 | 986 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38202312 | 1316 | 280.7766 | 0% | 100% | 100% | 100% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 127 | 41973007 | 4504 | 108.096 | 4.504 | 3.5 | 3.5 | 2B+1S | 0 | 1136 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38203440 | 1128 | 250.444 | 0% | 100% | 100% | 0% | 100% | 0% | 8617684 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 102 | 41977145 | 4138 | 99.312 | 4.138 | 2.8 | 2.8 | 2B+1S | 0 | 1140 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38204472 | 1032 | 249.3958 | 0% | 100% | 100% | 0% | 100% | 0% | 8617684 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 111 | 41980804 | 3659 | 87.816 | 3.659 | 3.5 | 3.5 | 2B | 0 | 0 | 1168 | 0 | 1187 | N/A | N/A | N/A | N/A | 38205426 | 954 | 260.727 | 0% | 0% | 100% | 0% | 100% | 65% | 8618580 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 105 | 41984280 | 3476 | 83.424 | 3.476 | 4.8 | 4.8 | 2B | 0 | 0 | 1167 | 0 | 1187 | N/A | N/A | N/A | N/A | 38206324 | 898 | 258.3429 | 0% | 0% | 100% | 0% | 100% | 65% | 8619719 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 106256 | 106256 | 106.256 | 106.256 | [12 empty] | 27648 | 27648 | 260.2018 | [6 empty] | 6608 | 6608 | 5.65 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 70psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:03 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 27, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS. SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 41984280 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38206324 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8619719 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 104 | 41987659 | 3379 | 81.096 | 3.379 | 5.6 | 5.6 | 2B | 0 | 0 | 1066 | 0 | 1188 | N/A | N/A | N/A | N/A | 38207208 | 884 | 261.6159 | 0% | 0% | 100% | 0% | 100% | 75% | 8620601 | 882 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 41990444 | 2785 | 66.84 | 2.785 | 6.8 | 6.8 | 2B | 0 | 0 | 1060 | 0 | 1188 | N/A | N/A | N/A | N/A | 38207956 | 748 | 268.5817 | 0% | 0% | 100% | 0% | 100% | 75% | 8621644 | 1043 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 92 | 41993286 | 2842 | 68.208 | 2.842 | 7.9 | 7.9 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38208724 | 768 | 270.2322 | 0% | 0% | 100% | 0% | 100% | 75% | 8622773 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 94 | 41996369 | 3083 | 73.992 | 3.083 | 9 | 9 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38209452 | 728 | 236.1336 | 0% | 0% | 100% | 0% | 100% | 75% | 8623744 | 971 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 111 | 41999812 | 3443 | 82.632 | 3.443 | 9.5 | 9.5 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38210212 | 760 | 220.7377 | 0% | 0% | 100% | 0% | 100% | 75% | 8624174 | 430 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 132 | 106 | 42003681 | 3869 | 92.856 | 3.869 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38210996 | 784 | 202.6363 | 0% | 0% | 100% | 0% | 100% | 0% | 8624174 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 158 | 42009190 | 5509 | 132.216 | 5.509 | 9.4 | 9.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38212332 | 1336 | 242.5123 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 157 | 42014702 | 5512 | 132.288 | 5.512 | 8.8 | 8.8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38213704 | 1372 | 248.9115 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 113 | 42020062 | 5360 | 128.64 | 5.36 | 8.3 | 8.3 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38215044 | 1340 | 250 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 140 | 42025700 | 5638 | 135.312 | 5.638 | 7.7 | 7.7 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38216476 | 1432 | 253.9908 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 141 | 42030911 | 5211 | 125.064 | 5.211 | 7.1 | 7.1 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38217850 | 1374 | 263.673 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 42036272 | 5361 | 128.664 | 5.361 | 6.6 | 6.6 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38219236 | 1386 | 258.5339 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 151 | 42041642 | 5370 | 128.88 | 5.37 | 6 | 6 | 3B+1S | 0 | 1058 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38220612 | 1376 | 256.2384 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 42046626 | 4984 | 119.616 | 4.984 | 5.4 | 5.4 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38222028 | 1416 | 284.1091 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 130 | 42051743 | 5117 | 122.808 | 5.117 | 4.9 | 4.9 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38223380 | 1352 | 264.2173 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 42056457 | 4714 | 113.136 | 4.714 | 4.3 | 4.3 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38224736 | 1356 | 287.6538 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 42061300 | 4843 | 116.232 | 4.843 | 3.7 | 3.7 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38226092 | 1356 | 279.9917 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 123 | 42065979 | 4679 | 112.296 | 4.679 | 3.2 | 3.2 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38227468 | 1376 | 294.0799 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 136 | 42070514 | 4535 | 108.84 | 4.535 | 2.9 | 2.9 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38228780 | 1312 | 289.3054 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 140 | 140 | 42075121 | 4607 | 110.568 | 4.607 | 2.8 | 2.8 | 3B+1S | 0 | 965 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38230092 | 1312 | 284.784 | 0% | 100% | 100% | 100% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 42079803 | 4682 | 112.368 | 4.682 | 2.1 | 2.1 | 2B+1S | 0 | 1139 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38231204 | 1112 | 237.5053 | 0% | 100% | 100% | 0% | 100% | 0% | 8624174 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 | 137 | 42084236 | 4433 | 106.392 | 4.433 | 1.3 | 1.3 | 2B+1S | 0 | 1138 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38232276 | 1072 | 241.8227 | 0% | 100% | 100% | 0% | 100% | 0% | 8624174 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 101 | 42087736 | 3500 | 84 | 3.5 | 2.4 | 2.4 | 2B | 0 | 0 | 1127 | 0 | 1188 | N/A | N/A | N/A | N/A | 38233156 | 880 | 251.4286 | 0% | 0% | 100% | 0% | 100% | 65% | 8625508 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 142 | 113 | 42090937 | 3201 | 76.824 | 3.201 | 3.7 | 3.7 | 2B | 0 | 0 | 1127 | 0 | 1188 | N/A | N/A | N/A | N/A | 38233964 | 808 | 252.4211 | 0% | 0% | 100% | 0% | 100% | 65% | 8626736 | 1228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 106657 | 106657 | 106.657 | 106.657 | [12 empty] | 27640 | 27640 | 259.1485 | [6 empty] | 7017 | 7017 | 5.83 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:27 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / A.DELOS ANGELES
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27704 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42090937 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38233964 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8626736 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 101 | 42094364 | 3427 | 82.248 | 3.427 | 5 | 5 | 2B | 0 | 0 | 1077 | 0 | 1187 | N/A | N/A | N/A | N/A | 38234852 | 888 | 259.1188 | 0% | 0% | 100% | 0% | 100% | 75% | 8627836 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 110 | 42096956 | 2592 | 62.208 | 2.592 | 6.1 | 6.1 | 2B | 0 | 0 | 1076 | 0 | 1187 | N/A | N/A | N/A | N/A | 38235628 | 776 | 299.3827 | 0% | 0% | 100% | 0% | 100% | 75% | 8628873 | 1037 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 42099966 | 3010 | 72.24 | 3.01 | 7.2 | 7.2 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38236412 | 784 | 260.4651 | 0% | 0% | 100% | 0% | 100% | 75% | 8629947 | 1074 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 99 | 42103133 | 3167 | 76.008 | 3.167 | 8.1 | 8.1 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38237184 | 772 | 243.7638 | 0% | 0% | 100% | 0% | 100% | 75% | 8630899 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 143 | 100 | 42106511 | 3378 | 81.072 | 3.378 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1187 | N/A | N/A | N/A | N/A | 38237932 | 748 | 221.4328 | 0% | 0% | 100% | 0% | 100% | 75% | 8631817 | 918 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 78 | 42110528 | 4017 | 96.408 | 4.017 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38238792 | 860 | 214.0901 | 0% | 0% | 100% | 0% | 100% | 0% | 8631817 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 141 | 42115918 | 5390 | 129.36 | 5.39 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38240052 | 1260 | 233.7662 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 42121069 | 5151 | 123.624 | 5.151 | 9.3 | 9.3 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38241384 | 1332 | 258.5906 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 161 | 42126342 | 5273 | 126.552 | 5.273 | 8.8 | 8.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38242742 | 1358 | 257.5384 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 146 | 42131737 | 5395 | 129.48 | 5.395 | 8.2 | 8.2 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38244164 | 1422 | 263.5774 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 | 0.65 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 145 | 42135005 | 3268 | 78.432 | 3.268 | 7.7 | 7.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38245548 | 1384 | 423.5006 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 143 | 42142113 | 7108 | 170.592 | 7.108 | 7.3 | 7.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38246892 | 1344 | 189.0827 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 42147044 | 4931 | 118.344 | 4.931 | 6.8 | 6.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38248260 | 1368 | 277.4285 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 42152367 | 5323 | 127.752 | 5.323 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38249700 | 1440 | 270.5241 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 141 | 42157032 | 4665 | 111.96 | 4.665 | 5.7 | 5.7 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38251052 | 1352 | 289.8178 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 42161921 | 4889 | 117.336 | 4.889 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38252396 | 1344 | 274.9028 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 131 | 42166811 | 4890 | 117.36 | 4.89 | 4.8 | 4.8 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38253740 | 1344 | 274.8466 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 130 | 42171392 | 4581 | 109.944 | 4.581 | 4.4 | 4.4 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38255054 | 1314 | 286.8369 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 143 | 139 | 42176093 | 4701 | 112.824 | 4.701 | 4 | 4 | 3B+1S | 0 | 975 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38256436 | 1382 | 293.98 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 130 | 42180793 | 4700 | 112.8 | 4.7 | 3.9 | 3.9 | 3B+1S | 0 | 950 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38257720 | 1284 | 273.1915 | 0% | 100% | 100% | 100% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 123 | 42185460 | 4667 | 112.008 | 4.667 | 3.2 | 3.2 | 2B+1S | 0 | 1119 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38258825 | 1105 | 236.7688 | 0% | 100% | 100% | 0% | 100% | 0% | 8631817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 125 | 42189958 | 4498 | 107.952 | 4.498 | 2.5 | 2.5 | 2B+1S | 0 | 1119 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38259896 | 1071 | 238.1058 | 0% | 100% | 100% | 0% | 100% | 0% | 8631817 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 113 | 42193352 | 3394 | 81.456 | 3.394 | 3.1 | 3.1 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38260804 | 908 | 267.5309 | 0% | 0% | 100% | 0% | 100% | 65% | 8633009 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 110 | 42196778 | 3426 | 82.224 | 3.426 | 4.4 | 4.4 | 2B | 0 | 0 | 1097 | 0 | 1188 | N/A | N/A | N/A | N/A | 38261668 | 864 | 252.1891 | 0% | 0% | 100% | 0% | 100% | 65% | 8634197 | 1188 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 105841 | 105841 | 105.841 | 105.841 | [12 empty] | 27704 | 27704 | 261.7511 | [6 empty] | 7461 | 7461 | 5.83 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (76%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:17 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 29, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | F.A.RAMOS / P.CINCO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27632 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42196778 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38261668 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8634197 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 104 | 42199965 | 3187 | 76.488 | 3.187 | 5.6 | 5.6 | 2B | 0 | 0 | 1098 | 0 | 1187 | N/A | N/A | N/A | N/A | 38262468 | 800 | 251.0198 | 0% | 0% | 100% | 0% | 100% | 75% | 8635260 | 1063 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 102 | 42203061 | 3096 | 74.304 | 3.096 | 6.8 | 6.8 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38263284 | 816 | 263.5659 | 0% | 0% | 100% | 0% | 100% | 75% | 8636478 | 1218 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 92 | 42206255 | 3194 | 76.656 | 3.194 | 8.2 | 8.2 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38264064 | 780 | 244.2079 | 0% | 0% | 100% | 0% | 100% | 75% | 8637816 | 1338 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 108 | 42209176 | 2921 | 70.104 | 2.921 | 9.3 | 9.3 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38264812 | 748 | 256.0767 | 0% | 0% | 100% | 0% | 100% | 75% | 8638770 | 954 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 122 | 101 | 42212189 | 3013 | 72.312 | 3.013 | 9.5 | 9.5 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38265556 | 744 | 246.93 | 0% | 0% | 100% | 0% | 100% | 75% | 8639159 | 389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 142 | 42215876 | 3687 | 88.488 | 3.687 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38266404 | 848 | 229.9973 | 0% | 0% | 100% | 0% | 100% | 0% | 8639159 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 159 | 42221214 | 5338 | 128.112 | 5.338 | 9.2 | 9.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38267804 | 1400 | 262.2705 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 101 | 42226634 | 5420 | 130.08 | 5.42 | 8.8 | 8.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38269124 | 1320 | 243.5424 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 146 | 42232170 | 5536 | 132.864 | 5.536 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38270532 | 1408 | 254.3353 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 114 | 42237372 | 5202 | 124.848 | 5.202 | 7.6 | 7.6 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38271844 | 1312 | 252.2107 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 | 0.93 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 143 | 42242951 | 5579 | 133.896 | 5.579 | 7.3 | 7.3 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38273216 | 1372 | 245.9222 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 149 | 42248405 | 5454 | 130.896 | 5.454 | 6.9 | 6.9 | 3B+1S | 0 | 11027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38274592 | 1376 | 252.2919 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 140 | 42253507 | 5102 | 122.448 | 5.102 | 6.5 | 6.5 | 3B+1S | 0 | 11026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38275924 | 1332 | 261.0741 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 134 | 42258512 | 5005 | 120.12 | 5.005 | 6.1 | 6.1 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38277312 | 1388 | 277.3227 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 42263384 | 4872 | 116.928 | 4.872 | 5.7 | 5.7 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38278660 | 1348 | 276.6831 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 148 | 42268090 | 4706 | 112.944 | 4.706 | 5.4 | 5.4 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38280008 | 1348 | 286.4428 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 42272731 | 4641 | 111.384 | 4.641 | 5 | 5 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38281324 | 1316 | 283.5596 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 42277454 | 4723 | 113.352 | 4.723 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38282668 | 1344 | 284.5649 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 142 | 42282177 | 4723 | 113.352 | 4.723 | 4.3 | 4.3 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38284012 | 1344 | 284.5649 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 131 | 42286866 | 4689 | 112.536 | 4.689 | 4.2 | 4.2 | 3B+1S | 0 | 985 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38285340 | 1328 | 283.216 | 0% | 100% | 100% | 100% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 42291260 | 4394 | 105.456 | 4.394 | 3.6 | 3.6 | 3B+1S | 0 | 1129 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38286436 | 1096 | 249.431 | 0% | 100% | 100% | 0% | 100% | 0% | 8639159 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 119 | 42295700 | 4440 | 106.56 | 4.44 | 2.5 | 2.5 | 2B+1S | 0 | 1127 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38287544 | 1108 | 249.5495 | 0% | 100% | 100% | 0% | 100% | 0% | 8639159 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 124 | 42299201 | 3501 | 84.024 | 3.501 | 3.1 | 3.1 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38288456 | 912 | 260.497 | 0% | 0% | 100% | 0% | 100% | 65% | 8639971 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 143 | 108 | 42302170 | 2969 | 71.256 | 2.969 | 4.4 | 4.4 | 2B | 0 | 0 | 1168 | 0 | 1187 | N/A | N/A | N/A | N/A | 38289300 | 844 | 284.2708 | 0% | 0% | 100% | 0% | 100% | 65% | 8641107 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 105392 | 105392 | 105.392 | 105.392 | [12 empty] | 27632 | 27632 | 262.1831 | [6 empty] | 6910 | 6910 | 6.04 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 30, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JUNE 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY/ ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-06-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27189 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42302170 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | N/A | 38289300 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8641107 |  | mg /l |  | Automatic - i2O | AI | GLITTERS. SY
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 144 | 99 | 42305331 | 3161 | 75.864 | 3.161 | 6.1 | 6.1 | 2B | 0 | 0 | 1026 | 0 | 1187 | N/A | N/A | N/A | N/A | 38290084 | 784 | 248.0228 | 0% | 0% | 100% | 0% | 100% | 75% | 8642461 | 1354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | ALEXANDER CABREROS
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 101 | 42308216 | 2885 | 69.24 | 2.885 | 7.5 | 7.5 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38290832 | 748 | 259.2721 | 0% | 0% | 100% | 0% | 100% | 75% | 8644040 | 1579 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL A. RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 104 | 42311229 | 3013 | 72.312 | 3.013 | 8.2 | 8.2 | 2B | 0 | 0 | 1027 | 0 | 1188 | N/A | N/A | N/A | N/A | 38291578 | 746 | 247.5938 | 0% | 0% | 100% | 0% | 100% | 75% | 8644788 | 748 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | F.A.RAMOS / P.CINCO
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 135 | 99 | 42314118 | 2889 | 69.336 | 2.889 | 8.8 | 8.8 | 2B | 0 | 0 | 1026 | 0 | 1187 | N/A | N/A | N/A | N/A | 38292300 | 722 | 249.9135 | 0% | 0% | 100% | 0% | 100% | 75% | 8645426 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | F.A.RAMOS / A.DELOS ANGELES
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 122 | 108 | 42317033 | 2915 | 69.96 | 2.915 | 9.5 | 9.5 | 2B | 0 | 0 | 1026 | 0 | 1188 | N/A | N/A | N/A | N/A | 38293040 | 740 | 253.8593 | 0% | 0% | 100% | 0% | 100% | 75% | 8646054 | 628 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY/ ANDRO MIRAFLOR
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 117 | 42320832 | 3799 | 91.176 | 3.799 | 9.5 | 9.5 | 2B | 0 |  | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38293928 | 888 | 233.7457 | 0% | 0% | 100% | 0% | 100% | 0% | 8646054 | 0 | 1.07 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 145 | 42326313 | 5481 | 131.544 | 5.481 | 9.2 | 9.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38295320 | 1392 | 253.9683 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 136 | 42331450 | 5137 | 123.288 | 5.137 | 8.7 | 8.7 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38296644 | 1324 | 257.738 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 143 | 42336756 | 5306 | 127.344 | 5.306 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38297992 | 1348 | 254.052 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 144 | 42342063 | 5307 | 127.368 | 5.307 | 7.8 | 7.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38299384 | 1392 | 262.2951 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 9 | 5.6 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 137 | 42347268 | 5205 | 124.92 | 5.205 | 7.4 | 7.4 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38300756 | 1372 | 263.5927 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 117 | 42352273 | 5005 | 120.12 | 5.005 | 7 | 7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38302100 | 1344 | 268.5315 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 143 | 42357221 | 4948 | 118.752 | 4.948 | 6.6 | 6.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38303480 | 1380 | 278.9006 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 42362035 | 4814 | 115.536 | 4.814 | 6.2 | 6.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38304796 | 1316 | 273.3693 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 42367128 | 5093 | 122.232 | 5.093 | 5.8 | 5.8 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38306220 | 1424 | 279.5995 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 42371684 | 4556 | 109.344 | 4.556 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38307532 | 1312 | 287.9719 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 42376166 | 4482 | 107.568 | 4.482 | 5.3 | 5.3 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38308840 | 1308 | 291.834 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 42380902 | 4736 | 113.664 | 4.736 | 5.1 | 5.1 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38310164 | 1324 | 279.5608 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 132 | 42385655 | 4753 | 114.072 | 4.753 | 5 | 5 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38311504 | 1340 | 281.9272 | 0% | 100% | 100% | 100% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 122 | 42390082 | 4427 | 106.248 | 4.427 | 4 | 4 | 2B+1S | 0 | 1118 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38312620 | 1116 | 252.0895 | 0% | 100% | 100% | 0% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 119 | 42394232 | 4150 | 99.6 | 4.15 | 3.1 | 3.1 | 2B+1S | 0 | 1118 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38313708 | 1088 | 262.1687 | 0% | 100% | 100% | 0% | 100% | 0% | 8646054 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 121 | 42398326 | 4094 | 98.256 | 4.094 | 2.4 | 2.4 | 2B+1S | 0 | 1117 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38314740 | 1032 | 252.0762 | 0% | 100% | 100% | 0% | 100% | 0% | 8646054 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 104 | 42401868 | 3542 | 85.008 | 3.542 | 3.1 | 3.1 | 2B | 0 | 0 | 1157 | 0 | 1187 | N/A | N/A | N/A | N/A | 38315656 | 916 | 258.611 | 0% | 0% | 100% | 0% | 100% | 60% | 8646886 | 832 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 142 | 141 | 42405060 | 3192 | 76.608 | 3.192 | 4.3 | 4.3 | 2B | 0 | 0 | 1157 | 0 | 1188 | N/A | N/A | N/A | N/A | 38316489 | 833 | 260.9649 | 0% | 0% | 100% | 0% | 100% | 60% | 8647935 | 1049 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 102890 | 102890 | 102.89 | 102.89 | [12 empty] | 27189 | 27189 | 264.2531 | [6 empty] | 6828 | 6828 | 5.72 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr. Frances Morla (SPM-South)
XCV1 - INCREASE OPENING TO (75%) @ 12:01 AM FOR REFILLING
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:04 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 01, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (60%)