## JULY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27331 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42405060 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38316489 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8647935 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 93 | 42408216 | 3156 | 75.744 | 3.156 | 5.3 | 5.3 | 2B | 0 | 0 | 1156 | 0 | 1188 | N/A | N/A | N/A | N/A | 38317388 | 899 | 284.8542 | 0% | 0% | 100% | 0% | 100% | 75% | 8648877 | 942 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 100 | 42411654 | 3438 | 82.512 | 3.438 | 6.5 | 6.5 | 2B | 0 | 0 | 1077 | 0 | 1188 | N/A | N/A | N/A | N/A | 38318268 | 880 | 255.9628 | 0% | 0% | 100% | 0% | 100% | 75% | 8650030 | 1153 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 160 | 42414558 | 2904 | 69.696 | 2.904 | 7.7 | 7.7 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38319020 | 752 | 258.9532 | 0% | 0% | 100% | 0% | 100% | 75% | 8651208 | 1178 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 101 | 42417882 | 3324 | 79.776 | 3.324 | 8.8 | 8.8 | 2B | 0 | 0 | 1035 | 0 | 1188 | N/A | N/A | N/A | N/A | 38319808 | 788 | 237.0638 | 0% | 0% | 100% | 0% | 100% | 75% | 8652211 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 125 | 111 | 42421036 | 3154 | 75.696 | 3.154 | 9.5 | 9.5 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38320572 | 764 | 242.2321 | 0% | 0% | 100% | 0% | 100% | 75% | 8652802 | 591 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 122 | 42424813 | 3777 | 90.648 | 3.777 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38321436 | 864 | 228.753 | 0% | 0% | 100% | 0% | 100% | 0% | 8652802 | 0 | 1.01 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 146 | 42429820 | 5007 | 120.168 | 5.007 | 9 | 9 | 3b+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38322764 | 1328 | 265.2287 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 148 | 42434934 | 5114 | 122.736 | 5.114 | 8.4 | 8.4 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38324144 | 1380 | 269.8475 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 153 | 42440350 | 5416 | 129.984 | 5.416 | 7.7 | 7.7 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38325536 | 1392 | 257.0162 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 168 | 42445897 | 5547 | 133.128 | 5.547 | 7.2 | 7.2 | 3B+1S | 0 | 1048 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38327008 | 1472 | 265.3687 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 132 | 42451592 | 5695 | 136.68 | 5.695 | 6.6 | 6.6 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38328436 | 1428 | 250.7463 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 42456022 | 4430 | 106.32 | 4.43 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38329672 | 1236 | 279.0068 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 133 | 42460868 | 4846 | 116.304 | 4.846 | 5.8 | 5.8 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38331036 | 1364 | 281.4693 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 141 | 139 | 42465799 | 4931 | 118.344 | 4.931 | 5.6 | 5.6 | 3B+1S | 0 | 973 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38332424 | 1388 | 281.4845 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 103 | 42470033 | 4234 | 101.616 | 4.234 | 5.5 | 5.5 | 3B+1S | 0 | 975 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38333700 | 1276 | 301.3699 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 137 | 42474326 | 4293 | 103.032 | 4.293 | 5.4 | 5.4 | 3B+1S | 0 | 996 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38335012 | 1312 | 305.6138 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 42478826 | 4500 | 108 | 4.5 | 5.3 | 5.3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38336324 | 1312 | 291.5556 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 134 | 42483828 | 5002 | 120.048 | 5.002 | 5.1 | 5.1 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38337732 | 1408 | 281.4874 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 102 | 42488087 | 4259 | 102.216 | 4.259 | 5 | 5 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38339020 | 1288 | 302.4184 | 0% | 100% | 100% | 100% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 133 | 42492578 | 4491 | 107.784 | 4.491 | 4.5 | 4.5 | 2B+1S | 0 | 996 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38340104 | 1084 | 241.3716 | 0% | 100% | 100% | 0% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 129 | 42496888 | 4310 | 103.44 | 4.31 | 4 | 4 | 2B+1S | 0 | 996 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38341116 | 1012 | 234.8028 | 0% | 100% | 100% | 0% | 100% | 0% | 8652802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 140 | 42501090 | 4202 | 100.848 | 4.202 | 3.5 | 3.5 | 2B+1S | 0 | 995 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38342116 | 1000 | 237.9819 | 0% | 100% | 100% | 0% | 100% | 0% | 8652802 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 98 | 42504590 | 3500 | 84 | 3.5 | 4.3 | 4.3 | 2B | 0 | 0 | 1127 | 0 | 1187 | N/A | N/A | N/A | N/A | 38342980 | 864 | 246.8571 | 0% | 0% | 100% | 0% | 100% | 60% | 8653580 | 778 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 115 | 42507875 | 3285 | 78.84 | 3.285 | 5.3 | 5.3 | 2B | 0 | 0 | 1128 | 0 | 1188 | N/A | N/A | N/A | N/A | 38343820 | 840 | 255.7078 | 0% | 0% | 100% | 0% | 100% | 60% | 8654565 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.5 | 102815 | 102815 | 102.815 | 102.815 | [12 empty] | 27331 | 27331 | 265.827 | [6 empty] | 6630 | 6630 | 1.0183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (%) @ 12:01 AM
XCV1 CLOSED @ 5:02 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 02, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
Mr. Jake Hernandez and team IT personnel preventive maintenance of network aquipment arrived at 1:53pm check out 2:24pm
Mr. Arturo Trinidad assisted the Makati Foundry personnel arrived at 2:28pm
Mr. Jun Naval assisted the Makati Foundry personnel to the install of reducer of BP#4 arrived at 3:47pm
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (60%)

## JULY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27224 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42507875 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38343820 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8654565 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 100 | 42511130 | 3255 | 78.12 | 3.255 | 6.1 | 6.1 | 2B | 0 | 0 | 1036 | 0 | 1188 | N/A | N/A | N/A | N/A | 38344652 | 832 | 255.6068 | 0% | 0% | 100% | 0% | 100% | 70% | 8655303 | 738 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 110 | 42513946 | 2816 | 67.584 | 2.816 | 7.1 | 7.1 | 2B | 0 | 0 | 1037 | 0 | 1188 | N/A | N/A | N/A | N/A | 38345412 | 760 | 269.8864 | 0% | 0% | 100% | 0% | 100% | 70% | 8656340 | 1037 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 105 | 42517125 | 3179 | 76.296 | 3.179 | 8.4 | 8.4 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38346212 | 800 | 251.6515 | 0% | 0% | 100% | 0% | 100% | 70% | 8657428 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 104 | 42520253 | 3128 | 75.072 | 3.128 | 9.2 | 9.2 | 2B | 0 | 0 | 1036 | 0 | 1187 | N/A | N/A | N/A | N/A | 38346948 | 736 | 235.2941 | 0% | 0% | 100% | 0% | 100% | 70% | 8658249 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 109 | 42523678 | 3425 | 82.2 | 3.425 | 9.5 | 9.5 | 2B | 0 | 0 | 1038 | 0 | 1188 | N/A | N/A | N/A | N/A | 38347740 | 792 | 231.2409 | 0% | 0% | 100% | 0% | 100% | 70% | 8658554 | 305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 131 | 42527486 | 3808 | 91.392 | 3.808 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38348588 | 848 | 222.6891 | 0% | 0% | 100% | 0% | 100% | 0% | 8658554 | 0 | 0.81 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 148 | 42532597 | 5111 | 122.664 | 5.111 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38349912 | 1324 | 259.0491 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 101 | 42537884 | 5287 | 126.888 | 5.287 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38351244 | 1332 | 251.9387 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 159 | 42543102 | 5218 | 125.232 | 5.218 | 8.1 | 8.1 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38352672 | 1428 | 273.6681 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 134 | 42548095 | 4993 | 119.832 | 4.993 | 7.6 | 7.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38354032 | 1360 | 272.3813 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 | 0.9 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 148 | 101 | 42553093 | 4998 | 119.952 | 4.998 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38355416 | 1384 | 276.9108 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 136 | 42557932 | 4839 | 116.136 | 4.839 | 6.8 | 6.8 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38356741 | 1325 | 273.8169 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 104 | 42562943 | 5011 | 120.264 | 5.011 | 6.4 | 6.4 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38358156 | 1415 | 282.3788 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 100 | 42567718 | 4775 | 114.6 | 4.775 | 6 | 6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38359524 | 1368 | 286.4921 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 129 | 42571907 | 4189 | 100.536 | 4.189 | 5.7 | 5.7 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38360772 | 1248 | 297.9231 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 124 | 42576378 | 4471 | 107.304 | 4.471 | 5.4 | 5.4 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38362124 | 1352 | 302.3932 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 42580988 | 4610 | 110.64 | 4.61 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38363448 | 1324 | 287.2017 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 142 | 42585466 | 4478 | 107.472 | 4.478 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38364788 | 1340 | 299.2407 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 138 | 42590278 | 4812 | 115.488 | 4.812 | 4.4 | 4.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38366140 | 1352 | 280.9643 | 0% | 100% | 100% | 100% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 120 | 136 | 42594653 | 4375 | 105 | 4.375 | 3.7 | 3.7 | 2B+1S | 0 | 1026 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 38367228 | 1088 | 248.6857 | 0% | 100% | 100% | 0% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 124 | 42598789 | 4136 | 99.264 | 4.136 | 3.2 | 3.2 | 2B+1S | 0 | 1026 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38368288 | 1060 | 256.2863 | 0% | 100% | 100% | 0% | 100% | 0% | 8658554 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 134 | 42602734 | 3945 | 94.68 | 3.945 | 2.7 | 2.7 | 2B+1S | 0 | 1025 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38369332 | 1044 | 264.6388 | 0% | 100% | 100% | 0% | 100% | 0% | 8658554 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 114 | 42606270 | 3536 | 84.864 | 3.536 | 3.7 | 3.7 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 38370244 | 912 | 257.9186 | 0% | 0% | 100% | 0% | 100% | 55% | 8659636 | 1082 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 108 | 42609542 | 3272 | 78.528 | 3.272 | 5.1 | 5.1 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 38371044 | 800 | 244.4988 | 0% | 0% | 100% | 0% | 100% | 55% | 8660774 | 1138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.125 | 101667 | 101667 | 101.667 | 101.667 | [12 empty] | 27224 | 27224 | 267.7762 | [6 empty] | 6209 | 6209 | 0.99167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (%) @ 12:01 AM
XCV1 CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 03, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25568 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42609542 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38371044 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8660774 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 96 | 42612621 | 3079 | 73.896 | 3.079 | 6.2 | 6.2 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38371783 | 739 | 240.013 | 0% | 0% | 100% | 0% | 100% | 65% | 8661774 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 93 | 42615704 | 3083 | 73.992 | 3.083 | 7.4 | 7.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38372493 | 710 | 230.2952 | 0% | 0% | 100% | 0% | 100% | 65% | 8662722 | 948 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 97 | 42618799 | 3095 | 74.28 | 3.095 | 8.2 | 8.2 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38373241 | 748 | 241.6801 | 0% | 0% | 100% | 0% | 100% | 65% | 8663690 | 968 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 103 | 42621879 | 3080 | 73.92 | 3.08 | 9.1 | 9.1 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38374000 | 759 | 246.4286 | 0% | 0% | 100% | 0% | 100% | 65% | 8664663 | 973 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 111 | 42625228 | 3349 | 80.376 | 3.349 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38374756 | 756 | 225.739 | 0% | 0% | 100% | 0% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 121 | 42628765 | 3537 | 84.888 | 3.537 | 9.5 | 9.5 | 2B | 0 | 0 | 1108 |  | 1107 | N/A | N/A | N/A | N/A | 38375472 | 716 | 202.4314 | 0% | 0% | 100% | 0% | 100% | 0% | 8664663 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 124 | 147 | 42633628 | 4863 | 116.712 | 4.863 | 8.8 | 8.8 | 3B+1S | 0 | 1027 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38376668 | 1196 | 245.9387 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 42638174 | 4546 | 109.104 | 4.546 | 8.2 | 8.2 | 3B+1S | 0 | 1138 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38377892 | 1224 | 269.2477 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 134 | 42642970 | 4796 | 115.104 | 4.796 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 38379128 | 1236 | 257.7148 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 42647702 | 4732 | 113.568 | 4.732 | 7 | 7 | 3B+1S | 0 | 1006 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38380356 | 1228 | 259.5097 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 | 0.69 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 134 | 42652767 | 5065 | 121.56 | 5.065 | 6.5 | 6.5 | 3B+1S | 0 | 1007 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38381572 | 1216 | 240.079 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 42657256 | 4489 | 107.736 | 4.489 | 6.1 | 6.1 | 3B+1S | 0 | 1005 | 1106 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38382776 | 1204 | 268.2112 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 122 | 42661608 | 4352 | 104.448 | 4.352 | 5.6 | 5.6 | 3B+1S | 0 | 1005 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38383980 | 1204 | 276.6544 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 109 | 42666377 | 4769 | 114.456 | 4.769 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 1106 | 1185 | 1107 | N/A | N/A | N/A | N/A | 38385204 | 1224 | 256.6576 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 130 | 42670198 | 3821 | 91.704 | 3.821 | 4.8 | 4.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38386472 | 1268 | 331.8503 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 104 | 42675236 | 5038 | 120.912 | 5.038 | 4.7 | 4.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38387760 | 1288 | 255.657 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 121 | 42680055 | 4819 | 115.656 | 4.819 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38389108 | 1348 | 279.7261 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 142 | 143 | 42684333 | 4278 | 102.672 | 4.278 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38390372 | 1264 | 295.4652 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 142 | 133 | 42688860 | 4527 | 108.648 | 4.527 | 4 | 4 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38391748 | 1376 | 303.9541 | 0% | 100% | 100% | 100% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 124 | 123 | 42692969 | 4109 | 98.616 | 4.109 | 3.5 | 3.5 | 2B+1S | 0 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38392788 | 1040 | 253.1029 | 0% | 100% | 100% | 0% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 122 | 131 | 42696966 | 3997 | 95.928 | 3.997 | 3.1 | 3.1 | 2B+1S | 0 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38393828 | 1040 | 260.1951 | 0% | 100% | 100% | 0% | 100% | 0% | 8664663 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 127 | 42700852 | 3886 | 93.264 | 3.886 | 2.7 | 2.7 | 2B+1S | 0 | 1006 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38394876 | 1048 | 269.6861 | 0% | 100% | 100% | 0% | 100% | 0% | 8664663 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 121 | 42704420 | 3568 | 85.632 | 3.568 | 3.7 | 3.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38395800 | 924 | 258.9686 | 0% | 0% | 100% | 0% | 100% | 65% | 8665769 | 1106 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 108 | 42707664 | 3244 | 77.856 | 3.244 | 4.9 | 4.9 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38396612 | 812 | 250.3083 | 0% | 0% | 100% | 0% | 100% | 65% | 8666873 | 1104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.5417 | 98122 | 98122 | 98.122 | 98.122 | [12 empty] | 25568 | 25568 | 260.5736 | [6 empty] | 6099 | 6099 | 0.885 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (65%) @ 12:01 AM
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 04, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (65%)

## JULY 4
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
| WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[14 empty] | 10pm - 6am | ALEXANDER CABREROS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2015-07-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26919 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42707664 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38396612 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8666873 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
| 48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 102 | 42711007 | 3343 | 80.232 | 3.343 | 5.9 | 5.9 | 2B | 0 | 0 | 1129 | 0 | 1129 | N/A | N/A | N/A | N/A | 38397384 | 772 | 230.9303 | 0% | 0% | 100% | 0% | 100% | 70% | 8667803 | 930 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 97 | 42714102 | 3095 | 74.28 | 3.095 | 7.3 | 7.3 | 2B | 0 | 0 | 1129 | 0 | 1129 | N/A | N/A | N/A | N/A | 38398118 | 734 | 237.1567 | 0% | 0% | 100% | 0% | 100% | 70% | 8668759 | 956 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
| 50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 99 | 42717173 | 3071 | 73.704 | 3.071 | 8 | 8 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 38398847 | 729 | 237.382 | 0% | 0% | 100% | 0% | 100% | 70% | 8669709 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
| 51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 101 | 42720250 | 3077 | 73.848 | 3.077 | 8.9 | 8.9 | 2B | 0 | 0 | 1097 | 0 | 1107 | N/A | N/A | N/A | N/A | 38399588 | 741 | 240.819 | 0% | 0% | 100% | 0% | 100% | 70% | 8670671 | 962 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
| 52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 92 | 42723796 | 3546 | 85.104 | 3.546 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1107 | N/A | N/A | N/A | N/A | 38400356 | 768 | 216.5821 | 0% | 0% | 100% | 0% | 100% | 70% | 8671482 | 811 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
| 53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 42727390 | 3594 | 86.256 | 3.594 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38401116 | 760 | 211.4636 | 0% | 0% | 100% | 0% | 100% | 0% | 8671482 | 0 | 0.57 | Normal operation schedule | Error - General | E
| 54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 151 | 142 | 42731961 | 4571 | 109.704 | 4.571 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38402356 | 1240 | 271.2754 | 0% | 0% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Normal operation schedule | Power Interruption | PI
| 55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 121 | 42737020 | 5059 | 121.416 | 5.059 | 9.4 | 9.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38403708 | 1352 | 267.2465 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 146 | 42742330 | 5310 | 127.44 | 5.31 | 9 | 9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38405108 | 1400 | 263.6535 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 134 | 42747182 | 4852 | 116.448 | 4.852 | 8.5 | 8.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38406452 | 1344 | 276.9992 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 | 0.64 | Normal operation schedule
| 58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 142 | 42752650 | 5468 | 131.232 | 5.468 | 8 | 8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38407856 | 1404 | 256.7666 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 134 | 42757981 | 5331 | 127.944 | 5.331 | 7.6 | 7.6 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38409196 | 1340 | 251.36 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 145 | 42762710 | 4729 | 113.496 | 4.729 | 7.1 | 7.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38410580 | 1384 | 292.6623 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 150 | 42767401 | 4691 | 112.584 | 4.691 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38411912 | 1332 | 283.948 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 | 0.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 145 | 42772082 | 4681 | 112.344 | 4.681 | 5.8 | 5.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38413278 | 1366 | 291.818 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 152 | 42776590 | 4508 | 108.192 | 4.508 | 5.4 | 5.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38414649 | 1371 | 304.126 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 42781142 | 4552 | 109.248 | 4.552 | 5 | 5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38415992 | 1343 | 295.0351 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 109 | 42785829 | 4687 | 112.488 | 4.687 | 4.6 | 4.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38417308 | 1316 | 280.7766 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 138 | 42790145 | 4316 | 103.584 | 4.316 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38418624 | 1316 | 304.912 | 0% | 100% | 100% | 100% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 42794289 | 4144 | 99.456 | 4.144 | 3.4 | 3.4 | 2B+1S | 0 | 1047 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38419704 | 1080 | 260.6178 | 0% | 100% | 100% | 0% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
s | 68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 124 | 42798276 | 3987 | 95.688 | 3.987 | 2.8 | 2.8 | 2B+1S | 0 | 1047 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38420748 | 1044 | 261.851 | 0% | 100% | 100% | 0% | 100% | 0% | 8671482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 120 | 42802105 | 3829 | 91.896 | 3.829 | 2.4 | 2.4 | 2B+1S | 0 | 1015 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38421780 | 1032 | 269.5221 | 0% | 100% | 100% | 0% | 100% | 0% | 8671482 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 105 | 42805425 | 3320 | 79.68 | 3.32 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38422662 | 882 | 265.6627 | 0% | 0% | 100% | 0% | 100% | 60% | 8672402 | 920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 97 | 42808543 | 3118 | 74.832 | 3.118 | 4.7 | 4.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38423531 | 869 | 278.7043 | 0% | 0% | 100% | 0% | 100% | 60% | 8673388 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL |  |  |  | 124.4167 | 100879 | 100879 | 100.879 | 100.879 | [12 empty] | 26919 | 26919 | 266.8444 | [7 empty] | 6515 | 0.8 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 05, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (60%)

## JULY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26673 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42808543 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38423531 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8673388 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 108 | 42811582 | 3039 | 72.936 | 3.039 | 5.6 | 5.6 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 38424399 | 868 | 285.6203 | 0% | 0% | 100% | 0% | 100% | 70% | 8674477 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 105 | 42814631 | 3049 | 73.176 | 3.049 | 6.9 | 6.9 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 38425261 | 862 | 282.7156 | 0% | 0% | 100% | 0% | 100% | 70% | 8675557 | 1080 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 90 | 42817683 | 3052 | 73.248 | 3.052 | 7.8 | 7.8 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 38426128 | 867 | 284.076 | 0% | 0% | 100% | 0% | 100% | 70% | 8676655 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 94 | 42820722 | 3039 | 72.936 | 3.039 | 9 | 9 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 38426892 | 764 | 251.3985 | 0% | 0% | 100% | 0% | 100% | 70% | 8677756 | 1101 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 104 | 42823891 | 3169 | 76.056 | 3.169 | 9.5 | 9.5 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 38427676 | 784 | 247.3967 | 0% | 0% | 100% | 0% | 100% | 70% | 8678254 | 498 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 106 | 42827191 | 3300 | 79.2 | 3.3 | 9.5 | 9.5 | 2B | 0 | 0 | 1128 | 0 | 1127 | N/A | N/A | N/A | N/A | 38428464 | 788 | 238.7879 | 0% | 0% | 100% | 0% | 100% | 0% | 8678254 | 0 | 0.63 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 122 | 42831550 | 4359 | 104.616 | 4.359 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38429700 | 1236 | 283.5513 | 0% | 0% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 134 | 42835857 | 4307 | 103.368 | 4.307 | 9.5 | 9.5 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38431004 | 1304 | 302.7629 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 147 | 42840620 | 4763 | 114.312 | 4.763 | 9.2 | 9.2 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38432364 | 1360 | 285.5343 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 106 | 42845329 | 4709 | 113.016 | 4.709 | 8.8 | 8.8 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38433676 | 1312 | 278.6154 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 | 0.46 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 143 | 42850020 | 4691 | 112.584 | 4.691 | 8.5 | 8.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38435008 | 1332 | 283.948 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 120 | 42854955 | 4935 | 118.44 | 4.935 | 8.1 | 8.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38436348 | 1340 | 271.5299 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 148 | 42859574 | 4619 | 110.856 | 4.619 | 7.7 | 7.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38437704 | 1356 | 293.57 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 42864169 | 4595 | 110.28 | 4.595 | 7.4 | 7.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38439060 | 1356 | 295.1034 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 | 0.77 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 42869041 | 4872 | 116.928 | 4.872 | 6.9 | 6.9 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38440444 | 1384 | 284.0722 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 42873070 | 4029 | 96.696 | 4.029 | 6.7 | 6.7 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38441672 | 1228 | 304.7903 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 118 | 42877720 | 4650 | 111.6 | 4.65 | 6.5 | 6.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38443012 | 1340 | 288.172 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 42882256 | 4536 | 108.864 | 4.536 | 6.2 | 6.2 | 3B+1S | 0 | 1013 | 1157 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38444288 | 1276 | 281.3051 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 42886589 | 4333 | 103.992 | 4.333 | 6 | 6 | 3B+1S | 0 | 1014 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38445596 | 1308 | 301.8694 | 0% | 100% | 100% | 100% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 110 | 42890278 | 3689 | 88.536 | 3.689 | 5.7 | 5.7 | 2B+1S | 0 | 1015 | 1157 | 0 | 1189 | N/A | N/A | N/A | N/A | 38446588 | 992 | 268.9076 | 0% | 100% | 100% | 0% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 115 | 42893980 | 3702 | 88.848 | 3.702 | 5.1 | 5.1 | 2B+1S | 0 | 1015 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38447612 | 1024 | 276.6072 | 0% | 100% | 100% | 0% | 100% | 0% | 8678254 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 113 | 42897668 | 3688 | 88.512 | 3.688 | 4.8 | 4.8 | 2B+1S | 0 | 1015 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38448668 | 1056 | 286.3341 | 0% | 100% | 100% | 0% | 100% | 0% | 8678254 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 105 | 42900750 | 3082 | 73.968 | 3.082 | 6 | 6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38449444 | 776 | 251.7846 | 0% | 0% | 100% | 0% | 100% | 50% | 8679526 | 1272 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 104 | 42903772 | 3022 | 72.528 | 3.022 | 7.5 | 7.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38450204 | 760 | 251.4891 | 0% | 0% | 100% | 0% | 100% | 50% | 8680881 | 1355 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.5 | 95229 | 95229 | 95.229 | 95.229 | [12 empty] | 26673 | 26673 | 280.0932 | [6 empty] | 7493 | 7493 | 0.83333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (70%) @ 12:01 AM
XCV1 CLOSED @ 4:39 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 06, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (60%)

## JULY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25820 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 42903772 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38450204 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8680881 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 112 | 88 | 42906507 | 2735 | 65.64 | 2.735 | 8.5 | 8.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 38450858 | 654 | 239.1225 | 0% | 0% | 100% | 0% | 100% | 60% | 8681917 | 1036 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 92 | 42909242 | 2735 | 65.64 | 2.735 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 38451512 | 654 | 239.1225 | 0% | 0% | 100% | 0% | 100% | 60% | 8682954 | 1037 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 105 | 102 | 42912267 | 3025 | 72.6 | 3.025 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 38452181 | 669 | 221.157 | 0% | 0% | 100% | 0% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 105 | 42915286 | 3019 | 72.456 | 3.019 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 38452848 | 667 | 220.9341 | 0% | 0% | 100% | 0% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 116 | 42918309 | 3023 | 72.552 | 3.023 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 38453512 | 664 | 219.6494 | 0% | 0% | 100% | 0% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 107 | 42921471 | 3162 | 75.888 | 3.162 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38454172 | 660 | 208.7287 | 0% | 0% | 100% | 0% | 100% | 0% | 8682954 | 0 | 0.66 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 140 | 42926110 | 4639 | 111.336 | 4.639 | 9.3 | 9.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38455468 | 1296 | 279.3706 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 151 | 42930694 | 4584 | 110.016 | 4.584 | 9.1 | 9.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38456812 | 1344 | 293.1937 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 144 | 42935650 | 4956 | 118.944 | 4.956 | 8.8 | 8.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38458164 | 1352 | 272.8006 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 146 | 142 | 42940907 | 5257 | 126.168 | 5.257 | 8.4 | 8.4 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38459512 | 1348 | 256.42 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 | 0.77 | Normal operation schedule
58:00 | 11:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 | 159 | 42946022 | 5115 | 122.76 | 5.115 | 8.1 | 8.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38460892 | 1380 | 269.7947 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 132 | 42951271 | 5249 | 125.976 | 5.249 | 7.9 | 7.9 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38462212 | 1320 | 251.4765 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 102 | 42956133 | 4862 | 116.688 | 4.862 | 7.7 | 7.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38463564 | 1352 | 278.0749 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 42960819 | 4686 | 112.464 | 4.686 | 7.5 | 7.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38464892 | 1328 | 283.3974 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 128 | 42965298 | 4479 | 107.496 | 4.479 | 7.3 | 7.3 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38466188 | 1296 | 289.3503 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 151 | 42970220 | 4922 | 118.128 | 4.922 | 7.1 | 7.1 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38467520 | 1332 | 270.6217 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 42974622 | 4402 | 105.648 | 4.402 | 7 | 7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38468812 | 1292 | 293.503 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 111 | 42979163 | 4541 | 108.984 | 4.541 | 6.8 | 6.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38470112 | 1300 | 286.2806 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 126 | 42983538 | 4375 | 105 | 4.375 | 6.6 | 6.6 | 3B+1S | 0 | 1003 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38471372 | 1260 | 288 | 0% | 100% | 100% | 100% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 121 | 42987217 | 3679 | 88.296 | 3.679 | 6 | 6 | 2B+1S | 0 | 1006 | 1106 | 0 | 1188 | N/A | N/A | N/A | N/A | 38472380 | 1008 | 273.9875 | 0% | 100% | 100% | 0% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 118 | 42990937 | 3720 | 89.28 | 3.72 | 5.5 | 5.5 | 2B+1S | 0 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38473372 | 992 | 266.6667 | 0% | 100% | 100% | 0% | 100% | 0% | 8682954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 104 | 42994463 | 3526 | 84.624 | 3.526 | 5.1 | 5.1 | 2B+1S | 0 | 1005 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38474356 | 984 | 279.0698 | 0% | 100% | 100% | 0% | 100% | 0% | 8682954 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 106 | 42997725 | 3262 | 78.288 | 3.262 | 6.1 | 6.1 | 2B | 0 | 0 | 1107 | 0 | 1188 | N/A | N/A | N/A | N/A | 38475224 | 868 | 266.0944 | 0% | 0% | 100% | 0% | 100% | 50% | 8684030 | 1076 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 98 | 43000755 | 3030 | 72.72 | 3.03 | 7.2 | 7.2 | 2B | 0 | 0 | 1107 | 0 | 1188 | N/A | N/A | N/A | N/A | 38476024 | 800 | 264.0264 | 0% | 0% | 100% | 0% | 100% | 50% | 8685188 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.625 | 96983 | 96983 | 96.983 | 96.983 | [12 empty] | 25820 | 25820 | 266.2322 | [6 empty] | 4307 | 4307 | 0.90667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 1:57 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 07, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26722 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43000755 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38476024 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8685188 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 96 | 43003858 | 3103 | 74.472 | 3.103 | 8.3 | 8.3 | 2B | 0 | 0 | 1006 | 0 | 1188 | N/A | N/A | N/A | N/A | 38476804 | 780 | 251.3696 | 0% | 0% | 100% | 0% | 100% | 60% | 8686166 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 95 | 43006656 | 2798 | 67.152 | 2.798 | 9.3 | 9.3 | 2B | 0 | 0 | 1006 | 0 | 1188 | N/A | N/A | N/A | N/A | 38477484 | 680 | 243.0307 | 0% | 0% | 100% | 0% | 100% | 60% | 8687130 | 964 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 93 | 43009679 | 3023 | 72.552 | 3.023 | 9.5 | 9.5 | 2B | 0 | 0 | 976 | 0 | 1188 | N/A | N/A | N/A | N/A | 38478216 | 732 | 242.1436 | 0% | 0% | 100% | 0% | 100% | 60% | 8687470 | 340 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 99 | 43012784 | 3105 | 74.52 | 3.105 | 9.5 | 9.5 | 2B | 0 | 0 | 976 | 0 | 1188 | N/A | N/A | N/A | N/A | 38478916 | 700 | 225.4428 | 0% | 0% | 100% | 0% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 106 | 43016008 | 3224 | 77.376 | 3.224 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 1188 | N/A | N/A | N/A | N/A | 38479648 | 732 | 227.0471 | 0% | 0% | 100% | 0% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 119 | 43019664 | 3656 | 87.744 | 3.656 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38480532 | 884 | 241.7943 | 0% | 0% | 100% | 0% | 100% | 0% | 8687470 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 43024774 | 5110 | 122.64 | 5.11 | 9.3 | 9.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38481852 | 1320 | 258.317 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 43030187 | 5413 | 129.912 | 5.413 | 8.8 | 8.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38483204 | 1352 | 249.7691 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 43035878 | 5691 | 136.584 | 5.691 | 8.3 | 8.3 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38484604 | 1400 | 246.0025 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 153 | 43041189 | 5311 | 127.464 | 5.311 | 7.7 | 7.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38485972 | 1368 | 257.5786 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 | 0.71 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 43047265 | 6076 | 145.824 | 6.076 | 7.1 | 7.1 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38487372 | 1400 | 230.4147 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 155 | 43052809 | 5544 | 133.056 | 5.544 | 6.7 | 6.7 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38488716 | 1344 | 242.4242 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 147 | 43058242 | 5433 | 130.392 | 5.433 | 6.3 | 6.3 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38490124 | 1408 | 259.157 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 43063427 | 5185 | 124.44 | 5.185 | 5.9 | 5.9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38491436 | 1312 | 253.0376 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 122 | 43068324 | 4897 | 117.528 | 4.897 | 5.5 | 5.5 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38492760 | 1324 | 270.3696 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 121 | 43073596 | 5272 | 126.528 | 5.272 | 5.3 | 5.3 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38494100 | 1340 | 254.173 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 43078689 | 5093 | 122.232 | 5.093 | 5 | 5 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38495452 | 1352 | 265.4624 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 43083286 | 4597 | 110.328 | 4.597 | 4.7 | 4.7 | 3B+1S | 0 | 1025 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38496676 | 1224 | 266.2606 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 43088200 | 4914 | 117.936 | 4.914 | 4.5 | 4.5 | 3B+1S | 0 | 1024 | 1157 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38497988 | 1312 | 266.9923 | 0% | 100% | 100% | 100% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 133 | 43092509 | 4309 | 103.416 | 4.309 | 3.7 | 3.7 | 2B+1S | 0 | 1026 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38499052 | 1064 | 246.925 | 0% | 100% | 100% | 0% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 115 | 43096958 | 4449 | 106.776 | 4.449 | 3.2 | 3.2 | 2B+1S | 0 | 1025 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38500060 | 1008 | 226.5678 | 0% | 100% | 100% | 0% | 100% | 0% | 8687470 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 109 | 43101346 | 4388 | 105.312 | 4.388 | 2.8 | 2.8 | 2B+1S | 0 | 1025 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38501108 | 1048 | 238.8332 | 0% | 100% | 100% | 0% | 100% | 0% | 8687470 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 100 | 43104868 | 3522 | 84.528 | 3.522 | 4 | 4 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38501948 | 840 | 238.5009 | 0% | 0% | 100% | 0% | 100% | 50% | 8688732 | 1262 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 99 | 43108127 | 3259 | 78.216 | 3.259 | 5.1 | 5.1 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38502746 | 798 | 244.8604 | 0% | 0% | 100% | 0% | 100% | 50% | 8689945 | 1213 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.3333 | 107372 | 107372 | 107.372 | 107.372 | [12 empty] | 26722 | 26722 | 248.8731 | [6 empty] | 4757 | 4757 | 0.96 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (60%) @ 12:01 AM
XCV1 CLOSED @ 2:19 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 08, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,683
GENSET 1 WARMUP EXERCISED @ 4:20PM / STOPPED @ 4:30PM
GENSET 2 WARMUP EXERCISED @ 4:10PM / STOPPED @ 4:20PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26442 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43108127 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38502746 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8689945 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 96 | 43111411 | 3284 | 78.816 | 3.284 | 6.5 | 6.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38503468 | 722 | 219.8538 | 0% | 0% | 100% | 0% | 100% | 60% | 8691077 | 1132 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 95 | 43114689 | 3278 | 78.672 | 3.278 | 7.6 | 7.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38504191 | 723 | 220.5613 | 0% | 0% | 100% | 0% | 100% | 60% | 8692219 | 1142 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 93 | 43117974 | 3285 | 78.84 | 3.285 | 8.6 | 8.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38504913 | 722 | 219.7869 | 0% | 0% | 100% | 0% | 100% | 60% | 8693341 | 1122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 99 | 43121264 | 3290 | 78.96 | 3.29 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38505636 | 723 | 219.7568 | 0% | 0% | 100% | 0% | 100% | 60% | 8694475 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 106 | 43124931 | 3667 | 88.008 | 3.667 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38506128 | 492 | 134.1696 | 0% | 0% | 100% | 0% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 119 | 43128598 | 3667 | 88.008 | 3.667 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38507220 | 1092 | 297.7911 | 0% | 0% | 100% | 0% | 100% | 0% | 8694475 | 0 | 0.8 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 43134194 | 5596 | 134.304 | 5.596 | 9.5 | 9.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38508556 | 1336 | 238.742 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 43139603 | 5409 | 129.816 | 5.409 | 9.2 | 9.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38509844 | 1288 | 238.1216 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 43145420 | 5817 | 139.608 | 5.817 | 8.7 | 8.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38511268 | 1424 | 244.7997 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 153 | 43151208 | 5788 | 138.912 | 5.788 | 8.3 | 8.3 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38512692 | 1424 | 246.0263 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 43156922 | 5714 | 137.136 | 5.714 | 7.9 | 7.9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38514036 | 1344 | 235.2118 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 155 | 43162349 | 5427 | 130.248 | 5.427 | 7.6 | 7.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38515356 | 1320 | 243.2283 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 120 | 43167629 | 5280 | 126.72 | 5.28 | 7.2 | 7.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38516692 | 1336 | 253.0303 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 124 | 43173005 | 5376 | 129.024 | 5.376 | 6.9 | 6.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38518044 | 1352 | 251.4881 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 101 | 43178441 | 5436 | 130.464 | 5.436 | 6.7 | 6.7 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38519412 | 1368 | 251.6556 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 43183546 | 5105 | 122.52 | 5.105 | 6.5 | 6.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38520708 | 1296 | 253.8688 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 126 | 43188285 | 4739 | 113.736 | 4.739 | 6.3 | 6.3 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38521932 | 1224 | 258.2823 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 139 | 43193611 | 5326 | 127.824 | 5.326 | 6 | 6 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38523304 | 1372 | 257.6042 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 122 | 43198406 | 4795 | 115.08 | 4.795 | 5.8 | 5.8 | 3B+1S | 0 | 1014 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38524588 | 1284 | 267.7789 | 0% | 100% | 100% | 100% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 43202733 | 4327 | 103.848 | 4.327 | 5.2 | 5.2 | 2B+1S | 0 | 1016 | 1157 | 0 | 1188 | N/A | N/A | N/A | N/A | 38525620 | 1032 | 238.5024 | 0% | 100% | 100% | 0% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 120 | 43206746 | 4013 | 96.312 | 4.013 | 4.7 | 4.7 | 2B+1S | 0 | 1015 | 1158 | 0 | 1188 | N/A | N/A | N/A | N/A | 38526584 | 964 | 240.2193 | 0% | 100% | 100% | 0% | 100% | 0% | 8694475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 128 | 43210725 | 3979 | 95.496 | 3.979 | 4.3 | 4.3 | 2B+1S | 0 | 1014 | 1157 | 0 | 1188 | N/A | N/A | N/A | N/A | 38527596 | 1012 | 254.3353 | 0% | 100% | 100% | 0% | 100% | 0% | 8694475 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 102 | 43213965 | 3240 | 77.76 | 3.24 | 5.2 | 5.2 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 38528436 | 840 | 259.2593 | 0% | 0% | 100% | 0% | 100% | 40% | 8695453 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 98 | 43217006 | 3041 | 72.984 | 3.041 | 6.3 | 6.3 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38529188 | 752 | 247.2871 | 0% | 0% | 100% | 0% | 100% | 40% | 8696616 | 1163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.7917 | 108879 | 108879 | 108.879 | 108.879 | [12 empty] | 26442 | 26442 | 242.8567 | [6 empty] | 6671 | 6671 | 1.02 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (60%) @ 12:01 AM
XCV1 CLOSED @ 3:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 09, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (40%)

## JULY 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26340 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43217006 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38529188 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8696616 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 120 | 43220052 | 3046 | 73.104 | 3.046 | 7.6 | 7.6 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38529896 | 708 | 232.436 | 0% | 0% | 100% | 0% | 100% | 40% | 8697575 | 959 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 121 | 43222969 | 2917 | 70.008 | 2.917 | 8.5 | 8.5 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38530586 | 690 | 236.5444 | 0% | 0% | 100% | 0% | 100% | 40% | 8698526 | 951 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 119 | 43225886 | 2917 | 70.008 | 2.917 | 9.4 | 9.4 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38531276 | 690 | 236.5444 | 0% | 0% | 100% | 0% | 100% | 40% | 8699478 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 110 | 43228975 | 3089 | 74.136 | 3.089 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38532013 | 737 | 238.5885 | 0% | 0% | 100% | 0% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 105 | 43232065 | 3090 | 74.16 | 3.09 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1087 | N/A | N/A | N/A | N/A | 38532751 | 738 | 238.835 | 0% | 0% | 100% | 0% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 104 | 43235155 | 3090 | 74.16 | 3.09 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38533488 | 737 | 238.5113 | 0% | 0% | 100% | 0% | 100% | 0% | 8699478 | 0 | 0.81 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 130 | 43240311 | 5156 | 123.744 | 5.156 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38534732 | 1244 | 241.2723 | 0% | 0% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 129 | 43245877 | 5566 | 133.584 | 5.566 | 9.3 | 9.3 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38536060 | 1328 | 238.5914 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 102 | 43251599 | 5722 | 137.328 | 5.722 | 8.9 | 8.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38537440 | 1380 | 241.1744 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 127 | 43257585 | 5986 | 143.664 | 5.986 | 8.5 | 8.3 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38538816 | 1376 | 229.8697 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 142 | 43263362 | 5777 | 138.648 | 5.777 | 8.2 | 7.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38540148 | 1332 | 230.5695 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 151 | 43269200 | 5838 | 140.112 | 5.838 | 7.9 | 7.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38541492 | 1344 | 230.2158 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 43274822 | 5622 | 134.928 | 5.622 | 7.5 | 7.5 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38542840 | 1348 | 239.7723 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 133 | 43280475 | 5653 | 135.672 | 5.653 | 7.1 | 7.1 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38544224 | 1384 | 244.8258 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 129 | 43285723 | 5248 | 125.952 | 5.248 | 6.9 | 6.9 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38545508 | 1284 | 244.6646 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 130 | 43290708 | 4985 | 119.64 | 4.985 | 6.7 | 6.7 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38546764 | 1256 | 251.9559 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 43295933 | 5225 | 125.4 | 5.225 | 6.4 | 6.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38548068 | 1304 | 249.5694 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 128 | 43301360 | 5427 | 130.248 | 5.427 | 6.1 | 6.1 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38549396 | 1328 | 244.7024 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 43306639 | 5279 | 126.696 | 5.279 | 5.9 | 5.9 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38550740 | 1344 | 254.5937 | 0% | 100% | 100% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 120 | 43310895 | 4256 | 102.144 | 4.256 | 5.3 | 5.3 | 2B+1S | 0 | 1015 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38551744 | 1004 | 235.9023 | 0% | 100% | 100% | 0% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 140 | 43315833 | 4938 | 118.512 | 4.938 | 4.8 | 4.8 | 2B+1S | 0 | 1014 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38552824 | 1080 | 218.712 | 0% | 100% | 0% | 100% | 100% | 0% | 8699478 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 110 | 43320534 | 4701 | 112.824 | 4.701 | 4.5 | 4.5 | 2B+1S | 0 | 1013 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38553820 | 996 | 211.8698 | 0% | 100% | 0% | 100% | 100% | 0% | 8699478 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 95 | 43325439 | 4905 | 117.72 | 4.905 | 5.7 | 5.7 | 2B | 0 | 0 | 1096 | 1185 | 0 | N/A | N/A | N/A | N/A | 38554892 | 1072 | 218.5525 | 0% | 0% | 100% | 100% | 0% | 50% | 8700784 | 1306 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 98 | 43328599 | 3160 | 75.84 | 3.16 | 6.9 | 6.9 | 2B | 0 | 0 | 1096 | 1185 | 0 | N/A | N/A | N/A | N/A | 38555528 | 636 | 201.2658 | 0% | 0% | 100% | 100% | 0% | 50% | 8701882 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.625 | 111593 | 111593 | 111.593 | 111.593 | [12 empty] | 26340 | 26340 | 236.0363 | [6 empty] | 5266 | 5266 | 1.0383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING TO (40%) @ 12:01 AM
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 10, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (40%)
PREVENTIVE MAINTENANCE OF ALL UNITS (SP2,BP1,BP2,BP3) ,GENSET 1&2 , MOTOR CONTROL ,TEMPERATURE AND VIBRATION TEST.
BP2 - START @ 8:21 PM
BP1 - STOP @ 8:22 PM
BP1 - START @10:10 PM
BP3 - STOP @ 10:13 PM

## JULY 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26116 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43328599 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38555528 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8701882 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 96 | 43332181 | 3582 | 85.968 | 3.582 | 7.9 | 7.9 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38556230 | 702 | 195.9799 | 0% | 0% | 100% | 0% | 100% | 50% | 8702861 | 979 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 43335764 | 3583 | 85.992 | 3.583 | 8.9 | 8.9 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38556932 | 702 | 195.9252 | 0% | 0% | 100% | 0% | 100% | 50% | 8703841 | 980 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 101 | 43339704 | 3940 | 94.56 | 3.94 | 9.5 | 9.5 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38557594 | 662 | 168.0203 | 0% | 0% | 100% | 0% | 100% | 50% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 103 | 43343639 | 3935 | 94.44 | 3.935 | 9.5 | 9.5 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38558252 | 658 | 167.2173 | 0% | 0% | 100% | 0% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 66 | 43347584 | 3945 | 94.68 | 3.945 | 9.5 | 9.5 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38558918 | 666 | 168.8213 | 0% | 0% | 100% | 0% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 112 | 107 | 43351524 | 3940 | 94.56 | 3.94 | 9.5 | 9.5 | 2B | 0 | 0 | 1076 | 0 | 1057 | N/A | N/A | N/A | N/A | 38559580 | 662 | 168.0203 | 0% | 0% | 100% | 0% | 100% | 0% | 8703841 | 0 | 1.39 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 43357139 | 5615 | 134.76 | 5.615 | 9.5 | 9.5 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38560824 | 1244 | 221.5494 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 145 | 43363204 | 6065 | 145.56 | 6.065 | 9.2 | 9.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38562172 | 1348 | 222.2589 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 147 | 43369445 | 6241 | 149.784 | 6.241 | 8.8 | 8.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38563564 | 1392 | 223.0412 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 151 | 43375440 | 5995 | 143.88 | 5.995 | 8.4 | 8.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38564876 | 1312 | 218.849 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 | 0.77 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 149 | 43381655 | 6215 | 149.16 | 6.215 | 8 | 8 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38566240 | 1364 | 219.469 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 152 | 43387880 | 6225 | 149.4 | 6.225 | 7.6 | 7.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38567604 | 1364 | 219.1165 | 0% | 100% | 100% | 100% | 1000% | 0% | 8703841 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 158 | 43393971 | 6091 | 146.184 | 6.091 | 7.3 | 7.3 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38568964 | 1360 | 223.2802 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 43400146 | 6175 | 148.2 | 6.175 | 6.9 | 6.9 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38570372 | 1408 | 228.0162 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 133 | 43405540 | 5394 | 129.456 | 5.394 | 6.6 | 6.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38571636 | 1264 | 234.3344 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 43411237 | 5697 | 136.728 | 5.697 | 6.4 | 6.4 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38572988 | 1352 | 237.3179 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 43416438 | 5201 | 124.824 | 5.201 | 6.1 | 6.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38574212 | 1224 | 235.3394 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 43422166 | 5728 | 137.472 | 5.728 | 5.8 | 5.8 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38575576 | 1364 | 238.1285 | 0% | 100% | 100% | 100% | 100% | 0% | 8703841 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 43427828 | 5662 | 135.888 | 5.662 | 5.6 | 5.6 | 3B+1S | 0 | 1014 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 38576900 | 1324 | 233.8396 | 0% | 100% | 100% | 0% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 126 | 43433055 | 5227 | 125.448 | 5.227 | 5 | 5 | 2B+1S | 0 | 1014 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 38577972 | 1072 | 205.089 | 0% | 100% | 100% | 0% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 43437958 | 4903 | 117.672 | 4.903 | 4.5 | 4.5 | 2B+1S | 0 | 1056 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38578960 | 988 | 201.5093 | 0% | 100% | 100% | 0% | 100% | 0% | 8703841 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 121 | 43443056 | 5098 | 122.352 | 5.098 | 3.7 | 3.7 | 2B+1S | 0 | 1056 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38580036 | 1076 | 211.0632 | 0% | 100% | 100% | 0% | 100% | 0% | 8703841 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 104 | 43447394 | 4338 | 104.112 | 4.338 | 4.8 | 4.8 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 38580876 | 840 | 193.6376 | 0% | 0% | 100% | 0% | 100% | 45% | 8705662 | 1821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 113 | 101 | 43451402 | 4008 | 96.192 | 4.008 | 5.9 | 5.9 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38581644 | 768 | 191.6168 | 0% | 0% | 100% | 0% | 100% | 45% | 8706693 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7083 | 122803 | 122803 | 122.803 | 122.803 | [12 empty] | 26116 | 26116 | 212.6658 | [6 empty] | 4811 | 4811 | 1 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - OPEN @ 12:01 AM (50%)
XCV1 CLOSED @ 2:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 11, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (45%)

## JULY 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26732 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43451402 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38581644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8706693 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 99 | 43455313 | 3911 | 93.864 | 3.911 | 6 | 6 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38582372 | 728 | 186.1417 | 0% | 0% | 100% | 0% | 100% | 45% | 8707549 | 856 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 97 | 43459212 | 3899 | 93.576 | 3.899 | 7.4 | 7.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38583092 | 720 | 184.6627 | 0% | 0% | 100% | 0% | 100% | 45% | 8708413 | 864 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 105 | 43463132 | 3920 | 94.08 | 3.92 | 8.6 | 8.6 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38583815 | 723 | 184.4388 | 0% | 0% | 100% | 0% | 100% | 45% | 8709266 | 853 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 101 | 43467048 | 3916 | 93.984 | 3.916 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38584548 | 733 | 187.1808 | 0% | 0% | 100% | 0% | 100% | 45% | 8710120 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 102 | 43470957 | 3909 | 93.816 | 3.909 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38585284 | 736 | 188.2834 | 0% | 0% | 100% | 0% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 108 | 113 | 43475741 | 4784 | 114.816 | 4.784 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38586072 | 788 | 164.7157 | 0% | 0% | 100% | 0% | 100% | 0% | 8710120 | 0 | 0.75 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 155 | 43481259 | 5518 | 132.432 | 5.518 | 9.3 | 9.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38587292 | 1220 | 221.0946 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 150 | 43487337 | 6078 | 145.872 | 6.078 | 8.9 | 8.9 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38588644 | 1352 | 222.4416 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 152 | 43493610 | 6273 | 150.552 | 6.273 | 8.5 | 8.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38590012 | 1368 | 218.0775 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 149 | 43499949 | 6339 | 152.136 | 6.339 | 7.9 | 7.9 | 3B+1S | 0 | 1025 | 1187 | 1187 | 1187 | N/A | N/A | N/A | N/A | 38591392 | 1380 | 217.7 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 | 1.06 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 150 | 43506307 | 6358 | 152.592 | 6.358 | 7.4 | 7.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38592768 | 1376 | 216.4203 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 151 | 43512533 | 6226 | 149.424 | 6.226 | 7 | 7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38594140 | 1372 | 220.3662 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 148 | 43518714 | 6181 | 148.344 | 6.181 | 6.6 | 6.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38595508 | 1368 | 221.3234 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 43524926 | 6212 | 149.088 | 6.212 | 6 | 6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38596911 | 1403 | 225.8532 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 142 | 43530694 | 5768 | 138.432 | 5.768 | 5.5 | 5.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38598236 | 1325 | 229.7157 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 138 | 43536584 | 5890 | 141.36 | 5.89 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38599594 | 1358 | 230.5603 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 43542303 | 5719 | 137.256 | 5.719 | 4.6 | 4.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38600916 | 1322 | 231.1593 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 115 | 43548035 | 5732 | 137.568 | 5.732 | 4.2 | 4.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38602244 | 1328 | 231.6818 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 43553815 | 5780 | 138.72 | 5.78 | 3.7 | 3.7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38603588 | 1344 | 232.526 | 0% | 100% | 100% | 100% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 125 | 43559088 | 5273 | 126.552 | 5.273 | 3.1 | 3.1 | 2B+1S | 0 | 1036 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38604660 | 1072 | 203.2998 | 0% | 100% | 100% | 0% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 126 | 43564128 | 5040 | 120.96 | 5.04 | 2.6 | 2.6 | 2B+1S | 0 | 1036 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38605672 | 1012 | 200.7937 | 0% | 100% | 100% | 0% | 100% | 0% | 8710120 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 123 | 43569133 | 5005 | 120.12 | 5.005 | 2.1 | 2.1 | 2B+1S | 0 | 1034 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38606712 | 1040 | 207.7922 | 0% | 100% | 100% | 0% | 100% | 0% | 8710120 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 99 | 43573661 | 4528 | 108.672 | 4.528 | 3.1 | 3.1 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 38607620 | 908 | 200.53 | 0% | 0% | 100% | 0% | 100% | 50% | 8711281 | 1161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 102 | 43577551 | 3890 | 93.36 | 3.89 | 4.9 | 4.9 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 38608376 | 756 | 194.3445 | 0% | 0% | 100% | 0% | 100% | 50% | 8712360 | 1079 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.5 | 126149 | 126149 | 126.149 | 126.149 | [12 empty] | 26732 | 26732 | 211.9081 | [6 empty] | 5667 | 5667 | 0.95333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - OPEN @ 12:01 AM (45%)
XCV1 CLOSED @ 4:13 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:18 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 12, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26536 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43577551 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38608376 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8712360 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 104 | 43581537 | 3986 | 95.664 | 3.986 | 5.9 | 5.9 | 2B | 0 | 0 | 1106 | 0 | 1107 | N/A | N/A | N/A | N/A | 38609162 | 786 | 197.1902 | 0% | 0% | 100% | 0% | 100% | 50% | 8713499 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 109 | 43585524 | 3987 | 95.688 | 3.987 | 7 | 7 | 2B | 0 | 0 | 1106 | 0 | 1107 | N/A | N/A | N/A | N/A | 38609948 | 786 | 197.1407 | 0% | 0% | 100% | 0% | 100% | 50% | 8714518 | 1019 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 98 | 43589356 | 3832 | 91.968 | 3.832 | 8.1 | 8.1 | 2B | 0 | 0 | 1106 | 0 | 1107 | N/A | N/A | N/A | N/A | 38610664 | 716 | 186.8476 | 0% | 0% | 100% | 0% | 100% | 50% | 8715803 | 1285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 94 | 43593188 | 3832 | 91.968 | 3.832 | 9.5 | 9.5 | 2B | 0 | 0 | 1106 | 0 | 1107 | N/A | N/A | N/A | N/A | 38611380 | 716 | 186.8476 | 0% | 0% | 100% | 0% | 100% | 50% | 8717088 | 1285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 109 | 43597343 | 4155 | 99.72 | 4.155 | 9.5 | 9.5 | 2B | 0 | 0 | 1106 | 0 | 1107 | N/A | N/A | N/A | N/A | 38612112 | 732 | 176.1733 | 0% | 0% | 100% | 0% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 112 | 43601852 | 4509 | 108.216 | 4.509 | 9.5 | 9.5 | 2B | 0 |  | 10107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38612860 | 748 | 165.8904 | 0% | 0% | 100% | 0% | 100% | 0% | 8717088 | 0 | 0.52 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 15 | 10.5634 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 122 | 43607377 | 5525 | 132.6 | 5.525 | 9.4 | 9.4 | 3B+1S | 0 | 1004 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 38614016 | 1156 | 209.2308 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 142 | 43613390 | 6013 | 144.312 | 6.013 | 9.1 | 9.1 | 3B+1S | 0 | 1005 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 38615264 | 1248 | 207.5503 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 156 | 43619628 | 6238 | 149.712 | 6.238 | 8.6 | 8.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38616640 | 1376 | 220.5835 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 154 | 43625804 | 6176 | 148.224 | 6.176 | 8.2 | 8.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38617988 | 1348 | 218.2642 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 | 0.62 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 145 | 43632041 | 6237 | 149.688 | 6.237 | 7.8 | 7.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38619348 | 1360 | 218.0536 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 43638206 | 6165 | 147.96 | 6.165 | 7.4 | 7.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38620708 | 1360 | 220.6002 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 43644180 | 5974 | 143.376 | 5.974 | 7.1 | 7.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38622048 | 1340 | 224.3053 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 43650186 | 6006 | 144.144 | 6.006 | 6.6 | 6.6 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38623420 | 1372 | 228.4382 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 43656098 | 5912 | 141.888 | 5.912 | 6.2 | 6.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38624780 | 1360 | 230.0406 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 43661436 | 5338 | 128.112 | 5.338 | 5.9 | 5.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38626020 | 1240 | 232.2967 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 43667348 | 5912 | 141.888 | 5.912 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38627412 | 1392 | 235.4533 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 138 | 43673047 | 5699 | 136.776 | 5.699 | 5.3 | 5.3 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38628764 | 1352 | 237.2346 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 43678568 | 5521 | 132.504 | 5.521 | 5 | 5 | 3B+1S | 0 | 1003 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38630052 | 1288 | 233.2911 | 0% | 100% | 100% | 100% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 128 | 43683836 | 5268 | 126.432 | 5.268 | 4.4 | 4.4 | 2B+1S | 0 | 1096 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38631140 | 1088 | 206.53 | 0% | 100% | 100% | 0% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 134 | 43689075 | 5239 | 125.736 | 5.239 | 3.5 | 3.5 | 2B+1S | 0 | 1096 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38632220 | 1080 | 206.1462 | 0% | 100% | 100% | 0% | 100% | 0% | 8717088 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 108 | 43694309 | 5234 | 125.616 | 5.234 | 2.8 | 2.8 | 2B+1S | 0 | 1096 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38633316 | 1096 | 209.4001 | 0% | 100% | 100% | 0% | 100% | 0% | 8717088 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 101 | 43698634 | 4325 | 103.8 | 4.325 | 4 | 4 | 2B | 0 | 0 | 1128 | 0 | 1137 | N/A | N/A | N/A | N/A | 38634164 | 848 | 196.0694 | 0% | 0% | 100% | 0% | 100% | 45% | 8718269 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 107 | 43702662 | 4028 | 96.672 | 4.028 | 5.5 | 5.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38634912 | 748 | 185.7001 | 0% | 0% | 100% | 0% | 100% | 45% | 8719644 | 1375 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.2917 | 125111 | 125111 | 125.111 | 125.111 | [12 empty] | 26536 | 26536 | 212.0997 | [6 empty] | 7284 | 7284 | 0.92333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - OPEN @ 12:01 AM (50%)
XCV1 CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 13, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:24PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (45%)

## JULY 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26668 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43702662 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38634912 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8719644 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 103 | 43706557 | 3895 | 93.48 | 3.895 | 6.3 | 6.3 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38635624 | 712 | 182.7985 | 0% | 0% | 100% | 0% | 100% | 50% | 8720658 | 1014 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 106 | 43710447 | 3890 | 93.36 | 3.89 | 7.4 | 7.4 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38636337 | 713 | 183.2905 | 0% | 0% | 100% | 0% | 100% | 50% | 8721676 | 1018 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 101 | 43714346 | 3899 | 93.576 | 3.899 | 8.8 | 8.8 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38637057 | 720 | 184.6627 | 0% | 0% | 100% | 0% | 100% | 50% | 8722689 | 1013 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 102 | 43718233 | 3887 | 93.288 | 3.887 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38637772 | 715 | 183.9465 | 0% | 0% | 100% | 0% | 100% | 50% | 8723384 | 695 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 108 | 43722138 | 3905 | 93.72 | 3.905 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38638476 | 704 | 180.2817 | 0% | 0% | 100% | 0% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 121 | 116 | 43726851 | 4713 | 113.112 | 4.713 | 9.4 | 9.4 | 2B | 0 |  | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38639264 | 788 | 167.1971 | 0% | 0% | 100% | 0% | 100% | 0% | 8723384 | 0 | 0.66 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 43732877 | 6026 | 144.624 | 6.026 | 9 | 9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38640588 | 1324 | 219.7146 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 43739195 | 6318 | 151.632 | 6.318 | 8.4 | 8.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38641972 | 1384 | 219.0567 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 147 | 43745451 | 6256 | 150.144 | 6.256 | 7.9 | 7.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38643348 | 1376 | 219.9488 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 149 | 43751611 | 6160 | 147.84 | 6.16 | 7.5 | 7.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38644708 | 1360 | 220.7792 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 151 | 43758827 | 7216 | 173.184 | 7.216 | 7.1 | 7.1 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38646072 | 1364 | 189.0244 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 150 | 43763990 | 5163 | 123.912 | 5.163 | 6.7 | 6.7 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38647416 | 1344 | 260.3138 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 148 | 43769996 | 6006 | 144.144 | 6.006 | 6.5 | 6.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38648772 | 1356 | 225.7742 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 43775826 | 5830 | 139.92 | 5.83 | 6.1 | 6.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38650100 | 1328 | 227.7873 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 43781732 | 5906 | 141.744 | 5.906 | 5.7 | 5.7 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38651468 | 1368 | 231.6289 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 43787385 | 5653 | 135.672 | 5.653 | 5.4 | 5.4 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38652768 | 1300 | 229.9664 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 129 | 43793393 | 6008 | 144.192 | 6.008 | 5.1 | 5.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38654156 | 1388 | 231.0253 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 43798885 | 5492 | 131.808 | 5.492 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38655420 | 1264 | 230.1529 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 43804509 | 5624 | 134.976 | 5.624 | 4.6 | 4.6 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38656724 | 1304 | 231.8634 | 0% | 100% | 100% | 100% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 126 | 43809816 | 5307 | 127.368 | 5.307 | 3.9 | 3.9 | 2B+1S | 0 | 1017 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38657812 | 1088 | 205.0122 | 0% | 100% | 100% | 0% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 148 | 43815310 | 5494 | 131.856 | 5.494 | 3.3 | 3.3 | 2B+1S | 0 | 1015 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38658914 | 1102 | 200.5825 | 0% | 100% | 100% | 0% | 100% | 0% | 8723384 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 121 | 43820366 | 5056 | 121.344 | 5.056 | 2.9 | 2.9 | 2B+1S | 0 | 1015 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38659884 | 970 | 191.8513 | 0% | 100% | 100% | 0% | 100% | 0% | 8723384 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 109 | 43824798 | 4432 | 106.368 | 4.432 | 3.8 | 3.8 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 38660780 | 896 | 202.1661 | 0% | 0% | 100% | 0% | 100% | 50% | 8724424 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 100 | 43829040 | 4242 | 101.808 | 4.242 | 5.1 | 5.1 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 38661580 | 800 | 188.5903 | 0% | 0% | 100% | 0% | 100% | 50% | 8725694 | 1270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.7917 | 126378 | 126378 | 126.378 | 126.378 | [12 empty] | 26668 | 26668 | 211.0177 | [6 empty] | 6050 | 6050 | 0.96833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - OPEN @ 12:01 AM (50%)
XCV1 CLOSED @ 3:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 14, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:23PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26704 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43829040 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38661580 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8725694 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 102 | 43833020 | 3980 | 95.52 | 3.98 | 6.4 | 6.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38662300 | 720 | 180.9045 | 0% | 0% | 100% | 0% | 100% | 64% | 8726717 | 1023 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 106 | 43837050 | 4030 | 96.72 | 4.03 | 7.6 | 7.6 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38663065 | 765 | 189.8263 | 0% | 0% | 100% | 0% | 100% | 64% | 8727753 | 1036 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 104 | 43840964 | 3914 | 93.936 | 3.914 | 8.4 | 8.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38663772 | 707 | 180.6336 | 0% | 0% | 100% | 0% | 100% | 64% | 8728762 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 101 | 43844837 | 3873 | 92.952 | 3.873 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 38664448 | 676 | 174.5417 | 0% | 0% | 100% | 0% | 100% | 64% | 8729730 | 968 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 102 | 43849039 | 4202 | 100.848 | 4.202 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 38665148 | 700 | 166.5873 | 0% | 0% | 100% | 0% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 101 | 43853983 | 4944 | 118.656 | 4.944 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38666060 | 912 | 184.466 | 0% | 0% | 100% | 0% | 100% | 0% | 8729730 | 0 | 0.58 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 159 | 43859980 | 5997 | 143.928 | 5.997 | 9.1 | 9.1 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38667380 | 1320 | 220.1101 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 43866197 | 6217 | 149.208 | 6.217 | 8.5 | 8.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38668752 | 1372 | 220.6852 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 151 | 43872290 | 6093 | 146.232 | 6.093 | 8 | 8 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38670100 | 1348 | 221.2375 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 152 | 43878600 | 6310 | 151.44 | 6.31 | 7.5 | 7.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38671492 | 1392 | 220.6022 | 0% | 100% | 100% | 100% | 1000% | 0% | 8729730 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 43884848 | 6248 | 149.952 | 6.248 | 7 | 7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38672868 | 1376 | 220.2305 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 147 | 43890853 | 6005 | 144.12 | 6.005 | 6.6 | 6.6 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38674212 | 1344 | 223.8135 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 150 | 43896836 | 5983 | 143.592 | 5.983 | 6.5 | 6.5 | 3B+1S | 0 | 1002 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38675548 | 1336 | 223.2993 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 43902711 | 5875 | 141 | 5.875 | 6.3 | 6.3 | 3B+1S | 0 | 1003 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38676900 | 1352 | 230.1277 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 43908320 | 5609 | 134.616 | 5.609 | 6.1 | 6.1 | 3B+1S | 0 | 1003 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38678212 | 1312 | 233.9098 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 43913861 | 5541 | 132.984 | 5.541 | 5.9 | 5.9 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38679516 | 1304 | 235.3366 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 151 | 43919516 | 5655 | 135.72 | 5.655 | 5.7 | 5.7 | 3B+1S | 0 | 1002 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38680852 | 1336 | 236.2511 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 128 | 43924856 | 5340 | 128.16 | 5.34 | 5.5 | 5.5 | 3B+1S | 0 | 1003 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38682108 | 1256 | 235.206 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 43930494 | 5638 | 135.312 | 5.638 | 5.4 | 5.4 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38683424 | 1316 | 233.4161 | 0% | 100% | 100% | 100% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 137 | 43935748 | 5254 | 126.096 | 5.254 | 4.8 | 4.8 | 2B+1S | 0 | 1055 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38684496 | 1072 | 204.035 | 0% | 100% | 100% | 0% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 122 | 43941033 | 5285 | 126.84 | 5.285 | 3.9 | 3.9 | 2B+1S | 0 | 1096 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38685584 | 1088 | 205.8657 | 0% | 100% | 100% | 0% | 100% | 0% | 8729730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 116 | 43946171 | 5138 | 123.312 | 5.138 | 3.1 | 3.1 | 2B+1S | 0 | 1096 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38686676 | 1092 | 212.5341 | 0% | 100% | 100% | 0% | 100% | 0% | 8729730 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 112 | 43950390 | 4219 | 101.256 | 4.219 | 4.1 | 4.1 | 2B | 0 | 0 | 1147 | 0 | 1147 | N/A | N/A | N/A | N/A | 38687524 | 848 | 200.9955 | 0% | 0% | 100% | 0% | 100% | 48% | 8730931 | 1201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 98 | 43954273 | 3883 | 93.192 | 3.883 | 5.3 | 5.3 | 2B | 0 | 0 | 1116 | 0 | 1117 | N/A | N/A | N/A | N/A | 38688284 | 760 | 195.725 | 0% | 0% | 100% | 0% | 100% | 48% | 8731967 | 1036 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.2917 | 125233 | 125233 | 125.233 | 125.233 | [12 empty] | 26704 | 26704 | 213.2345 | [6 empty] | 6273 | 6273 | 0.86833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - OPEN @ 12:01 AM (64%)
XCV1 CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 15, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:30PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (48%)

## JULY 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26624 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 43954273 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38688284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8731967 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 101 | 43957993 | 3720 | 89.28 | 3.72 | 6.5 | 6.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38688993 | 709 | 190.5914 | 0% | 0% | 100% | 0% | 100% | 50% | 8733018 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 97 | 43961702 | 3709 | 89.016 | 3.709 | 7.6 | 7.6 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38689706 | 713 | 192.2351 | 0% | 0% | 100% | 0% | 100% | 50% | 8734094 | 1076 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 91 | 43965405 | 3703 | 88.872 | 3.703 | 8.8 | 8.8 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38690412 | 706 | 190.6562 | 0% | 0% | 100% | 0% | 100% | 50% | 8735121 | 1027 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 93 | 43969327 | 3922 | 94.128 | 3.922 | 9.4 | 9.4 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38691133 | 721 | 183.8348 | 0% | 0% | 100% | 0% | 100% | 50% | 8736222 | 1101 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 107 | 43973250 | 3923 | 94.152 | 3.923 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38691856 | 723 | 184.2977 | 0% | 0% | 100% | 0% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 115 | 109 | 43977863 | 4613 | 110.712 | 4.613 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 38692604 | 748 | 162.1504 | 0% | 0% | 100% | 0% | 100% | 0% | 8736222 | 0 | 0.75 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 158 | 43983433 | 5570 | 133.68 | 5.57 | 9.5 | 9.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38693812 | 1208 | 216.8761 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 43989564 | 6131 | 147.144 | 6.131 | 9.2 | 9.2 | 3B+1S | 0 | 1035 | 1887 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38695172 | 1360 | 221.8235 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 43995863 | 6299 | 151.176 | 6.299 | 8.6 | 8.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38696564 | 1392 | 220.9875 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 44002072 | 6209 | 149.016 | 6.209 | 8 | 8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38697940 | 1376 | 221.6138 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 44008158 | 6086 | 146.064 | 6.086 | 7.5 | 7.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38699292 | 1352 | 222.1492 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 160 | 44014375 | 6217 | 149.208 | 6.217 | 7 | 7 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38700668 | 1376 | 221.3286 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 44020285 | 5910 | 141.84 | 5.91 | 6.6 | 6.6 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38702020 | 1352 | 228.7648 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 135 | 44026464 | 6179 | 148.296 | 6.179 | 6.3 | 6.3 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38703460 | 1440 | 233.0474 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 44031885 | 5421 | 130.104 | 5.421 | 5.8 | 5.8 | 3B+1S | 0 | 1033 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38704716 | 1256 | 231.6916 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 44037536 | 5651 | 135.624 | 5.651 | 5.7 | 5.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38706044 | 1328 | 235.0027 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 132 | 44043167 | 5631 | 135.144 | 5.631 | 5.4 | 5.4 | 3B+1S | 0 | 1002 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38707356 | 1312 | 232.9959 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 44048898 | 5731 | 137.544 | 5.731 | 5.2 | 5.2 | 3B+1S | 0 | 1003 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38708676 | 1320 | 230.3263 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 127 | 44054263 | 5365 | 128.76 | 5.365 | 5.1 | 5.1 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38709948 | 1272 | 237.0923 | 0% | 100% | 100% | 100% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 123 | 44059403 | 5140 | 123.36 | 5.14 | 4.5 | 4.5 | 2B+1S | 0 | 1065 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38711036 | 1088 | 211.6732 | 0% | 100% | 100% | 0% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 44064366 | 4963 | 119.112 | 4.963 | 3.7 | 3.7 | 2B+1S | 0 | 1065 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38712076 | 1040 | 209.5507 | 0% | 100% | 100% | 0% | 100% | 0% | 8736222 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 122 | 44069535 | 5169 | 124.056 | 5.169 | 3 | 3 | 2B+1S | 0 | 1065 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38713156 | 1080 | 208.9379 | 0% | 100% | 100% | 0% | 100% | 0% | 8736222 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 103 | 44073936 | 4401 | 105.624 | 4.401 | 3.8 | 3.8 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38714068 | 912 | 207.2256 | 0% | 0% | 100% | 0% | 100% | 50% | 8737076 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 100 | 44078132 | 4196 | 100.704 | 4.196 | 5 | 5 | 2B | 0 | 0 | 1119 | 0 | 1119 | N/A | N/A | N/A | N/A | 38714908 | 840 | 200.1907 | 0% | 0% | 100% | 0% | 100% | 50% | 8738089 | 1013 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.875 | 123859 | 123859 | 123.859 | 123.859 | [12 empty] | 26624 | 26624 | 214.9541 | [6 empty] | 6122 | 6122 | 0.89667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 3:01 AM (55%)
XCV1 CLOSED @ 4:16 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 16, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,670
GENSET 1 WARMUP EXERCISED @ 4:20PM / STOPPED @ 4:30PM
GENSET 2 WARMUP EXERCISED @ 4:10PM / STOPPED @ 4:20PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26736 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44078132 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38714908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8738089 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 9 | 102 | 44082061 | 3929 | 94.296 | 3.929 | 6.2 | 6.2 | 2B | 0 | 0 | 1116 | 0 | 1118 | N/A | N/A | N/A | N/A | 38715662 | 754 | 191.9063 | 0% | 0% | 100% | 0% | 100% | 50% | 8739066 | 977 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 9 | 100 | 44085993 | 3932 | 94.368 | 3.932 | 6.4 | 6.4 | 2B | 0 | 0 | 1116 | 0 | 1118 | N/A | N/A | N/A | N/A | 38716417 | 755 | 192.0142 | 0% | 0% | 100% | 0% | 100% | 50% | 8740044 | 978 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 10 | 108 | 44089919 | 3926 | 94.224 | 3.926 | 8.8 | 8.8 | 2B | 0 | 0 | 1116 | 0 | 1118 | N/A | N/A | N/A | N/A | 38717172 | 755 | 192.3077 | 0% | 0% | 100% | 0% | 100% | 60% | 8741022 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 11 | 99 | 44093859 | 3940 | 94.56 | 3.94 | 9.2 | 9.2 | 2B | 0 | 0 | 1116 | 0 | 1118 | N/A | N/A | N/A | N/A | 38717908 | 736 | 186.802 | 0% | 0% | 100% | 0% | 100% | 60% | 8742041 | 1019 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 16 | 111 | 44098150 | 4291 | 102.984 | 4.291 | 9.5 | 9.5 | 2B | 0 | 0 | 1116 | 0 | 1118 | N/A | N/A | N/A | N/A | 38718676 | 768 | 178.9793 | 0% | 0% | 100% | 0% | 100% | 60% | 8742546 | 505 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 114 | 44102690 | 4540 | 108.96 | 4.54 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38719436 | 760 | 167.4009 | 0% | 0% | 100% | 0% | 100% | 0% | 8742546 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 44108684 | 5994 | 143.856 | 5.994 | 9.2 | 9.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38720764 | 1328 | 221.5549 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 44114828 | 6144 | 147.456 | 6.144 | 8.7 | 8.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38722132 | 1368 | 222.6562 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 143 | 44121048 | 6220 | 149.28 | 6.22 | 8.2 | 8.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38723491 | 1359 | 218.4887 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 136 | 44127278 | 6230 | 149.52 | 6.23 | 7.7 | 8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38724854 | 1363 | 218.7801 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 44133440 | 6162 | 147.888 | 6.162 | 7.3 | 7.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38726232 | 1378 | 223.6287 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 44139466 | 6026 | 144.624 | 6.026 | 7 | 7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38727541 | 1309 | 217.2254 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 134 | 44145377 | 5911 | 141.864 | 5.911 | 6.6 | 6.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38728932 | 1391 | 235.324 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 44151140 | 5763 | 138.312 | 5.763 | 6.3 | 6.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38730264 | 1332 | 231.1296 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 44156804 | 5664 | 135.936 | 5.664 | 5.9 | 5.9 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38731584 | 1320 | 233.0508 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 127 | 44162290 | 5486 | 131.664 | 5.486 | 5.7 | 5.7 | 3B+1S | 0 | 1023 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38732884 | 1300 | 236.9668 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 44167946 | 5656 | 135.744 | 5.656 | 5.5 | 5.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38734220 | 1336 | 236.2093 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 11 | 7.7465 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 44173482 | 5536 | 132.864 | 5.536 | 5.1 | 5.1 | 3B+1S | 0 | 1054 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38735532 | 1312 | 236.9942 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 44179306 | 5824 | 139.776 | 5.824 | 4.7 | 4.7 | 3B+1S | 0 | 1053 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38736920 | 1388 | 238.3242 | 0% | 100% | 100% | 100% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 121 | 44184310 | 5004 | 120.096 | 5.004 | 4.1 | 4.1 | 2B+1S | 0 | 1056 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38737956 | 1036 | 207.0344 | 0% | 100% | 100% | 0% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 126 | 44189286 | 4976 | 119.424 | 4.976 | 3.4 | 3.4 | 2B+1S | 0 | 1059 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38738980 | 1024 | 205.7878 | 0% | 100% | 100% | 0% | 100% | 0% | 8742546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 113 | 44194372 | 5086 | 122.064 | 5.086 | 3 | 3 | 2B+1S | 0 | 1002 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38740052 | 1072 | 210.7747 | 0% | 100% | 100% | 0% | 100% | 0% | 8742546 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 108 | 44198434 | 4062 | 97.488 | 4.062 | 4.3 | 4.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38740868 | 816 | 200.8863 | 0% | 0% | 100% | 0% | 100% | 45% | 8743768 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 103 | 44202497 | 4063 | 97.512 | 4.063 | 5.5 | 5.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38741644 | 776 | 190.9919 | 0% | 0% | 100% | 0% | 100% | 45% | 8744990 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.625 | 124365 | 124365 | 124.365 | 124.365 | [12 empty] | 26736 | 26736 | 214.9801 | [6 empty] | 6901 | 6901 | 1.015 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 3:01 AM (60%)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 17, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 6:28PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (45%)

## JULY 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26956 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44202497 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38741644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8744990 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 103 | 44206165 | 3668 | 88.032 | 3.668 | 6.7 | 6.7 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38742360 | 716 | 195.2017 | 0% | 0% | 100% | 0% | 100% | 50% | 8746012 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 100 | 44209840 | 3675 | 88.2 | 3.675 | 7.8 | 7.8 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38743079 | 719 | 195.6463 | 0% | 0% | 100% | 0% | 100% | 50% | 8747034 | 1022 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 98 | 44213501 | 3661 | 87.864 | 3.661 | 8.8 | 8.8 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38743804 | 725 | 198.0333 | 0% | 0% | 100% | 0% | 100% | 50% | 8748056 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 101 | 44217500 | 3999 | 95.976 | 3.999 | 9.3 | 9.3 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38744554 | 750 | 187.5469 | 0% | 0% | 100% | 0% | 100% | 50% | 8748911 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 106 | 44221499 | 3999 | 95.976 | 3.999 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38745304 | 750 | 187.5469 | 0% | 0% | 100% | 0% | 100% |  | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 108 | 44226001 | 4502 | 108.048 | 4.502 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1118 | N/A | N/A | N/A | N/A | 38746068 | 764 | 169.7024 | 0% | 0% | 100% | 0% | 100% | 0% | 8748911 | 0 | 0.66 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 44231730 | 5729 | 137.496 | 5.729 | 9.5 | 9.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38747348 | 1280 | 223.4247 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 44237878 | 6148 | 147.552 | 6.148 | 9.2 | 9.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38748716 | 1368 | 222.5114 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 44244018 | 6140 | 147.36 | 6.14 | 8.8 | 8.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38750068 | 1352 | 220.1954 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 153 | 44250191 | 6173 | 148.152 | 6.173 | 8.3 | 8.3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38751444 | 1376 | 222.9062 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 44256372 | 6181 | 148.344 | 6.181 | 7.8 | 7.8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38752836 | 1392 | 225.2063 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 44262454 | 6082 | 145.968 | 6.082 | 7.2 | 7.2 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38754212 | 1376 | 226.2414 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 150 | 44268466 | 6012 | 144.288 | 6.012 | 6.8 | 6.8 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38755584 | 1372 | 228.2102 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 137 | 44274425 | 5959 | 143.016 | 5.959 | 6.1 | 6.1 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38756988 | 1404 | 235.61 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 148 | 44280502 | 6077 | 145.848 | 6.077 | 5.5 | 5.5 | 3B+1S | 0 | 1064 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38758446 | 1458 | 239.921 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 44286034 | 5532 | 132.768 | 5.532 | 5 | 5 | 3B+1S | 0 | 1064 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38759724 | 1278 | 231.0195 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 143 | 44291912 | 5878 | 141.072 | 5.878 | 4.4 | 4.4 | 3B+1S | 0 | 1065 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38761104 | 1380 | 234.7737 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 44297540 | 5628 | 135.072 | 5.628 | 3.9 | 3.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38762428 | 1324 | 235.2523 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 140 | 44303124 | 5584 | 134.016 | 5.584 | 3.6 | 3.6 | 3B+1S | 0 | 1022 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38763752 | 1324 | 237.106 | 0% | 100% | 100% | 100% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 137 | 44308336 | 5212 | 125.088 | 5.212 | 2.9 | 2.9 | 2B+1S | 0 | 1075 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38764844 | 1092 | 209.5165 | 0% | 100% | 100% | 0% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 135 | 44313545 | 5209 | 125.016 | 5.209 | 2.3 | 2.3 | 2B+1S | 0 | 1075 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38765924 | 1080 | 207.3335 | 0% | 100% | 100% | 0% | 100% | 0% | 8748911 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 120 | 44318632 | 5087 | 122.088 | 5.087 | 1.7 | 1.7 | 2B+1S | 0 | 1073 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38766996 | 1072 | 210.7332 | 0% | 100% | 100% | 0% | 100% | 0% | 8748911 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 100 | 44322917 | 4285 | 102.84 | 4.285 | 2.9 | 2.9 | 2B | 0 | 0 | 1127 | 0 | 1138 | N/A | N/A | N/A | N/A | 38767864 | 868 | 202.5671 | 0% |  | 100% | 0% | 100% | 45% | 8750174 | 1263 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 107 | 44326983 | 4066 | 97.584 | 4.066 | 4.4 | 4.4 | 2B | 0 | 0 | 1127 | 0 | 1138 | N/A | N/A | N/A | N/A | 38768600 | 736 | 181.0133 | 0% |  | 100% | 0% | 100% | 45% | 8751477 | 1303 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.5417 | 124486 | 124486 | 124.486 | 124.486 | [12 empty] | 26956 | 26956 | 216.5384 | [6 empty] | 6487 | 6487 | 0.98167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (50%)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26832 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44326983 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38768600 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8751477 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 100 | 44330810 | 3827 | 91.848 | 3.827 | 5.3 | 5.3 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38769390 | 790 | 206.428 | 0% | 0% | 100% | 0% | 100% | 55% | 8752565 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 95 | 44334638 | 3828 | 91.872 | 3.828 | 6.5 | 6.5 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38770123 | 733 | 191.4838 | 0% | 0% | 100% | 0% | 100% | 55% | 8753654 | 1089 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 92 | 44338465 | 3827 | 91.848 | 3.827 | 7.8 | 7.8 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38770856 | 733 | 191.5338 | 0% | 0% | 100% | 0% | 100% | 55% | 8754743 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 93 | 44342402 | 3937 | 94.488 | 3.937 | 8.9 | 8.9 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38771604 | 748 | 189.9924 | 0% | 0% | 100% | 0% | 100% | 55% | 8755750 | 1007 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 110 | 44346424 | 4022 | 96.528 | 4.022 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38772340 | 736 | 182.9935 | 0% | 0% | 100% | 0% | 100% | 55% | 8756605 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 112 | 44350902 | 4478 | 107.472 | 4.478 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1118 | N/A | N/A | N/A | N/A | 38773084 | 744 | 166.1456 | 0% | 0% | 100% | 0% | 100% | 0% | 8756605 | 0 | 0.81 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 136 | 44356594 | 5692 | 136.608 | 5.692 | 9.5 | 9.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38774372 | 1288 | 226.2825 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 44362699 | 6105 | 146.52 | 6.105 | 9.4 | 9.4 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38775732 | 1360 | 222.7682 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 148 | 44368687 | 5988 | 143.712 | 5.988 | 9 | 9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38777068 | 1336 | 223.1129 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 147 | 44374931 | 6244 | 149.856 | 6.244 | 8.5 | 8.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38778452 | 1384 | 221.6528 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 | 0.95 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 145 | 44381057 | 6126 | 147.024 | 6.126 | 8.1 | 8.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38779816 | 1364 | 222.6575 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 44387235 | 6178 | 148.272 | 6.178 | 7.5 | 7.5 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38781196 | 1380 | 223.3733 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 138 | 44393182 | 5947 | 142.728 | 5.947 | 7 | 7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38782540 | 1344 | 225.9963 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 136 | 44399082 | 5900 | 141.6 | 5.9 | 6.5 | 6.5 | 3B+1S | 0 | 1033 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38783940 | 1400 | 237.2881 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 158 | 44404962 | 5880 | 141.12 | 5.88 | 6.1 | 6.1 | 3B+1S | 0 | 1033 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38785320 | 1380 | 234.6939 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 133 | 44410503 | 5541 | 132.984 | 5.541 | 5.6 | 5.6 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38786620 | 1300 | 234.6147 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 44416151 | 5648 | 135.552 | 5.648 | 5.2 | 5.2 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38787944 | 1324 | 234.4193 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 130 | 44421745 | 5594 | 134.256 | 5.594 | 4.7 | 4.7 | 3B+1S | 0 | 1033 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38789270 | 1326 | 237.0397 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 127 | 44427339 | 5594 | 134.256 | 5.594 | 4.6 | 4.6 | 3B+1S | 0 | 1033 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38790596 | 1326 | 237.0397 | 0% | 100% | 100% | 100% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 124 | 44432546 | 5207 | 124.968 | 5.207 | 3.7 | 3.7 | 2B+1S | 0 | 1116 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38791688 | 1092 | 209.7177 | 0% | 100% | 100% | 0% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 121 | 44437742 | 5196 | 124.704 | 5.196 | 2.9 | 2.9 | 2B+1S | 0 | 1054 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38792764 | 1076 | 207.0824 | 0% | 100% | 100% | 0% | 100% | 0% | 8756605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 120 | 44442773 | 5031 | 120.744 | 5.031 | 2.4 | 2.4 | 2B+1S | 0 | 1053 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38793788 | 1024 | 203.5381 | 0% | 100% | 100% | 0% | 100% | 0% | 8756605 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 118 | 44447017 | 4244 | 101.856 | 4.244 | 3.7 | 3.7 | 2B | 0 | 0 | 1149 | 0 | 1149 | N/A | N/A | N/A | N/A | 38794610 | 822 | 193.6852 | 0% | 0% | 100% | 0% | 100% | 48% | 8757736 | 1131 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 121 | 119 | 44451262 | 4245 | 101.88 | 4.245 | 4.9 | 4.9 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38795432 | 822 | 193.6396 | 0% | 0% | 100% | 0% | 100% | 48% | 8758867 | 1131 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.125 | 124279 | 124279 | 124.279 | 124.279 | [12 empty] | 26832 | 26832 | 215.9013 | [6 empty] | 7390 | 7390 | 0.935 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 19, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (48%)

## JULY 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26448 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44451262 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38795432 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8758867 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 98 | 44455142 | 3880 | 93.12 | 3.88 | 6 | 6 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38796158 | 726 | 187.1134 | 0% | 0% | 100% | 0% | 100% | 52% | 8760002 | 1135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 44459014 | 3872 | 92.928 | 3.872 | 7.2 | 7.2 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38796878 | 720 | 185.9504 | 0% | 0% | 100% | 0% | 100% | 52% | 8761132 | 1130 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 96 | 44462904 | 3890 | 93.36 | 3.89 | 8.4 | 8.4 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38797612 | 734 | 188.6889 | 0% | 0% | 100% | 0% | 100% | 52% | 8762273 | 1141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 97 | 44466734 | 3830 | 91.92 | 3.83 | 9.5 | 9.5 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38798320 | 708 | 184.8564 | 0% | 0% | 100% | 0% | 100% | 52% | 8763349 | 1076 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 107 | 44471221 | 4487 | 107.688 | 4.487 | 9.5 | 9.5 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38799116 | 796 | 177.4014 | 0% | 0% | 100% | 0% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 110 | 44475549 | 4328 | 103.872 | 4.328 | 9.5 | 9.5 | 2B | 0 | 0 | 1109 | 0 | 1109 | N/A | N/A | N/A | N/A | 38799824 | 708 | 163.586 | 0% | 0% | 100% | 0% | 100% | 0% | 8763349 | 0 | 0.52 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 17 | 11.9718 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 133 | 44481021 | 5472 | 131.328 | 5.472 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 38800908 | 1084 | 198.0994 | 0% |  | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 44487040 | 6019 | 144.456 | 6.019 | 9.4 | 9.4 | 3B+1S | 0 | 1003 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 38802204 | 1296 | 215.3182 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 154 | 44493039 | 5999 | 143.976 | 5.999 | 9 | 9 | 3B+1S | 0 | 1003 | 1168 | 1185 | 1168 | N/A | N/A | N/A | N/A | 38803504 | 1300 | 216.7028 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 44499250 | 6211 | 149.064 | 6.211 | 8.5 | 8.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38804892 | 1388 | 223.4745 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 | 0.79 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 44505377 | 6127 | 147.048 | 6.127 | 8 | 8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38806252 | 1360 | 221.9683 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 44511450 | 6073 | 145.752 | 6.073 | 7.5 | 7.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38807616 | 1364 | 224.6007 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 153 | 44517524 | 6074 | 145.776 | 6.074 | 7 | 7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38808992 | 1376 | 226.5393 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 147 | 44523389 | 5865 | 140.76 | 5.865 | 6.5 | 6.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38810340 | 1348 | 229.838 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 133 | 44529222 | 5833 | 139.992 | 5.833 | 6 | 6 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38811716 | 1376 | 235.8992 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 44534883 | 5661 | 135.864 | 5.661 | 5.6 | 5.6 | 3B+1S | 0 | 1034 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38813044 | 1328 | 234.5875 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 44540416 | 5533 | 132.792 | 5.533 | 5.2 | 5.2 | 3B+1S | 0 | 1033 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38814340 | 1296 | 234.231 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 44546050 | 5634 | 135.216 | 5.634 | 4.8 | 4.8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38815668 | 1328 | 235.7118 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 123 | 44551763 | 5713 | 137.112 | 5.713 | 4.4 | 4.4 | 3B+1S | 0 | 1031 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38817016 | 1348 | 235.9531 | 0% | 100% | 100% | 100% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 44557018 | 5255 | 126.12 | 5.255 | 3.5 | 3.5 | 2B+1S | 0 | 1115 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38818116 | 1100 | 209.3245 | 0% | 100% | 100% | 0% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 44562305 | 5287 | 126.888 | 5.287 | 2.8 | 2.8 | 2B+1S | 0 | 1116 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38819216 | 1100 | 208.0575 | 0% | 100% | 100% | 0% | 100% | 0% | 8763349 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 44567328 | 5023 | 120.552 | 5.023 | 2.2 | 2.2 | 2B+1S | 0 | 1010 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38820296 | 1080 | 215.0109 | 0% | 100% | 100% | 0% | 100% | 0% | 8763349 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 100 | 44571570 | 4242 | 101.808 | 4.242 | 3.3 | 3.3 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38821132 | 836 | 197.0769 | 0% | 0% | 100% | 0% | 100% | 48% | 8764519 | 1170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 97 | 44575482 | 3912 | 93.888 | 3.912 | 4.8 | 4.8 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38821880 | 748 | 191.2065 | 0% | 0% | 100% | 0% | 100% | 48% | 8765858 | 1339 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5 | 124220 | 124220 | 124.22 | 124.22 | [12 empty] | 26448 | 26448 | 212.9126 | [6 empty] | 6991 | 6991 | 0.91167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (52%)
XCV1 CLOSED @ 5AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:04 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 20, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (48%)

## JULY 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26932 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44575482 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38821880 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8765858 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 98 | 44579322 | 3840 | 92.16 | 3.84 | 5.7 | 5.7 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38822622 | 742 | 193.2292 | 0% | 0% | 100% | 0% | 100% | 53% | 8767009 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 96 | 44583166 | 3844 | 92.256 | 3.844 | 7.1 | 7.1 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38823368 | 746 | 194.0687 | 0% | 0% | 100% | 0% | 100% | 53% | 8768157 | 1148 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 44587010 | 3844 | 92.256 | 3.844 | 8.4 | 8.4 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38824108 | 740 | 192.5078 | 0% | 0% | 100% | 0% | 100% | 53% | 8769312 | 1155 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 93 | 44590784 | 3774 | 90.576 | 3.774 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38824844 | 736 | 195.0185 | 0% | 0% | 100% | 0% | 100% | 53% | 8770328 | 1016 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 110 | 44595171 | 4387 | 105.288 | 4.387 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38825628 | 784 | 178.7098 | 0% | 0% | 100% | 0% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 115 | 44599781 | 4610 | 110.64 | 4.61 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38826392 | 764 | 165.7267 | 0% | 0% | 100% | 0% | 100% | 0% | 8770328 | 0 | 0.53 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 150 | 44605752 | 5971 | 143.304 | 5.971 | 9.1 | 9.1 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38827728 | 1336 | 223.7481 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 44611826 | 6074 | 145.776 | 6.074 | 8.5 | 8.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38829092 | 1364 | 224.5637 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 146 | 44617948 | 6122 | 146.928 | 6.122 | 8 | 8 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38830472 | 1380 | 225.4165 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 151 | 44624276 | 6328 | 151.872 | 6.328 | 7.5 | 7.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38831876 | 1404 | 221.871 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 | 0.91 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 146 | 44630331 | 6055 | 145.32 | 6.055 | 7 | 7 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38833212 | 1336 | 220.6441 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 44636370 | 6039 | 144.936 | 6.039 | 6.6 | 6.6 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38834564 | 1352 | 223.8781 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 139 | 44642226 | 5856 | 140.544 | 5.856 | 6.4 | 6.4 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38835904 | 1340 | 228.8251 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 44648070 | 5844 | 140.256 | 5.844 | 6 | 6 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38837252 | 1348 | 230.6639 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 44653792 | 5722 | 137.328 | 5.722 | 5.7 | 5.7 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38838596 | 1344 | 234.8829 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 44659338 | 5546 | 133.104 | 5.546 | 5.4 | 5.4 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38839892 | 1296 | 233.6819 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 44665031 | 5693 | 136.632 | 5.693 | 5.1 | 5.1 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38841228 | 1336 | 234.6742 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 44670523 | 5492 | 131.808 | 5.492 | 4.8 | 4.8 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38842548 | 1320 | 240.3496 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 44676071 | 5548 | 133.152 | 5.548 | 4.5 | 4.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38843864 | 1316 | 237.2026 | 0% | 100% | 100% | 100% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 127 | 44681339 | 5268 | 126.432 | 5.268 | 3.6 | 3.6 | 2B+1S | 0 | 1127 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38844984 | 1120 | 212.6044 | 0% | 100% | 100% | 0% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 125 | 44686514 | 5175 | 124.2 | 5.175 | 2.7 | 2.7 | 2B+1S | 0 | 1125 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38846076 | 1092 | 211.0145 | 0% | 100% | 100% | 0% | 100% | 0% | 8770328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 104 | 44691633 | 5119 | 122.856 | 5.119 | 1.9 | 1.9 | 2B+1S | 0 | 1125 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38847172 | 1096 | 214.1043 | 0% | 100% | 100% | 0% | 100% | 0% | 8770328 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 101 | 44695876 | 4243 | 101.832 | 4.243 | 2.7 | 2.7 | 2B | 0 | 0 | 1148 | 0 | 1147 | N/A | N/A | N/A | N/A | 38848036 | 864 | 203.6295 | 0% | 0% | 100% | 0% | 100% | 50% | 8771475 | 1147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 88 | 44699802 | 3926 | 94.224 | 3.926 | 4.4 | 4.4 | 2B | 0 | 0 | 1108 | 0 | 1108 | N/A | N/A | N/A | N/A | 38848812 | 776 | 197.6566 | 0% | 0% | 100% | 0% | 100% | 50% | 8772790 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.8333 | 124320 | 124320 | 124.32 | 124.32 | [12 empty] | 26932 | 26932 | 216.6345 | [6 empty] | 6932 | 6932 | 0.94667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (53%)
XCV1 CLOSED @ 4 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27376 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44699802 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38848812 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8772790 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 95 | 44703740 | 3938 | 94.512 | 3.938 | 5.8 | 5.8 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38849565 | 753 | 191.2138 | 0% | 0% | 100% | 0% | 100% | 60% | 8773932 | 1142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 94 | 44707640 | 3900 | 93.6 | 3.9 | 6.5 | 6.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38850324 | 759 | 194.6154 | 0% | 0% | 100% | 0% | 100% | 60% | 8775072 | 1140 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 92 | 44711473 | 3833 | 91.992 | 3.833 | 7.9 | 7.9 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38851012 | 688 | 179.4939 | 0% | 0% | 100% | 0% | 100% | 60% | 8776934 | 1862 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 98 | 44715620 | 4147 | 99.528 | 4.147 | 8.9 | 8.9 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38851747 | 735 | 177.2366 | 0% | 0% | 100% | 0% | 100% | 60% | 8777650 | 716 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 102 | 44719731 | 4111 | 98.664 | 4.111 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38852500 | 753 | 183.1671 | 0% | 0% | 100% | 0% | 100% |  | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 120 | 44724635 | 4904 | 117.696 | 4.904 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38853420 | 920 | 187.602 | 0% | 0% | 100% | 0% | 100% | 0% | 8777650 | 0 | 0.65 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 143 | 44730632 | 5997 | 143.928 | 5.997 | 9 | 9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38854756 | 1336 | 222.7781 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 44736716 | 6084 | 146.016 | 6.084 | 8.5 | 8.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38856148 | 1392 | 228.7968 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 148 | 44742709 | 5993 | 143.832 | 5.993 | 8 | 8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38857492 | 1344 | 224.2616 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 144 | 44748968 | 6259 | 150.216 | 6.259 | 7.5 | 7.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38858908 | 1416 | 226.2342 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 | 1.03 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 143 | 44755116 | 6148 | 147.552 | 6.148 | 7.1 | 7.1 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38860294 | 1386 | 225.4392 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 142 | 44761104 | 5988 | 143.712 | 5.988 | 6.6 | 6.6 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38861620 | 1326 | 221.4429 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 153 | 44767090 | 5986 | 143.664 | 5.986 | 6.3 | 6.3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38862996 | 1376 | 229.8697 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 44773096 | 6006 | 144.144 | 6.006 | 5.7 | 5.7 | 3B+1S | 0 | 1044 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38864388 | 1392 | 231.7682 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 44778960 | 5864 | 140.736 | 5.864 | 5.3 | 5.3 | 3B+1S | 0 | 1042 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38865748 | 1360 | 231.9236 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 130 | 44784743 | 5783 | 138.792 | 5.783 | 4.8 | 4.8 | 3B+1S | 0 | 1013 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38867100 | 1352 | 233.7887 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 44790433 | 5690 | 136.56 | 5.69 | 4.5 | 4.5 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38868440 | 1340 | 235.5009 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 44795992 | 5559 | 133.416 | 5.559 | 4.2 | 4.2 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38869740 | 1300 | 233.855 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 44801750 | 5758 | 138.192 | 5.758 | 3.8 | 3.8 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38871134 | 1394 | 242.098 | 0% | 100% | 100% | 100% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 127 | 44807010 | 5260 | 126.24 | 5.26 | 3.1 | 3.1 | 2B+1S | 0 | 1085 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38872220 | 1086 | 206.4639 | 0% | 100% | 100% | 0% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 133 | 44812028 | 5018 | 120.432 | 5.018 | 2.3 | 2.3 | 2B+1S | 0 | 1084 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38873252 | 1032 | 205.6596 | 0% | 100% | 100% | 0% | 100% | 0% | 8777650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 135 | 120 | 44817440 | 5412 | 129.888 | 5.412 | 1.5 | 1.5 | 2B+1S | 0 | 1085 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38874404 | 1152 | 212.8603 | 0% | 100% | 100% | 0% | 100% | 0% | 8777650 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 106 | 44821818 | 4378 | 105.072 | 4.378 | 2.4 | 2.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38875316 | 912 | 208.3143 | 0% | 0% | 100% | 0% | 100% | 45% | 8778528 | 878 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 88 | 44826143 | 4325 | 103.8 | 4.325 | 3.6 | 3.6 | 2B | 0 | 0 | 1188 | 0 | 1107 | N/A | N/A | N/A | N/A | 38876188 | 872 | 201.6185 | 0% | 0% | 100% | 0% | 100% | 45% | 8779721 | 1193 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.8333 | 126341 | 126341 | 126.341 | 126.341 | [12 empty] | 27376 | 27376 | 216.6834 | [6 empty] | 6931 | 6931 | 1.0067 |  | MLD | 1 | bar: Motor Speed (RPM) SP1 to Motor Speed (RPM) SP2; Motor Speed (RPM) BP2 to Motor Speed (RPM) BP6
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 22, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27160 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44826143 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38876188 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8779721 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 100 | 44830123 | 3980 | 95.52 | 3.98 | 5.3 | 5.3 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38876937 | 749 | 188.191 | 0% | 0% | 100% | 0% | 100% | 55% | 8780820 | 1099 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 99 | 44834104 | 3981 | 95.544 | 3.981 | 6.4 | 6.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38877677 | 740 | 185.8829 | 0% | 0% | 100% | 0% | 100% | 55% | 8781920 | 1100 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 95 | 44838079 | 3975 | 95.4 | 3.975 | 7.5 | 7.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38878416 | 739 | 185.9119 | 0% | 0% | 100% | 0% | 100% | 55% | 8783025 | 1105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 97 | 44842065 | 3986 | 95.664 | 3.986 | 8.3 | 8.3 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38879184 | 768 | 192.6744 | 0% | 0% | 100% | 0% | 100% | 55% | 8784119 | 1094 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 132 | 110 | 44846242 | 4177 | 100.248 | 4.177 | 8.9 | 8.9 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38879928 | 744 | 178.1183 | 0% | 0% | 100% | 0% | 100% | 55% | 8784706 | 587 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 121 | 44850868 | 4626 | 111.024 | 4.626 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38880804 | 876 | 189.3645 | 0% | 0% | 100% | 0% | 100% | 0% | 8784706 | 0 | 0.57 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 150 | 44857020 | 6152 | 147.648 | 6.152 | 8.8 | 8.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38882176 | 1372 | 223.0169 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 44863103 | 6083 | 145.992 | 6.083 | 8.3 | 8.3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38883532 | 1356 | 222.9163 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 44868932 | 5829 | 139.896 | 5.829 | 7.8 | 7.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38884824 | 1292 | 221.6504 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 44875356 | 6424 | 154.176 | 6.424 | 7.3 | 7.3 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38886268 | 1444 | 224.7821 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 | 0.96 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 44881586 | 6230 | 149.52 | 6.23 | 6.6 | 6.6 | 3B+1S | 0 | 1084 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38887660 | 1392 | 223.435 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 44887569 | 5983 | 143.592 | 5.983 | 5.9 | 5.9 | 3B+1S | 0 | 1084 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38889036 | 1376 | 229.985 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 44893624 | 6055 | 145.32 | 6.055 | 5.3 | 5.3 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38890428 | 1392 | 229.8927 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 134 | 44899533 | 5909 | 141.816 | 5.909 | 4.9 | 4.9 | 3B+1S | 0 | 1021 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38891788 | 1360 | 230.1574 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 134 | 44905179 | 5646 | 135.504 | 5.646 | 4.7 | 4.7 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38893108 | 1320 | 233.7938 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 44910856 | 5677 | 136.248 | 5.677 | 4.5 | 4.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38894428 | 1320 | 232.5172 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 44916555 | 5699 | 136.776 | 5.699 | 4.2 | 4.2 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38895756 | 1328 | 233.0233 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 44922023 | 5468 | 131.232 | 5.468 | 3.9 | 3.9 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38897060 | 1304 | 238.4784 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 44927676 | 5653 | 135.672 | 5.653 | 3.7 | 3.7 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38898404 | 1344 | 237.7499 | 0% | 100% | 100% | 100% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 113 | 123 | 44932826 | 5150 | 123.6 | 5.15 | 3.1 | 3.1 | 2B+1S | 0 | 1076 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 38899516 | 1112 | 215.9223 | 0% | 100% | 100% | 0% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 127 | 44938169 | 5343 | 128.232 | 5.343 | 2.4 | 2.4 | 2B+1S | 0 | 1073 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38900610 | 1094 | 204.7539 | 0% | 100% | 100% | 0% | 100% | 0% | 8784706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 117 | 44942934 | 4765 | 114.36 | 4.765 | 1.8 | 1.8 | 2B+1S | 0 | 1074 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38901620 | 1010 | 211.9622 | 0% | 100% | 100% | 0% | 100% | 0% | 8784706 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 143 | 125 | 44947539 | 4605 | 110.52 | 4.605 | 2.9 | 2.9 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38902570 | 950 | 206.2975 | 0% | 0% | 100% | 0% | 100% | 45% | 8785954 | 1248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 97 | 44951610 | 4071 | 97.704 | 4.071 | 4.6 | 4.6 | 2B | 0 | 0 | 1177 | 0 | 1117 | N/A | N/A | N/A | N/A | 38903348 | 778 | 191.1078 | 0% | 0% | 100% | 0% | 100% | 45% | 8787558 | 1604 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
|  |  | 0 | [6 empty] | TOTAL |  |  |  | 126.5 | 125467 | 125467 | 125.467 | 125.467 | [12 empty] | 27160 | 27160 | 216.4713 | [6 empty] | 7837 | 7837 | 0.93667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,657
GENSET 1 WARMUP EXERCISED @ 4:20PM / STOPPED @ 4:30PM
GENSET 2 WARMUP EXERCISED @ 4:10PM / STOPPED @ 4:20PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27652 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 44951610 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38903348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8787558 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 99 | 44955680 | 4070 | 97.68 | 4.07 | 5.6 | 5.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38904098 | 750 | 184.2752 | 0% | 0% | 100% | 0% | 100% | 55% | 8788577 | 1019 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 97 | 44959755 | 4075 | 97.8 | 4.075 | 7.4 | 7.4 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38904843 | 745 | 182.8221 | 0% | 0% | 100% | 0% | 100% | 55% | 8789592 | 1015 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 44963823 | 4068 | 97.632 | 4.068 | 8.2 | 8.2 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38905591 | 748 | 183.8741 | 0% | 0% | 100% | 0% | 100% | 55% | 8790603 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 103 | 44967894 | 4071 | 97.704 | 4.071 | 9.3 | 9.3 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38906343 | 752 | 184.7212 | 0% | 0% | 100% | 0% | 100% | 55% | 8791616 | 1013 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 107 | 44971963 | 4069 | 97.656 | 4.069 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38907100 | 757 | 186.0408 | 0% | 0% | 100% | 0% | 100% | 55% | 8792613 | 997 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 112 | 44976870 | 4907 | 117.768 | 4.907 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38907932 | 832 | 169.5537 | 0% | 0% | 100% | 0% | 100% | 0% | 8792613 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 117 | 44982990 | 6120 | 146.88 | 6.12 | 9.3 | 9.3 | 3B+1S | 0 | 1075 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38909316 | 1384 | 226.1438 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 44989130 | 6140 | 147.36 | 6.14 | 8.4 | 8.4 | 3B+1S | 0 | 1075 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38910670 | 1354 | 220.5212 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 44995283 | 6153 | 147.672 | 6.153 | 8 | 8 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38912114 | 1444 | 234.6823 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 45001314 | 6031 | 144.744 | 6.031 | 7.4 | 8.5 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38913444 | 1330 | 220.5273 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 45007358 | 6044 | 145.056 | 6.044 | 6.8 | 8.1 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38914850 | 1406 | 232.6274 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 45013210 | 5852 | 140.448 | 5.852 | 6.4 | 6.4 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38916216 | 1366 | 233.4245 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 152 | 45019132 | 5922 | 142.128 | 5.922 | 5.7 | 5.7 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38917576 | 1360 | 229.6521 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 137 | 45025142 | 6010 | 144.24 | 6.01 | 5.2 | 5.2 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38918980 | 1404 | 233.6106 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 130 | 45030586 | 5444 | 130.656 | 5.444 | 4.7 | 4.7 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38920272 | 1292 | 237.3255 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 45036348 | 5762 | 138.288 | 5.762 | 4.2 | 4.2 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38921616 | 1344 | 233.2523 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 45042094 | 5746 | 137.904 | 5.746 | 3.6 | 3.6 | 3B+1S | 0 | 1052 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38922972 | 1356 | 235.9903 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 45047708 | 5614 | 134.736 | 5.614 | 3.2 | 3.2 | 3B+1S | 0 | 1052 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38924312 | 1340 | 238.689 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 134 | 45053306 | 5598 | 134.352 | 5.598 | 2.9 | 2.9 | 3B+1S | 0 | 1022 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38925656 | 1344 | 240.0857 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 45058674 | 5368 | 128.832 | 5.368 | 2.7 | 2.7 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38926916 | 1260 | 234.7243 | 0% | 100% | 100% | 100% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 129 | 45064033 | 5359 | 128.616 | 5.359 | 1.9 | 1.9 | 2B+1S | 0 | 1135 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 38928052 | 1136 | 211.9798 | 0% | 100% | 100% | 0% | 100% | 0% | 8792613 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 124 | 45069388 | 5355 | 128.52 | 5.355 | 1.3 | 1.3 | 2B+1S | 0 | 1135 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38929180 | 1128 | 210.6443 | 0% | 100% | 100% | 0% | 100% | 0% | 8792613 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 144 | 107 | 45073993 | 4605 | 110.52 | 4.605 | 2.3 | 2.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38930108 | 928 | 201.5201 | 0% | 0% | 100% | 0% | 100% | 50% | 8793805 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 98 | 45078492 | 4499 | 107.976 | 4.499 | 3.5 | 3.5 | 2B | 0 | 0 | 1108 | 0 | 1108 | N/A | N/A | N/A | N/A | 38931000 | 892 | 198.2663 | 0% | 0% | 100% | 0% | 100% | 50% | 8795276 | 1471 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0417 | 126882 | 126882 | 126.882 | 126.882 | [12 empty] | 27652 | 27652 | 217.9348 | [6 empty] | 7718 | 7718 | 0.96833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 24, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27116 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45078492 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38931000 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8795276 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 98 | 45082560 | 4068 | 97.632 | 4.068 | 5.8 | 5.8 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 38931730 | 730 | 179.4494 | 0% | 0% | 100% | 0% | 100% | 58% | 8796647 | 1371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 97 | 45086629 | 4069 | 97.656 | 4.069 | 7.6 | 7.6 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 38932467 | 737 | 181.1256 | 0% | 0% | 100% | 0% | 100% | 58% | 8797907 | 1260 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 95 | 45090702 | 4073 | 97.752 | 4.073 | 8.4 | 8.4 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 38933207 | 740 | 181.6843 | 0% | 0% | 100% | 0% | 100% | 58% | 8799365 | 1458 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 103 | 45094765 | 4063 | 97.512 | 4.063 | 9.2 | 9.2 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 38933942 | 735 | 180.9008 | 0% | 0% | 100% | 0% | 100% | 58% | 8800451 | 1086 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 109 | 45098835 | 4070 | 97.68 | 4.07 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 38934676 | 734 | 180.344 | 0% | 0% | 100% | 0% | 100% | 58% | 8800762 | 311 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 112 | 45103544 | 4709 | 113.016 | 4.709 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 38935428 | 752 | 159.6942 | 0% | 0% | 100% | 0% | 100% | 0% | 8800762 | 0 | 1.5 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 143 | 45109453 | 5909 | 141.816 | 5.909 | 9.1 | 9.1 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38936740 | 1312 | 222.0342 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 45115509 | 6056 | 145.344 | 6.056 | 8.5 | 8.5 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38938116 | 1376 | 227.2127 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 144 | 45121530 | 6021 | 144.504 | 6.021 | 8.1 | 8.1 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38939488 | 1372 | 227.8691 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 45127628 | 6098 | 146.352 | 6.098 | 7.6 | 8.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38940860 | 1372 | 224.9918 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 | 1.22 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 45133662 | 6034 | 144.816 | 6.034 | 7 | 8.1 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38942216 | 1356 | 224.7265 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 45139534 | 5872 | 140.928 | 5.872 | 6.4 | 6.4 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38943584 | 1368 | 232.97 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 45145487 | 5953 | 142.872 | 5.953 | 5.8 | 5.8 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38944948 | 1364 | 229.1282 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 135 | 45151329 | 5842 | 140.208 | 5.842 | 5.2 | 5.2 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38946320 | 1372 | 234.8511 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 | 1.42 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 147 | 45157196 | 5867 | 140.808 | 5.867 | 4.7 | 4.7 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 38947684 | 1364 | 232.4868 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 45162893 | 5697 | 136.728 | 5.697 | 4.2 | 4.2 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38949036 | 1352 | 237.3179 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 143 | 45168732 | 5839 | 140.136 | 5.839 | 3.7 | 3.7 | 3B+1S | 0 | 1053 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38950404 | 1368 | 234.2867 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 132 | 45174403 | 5671 | 136.104 | 5.671 | 3.4 | 3.4 | 3B+1S | 0 | 1011 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38951752 | 1348 | 237.7006 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 136 | 45179993 | 5590 | 134.16 | 5.59 | 3.2 | 3.2 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 38953072 | 1320 | 236.136 | 0% | 100% | 100% | 100% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 104 | 45185256 | 5263 | 126.312 | 5.263 | 2.7 | 2.7 | 3B+1S | 0 | 1084 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 38954140 | 1068 | 202.9261 | 0% | 100% | 100% | 0% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 45190446 | 5190 | 124.56 | 5.19 | 1.9 | 1.9 | 2B+1S | 0 | 1083 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38955204 | 1064 | 205.0096 | 0% | 100% | 100% | 0% | 100% | 0% | 8800762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 123 | 45195672 | 5226 | 125.424 | 5.226 | 1.3 | 1.3 | 2B+1S | 0 | 1084 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38956304 | 1100 | 210.486 | 0% | 100% | 100% | 0% | 100% | 0% | 8800762 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 144 | 109 | 45200173 | 4501 | 108.024 | 4.501 | 2.3 | 2.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38957228 | 924 | 205.2877 | 0% | 0% | 100% | 0% | 100% | 55% | 8801979 | 1217 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 142 | 108 | 45204548 | 4375 | 105 | 4.375 | 4 | 4 | 2B | 0 | 0 | 1108 | 0 | 1109 | N/A | N/A | N/A | N/A | 38958116 | 888 | 202.9714 | 0% | 0% | 100% | 0% | 100% | 55% | 8803274 | 1295 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.7083 | 126056 | 126056 | 126.056 | 126.056 | [12 empty] | 27116 | 27116 | 215.1107 | [6 empty] | 7998 | 7998 | 1.205 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (58%)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:05 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 25, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28396 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45204548 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38958116 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8803274 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 138 | 103 | 45209064 | 4516 | 108.384 | 4.516 | 5 | 5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38959036 | 920 | 203.7201 | 0% | 0% | 100% | 0% | 100% | 65% | 8804280 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 100 | 45213579 | 4515 | 108.36 | 4.515 | 6.1 | 6.1 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38959954 | 918 | 203.3223 | 0% | 0% | 100% | 0% | 100% | 65% | 8805289 | 1009 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 102 | 45218092 | 4513 | 108.312 | 4.513 | 7 | 7 | 2B | 0 | 0 | 1099 | 0 | 1099 | N/A | N/A | N/A | N/A | 38960868 | 914 | 202.526 | 0% | 0% | 100% | 0% | 100% | 65% | 8806299 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 97 | 45222187 | 4095 | 98.28 | 4.095 | 8.4 | 8.4 | 2B | 0 | 0 | 1099 | 0 | 1098 | N/A | N/A | N/A | N/A | 38961592 | 724 | 176.801 | 0% | 0% | 100% | 0% | 100% | 65% | 8807534 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 100 | 45226283 | 4096 | 98.304 | 4.096 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 38962316 | 724 | 176.7578 | 0% | 0% | 100% | 0% | 100% | 65% | 8808744 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 113 | 45231042 | 4759 | 114.216 | 4.759 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 38963068 | 752 | 158.0164 | 0% | 0% | 100% | 0% | 100% | 0% | 8808744 | 0 | 1.07 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 45236907 | 5865 | 140.76 | 5.865 | 9.4 | 9.4 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38964352 | 1284 | 218.9258 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 45243199 | 6292 | 151.008 | 6.292 | 8.9 | 8.9 | 3B+1S | 0 | 1021 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38965768 | 1416 | 225.0477 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 145 | 45249239 | 6040 | 144.96 | 6.04 | 8.3 | 8.3 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38967120 | 1352 | 223.8411 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 144 | 45255844 | 6605 | 158.52 | 6.605 | 7.6 | 8.5 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38968604 | 1484 | 224.6783 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 | 0.8 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 143 | 45261582 | 5738 | 137.712 | 5.738 | 6.9 | 8.1 | 3B+1S | 0 | 1144 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38969924 | 1320 | 230.0453 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 151 | 45267644 | 6062 | 145.488 | 6.062 | 6 | 6 | 3B+1S | 0 | 1178 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38971416 | 1492 | 246.1234 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 152 | 45273749 | 6105 | 146.52 | 6.105 | 5 | 5 | 3B+1S | 0 | 1147 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38972780 | 1364 | 223.4234 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 140 | 45279742 | 5993 | 143.832 | 5.993 | 4.4 | 4.4 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38974144 | 1364 | 227.5989 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 155 | 45285570 | 5828 | 139.872 | 5.828 | 3.7 | 3.7 | 3B+1S | 0 | 1107 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38975564 | 1420 | 243.6513 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 141 | 45291433 | 5863 | 140.712 | 5.863 | 3.1 | 3.1 | 3B+1S | 0 | 1127 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38976924 | 1360 | 231.9632 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 2 | 1.4085 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 45297287 | 5854 | 140.496 | 5.854 | 2.7 | 2.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38978292 | 1368 | 233.6864 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 139 | 45302974 | 5687 | 136.488 | 5.687 | 2.5 | 2.5 | 3B+1S | 0 | 1009 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38979620 | 1328 | 233.515 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 140 | 132 | 45308603 | 5629 | 135.096 | 5.629 | 2.4 | 2.4 | 3B+1S | 0 | 983 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38980940 | 1320 | 234.4999 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 140 | 136 | 45314054 | 5451 | 130.824 | 5.451 | 2.3 | 2.3 | 3B+1S | 0 | 983 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38982232 | 1292 | 237.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 137 | 130 | 45319698 | 5644 | 135.456 | 5.644 | 2.1 | 2.1 | 2B+1S | 0 | 1002 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38983556 | 1324 | 234.5854 | 0% | 100% | 100% | 100% | 100% | 0% | 8808744 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 140 | 123 | 45324922 | 5224 | 125.376 | 5.224 | 1.6 | 1.6 | 2B+1S | 0 | 1002 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38984664 | 1108 | 212.098 | 0% | 100% | 100% | 0% | 100% | 0% | 8808744 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 143 | 110 | 45329518 | 4596 | 110.304 | 4.596 | 2.6 | 2.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38985580 | 916 | 199.3037 | 0% | 0% | 100% | 0% | 100% | 55% | 8809851 | 1107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 111 | 45334263 | 4745 | 113.88 | 4.745 | 3.8 | 3.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 38986512 | 932 | 196.4173 | 0% | 0% | 100% | 0% | 100% | 55% | 8810968 | 1117 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129 | 129715 | 129715 | 129.715 | 129.715 | [12 empty] | 28396 | 28396 | 218.9107 | [6 empty] | 7694 | 7694 | 0.89 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (65%)
XCV1 CLOSED @ 4:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 26, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27612 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45334263 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 38986512 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8810968 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 100 | 45338593 | 4330 | 103.92 | 4.33 | 5 | 5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38987292 | 780 | 180.1386 | 0% | 0% | 100% | 0% | 100% | 63% | 8812033 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 103 | 45342915 | 4322 | 103.728 | 4.322 | 6.2 | 6.2 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38988067 | 775 | 179.3151 | 0% | 0% | 100% | 0% | 100% | 63% | 8813099 | 1066 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 106 | 45347242 | 4327 | 103.848 | 4.327 | 7.1 | 7.1 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38988837 | 770 | 177.9524 | 0% | 0% | 100% | 0% | 100% | 63% | 8814168 | 1069 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 104 | 45351567 | 4325 | 103.8 | 4.325 | 8.3 | 8.3 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38989605 | 768 | 177.5723 | 0% | 0% | 100% | 0% | 100% | 63% | 8815225 | 1057 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 105 | 45355900 | 4333 | 103.992 | 4.333 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38990376 | 771 | 177.9368 | 0% | 0% | 100% | 0% | 100% | 63% | 8816275 | 1050 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 115 | 45360734 | 4834 | 116.016 | 4.834 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 38991164 | 788 | 163.012 | 0% | 0% | 100% | 0% | 100% | 0% | 8816275 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 128 | 45366370 | 5636 | 135.264 | 5.636 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1158 | 1185 | 1158 | N/A | N/A | N/A | N/A | 38992368 | 1204 | 213.6267 | 0% | 0% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 137 | 45371984 | 5614 | 134.736 | 5.614 | 9.2 | 9.2 | 3B+1S | 0 | 1015 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 38993572 | 1204 | 214.4638 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 45377888 | 5904 | 141.696 | 5.904 | 8.7 | 8.7 | 3B+1S | 0 | 1015 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 38994836 | 1264 | 214.0921 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 144 | 45384074 | 6186 | 148.464 | 6.186 | 8.1 | 8.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38996232 | 1396 | 225.6709 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 45390128 | 6054 | 145.296 | 6.054 | 7.6 | 8.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38997608 | 1376 | 227.2877 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 159 | 45396126 | 5998 | 143.952 | 5.998 | 6.9 | 6.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38998972 | 1364 | 227.4091 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 150 | 45402260 | 6134 | 147.216 | 6.134 | 6.2 | 6.2 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39000364 | 1392 | 226.9319 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 144 | 45408224 | 5964 | 143.136 | 5.964 | 5.5 | 5.5 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39001820 | 1456 | 244.1315 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 143 | 45414282 | 6058 | 145.392 | 6.058 | 4.6 | 4.6 | 3B+1S | 0 | 1117 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39003244 | 1424 | 235.0611 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 45420193 | 5911 | 141.864 | 5.911 | 3.7 | 3.7 | 3B+1S | 0 | 1086 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39004636 | 1392 | 235.4931 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 45426081 | 5888 | 141.312 | 5.888 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39006012 | 1376 | 233.6957 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 45431970 | 5889 | 141.336 | 5.889 | 2.7 | 2.7 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39007388 | 1376 | 233.656 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 129 | 45437702 | 5732 | 137.568 | 5.732 | 2.4 | 2.4 | 3B+1S | 0 | 1023 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39008720 | 1332 | 232.3796 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 143 | 45443343 | 5641 | 135.384 | 5.641 | 2.1 | 2.1 | 3B+1S | 0 | 1024 | 1188 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39010044 | 1324 | 234.7102 | 0% | 100% | 100% | 100% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 129 | 45448654 | 5311 | 127.464 | 5.311 | 1.4 | 1.4 | 2B+1S | 0 | 1097 | 1188 | 0 | 1185 | N/A | N/A | N/A | N/A | 39011152 | 1108 | 208.6236 | 0% | 100% | 100% | 0% | 100% | 0% | 8816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 118 | 45453965 | 5311 | 127.464 | 5.311 | 1.3 | 1.3 | 2B+1S | 0 | 1097 | 1188 | 0 | 1185 | N/A | N/A | N/A | N/A | 39012260 | 1108 | 208.6236 | 0% | 100% | 100% | 0% | 100% | 0% | 8816275 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 115 | 45458587 | 4622 | 110.928 | 4.622 | 2.1 | 2.1 | 2B | 0 | 0 | 1188 | 0 | 1185 | N/A | N/A | N/A | N/A | 39013192 | 932 | 201.6443 | 0% | 0% | 100% | 0% | 100% | 45% | 8817763 | 1488 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 143 | 111 | 45463209 | 4622 | 110.928 | 4.622 | 3.6 | 3.6 | 2B | 0 | 0 | 1188 | 0 | 1185 | N/A | N/A | N/A | N/A | 39014124 | 932 | 201.6443 | 0% | 0% | 100% | 0% | 100% | 45% | 8819251 | 1488 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.8333 | 128946 | 128946 | 128.946 | 128.946 | [12 empty] | 27612 | 27612 | 214.1362 | [6 empty] | 8283 | 8283 | 0.955 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (63%)
XCV1 CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 27, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27304 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45463209 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39014124 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8819251 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 137 | 104 | 45467415 | 4206 | 100.944 | 4.206 | 4.7 | 4.7 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39014876 | 752 | 178.7922 | 0% | 0% | 100% | 0% | 100% | 68% | 8820573 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 101 | 45471629 | 4214 | 101.136 | 4.214 | 5.9 | 5.9 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39015626 | 750 | 177.9782 | 0% | 0% | 100% | 0% | 100% | 68% | 8821896 | 1323 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 139 | 102 | 45475842 | 4213 | 101.112 | 4.213 | 6.6 | 6.6 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39016380 | 754 | 178.9699 | 0% | 0% | 100% | 0% | 100% | 68% | 8823218 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 140 | 106 | 45480054 | 4212 | 101.088 | 4.212 | 9 | 9 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39017132 | 752 | 178.5375 | 0% | 0% | 100% | 0% | 100% | 78% | 8824541 | 1323 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 132 | 45484590 | 4536 | 108.864 | 4.536 | 9.5 | 9.5 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39017908 | 776 | 171.0758 | 0% | 0% | 100% | 0% | 100% | 78% | 8824869 | 328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 118 | 45489374 | 4784 | 114.816 | 4.784 | 9.5 | 9.5 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39018704 | 796 | 166.388 | 0% | 0% | 100% | 0% | 100% | 0% | 8824869 | 0 | 0.74 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 119 | 141 | 45495110 | 5736 | 137.664 | 5.736 | 9.3 | 9.3 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39019996 | 1292 | 225.2441 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 45500893 | 5783 | 138.792 | 5.783 | 8.9 | 8.9 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39021324 | 1328 | 229.6386 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 45506972 | 6079 | 145.896 | 6.079 | 8.4 | 8.4 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39022716 | 1392 | 228.985 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 45513529 | 6557 | 157.368 | 6.557 | 7.7 | 8.5 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39024204 | 1488 | 226.933 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 45519170 | 5641 | 135.384 | 5.641 | 7.2 | 8.1 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39025484 | 1280 | 226.9101 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 148 | 45525191 | 6021 | 144.504 | 6.021 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39026856 | 1372 | 227.8691 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 45530908 | 5717 | 137.208 | 5.717 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39028196 | 1340 | 234.3887 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 45537044 | 6136 | 147.264 | 6.136 | 5.5 | 5.5 | 3B+1S | 0 | 1044 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39029630 | 1434 | 233.7027 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 45542823 | 5779 | 138.696 | 5.779 | 5 | 5 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39030998 | 1368 | 236.7192 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 133 | 45548446 | 5623 | 134.952 | 5.623 | 4.6 | 4.6 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39032316 | 1318 | 234.3945 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 45553998 | 5552 | 133.248 | 5.552 | 4.1 | 4.1 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39033612 | 1296 | 233.4294 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 130 | 45559836 | 5838 | 140.112 | 5.838 | 3.6 | 3.6 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39034988 | 1376 | 235.6972 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 45565415 | 5579 | 133.896 | 5.579 | 3.3 | 3.3 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39036300 | 1312 | 235.1676 | 0% | 100% | 100% | 100% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 131 | 45570941 | 5526 | 132.624 | 5.526 | 2.4 | 2.4 | 2B+1S | 0 | 1147 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39037456 | 1156 | 209.1929 | 0% | 100% | 100% | 0% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 45575998 | 5057 | 121.368 | 5.057 | 1.6 | 1.6 | 2B+1S | 0 | 1147 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39038516 | 1060 | 209.6104 | 0% | 100% | 100% | 0% | 100% | 0% | 8824869 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 127 | 45581394 | 5396 | 129.504 | 5.396 | 1.3 | 1.3 | 2B+1S | 0 | 1055 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39039612 | 1096 | 203.1134 | 0% | 100% | 100% | 0% | 100% | 0% | 8824869 | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 115 | 45588231 | 6837 | 164.088 | 6.837 | 2 | 2 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39040532 | 920 | 134.5619 | 0% | 0% | 100% | 0% | 100% | 55% | 8826149 | 1280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 149 | 107 | 45590616 | 2385 | 57.24 | 2.385 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39041428 | 896 | 375.6813 | 0% | 0% | 100% | 0% | 100% | 55% | 8827447 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.7917 | 127407 | 127407 | 127.407 | 127.407 | [12 empty] | 27304 | 27304 | 214.3053 | [6 empty] | 8196 | 8196 | 0.93167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 3:01 AM (78%)
XCV1 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27936 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45590616 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39041428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8827447 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 139 | 107 | 45594916 | 4300 | 103.2 | 4.3 | 5.2 | 5.2 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 39042233 | 805 | 187.2093 | 0% | 0% | 100% | 0% | 100% | 75% | 8828856 | 1409 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 138 | 105 | 45599212 | 4296 | 103.104 | 4.296 | 6.3 | 6.3 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 39043028 | 795 | 185.0559 | 0% | 0% | 100% | 0% | 100% | 75% | 8830134 | 1278 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 103 | 45603577 | 4365 | 104.76 | 4.365 | 8.5 | 8.5 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 39043836 | 808 | 185.1088 | 0% | 0% | 100% | 0% | 100% | 75% | 8831348 | 1214 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 140 | 104 | 45607935 | 4358 | 104.592 | 4.358 | 8.6 | 8.6 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 39044644 | 808 | 185.4061 | 0% | 0% | 100% | 0% | 100% | 75% | 8832396 | 1048 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 113 | 45612449 | 4514 | 108.336 | 4.514 | 9.5 | 9.5 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 39045456 | 812 | 179.8848 | 0% | 0% | 100% | 0% | 100% | 75% | 8833233 | 837 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 128 | 45617460 | 5011 | 120.264 | 5.011 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 |  | 1187 | N/A | N/A | N/A | N/A | 39046380 | 924 | 184.3943 | 0% | 0% | 100% |  | 100% | 0% | 8833233 | 0 | 0.83 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 45623332 | 5872 | 140.928 | 5.872 | 9.2 | 9.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39047692 | 1312 | 223.4332 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 45629375 | 6043 | 145.032 | 6.043 | 8.7 | 8.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39049068 | 1376 | 227.7015 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 45635262 | 5887 | 141.288 | 5.887 | 8.1 | 8.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39050412 | 1344 | 228.2996 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 143 | 45641433 | 6171 | 148.104 | 6.171 | 7.6 | 8.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39051812 | 1400 | 226.8676 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 45647381 | 5948 | 142.752 | 5.948 | 7 | 8.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39053172 | 1360 | 228.6483 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 45653527 | 6146 | 147.504 | 6.146 | 6.4 | 6.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39054572 | 1400 | 227.7904 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 141 | 45659264 | 5737 | 137.688 | 5.737 | 5.8 | 5.8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39055900 | 1328 | 231.4799 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 45665233 | 5969 | 143.256 | 5.969 | 5.3 | 5.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39057292 | 1392 | 233.2049 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 45671112 | 5879 | 141.096 | 5.879 | 4.8 | 4.8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39058654 | 1362 | 231.6721 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 45676733 | 5621 | 134.904 | 5.621 | 4.4 | 4.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39059980 | 1326 | 235.9011 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 45682627 | 5894 | 141.456 | 5.894 | 3.8 | 3.8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39061352 | 1372 | 232.7791 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 45688144 | 5517 | 132.408 | 5.517 | 3.3 | 3.3 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39062660 | 1308 | 237.0854 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 45694193 | 6049 | 145.176 | 6.049 | 3 | 3 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39064088 | 1428 | 236.0721 | 0% | 100% | 100% | 100% | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 130 | 45699466 | 5273 | 126.552 | 5.273 | 2.7 | 2.7 | 2B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39065348 | 1260 | 238.9532 | 0% | 100% | 100% |  | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 122 | 45704746 | 5280 | 126.72 | 5.28 | 1.9 | 1.9 | 2B+1S | 0 | 1116 | 1188 |  | 1187 | N/A | N/A | N/A | N/A | 39066440 | 1092 | 206.8182 | 0% | 100% | 100% |  | 100% | 0% | 8833233 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 142 | 128 | 45710088 | 5342 | 128.208 | 5.342 | 1.3 | 1.3 | 2B+1S | 0 | 1115 | 1188 |  | 1187 | N/A | N/A | N/A | N/A | 39067600 | 1160 | 217.1471 | 0% | 100% | 100% |  | 100% | 0% | 8833233 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 144 | 109 | 45714760 | 4672 | 112.128 | 4.672 | 2.2 | 2.2 | 2B | 0 |  | 1188 |  | 1188 | N/A | N/A | N/A | N/A | 39068500 | 900 | 192.637 | 0% |  | 100% |  | 100% | 55% | 8834391 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 146 | 100 | 45719254 | 4494 | 107.856 | 4.494 | 3.6 | 3.6 | 2B | 0 |  | 1117 |  | 1117 | N/A | N/A | N/A | N/A | 39069364 | 864 | 192.2563 | 0% |  | 100% |  | 100% | 55% | 8835756 | 1365 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.7083 | 128638 | 128638 | 128.638 | 128.638 | [12 empty] | 27936 | 27936 | 217.1676 | [6 empty] | 8309 | 8309 | 1.0083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (75%)
XCV1 CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 29, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## JULY 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27224 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45719254 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39069364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8835756 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 105 | 45723490 | 4236 | 101.664 | 4.236 | 5.7 | 5.7 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39070133 | 769 | 181.5392 | 0% | 0% | 100% | 0% | 100% | 70% | 8836985 | 1229 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 104 | 45727717 | 4227 | 101.448 | 4.227 | 6.4 | 6.4 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39070905 | 772 | 182.6354 | 0% | 0% | 100% | 0% | 100% | 70% | 8838216 | 1231 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 102 | 45731951 | 4234 | 101.616 | 4.234 | 7.7 | 7.7 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39071668 | 763 | 180.2078 | 0% | 0% | 100% | 0% | 100% | 70% | 8839443 | 1227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 129 | 106 | 45736374 | 4423 | 106.152 | 4.423 | 8.6 | 8.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39072448 | 780 | 176.3509 | 0% | 0% | 100% | 0% | 100% | 70% | 8840469 | 1026 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 118 | 109 | 45740798 | 4424 | 106.176 | 4.424 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39073228 | 780 | 176.311 | 0% | 0% | 100% | 0% | 100% | 70% | 8841281 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 45745618 | 4820 | 115.68 | 4.82 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39074060 | 832 | 172.6141 | 0% | 0% | 100% |  | 100% | 0% | 8841281 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 140 | 45751517 | 5899 | 141.576 | 5.899 | 9.1 | 9.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39075380 | 1320 | 223.7667 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 45757730 | 6213 | 149.112 | 6.213 | 8.4 | 8.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39076792 | 1412 | 227.2654 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 143 | 45763545 | 5815 | 139.56 | 5.815 | 7.8 | 7.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39078124 | 1332 | 229.0628 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 144 | 45769704 | 6159 | 147.816 | 6.159 | 7.3 | 7.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39079524 | 1400 | 227.3096 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 142 | 45775673 | 5969 | 143.256 | 5.969 | 6.9 | 6.9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39080876 | 1352 | 226.5036 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 141 | 45781556 | 5883 | 141.192 | 5.883 | 6.5 | 6.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39082228 | 1352 | 229.8147 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 131 | 45787193 | 5637 | 135.288 | 5.637 | 6.3 | 6.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39083564 | 1336 | 237.0055 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 133 | 45792814 | 5621 | 134.904 | 5.621 | 6 | 6 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39084916 | 1352 | 240.5266 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 | 1.38 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 45798278 | 5464 | 131.136 | 5.464 | 5.8 | 5.8 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39086220 | 1304 | 238.653 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 128 | 45803876 | 5598 | 134.352 | 5.598 | 5.6 | 5.6 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39087576 | 1356 | 242.2294 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 45809285 | 5409 | 129.816 | 5.409 | 5.5 | 5.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39088868 | 1292 | 238.8612 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 45814726 | 5441 | 130.584 | 5.441 | 5.2 | 5.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39090188 | 1320 | 242.6025 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 129 | 45820307 | 5581 | 133.944 | 5.581 | 5 | 5 | 3B+1S | 0 | 1003 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39091532 | 1344 | 240.8171 | 0% | 100% | 100% | 100% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 123 | 45825520 | 5213 | 125.112 | 5.213 | 4.2 | 4.2 | 2B+1S | 0 | 1086 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39092652 | 1120 | 214.8475 | 0% | 100% | 100% | 0% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 45830669 | 5149 | 123.576 | 5.149 | 3.3 | 3.3 | 2B+1S | 0 | 1087 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39093704 | 1052 | 204.3115 | 0% | 100% | 100% | 0% | 100% | 0% | 8841281 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 124 | 45836002 | 5333 | 127.992 | 5.333 | 2.5 | 2.5 | 2B+1S | 0 | 1088 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39094812 | 1108 | 207.763 | 0% | 100% | 100% | 0% | 100% | 0% | 8841281 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 109 | 45840573 | 4571 | 109.704 | 4.571 | 3.3 | 3.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39095732 | 920 | 201.2689 | 0% | 0% | 100% | 0% | 100% | 50% | 8842127 | 846 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 105 | 45844962 | 4389 | 105.336 | 4.389 | 4.6 | 4.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39096588 | 856 | 195.033 | 0% | 0% | 100% | 0% | 100% | 50% | 8843113 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.5417 | 125708 | 125708 | 125.708 | 125.708 | [12 empty] | 27224 | 27224 | 216.5654 | [6 empty] | 7357 | 7357 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (70%)
XCV1 CLOSED @ 4:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 30, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27177 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45844962 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39096588 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8843113 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 103 | 45849077 | 4115 | 98.76 | 4.115 | 5.8 | 5.8 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39097328 | 740 | 179.8299 | 0% | 0% | 100% | 0% | 100% | 70% | 8844119 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 106 | 45853182 | 4105 | 98.52 | 4.105 | 6.7 | 6.7 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39098065 | 737 | 179.5371 | 0% | 0% | 100% | 0% | 100% | 70% | 8845126 | 1007 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 100 | 45857293 | 4111 | 98.664 | 4.111 | 7.6 | 7.6 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39098812 | 747 | 181.7076 | 0% | 0% | 100% | 0% | 100% | 70% | 8846135 | 1009 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 102 | 45861481 | 4188 | 100.512 | 4.188 | 8.8 | 8.8 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39099640 | 828 | 197.7077 | 0% | 0% | 100% | 0% | 100% | 70% | 8847036 | 901 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 128 | 111 | 45865670 | 4189 | 100.536 | 4.189 | 9.5 | 9.5 | 2B | 0 | 0 | 1117 | 0 | 1117 | N/A | N/A | N/A | N/A | 39100468 | 828 | 197.6605 | 0% | 0% | 100% | 0% | 100% | 70% | 8847938 | 902 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 110 | 45870650 | 4980 | 119.52 | 4.98 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39101268 | 800 | 160.6426 | 0% | 0% | 100% | 0% | 100% | 0% | 8847938 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 141 | 45876807 | 6157 | 147.768 | 6.157 | 9.1 | 9.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39102676 | 1408 | 228.6828 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 141 | 45882703 | 5896 | 141.504 | 5.896 | 8.5 | 8.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39104028 | 1352 | 229.308 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 45888712 | 6009 | 144.216 | 6.009 | 8 | 8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39105341 | 1313 | 218.5056 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 45894830 | 6118 | 146.832 | 6.118 | 7.5 | 8.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39106756 | 1415 | 231.2847 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 139 | 45900861 | 6031 | 144.744 | 6.031 | 7.1 | 8.1 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39108116 | 1360 | 225.5016 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 136 | 45906831 | 5970 | 143.28 | 5.97 | 6.8 | 6.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39109464 | 1348 | 225.7956 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 135 | 45912612 | 5781 | 138.744 | 5.781 | 6.5 | 6.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39110812 | 1348 | 233.1777 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 45918293 | 5681 | 136.344 | 5.681 | 6.1 | 6.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39112128 | 1316 | 231.6494 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 45923826 | 5533 | 132.792 | 5.533 | 5.9 | 5.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39113436 | 1308 | 236.3998 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 45929502 | 5676 | 136.224 | 5.676 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39114776 | 1340 | 236.0817 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 45935228 | 5726 | 137.424 | 5.726 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39116116 | 1340 | 234.0203 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 136 | 45940605 | 5377 | 129.048 | 5.377 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39117372 | 1256 | 233.5875 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 131 | 45946243 | 5638 | 135.312 | 5.638 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39118690 | 1318 | 233.7708 | 0% | 100% | 100% | 100% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 124 | 45951588 | 5345 | 128.28 | 5.345 | 4.1 | 4.1 | 2B+1S | 0 | 1086 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39119820 | 1130 | 211.4125 | 0% | 100% | 100% | 0% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 131 | 45956847 | 5259 | 126.216 | 5.259 | 3.3 | 3.3 | 2B+1S | 0 | 1086 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39120900 | 1080 | 205.3622 | 0% | 100% | 100% | 0% | 100% | 0% | 8847938 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 119 | 45961958 | 5111 | 122.664 | 5.111 | 2.6 | 2.6 | 2B+1S | 0 | 954 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39121964 | 1064 | 208.1784 | 0% | 100% | 100% | 0% | 100% | 0% | 8847938 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 109 | 45966510 | 4552 | 109.248 | 4.552 | 3.6 | 3.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39122884 | 920 | 202.109 | 0% | 0% | 100% | 0% | 100% | 50% | 8848867 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 99 | 45970970 | 4460 | 107.04 | 4.46 | 5.2 | 5.2 | 2B | 0 | 0 | 1108 | 0 | 1108 | N/A | N/A | N/A | N/A | 39123765 | 881 | 197.5336 | 0% | 0% | 100% | 0% | 100% | 50% | 8849970 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.375 | 126008 | 126008 | 126.008 | 126.008 | [12 empty] | 27177 | 27177 | 215.6768 | [6 empty] | 6857 | 6857 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (70%)
XCV1 CLOSED @ 5:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JULY 31, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-07-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26919 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 45970970 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39123765 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8849970 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 112 | 45975051 | 4081 | 97.944 | 4.081 | 6.5 | 6.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39124486 | 721 | 176.6724 | 0% | 0% | 100% | 0% | 100% | 60% | 8851091 | 1121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 109 | 45979127 | 4076 | 97.824 | 4.076 | 7.3 | 7.3 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39125211 | 725 | 177.8705 | 0% | 0% | 100% | 0% | 100% | 60% | 8852220 | 1129 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 105 | 45983214 | 4087 | 98.088 | 4.087 | 8.4 | 8.4 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39125927 | 716 | 175.1896 | 0% | 0% | 100% | 0% | 100% | 60% | 8853336 | 1116 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 135 | 109 | 45987294 | 4080 | 97.92 | 4.08 | 9.1 | 9.1 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39126652 | 725 | 177.6961 | 0% | 0% | 100% | 0% | 100% | 68% | 8854454 | 1118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 107 | 45991609 | 4315 | 103.56 | 4.315 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39127396 | 744 | 172.4218 | 0% | 0% | 100% | 0% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 121 | 45996456 | 4847 | 116.328 | 4.847 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39128248 | 852 | 175.7788 | 0% | 0% | 100% | 0% | 100% | 0% | 8854454 | 0 | 0.65 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 46002183 | 5727 | 137.448 | 5.727 | 9.3 | 9.3 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39129528 | 1280 | 223.5027 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 46008575 | 6392 | 153.408 | 6.392 | 8.6 | 8.6 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39130972 | 1444 | 225.9074 | 0% | 100% | 100% | 1000% | 100% | 0% | 8854454 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 46014442 | 5867 | 140.808 | 5.867 | 8 | 8 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39132257 | 1285 | 219.0216 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 46020609 | 6167 | 148.008 | 6.167 | 7.3 | 7.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39133700 | 1443 | 233.9874 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 | 0.93 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 157 | 46026650 | 6041 | 144.984 | 6.041 | 6.8 | 6.8 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39135068 | 1368 | 226.4526 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 46032579 | 5929 | 142.296 | 5.929 | 6.3 | 6.3 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39136432 | 1364 | 230.0557 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 133 | 46038447 | 5868 | 140.832 | 5.868 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39137792 | 1360 | 231.7655 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 134 | 46044309 | 5862 | 140.688 | 5.862 | 5.4 | 5.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39139144 | 1352 | 230.638 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 131 | 46050056 | 5747 | 137.928 | 5.747 | 5 | 5 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39140528 | 1384 | 240.8213 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 46055693 | 5637 | 135.288 | 5.637 | 4.6 | 4.6 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39141884 | 1356 | 240.5535 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 46061267 | 5574 | 133.776 | 5.574 | 4.2 | 4.2 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39143196 | 1312 | 235.3785 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 46066854 | 5587 | 134.088 | 5.587 | 3.7 | 3.7 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39144516 | 1320 | 236.2628 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 46072325 | 5471 | 131.304 | 5.471 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39145820 | 1304 | 238.3477 | 0% | 100% | 100% | 100% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 122 | 46077602 | 5277 | 126.648 | 5.277 | 2.8 | 2.8 | 2B+1S | 0 | 1047 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39146924 | 1104 | 209.2098 | 0% | 100% | 100% | 0% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 125 | 46082771 | 5169 | 124.056 | 5.169 | 2.2 | 2.2 | 2B+1S | 0 | 1046 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39147964 | 1040 | 201.1995 | 0% | 100% | 100% | 0% | 100% | 0% | 8854454 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 117 | 46087770 | 4999 | 119.976 | 4.999 | 1.7 | 1.7 | 2B+1S | 0 | 1046 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39149020 | 1056 | 211.2422 | 0% | 100% | 100% | 0% | 100% | 0% | 8854454 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 103 | 46092162 | 4392 | 105.408 | 4.392 | 2.7 | 2.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39149932 | 912 | 207.6503 | 0% | 0% | 100% | 0% | 100% | 50% | 8855421 | 967 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 92 | 46096168 | 4006 | 96.144 | 4.006 | 4.2 | 4.2 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39150684 | 752 | 187.7184 | 0% | 0% | 100% | 0% | 100% | 50% | 8856740 | 1319 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.625 | 125198 | 125198 | 125.198 | 125.198 | [12 empty] | 26919 | 26919 | 215.0114 | [6 empty] | 6770 | 6770 | 1.005 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:28 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 1, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
WARM-UP EXERCISE GENSET 1 & 2 w/o load for 10mins each. Fuel consumption = 13litters / Fuel stock = 10,644
GENSET 1 WARMUP EXERCISED @ 4:20PM / STOPPED @ 4:30PM
GENSET 2 WARMUP EXERCISED @ 4:10PM / STOPPED @ 4:20PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
CONDUCTED MONITORING @ MAGALLANES- ONLINE BOOSTER @ 5:35PM , NORMAL OPERATION
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)