## AUG 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27384 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46096168 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39150684 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8856740 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 106 | 46099893 | 3725 | 89.4 | 3.725 | 5.3 | 5.3 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39151400 | 716 | 192.2148 | 0% | 0% | 100% | 0% | 100% | 68% | 8857886 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 103 | 46103621 | 3728 | 89.472 | 3.728 | 6.5 | 6.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39152119 | 719 | 192.8648 | 0% | 0% | 100% | 0% | 100% | 68% | 8859038 | 1152 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 100 | 46107360 | 3739 | 89.736 | 3.739 | 7.8 | 7.8 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39152844 | 725 | 193.9021 | 0% | 0% | 100% | 0% | 100% | 68% | 8860192 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 128 | 94 | 46111108 | 3748 | 89.952 | 3.748 | 9 | 9 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39153560 | 716 | 191.0352 | 0% | 0% | 100% | 0% | 100% | 68% | 8861325 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 109 | 46115470 | 4362 | 104.688 | 4.362 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39154348 | 788 | 180.6511 | 0% | 0% | 100% | 0% | 100% | 68% | 8861856 | 531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 119 | 46119800 | 4330 | 103.92 | 4.33 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39155072 | 724 | 167.2055 | 0% | 0% | 100% | 0% | 100% | 0% | 8861856 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 141 | 46125544 | 5744 | 137.856 | 5.744 | 9.3 | 9.3 | 3B+1S | 0 | 1077 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39156404 | 1332 | 231.8942 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 148 | 46131664 | 6120 | 146.88 | 6.12 | 8.6 | 8.6 | 3B+1S | 0 | 1078 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39157816 | 1412 | 230.719 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 46137819 | 6155 | 147.72 | 6.155 | 7.9 | 7.9 | 3B+1S | 0 | 1138 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39159220 | 1404 | 228.1072 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 152 | 46144094 | 6275 | 150.6 | 6.275 | 7 | 7.3 | 3B+1S | 0 | 1137 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39160668 | 1448 | 230.757 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 | 0.87 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 46150370 | 6276 | 150.624 | 6.276 | 6.1 | 6.8 | 3B+1S | 0 | 1137 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39162104 | 1436 | 228.8082 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 46156583 | 6213 | 149.112 | 6.213 | 5.2 | 5.2 | 3B+1S | 0 | 1136 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39163528 | 1424 | 229.1968 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 144 | 46162501 | 5918 | 142.032 | 5.918 | 4.6 | 4.6 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39164908 | 1380 | 233.1869 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 140 | 46168249 | 5748 | 137.952 | 5.748 | 4 | 4 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39166236 | 1328 | 231.0369 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 46174071 | 5822 | 139.728 | 5.822 | 3.5 | 3.5 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39167612 | 1376 | 236.3449 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 46179492 | 5421 | 130.104 | 5.421 | 3.2 | 3.2 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39168908 | 1296 | 239.0703 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 148 | 46185086 | 5594 | 134.256 | 5.594 | 2.8 | 2.8 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39170220 | 1312 | 234.537 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 133 | 46190665 | 5579 | 133.896 | 5.579 | 2.6 | 2.6 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39171548 | 1328 | 238.0355 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 46196109 | 5444 | 130.656 | 5.444 | 2.4 | 2.4 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39172868 | 1320 | 242.4688 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 125 | 46201400 | 5291 | 126.984 | 5.291 | 2.2 | 2.2 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39174125 | 1257 | 237.5732 | 0% | 100% | 100% | 100% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 120 | 46206365 | 4965 | 119.16 | 4.965 | 2 | 2 | 2B+1S | 0 | 1057 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39175288 | 1163 | 234.2397 | 0% | 100% | 100% | 0% | 100% | 0% | 8861856 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 119 | 46211373 | 5008 | 120.192 | 5.008 | 1.5 | 1.5 | 2B+1S | 0 | 1055 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39176332 | 1044 | 208.4665 | 0% | 100% | 100% | 0% | 100% | 0% | 8861856 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 138 | 46215814 | 4441 | 106.584 | 4.441 | 2.6 | 2.6 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39177236 | 904 | 203.5578 | 0% | 0% | 100% | 0% | 100% | 55% | 8863138 | 1282 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 98 | 46219962 | 4148 | 99.552 | 4.148 | 4.4 | 4.4 | 2B | 0 | 0 | 1147 | 0 | 1147 | N/A | N/A | N/A | N/A | 39178068 | 832 | 200.5786 | 0% | 0% | 100% | 0% | 100% | 55% | 8864643 | 1505 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.4167 | 123794 | 123794 | 123.794 | 123.794 | [12 empty] | 27384 | 27384 | 221.2062 | [6 empty] | 7903 | 7903 | 1.01 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (68%)
XCV1 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 2, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## AUG 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26616 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46219962 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39178068 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8864643 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 90 | 46223749 | 3787 | 90.888 | 3.787 | 5.6 | 5.6 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39178792 | 724 | 191.1804 | 0% | 0% | 100% | 0% | 100% | 60% | 8865785 | 1142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 46227557 | 3808 | 91.392 | 3.808 | 6.8 | 6.8 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39179512 | 720 | 189.0756 | 0% | 0% | 100% | 0% | 100% | 60% | 8867015 | 1230 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 94 | 46231306 | 3749 | 89.976 | 3.749 | 8 | 8 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39180224 | 712 | 189.9173 | 0% | 0% | 100% | 0% | 100% | 60% | 8868246 | 1231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 138 | 96 | 46235072 | 3766 | 90.384 | 3.766 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39180940 | 716 | 190.1221 | 0% | 0% | 100% | 0% | 100% | 60% | 8869626 | 1380 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 97 | 46238866 | 3794 | 91.056 | 3.794 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 39181524 | 584 | 153.9273 | 0% | 0% | 100% | 0% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 122 | 46243417 | 4551 | 109.224 | 4.551 | 9.5 | 9.5 | 2B | 0 | 0 | 1157 | 0 | 1187 | N/A | N/A | N/A | N/A | 39182292 | 768 | 168.7541 | 0% | 0% | 100% | 0% | 100% | 0% | 8869626 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 134 | 46249034 | 5617 | 134.808 | 5.617 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1116 | 1185 | 1167 | N/A | N/A | N/A | N/A | 39183464 | 1172 | 208.6523 | 0% | 0% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 134 | 46254696 | 5662 | 135.888 | 5.662 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39184708 | 1244 | 219.7103 | 0% | 0% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 46260751 | 6055 | 145.32 | 6.055 | 9.3 | 9.3 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39186068 | 1360 | 224.6078 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 46266905 | 6154 | 147.696 | 6.154 | 8.6 | 7.3 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39187472 | 1404 | 228.1443 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 | 1.42 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 142 | 46273053 | 6148 | 147.552 | 6.148 | 7.8 | 6.8 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39188888 | 1416 | 230.3188 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 138 | 46278922 | 5869 | 140.856 | 5.869 | 7.2 | 7.2 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39190240 | 1352 | 230.3629 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 132 | 46284948 | 6026 | 144.624 | 6.026 | 6.5 | 6.5 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39191656 | 1416 | 234.9817 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 136 | 46290607 | 5659 | 135.816 | 5.659 | 6 | 6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39192980 | 1324 | 233.9636 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 147 | 46296184 | 5577 | 133.848 | 5.577 | 5.5 | 5.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39194304 | 1324 | 237.4036 | 0% | 100% | 100% | 100% | 1000% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 147 | 46301723 | 5539 | 132.936 | 5.539 | 5.2 | 5.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39195624 | 1320 | 238.3102 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 132 | 46307236 | 5513 | 132.312 | 5.513 | 4.8 | 4.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39196956 | 1332 | 241.6107 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 46312629 | 5393 | 129.432 | 5.393 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39198252 | 1296 | 240.3115 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 46318211 | 5582 | 133.968 | 5.582 | 4.4 | 4.4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39199576 | 1324 | 237.191 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 131 | 46323607 | 5396 | 129.504 | 5.396 | 4.2 | 4.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39200876 | 1300 | 240.9192 | 0% | 100% | 100% | 100% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 146 | 46328826 | 5219 | 125.256 | 5.219 | 3.6 | 3.6 | 2B+1S | 0 | 1066 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39201964 | 1088 | 208.4691 | 0% | 100% | 100% | 0% | 100% | 0% | 8869626 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 131 | 46333833 | 5007 | 120.168 | 5.007 | 3 | 3 | 2B+1S | 0 | 1034 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39203028 | 1064 | 212.5025 | 0% | 100% | 100% | 0% | 100% | 0% | 8869626 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 104 | 46338173 | 4340 | 104.16 | 4.34 | 4.1 | 4.1 | 2B | 0 | 0 | 1157 | 0 | 1156 | N/A | N/A | N/A | N/A | 39203908 | 880 | 202.765 | 0% | 0% | 100% | 0% | 100% | 50% | 8870772 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 93 | 46342184 | 4011 | 96.264 | 4.011 | 5.5 | 5.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 39204684 | 776 | 193.468 | 0% | 0% | 100% | 0% | 100% | 50% | 8872042 | 1270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.75 | 122222 | 122222 | 122.222 | 122.222 | [12 empty] | 26616 | 26616 | 217.7677 | [6 empty] | 7399 | 7399 | 1.1883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 2, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26956 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46342184 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39204684 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8872042 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 89 | 46345872 | 3688 | 88.512 | 3.688 | 6.6 | 6.6 | 2B | 0 | 0 | 1096 | 0 | 1097 | N/A | N/A | N/A | N/A | 39205376 | 692 | 187.6356 | 0% | 0% | 100% | 0% | 100% | 55% | 8873093 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 88 | 46349607 | 3735 | 89.64 | 3.735 | 7.8 | 7.8 | 2B | 0 | 0 | 1096 | 0 | 1096 | N/A | N/A | N/A | N/A | 39206100 | 724 | 193.842 | 0% | 0% | 100% | 0% | 100% | 55% | 8874297 | 1204 | 1.38 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 84 | 46352964 | 3357 | 80.568 | 3.357 | 9.2 | 9.2 | 2B | 0 | 0 | 1027 | 0 | 1027 | N/A | N/A | N/A | N/A | 39206688 | 588 | 175.1564 | 0% | 0% | 100% | 0% | 100% | 55% | 8875618 | 1321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 111 | 46356332 | 3368 | 80.832 | 3.368 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 39207230 | 542 | 160.9264 | 0% | 0% | 100% | 0% | 100% | 55% | 8875978 | 360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 108 | 46360526 | 4194 | 100.656 | 4.194 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39207908 | 678 | 161.6595 | 0% | 0% | 100% | 0% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 121 | 46365364 | 4838 | 116.112 | 4.838 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39208820 | 912 | 188.5076 | 0% | 0% | 100% | 0% | 100% | 0% | 8875978 | 0 | 0.99 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 138 | 46371465 | 6101 | 146.424 | 6.101 | 8.9 | 8.9 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39210220 | 1400 | 229.4706 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 46377596 | 6131 | 147.144 | 6.131 | 8.3 | 8.3 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39211604 | 1384 | 225.7381 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 137 | 46383777 | 6181 | 148.344 | 6.181 | 7.5 | 7.5 | 3B+1S | 0 | 1097 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39213030 | 1426 | 230.707 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 46390053 | 6276 | 150.624 | 6.276 | 6.7 | 7.3 | 3B+1S | 0 | 1096 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39214436 | 1406 | 224.028 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 | 0.35 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 46396129 | 6076 | 145.824 | 6.076 | 5.89 | 6.8 | 3B+1S | 0 | 1096 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39215828 | 1392 | 229.0981 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 135 | 46402127 | 5998 | 143.952 | 5.998 | 5.6 | 5.6 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39217196 | 1368 | 228.076 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 46407900 | 5773 | 138.552 | 5.773 | 5.2 | 5.2 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39218536 | 1340 | 232.115 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 147 | 46413506 | 5606 | 134.544 | 5.606 | 5.1 | 5.1 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39219828 | 1292 | 230.4674 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 133 | 46419226 | 5720 | 137.28 | 5.72 | 4.4 | 4.4 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39221180 | 1352 | 236.3636 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 130 | 46424713 | 5487 | 131.688 | 5.487 | 3.9 | 3.9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39222464 | 1284 | 234.0077 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 46430396 | 5683 | 136.392 | 5.683 | 3.5 | 3.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39223808 | 1344 | 236.4948 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 133 | 46436031 | 5635 | 135.24 | 5.635 | 3.2 | 3.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39225140 | 1332 | 236.3798 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 46441611 | 5580 | 133.92 | 5.58 | 2.9 | 2.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39226460 | 1320 | 236.5591 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 129 | 46447430 | 5819 | 139.656 | 5.819 | 2.8 | 2.8 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39227860 | 1400 | 240.5912 | 0% | 100% | 100% | 100% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 46452576 | 5146 | 123.504 | 5.146 | 2.1 | 2.1 | 2B+1S | 0 | 1046 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39228932 | 1072 | 208.3171 | 0% | 100% | 100% | 0% | 100% | 0% | 8875978 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 120 | 46457666 | 5090 | 122.16 | 5.09 | 1.5 | 1.5 | 2B+1S | 0 | 1045 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39229992 | 1060 | 208.2515 | 0% | 100% | 100% | 0% | 100% | 0% | 8875978 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 104 | 46461951 | 4285 | 102.84 | 4.285 | 2.7 | 2.7 | 2B | 0 | 0 | 1136 | 0 | 1137 | N/A | N/A | N/A | N/A | 39230824 | 832 | 194.1657 | 0% | 0% | 100% | 0% | 100% | 50% | 8877267 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 141 | 104 | 46466260 | 4309 | 103.416 | 4.309 | 4.2 | 4.2 | 2B | 0 | 0 | 1136 | 0 | 1137 | N/A | N/A | N/A | N/A | 39231640 | 816 | 189.3711 | 0% | 0% | 100% | 0% | 100% | 50% | 8878795 | 1528 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.5417 | 124076 | 124076 | 124.076 | 124.076 | [12 empty] | 26956 | 26956 | 217.2539 | [6 empty] | 6753 | 6753 | 0.98333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 3:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 4, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27772 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46466260 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39231640 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8878795 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 110 | 46470360 | 4100 | 98.4 | 4.1 | 6.3 | 6.3 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39232393 | 753 | 183.6585 | 0% | 0% | 100% | 0% | 100% | 55% | 8880084 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 102 | 46474450 | 4090 | 98.16 | 4.09 | 7.8 | 7.8 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39233140 | 747 | 182.6406 | 0% | 0% | 100% | 0% | 100% | 55% | 8881370 | 1286 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 99 | 46478562 | 4112 | 98.688 | 4.112 | 8.5 | 8.5 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 39233892 | 752 | 182.8794 | 0% | 0% | 100% | 0% | 100% | 55% | 8882670 | 1300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 97 | 46482536 | 3974 | 95.376 | 3.974 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 0 | 1067 | N/A | N/A | N/A | N/A | 39234576 | 684 | 172.1188 | 0% | 0% | 100% | 0% | 100% | 55% | 8883537 | 867 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 109 | 46486847 | 4311 | 103.464 | 4.311 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 0 | 1067 | N/A | N/A | N/A | N/A | 39235268 | 692 | 160.5196 | 0% | 0% | 100% | 0% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 125 | 46491954 | 5107 | 122.568 | 5.107 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39236236 | 968 | 189.5438 | 0% | 0% | 100% | 0% | 100% | 0% | 8883537 | 0 | 0.86 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 46498087 | 6133 | 147.192 | 6.133 | 8.8 | 8.8 | 3B+1S | 0 | 1107 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39237648 | 1412 | 230.2299 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 152 | 46504220 | 6133 | 147.192 | 6.133 | 7.9 | 7.9 | 3B+1S | 0 | 1107 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39239060 | 1412 | 230.2299 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 46510346 | 6126 | 147.024 | 6.126 | 7.1 | 7.1 | 3B+1S | 0 | 1106 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39240452 | 1392 | 227.2282 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 145 | 46516541 | 6195 | 148.68 | 6.195 | 6.3 | 7.3 | 3B+1S | 0 | 1106 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39241868 | 1416 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 | 0.93 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 141 | 46522590 | 6049 | 145.176 | 6.049 | 5.3 | 6.8 | 3B+1S | 0 | 1166 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39243296 | 1428 | 236.0721 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 145 | 46528648 | 6058 | 145.392 | 6.058 | 4.3 | 4.3 | 3B+1S | 0 | 1167 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39244732 | 1436 | 237.0419 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 137 | 46534355 | 5707 | 136.968 | 5.707 | 3.7 | 3.7 | 3B+1S | 0 | 1064 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39246076 | 1344 | 235.5003 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 46540095 | 5740 | 137.76 | 5.74 | 3.2 | 3.2 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39247396 | 1320 | 229.9652 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 131 | 46545712 | 5617 | 134.808 | 5.617 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39248728 | 1332 | 237.1373 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 134 | 46551125 | 5413 | 129.912 | 5.413 | 2.8 | 2.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39250028 | 1300 | 240.1626 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 131 | 46556581 | 5456 | 130.944 | 5.456 | 2.7 | 2.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39251328 | 1300 | 238.2698 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 130 | 46562268 | 5687 | 136.488 | 5.687 | 2.5 | 2.5 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39252676 | 1348 | 237.0318 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 129 | 46567978 | 5710 | 137.04 | 5.71 | 2.4 | 2.4 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39254028 | 1352 | 236.7776 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 134 | 46573461 | 5483 | 131.592 | 5.483 | 2.3 | 2.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39255340 | 1312 | 239.2851 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 136 | 133 | 46578740 | 5279 | 126.696 | 5.279 | 2.2 | 2.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39256612 | 1272 | 240.9547 | 0% | 100% | 100% | 100% | 100% | 0% | 8883537 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 119 | 46583834 | 5094 | 122.256 | 5.094 | 1.9 | 1.9 | 2B+1S | 0 | 1005 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39257676 | 1064 | 208.8732 | 0% | 100% | 100% | 0% | 100% | 0% | 8883537 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 131 | 46588259 | 4425 | 106.2 | 4.425 | 2.9 | 2.9 | 2B | 0 | 0 | 1158 | 0 | 1157 | N/A | N/A | N/A | N/A | 39258552 | 876 | 197.9661 | 0% | 0% | 100% | 0% | 100% | 50% | 8884756 | 1219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 107 | 46592796 | 4537 | 108.888 | 4.537 | 4.4 | 4.4 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 39259412 | 860 | 189.5526 | 0% | 0% | 100% | 0% | 100% | 50% | 8886085 | 1329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.0417 | 126536 | 126536 | 126.536 | 126.536 | [13 empty] | 27772 | 219.479 | [6 empty] | 7290 | 7290 | 0.975 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 3:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 5, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27416 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46592796 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39259412 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8886085 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 102 | 46597108 | 4312 | 103.488 | 4.312 | 5.7 | 5.7 | 2B | 0 | 0 | 1127 | 0 | 1128 | N/A | N/A | N/A | N/A | 39260228 | 816 | 189.2393 | 0% | 0% | 100% | 0% | 100% | 55% | 8887215 | 1130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 130 | 46601033 | 3925 | 94.2 | 3.925 | 6.7 | 6.7 | 2B | 0 | 0 | 1128 | 0 | 1128 | N/A | N/A | N/A | N/A | 39260964 | 736 | 187.5159 | 0% | 0% | 100% | 0% | 100% | 55% | 8888231 | 1016 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 99 | 46605145 | 4112 | 98.688 | 4.112 | 7.9 | 7.9 | 2B | 0 | 0 | 1097 | 0 | 1096 | N/A | N/A | N/A | N/A | 39261692 | 728 | 177.0428 | 0% | 0% | 100% | 0% | 100% | 55% | 8889369 | 1138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 131 | 97 | 46609065 | 3920 | 94.08 | 3.92 | 9.3 | 9.3 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 39262356 | 664 | 169.3878 | 0% | 0% | 100% | 0% | 100% | 55% | 8890714 | 1345 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 101 | 46613224 | 4159 | 99.816 | 4.159 | 9.5 | 9.5 | 2B | 0 | 0 | 1016 | 0 | 1017 | N/A | N/A | N/A | N/A | 39262980 | 624 | 150.0361 | 0% | 0% | 100% | 0% | 100% | 55% | 8890943 | 229 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 123 | 46618056 | 4832 | 115.968 | 4.832 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39263832 | 852 | 176.3245 | 0% | 0% | 100% | 0% | 100% | 0% | 8890943 | 0 | 1.42 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 122 | 46623887 | 5831 | 139.944 | 5.831 | 9.3 | 9.3 | 3B+1S | 0 | 1117 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39265172 | 1340 | 229.8062 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 46630038 | 6151 | 147.624 | 6.151 | 8.4 | 8.4 | 3B+1S | 0 | 1117 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39266588 | 1416 | 230.2065 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 143 | 46636181 | 6143 | 147.432 | 6.143 | 7.4 | 7.4 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39268016 | 1428 | 232.4597 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 46642387 | 6206 | 148.944 | 6.206 | 6.7 | 7.3 | 3B+1S | 0 | 1137 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39269444 | 1428 | 230.0999 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 125 | 140 | 46648536 | 6149 | 147.576 | 6.149 | 5.8 | 6.8 | 3B+1S | 0 | 1186 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39270876 | 1432 | 232.8834 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 139 | 46654630 | 6094 | 146.256 | 6.094 | 4.7 | 4.7 | 3B+1S | 0 | 1137 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39272316 | 1440 | 236.298 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 153 | 46660241 | 5611 | 134.664 | 5.611 | 4.2 | 4.2 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39273652 | 1336 | 238.1037 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 134 | 46665747 | 5506 | 132.144 | 5.506 | 3.7 | 3.7 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39274924 | 1272 | 231.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 130 | 46671282 | 5535 | 132.84 | 5.535 | 3.4 | 3.4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39276252 | 1328 | 239.9277 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 46676700 | 5418 | 130.032 | 5.418 | 3.3 | 3.3 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39277564 | 1312 | 242.1558 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 132 | 46682289 | 5589 | 134.136 | 5.589 | 3.2 | 3.2 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39278892 | 1328 | 237.6096 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 131 | 46687695 | 5406 | 129.744 | 5.406 | 3 | 3 | 3B+1S | 0 | 103 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39280188 | 1296 | 239.7336 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 132 | 46693129 | 5434 | 130.416 | 5.434 | 2.8 | 2.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39281476 | 1288 | 237.0261 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 129 | 46698703 | 5574 | 133.776 | 5.574 | 2.6 | 2.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39282808 | 1332 | 238.9666 | 0% | 100% | 100% | 100% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 126 | 46704188 | 5485 | 131.64 | 5.485 | 1.9 | 1.9 | 2B+1S | 0 | 1086 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39283900 | 1092 | 199.0884 | 0% | 100% | 100% | 0% | 100% | 0% | 8890943 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 119 | 46709258 | 5070 | 121.68 | 5.07 | 1.3 | 1.3 | 2B+1S | 0 | 1086 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39285036 | 1136 | 224.0631 | 0% | 100% | 100% | 0% | 100% | 0% | 8890943 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 109 | 46713527 | 4269 | 102.456 | 4.269 | 1.8 | 1.8 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39285916 | 880 | 206.1373 | 0% | 0% | 100% | 0% | 100% | 55% | 8891722 | 779 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 156 | 110 | 46718095 | 4568 | 109.632 | 4.568 | 3.4 | 3.4 | 2B | 0 | 0 | 1148 | 0 | 1157 | N/A | N/A | N/A | N/A | 39286828 | 912 | 199.6497 | 0% | 0% | 100% | 0% | 100% | 55% | 8893481 | 1759 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126 | 125299 | 125299 | 125.299 | 125.299 | [13 empty] | 27416 | 218.8046 | [6 empty] | 7396 | 7396 | 1.1467 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (55%)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 6, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## AUG 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27480 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46718095 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39286828 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8893481 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 160 | 100 | 46722649 | 4554 | 109.296 | 4.554 | 5.8 | 5.8 | 2B | 0 | 0 | 1117 | 0 | 1127 | N/A | N/A | N/A | N/A | 39287696 | 868 | 190.6017 | 0% | 0% | 100% | 0% | 100% | 60% | 8895603 | 2122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 103 | 46726907 | 4258 | 102.192 | 4.258 | 7.9 | 7.9 | 2B | 0 | 0 | 1117 | 0 | 1128 | N/A | N/A | N/A | N/A | 39288468 | 772 | 181.3058 | 0% | 0% | 100% | 0% | 100% | 60% | 8897677 | 2074 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 98 | 46730836 | 3929 | 94.296 | 3.929 | 9.1 | 9.1 | 2B | 0 | 0 | 1087 | 0 | 1086 | N/A | N/A | N/A | N/A | 39289180 | 712 | 181.2166 | 0% | 0% | 100% | 0% | 100% | 60% | 8898713 | 1036 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 98 | 46734813 | 3977 | 95.448 | 3.977 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1087 | N/A | N/A | N/A | N/A | 39289856 | 676 | 169.9774 | 0% | 0% | 100% | 0% | 100% | 60% | 8899069 | 356 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 109 | 46739132 | 4319 | 103.656 | 4.319 | 9.5 | 9.5 | 2B | 0 | 0 | 1046 | 0 | 1058 | N/A | N/A | N/A | N/A | 39290548 | 692 | 160.2223 | 0% | 0% | 100% | 0% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 124 | 46744084 | 4952 | 118.848 | 4.952 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39291444 | 896 | 180.937 | 0% | 0% | 100% | 0% | 100% | 0% | 8899069 | 0 | 0.75 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 147 | 46749986 | 5902 | 141.648 | 5.902 | 9.3 | 9.3 | 2B | 0 | 1014 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39292788 | 1344 | 227.7194 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 46755982 | 5996 | 143.904 | 5.996 | 8.8 | 8.8 | 2B | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39294148 | 1360 | 226.8179 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 46762028 | 6046 | 145.104 | 6.046 | 8.2 | 8.2 | 2B | 0 | 1034 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39295524 | 1376 | 227.5885 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 46768176 | 6148 | 147.552 | 6.148 | 7.6 | 7.6 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39296914 | 1390 | 226.0898 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 142 | 46774059 | 5883 | 141.192 | 5.883 | 6.9 | 6.9 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39298254 | 1340 | 227.7749 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 46779905 | 5846 | 140.304 | 5.846 | 6.3 | 6.3 | 3B+1S | 0 | 1045 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39299636 | 1382 | 236.401 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 151 | 46785725 | 5820 | 139.68 | 5.82 | 5.8 | 5.8 | 3B+1S | 0 | 1034 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39300996 | 1360 | 233.677 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 130 | 46791253 | 5528 | 132.672 | 5.528 | 5.3 | 5.3 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39302300 | 1304 | 235.89 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 46796804 | 5551 | 133.224 | 5.551 | 5 | 5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39303612 | 1312 | 236.3538 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 46802439 | 5635 | 135.24 | 5.635 | 4.7 | 4.7 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39304948 | 1336 | 237.0896 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 46807913 | 5474 | 131.376 | 5.474 | 4.4 | 4.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39306284 | 1336 | 244.0628 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 122 | 46813605 | 5692 | 136.608 | 5.692 | 4.1 | 4.1 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39307648 | 1364 | 239.6346 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 134 | 46818945 | 5340 | 128.16 | 5.34 | 3.8 | 3.8 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39308924 | 1276 | 238.9513 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 133 | 46824473 | 5528 | 132.672 | 5.528 | 3.6 | 3.6 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39310252 | 1328 | 240.2315 | 0% | 100% | 100% | 100% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 143 | 46829663 | 5190 | 124.56 | 5.19 | 2.9 | 2.9 | 2B+1S | 0 | 1075 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39311340 | 1088 | 209.6339 | 0% | 100% | 100% | 0% | 100% | 0% | 8899069 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 111 | 46834591 | 4928 | 118.272 | 4.928 | 3.1 | 3.1 | 2B+1S | 0 | 1076 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 39312380 | 1040 | 211.039 | 0% | 100% | 100% | 0% | 100% | 0% | 8899069 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 143 | 110 | 46839832 | 5241 | 125.784 | 5.241 | 3.4 | 3.4 | 2B | 0 | 0 | 1157 | 0 | 1156 | N/A | N/A | N/A | N/A | 39313374 | 994 | 189.6585 | 0% | 0% | 100% | 0% | 100% | 50% | 8900059 | 990 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 142 | 108 | 46844023 | 4191 | 100.584 | 4.191 | 4.5 | 4.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39314308 | 934 | 222.8585 | 0% | 0% | 100% | 0% | 100% | 50% | 8901355 | 1296 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.625 | 125928 | 125928 | 125.928 | 125.928 | [13 empty] | 27480 | 218.2199 | [6 empty] | 7874 | 7874 | 0.95167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 3:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 7, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28896 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46844023 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39314308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8901355 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 105 | 98 | 46848126 | 4103 | 98.472 | 4.103 | 5 | 5 | 2B | 0 | 0 | 1107 | 0 | 1106 | N/A | N/A | N/A | N/A | 39314998 | 690 | 168.1696 | 0% | 0% | 100% | 0% | 100% | 60% | 8902555 | 1200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 100 | 46852189 | 4063 | 97.512 | 4.063 | 6.1 | 6.1 | 2B | 0 | 0 | 1106 | 0 | 1108 | N/A | N/A | N/A | N/A | 39315789 | 791 | 194.6837 | 0% | 0% | 100% | 0% | 100% | 60% | 8903801 | 1246 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 109 | 98 | 46856234 | 4045 | 97.08 | 4.045 | 7.6 | 7.6 | 2B | 0 | 0 | 1105 | 0 | 1107 | N/A | N/A | N/A | N/A | 39316609 | 820 | 202.7194 | 0% | 0% | 100% | 0% | 100% | 60% | 8904997 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 101 | 46860292 | 4058 | 97.392 | 4.058 | 8.7 | 8.7 | 2B | 0 | 0 | 1107 | 0 | 1106 | N/A | N/A | N/A | N/A | 39317602 | 993 | 244.7018 | 0% | 0% | 100% | 0% | 100% | 60% | 8906198 | 1201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 122 | 114 | 46866468 | 6176 | 148.224 | 6.176 | 9.5 | 9.5 | 2B | 0 | 0 | 1108 | 0 | 1107 | N/A | N/A | N/A | N/A | 39318432 | 830 | 134.3912 | 0% | 0% | 100% | 0% | 100% | 60% | 8906859 | 661 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 126 | 46871194 | 4726 | 113.424 | 4.726 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39319828 | 1396 | 295.3872 | 0% | 0% | 100% | 0% | 100% | 0% | 8906859 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 46877430 | 6236 | 149.664 | 6.236 | 9.3 | 9.3 | 3B+1S | 0 | 1096 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39321260 | 1432 | 229.6344 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 46883493 | 6063 | 145.512 | 6.063 | 8.8 | 8.8 | 3B+1S | 0 | 1157 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39322656 | 1396 | 230.2491 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 129 | 148 | 46889814 | 6321 | 151.704 | 6.321 | 7.8 | 7.8 | 3B+1S | 0 | 1157 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39324124 | 1468 | 232.2417 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 169 | 46895931 | 6117 | 146.808 | 6.117 | 6.7 | 7.6 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39325560 | 1436 | 234.7556 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 | 0.92 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 160 | 46902193 | 6262 | 150.288 | 6.262 | 5.7 | 6.9 | 3B+1S | 0 | 1183 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39327036 | 1476 | 235.7074 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 140 | 46908126 | 5933 | 142.392 | 5.933 | 4.7 | 4.7 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39328442 | 1406 | 236.9796 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 130 | 46914113 | 5987 | 143.688 | 5.987 | 3.7 | 3.7 | 3B+1S | 0 | 1095 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39329848 | 1406 | 234.8422 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 130 | 46919485 | 5372 | 128.928 | 5.372 | 3.3 | 3.3 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39331116 | 1268 | 236.0387 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 131 | 46924929 | 5444 | 130.656 | 5.444 | 3 | 3 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39332428 | 1312 | 240.9993 | 0% | 100% | 100% | 100% | 1000% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 46930460 | 5531 | 132.744 | 5.531 | 2.7 | 2.7 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39333764 | 1336 | 241.5476 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 46935948 | 5488 | 131.712 | 5.488 | 2.4 | 2.4 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39335084 | 1320 | 240.5248 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 127 | 46941475 | 5527 | 132.648 | 5.527 | 2.2 | 2.2 | 3B+1S | 0 | 1002 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39336412 | 1328 | 240.275 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 133 | 46947014 | 5539 | 132.936 | 5.539 | 2 | 2 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39337748 | 1336 | 241.1988 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 129 | 46952349 | 5335 | 128.04 | 5.335 | 2 | 2 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39339060 | 1312 | 245.9231 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 135 | 128 | 46957677 | 5328 | 127.872 | 5.328 | 1.9 | 1.9 | 3B+1S | 0 | 1002 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39340372 | 1312 | 246.2462 | 0% | 100% | 100% | 100% | 100% | 0% | 8906859 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 104 | 46962453 | 4776 | 114.624 | 4.776 | 1.7 | 1.7 | 2B+1S | 0 | 992 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39341428 | 1056 | 221.1055 | 0% | 100% | 100% | 0% | 100% | 0% | 8906859 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 105 | 46966835 | 4382 | 105.168 | 4.382 | 2.6 | 2.6 | 2B | 0 | 0 | 1167 | 0 | 1166 | N/A | N/A | N/A | N/A | 39342356 | 928 | 211.7754 | 0% | 0% | 100% | 0% | 100% | 50% | 8907905 | 1046 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 106 | 46970984 | 4149 | 99.576 | 4.149 | 3.9 | 3.9 | 2B | 0 | 0 | 1167 | 0 | 1167 | N/A | N/A | N/A | N/A | 39343204 | 848 | 204.3866 | 0% | 0% | 100% | 0% | 100% | 50% | 8909109 | 1204 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.7917 | 126961 | 126961 | 126.961 | 126.961 | [13 empty] | 28896 | 227.5975 | [6 empty] | 7754 | 7754 | 1.0133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 8, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ALEXANDER CABREROS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 46970984 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39343204 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8909109 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 99 | 46974996 | 4012 | 96.288 | 4.012 | 5.4 | 5.4 | 2B | 0 | 0 | 1117 | 0 | 1127 | N/A | N/A | N/A | N/A | 39344008 | 804 | 200.3988 | 0% | 0% | 100% | 0% | 100% | 60% | 8910457 | 1348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 46979808 | 4812 | 115.488 | 4.812 | 6.9 | 6.9 | 2B | 0 | 0 | 1117 | 0 | 1127 | N/A | N/A | N/A | N/A | 39344938 | 930 | 193.2668 | 0% | 0% | 100% | 0% | 100% | 60% | 8911838 | 1381 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 92 | 46982864 | 3056 | 73.344 | 3.056 | 7.8 | 7.8 | 2B | 0 | 0 | 1086 | 0 | 1086 | N/A | N/A | N/A | N/A | 39345616 | 678 | 221.8586 | 0% | 0% | 100% | 0% | 100% | 60% | 8912948 | 1110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 122 | 46986367 | 3503 | 84.072 | 3.503 | 9 | 9 | 2B | 0 | 0 | 1087 | 0 | 1087 | N/A | N/A | N/A | N/A | 39346196 | 580 | 165.5724 | 0% | 0% | 100% | 0% | 100% | 60% | 8913959 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 105 | 46990300 | 3933 | 94.392 | 3.933 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1087 | N/A | N/A | N/A | N/A | 39346892 | 696 | 176.9641 | 0% | 0% | 100% | 0% | 100% | 60% | 8914928 | 969 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 114 | 46995262 | 4962 | 119.088 | 4.962 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39347816 | 924 | 186.2152 | 0% | 0% | 100% | 0% | 100% | 0% | 8914928 | 0 | 0.87 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 47001095 | 5833 | 139.992 | 5.833 | 9.5 | 9.5 | 3B+1S | 0 | 1000 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39349176 | 1360 | 233.1562 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 148 | 47007121 | 6026 | 144.624 | 6.026 | 8.9 | 8.9 | 3B+1S | 0 | 1126 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39350548 | 1372 | 227.6801 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 129 | 149 | 47013286 | 6165 | 147.96 | 6.165 | 7.7 | 7.7 | 3B+1S | 0 | 1185 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39351996 | 1448 | 234.8743 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 | 144 | 47019503 | 6217 | 149.208 | 6.217 | 6.8 | 7.6 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39353444 | 1448 | 232.9098 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 | 148 | 47025657 | 6154 | 147.696 | 6.154 | 5.7 | 6.9 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39354900 | 1456 | 236.5941 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 128 | 135 | 47031834 | 6177 | 148.248 | 6.177 | 4.6 | 4.6 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39356364 | 1464 | 237.0083 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 2 | 8 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 132 | 135 | 47037721 | 5887 | 141.288 | 5.887 | 3.7 | 3.7 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39357756 | 1392 | 236.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 133 | 137 | 47043466 | 5745 | 137.88 | 5.745 | 3.1 | 3.1 | 3B+1S | 0 | 1180 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39359108 | 1352 | 235.3351 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 132 | 134 | 47049222 | 5756 | 138.144 | 5.756 | 2.6 | 2.6 | 3B+1S | 0 | 1180 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39360460 | 1352 | 234.8853 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 2 | 1.4085 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 47054882 | 5660 | 135.84 | 5.66 | 2.2 | 2.2 | 3B+1S | 0 | 1130 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39361780 | 1320 | 233.2155 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 2 | 1.4085 | 79 | 55.6338 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 135 | 148 | 47060447 | 5565 | 133.56 | 5.565 | 1.5 | 1.5 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39363130 | 1350 | 242.5876 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 1 | 0.70423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 145 | 47066012 | 5565 | 133.56 | 5.565 | 1.3 | 1.3 | 3B+1S | 0 | 1135 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39364460 | 1330 | 238.9937 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 1 | 0.70423 | 71 | 50 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.6 | 137 | 121 | 47071357 | 5345 | 128.28 | 5.345 | 1.3 | 1.3 | 3B+1S | 0 | 971 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39365764 | 1304 | 243.9663 | 0% | 100% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 1 | 0.70423 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 136 | 129 | 47076943 | 5586 | 134.064 | 5.586 | 1.3 | 1.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39367064 | 1300 | 232.7247 | 0% | 0% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 2 | 1.4085 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 136 | 129 | 47082015 | 5072 | 121.728 | 5.072 | 1.3 | 1.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39368260 | 1196 | 235.8044 | 0% | 0% | 100% | 100% | 100% | 0% | 8914928 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 130 | 120 | 47087322 | 5307 | 127.368 | 5.307 | 1.3 | 1.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39369504 | 1244 | 234.4074 | 0% | 0% | 100% | 0% | 100% | 0% | 8914928 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 103 | 47091759 | 4437 | 106.488 | 4.437 | 2.1 | 2.1 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39370422 | 918 | 206.8966 | 0% | 0% | 100% | 0% | 100% | 58% | 8915931 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 106 | 47096196 | 4437 | 106.488 | 4.437 | 3.2 | 3.2 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39371340 | 918 | 206.8966 | 0% | 0% | 100% | 0% | 100% | 58% | 8916935 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.2917 | 125212 | 125212 | 125.212 | 125.212 | [13 empty] | 28136 | 224.7069 | [6 empty] | 7826 | 7826 | 1.1067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 4:52 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
NOTE: UNREACH THE 83psi DISC.PRESS. @ 8:30AM DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 9, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
NOTE: UNREACH THE 81psi DISC.PRESS. @ 8:30AM DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
DECREASE DISCHARGE PRESSURE 78psi DOWN TO 71psi DUE TO WATER LEVEL EXCESS CAPACITY TO THE MINIMUM WATER LEVEL 1.2M
SP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (58%)

## AUG 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27840 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47096196 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39371340 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8916935 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 106 | 47100097 | 3901 | 93.624 | 3.901 | 5.6 | 5.6 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39372080 | 740 | 189.695 | 0% | 0% | 100% | 0% | 100% | 70% | 8918098 | 1163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 103 | 47103994 | 3897 | 93.528 | 3.897 | 6.8 | 6.8 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39372823 | 743 | 190.6595 | 0% | 0% | 100% | 0% | 100% | 70% | 8919258 | 1160 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 101 | 47107893 | 3899 | 93.576 | 3.899 | 7.6 | 7.6 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39373562 | 739 | 189.5358 | 0% | 0% | 100% | 0% | 100% | 70% | 8920416 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 99 | 47111807 | 3914 | 93.936 | 3.914 | 8.8 | 8.8 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39374303 | 741 | 189.3204 | 0% | 0% | 100% | 0% | 100% | 70% | 8921577 | 1161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 100 | 47115712 | 3905 | 93.72 | 3.905 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39375040 | 737 | 188.7324 | 0% | 0% | 100% | 0% | 100% | 70% | 8922751 | 1174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 133 | 47120139 | 4427 | 106.248 | 4.427 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39375796 | 756 | 170.7703 | 0% | 0% | 100% | 0% | 100% | 0% | 8922751 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 140 | 47125823 | 5684 | 136.416 | 5.684 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39377052 | 1256 | 220.9711 | 0% | 0% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 47131956 | 6133 | 147.192 | 6.133 | 9 | 9 | 3B+1S | 0 | 1085 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39378440 | 1388 | 226.3166 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 139 | 47138195 | 6239 | 149.736 | 6.239 | 8.1 | 8.1 | 3B+1S | 0 | 1186 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39379872 | 1432 | 229.524 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 | 145 | 47144425 | 6230 | 149.52 | 6.23 | 7 | 7.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39381332 | 1460 | 234.3499 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 | 157 | 47150575 | 6150 | 147.6 | 6.15 | 6.4 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39382752 | 1420 | 230.8943 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 | 141 | 47156688 | 6113 | 146.712 | 6.113 | 5 | 5 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39384192 | 1440 | 235.5636 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 8 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 131 | 148 | 47162620 | 5932 | 142.368 | 5.932 | 4.2 | 4.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39385552 | 1360 | 229.265 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 129 | 149 | 47168503 | 5883 | 141.192 | 5.883 | 3.2 | 3.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39386932 | 1380 | 234.5742 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 133 | 138 | 47174450 | 5947 | 142.728 | 5.947 | 2.6 | 2.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39388324 | 1392 | 234.0676 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 2 | 1.4085 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 136 | 47180105 | 5655 | 135.72 | 5.655 | 2.2 | 2.2 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39389648 | 1324 | 234.1291 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 1 | 0.70423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 47185688 | 5583 | 133.992 | 5.583 | 1.8 | 1.8 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39390968 | 1320 | 236.432 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 1 | 0.70423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 133 | 47191295 | 5607 | 134.568 | 5.607 | 1.6 | 1.6 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39392292 | 1324 | 236.1334 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 1 | 0.70423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 132 | 47196730 | 5435 | 130.44 | 5.435 | 1.5 | 1.5 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39393588 | 1296 | 238.4545 | 0% | 100% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 1 | 0.70423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 131 | 47202341 | 5611 | 134.664 | 5.611 | 1.5 | 1.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39394880 | 1292 | 230.262 | 0% | 0% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 1 | 0.70423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 137 | 128 | 47207545 | 5204 | 124.896 | 5.204 | 1.5 | 1.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39396076 | 1196 | 229.8232 | 0% | 0% | 100% | 100% | 100% | 0% | 8922751 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 1 | 0.70423 | 66 | 46.4789 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 12.6 | 133 | 126 | 47213114 | 5569 | 133.656 | 5.569 | 1.5 | 1.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39397372 | 1296 | 232.7168 | 0% | 0% | 100% | 100% | 100% | 0% | 8922751 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 107 | 47217684 | 4570 | 109.68 | 4.57 | 2.1 | 2.1 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39398312 | 940 | 205.6893 | 0% | 0% | 100% | 0% | 100% | 55% | 8923461 | 710 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 144 | 129 | 47221956 | 4272 | 102.528 | 4.272 | 3.2 | 3.2 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39399180 | 868 | 203.1835 | 0% | 0% | 100% | 0% | 100% | 55% | 8924526 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 129.5833 | 125760 | 125760 | 125.76 | 125.76 | [13 empty] | 27840 | 221.374 | [6 empty] | 7591 | 7591 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (70%)
XCV1 CLOSED @ 4:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
NOTE: UNREACH THE 83psi DISC.PRESS. @ 9:00AM DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 9, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
NOTE: UNREACH THE 81psi DISC.PRESS. DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
DECREASE DISCHARGE PRESSURE 78psi DOWN TO 71psi DUE TO WATER LEVEL EXCESS CAPACITY TO THE MINIMUM WATER LEVEL 1.2M
SP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (55%)

## AUG 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24704 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47221956 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39399180 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8924526 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 138 | 99 | 47226413 | 4457 | 106.968 | 4.457 | 4.7 | 4.7 | 2B | 0 | 0 | 1147 | 0 | 1147 | N/A | N/A | N/A | N/A | 39400108 | 928 | 208.2118 | 0% | 0% | 100% | 0% | 100% | 65% | 8925815 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 137 | 100 | 47230444 | 4031 | 96.744 | 4.031 | 6.2 | 6.2 | 2B | 0 | 0 | 1147 | 0 | 1147 | N/A | N/A | N/A | N/A | 39400916 | 808 | 200.4465 | 0% | 0% | 100% | 0% | 100% | 65% | 8927247 | 1432 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 101 | 47234357 | 3913 | 93.912 | 3.913 | 7.5 | 7.5 | 2B | 0 | 0 | 1147 | 0 | 1147 | N/A | N/A | N/A | N/A | 39401684 | 768 | 196.2688 | 0% | 0% | 100% | 0% | 100% | 65% | 8928572 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 129 | 47238089 | 3732 | 89.568 | 3.732 | 9 | 9 | 2B | 0 | 0 | 1046 | 0 | 1047 | N/A | N/A | N/A | N/A | 39402316 | 632 | 169.3462 | 0% | 0% | 100% | 0% | 100% | 65% | 8930039 | 1467 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 111 | 47242372 | 4283 | 102.792 | 4.283 | 9.5 | 9.5 | 2B | 0 | 0 | 1107 | 0 | 1108 | N/A | N/A | N/A | N/A | 39403012 | 696 | 162.5029 | 0% | 0% | 100% | 0% | 100% | 65% | 8930489 | 450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 123 | 47247691 | 5319 | 127.656 | 5.319 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39403956 | 944 | 177.477 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 143 | 47253448 | 5757 | 138.168 | 5.757 | 9.5 | 9.5 | 3B | 0 | 1100 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39405228 | 1272 | 220.9484 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 47259706 | 6258 | 150.192 | 6.258 | 8.7 | 8.7 | 3B+1S | 0 | 1101 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39406648 | 1420 | 226.9096 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 3 | 2.1127 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 130 | 150 | 47265811 | 6105 | 146.52 | 6.105 | 7.8 | 7.8 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39408036 | 1388 | 227.3546 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 2 | 1.4085 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 | 146 | 47271918 | 6107 | 146.568 | 6.107 | 6.7 | 7.6 | 3B+1S | 0 | 1180 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39409468 | 1432 | 234.485 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 2 | 1.4085 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 | 157 | 47277992 | 6074 | 145.776 | 6.074 | 5.7 | 6.9 | 3B+1S | 0 | 1180 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39410908 | 1440 | 237.0761 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule
59:00 | 12:00 | 2 | 1.4085 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 | 145 | 47284138 | 6146 | 147.504 | 6.146 | 4.6 | 4.6 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39412364 | 1456 | 236.9021 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 47290149 | 6011 | 144.264 | 6.011 | 3.7 | 3.7 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39413756 | 1392 | 231.5754 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 59 | 41.5493 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 18 | A ONG | 17.3 | 138 | 137 | 47295719 | 5570 | 133.68 | 5.57 | 3.5 | 3.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39415012 | 1256 | 225.4937 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | -2 | -1.4085 | 53 | 37.3239 | Automatic - Pressure Setting | 35.9155 | 37.3239 | 41.5493 | 18 | A ONG | 16.9 | 75 | 105 | 47300692 | 4973 | 119.352 | 4.973 | 2.8 | 2.8 | 3B+1S | 0 | 1038 | 915 | 1185 | 905 | N/A | N/A | N/A | N/A | 39416204 | 1192 | 239.6943 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | -2 | -1.4085 | 49 | 34.507 | Automatic - Pressure Setting | 30.9859 | 32.3944 | 36.6197 | 18 | A ONG | 16.7 | 66 | 86 | 47304531 | 3839 | 92.136 | 3.839 | 1.8 | 1.8 | 3B+1S | 0 | 1027 | 567 | 1185 | 856 | N/A | N/A | N/A | N/A | 39417124 | 920 | 239.6457 | 0% | 100% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | -2 | -1.4085 | 46 | 32.3944 | Automatic - Pressure Setting | 28.8732 | 30.2817 | 34.507 | 18 | A ONG | 16.7 | 84 | 81 | 47308554 | 4023 | 96.552 | 4.023 | 1.3 | 1.3 | 3B | 0 | 0 | 846 | 1185 | 856 | N/A | N/A | N/A | N/A | 39417908 | 784 | 194.8794 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | -2 | -1.4085 | 55 | 38.7324 | Automatic - Pressure Setting | 35.2113 | 36.6197 | 40.8451 | 18 | A ONG | 16.7 | 104 | 102 | 47312060 | 3506 | 84.144 | 3.506 | 1.3 | 1.3 | 3B | 0 | 0 | 1027 | 1185 | 1027 | N/A | N/A | N/A | N/A | 39418748 | 840 | 239.5893 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 0 | 0 | 56 | 39.4366 | Automatic - Pressure Setting | 35.9155 | 37.3239 | 41.5493 | 18 | A ONG | 16.6 | 107 | 121 | 47316336 | 4276 | 102.624 | 4.276 | 1.3 | 1.3 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 39419744 | 996 | 232.928 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 0 | 0 | 53 | 37.3239 | Automatic - Pressure Setting | 33.8028 | 35.2113 | 39.4366 | 18 | A ONG | 16.6 | 103 | 100 | 47320598 | 4262 | 102.288 | 4.262 | 1.3 | 1.3 | 3B | 0 | 0 | 1176 | 1185 | 1176 | N/A | N/A | N/A | N/A | 39420796 | 1052 | 246.8325 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 0 | 0 | 53 | 37.3239 | Automatic - Pressure Setting | 33.8028 | 35.2113 | 39.4366 | 18 | A ONG | 16.1 | 101 | 92 | 47324805 | 4207 | 100.968 | 4.207 | 1.3 | 1.3 | 3B | 0 | 0 | 1017 | 1185 | 1017 | N/A | N/A | N/A | N/A | 39421816 | 1020 | 242.4531 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 0 | 0 | 54 | 38.0282 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 12.6 | 101 | 93 | 47329117 | 4312 | 103.488 | 4.312 | 1.3 | 1.3 | 3B | 0 | 0 | 1017 | 1185 | 1015 | N/A | N/A | N/A | N/A | 39422724 | 908 | 210.5751 | 0% | 0% | 100% | 100% | 100% | 0% | 8930489 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 0 | 0 | 51 | 35.9155 | Automatic - Pressure Setting | 30.9859 | 32.3944 | 36.6197 | 14 | A ONG | 11.9 | 93 | 95 | 47332527 | 3410 | 81.84 | 3.41 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1017 | N/A | N/A | N/A | N/A | 39423308 | 584 | 171.261 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 0 | 0 | 54 | 38.0282 | Automatic - Pressure Setting | 33.0986 | 34.507 | 38.7324 | 14 | A ONG | 11.5 | 95 | 93 | 47336226 | 3699 | 88.776 | 3.699 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1017 | N/A | N/A | N/A | N/A | 39423884 | 576 | 155.7178 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 116.625 | 114270 | 114270 | 114.27 | 114.27 | [13 empty] | 24704 | 216.1897 | [6 empty] | 5963 | 5963 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (65%)
XCV1 CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
NOTE: UNREACH THE 83psi DISC.PRESS. @ 9:00AM DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 11, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
NOTE: UNREACH THE 81psi DISC.PRESS. DUE TO HIGH USED OF WATER. ALL MOTORS FULLSPEED.
NOTE: 3B+1S UNABLE TO MEET THE NORMAL OPERARTION/SETTING DUE TO LOW MAIN SUCTION PREASURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
DECREASE DISCHARGE PRESSURE 78psi DOWN TO 71psi DUE TO WATER LEVEL EXCESS CAPACITY TO THE MINIMUM WATER LEVEL 1.2M
SP2 - STOPPED @ 4:30 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10 PM
NOTE: UNREACH THE 66psi DISC.PRESS. @ 10:00PM DUE TO HIGH USED OF WATER.
UNABLE TO OPEN XCV1 @ 10:00PM DUE TO LOW SUCTION PRESSURE

## AUG 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 6752 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47336226 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39423884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8930489 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 0 | 0 | 55 | 38.7324 | Automatic - Pressure Setting | 33.8028 | 35.2113 | 39.4366 | 14 | A.ONG | 11.4 | 93 | 92 | 47339946 | 3720 | 89.28 | 3.72 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1016 | N/A | N/A | N/A | N/A | 39424464 | 580 | 155.914 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 0 | 0 | 55 | 38.7324 | Automatic - Pressure Setting | 33.8028 | 35.2113 | 39.4366 | 14 | A.ONG | 11.2 | 93 | 90 | 47343667 | 3721 | 89.304 | 3.721 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1016 | N/A | N/A | N/A | N/A | 39425045 | 581 | 156.1408 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 0 | 0 | 57 | 40.1408 | Automatic - Pressure Setting | 35.2113 | 36.6197 | 40.8451 | 14 | A.ONG | 11.2 | 91 | 90 | 47347404 | 3737 | 89.688 | 3.737 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1016 | N/A | N/A | N/A | N/A | 39425644 | 599 | 160.289 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 0 | 0 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 12.8 | 92 | 92 | 47351098 | 3694 | 88.656 | 3.694 | 1.3 | 1.3 | 2B | 0 | 0 | 1016 | 0 | 1016 | N/A | N/A | N/A | N/A | 39426220 | 576 | 155.9285 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 0 | 0 | 51 | 35.9155 | Automatic - Pressure Setting | 30.9859 | 32.3944 | 36.6197 | 18 | A.ONG | 13.1 | 95 | 95 | 47354890 | 3792 | 91.008 | 3.792 | 1.3 | 1.3 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 39426812 | 592 | 156.1181 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 0 | 0 | 47 | 33.0986 | Automatic - Pressure Setting | 31.6901 | 33.0986 | 34.5186 | 19 | A ONG | 13.1 | 93 | 90 | 47358669 | 3779 | 90.696 | 3.779 | 1.4 | 1.4 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 39427404 | 592 | 156.6552 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | -3 | -2.1127 | 45 | 31.6901 | Automatic - Pressure Setting | 30.2817 | 31.6901 | 33.1101 | 19 | A ONG | 16.7 | 84 | 84 | 47362701 | 4032 | 96.768 | 4.032 | 1.4 | 1.4 | 1B | 0 | 0 | 1107 | 0 | 925 | N/A | N/A | N/A | N/A | 39428100 | 696 | 172.619 | 0% | 0% | 100% | 0% | 100% | 0% | 8930489 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 2 | 1.4085 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 22.5468 | 19 | A ONG | 17.3 | 15 | 15 | 47363970 | 1269 | 30.456 | 1.269 | 1.4 | 1.4 | 1B | 0 | 0 | 627 | 0 | 0 | N/A | N/A | N/A | N/A | 39428236 | 136 | 107.171 | 0% | 0% | 100% | 0% | 0% | 0% | 8930489 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 3 | 2.1127 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 22.5468 | 19 | A ONG | 18.4 | 18 | 18 | 47364705 | 735 | 17.64 | 0.735 | 1.4 | 1.4 | 1B | 0 | 0 | 676 | 0 | 0 | N/A | N/A | N/A | N/A | 39428316 | 80 | 108.8435 | 0% | 0% | 100% | 0% | 0% | 0% | 8930489 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 0 | 0 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 22.5468 | 19 | A ONG | 17.7 | 19 | 19 | 47365643 | 938 | 22.512 | 0.938 | 1.3 | 7.6 | 1B | 0 | 0 | 706 | 0 | 0 | N/A | N/A | N/A | N/A | 39428436 | 120 | 127.9318 | 0% | 0% | 100% | 0% | 0% | 0% | 8930489 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 0 | 0 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 22.5468 | 19 | A ONG | 17.7 | 19 | 20 | 47366413 | 770 | 18.48 | 0.77 | 1.3 | 6.9 | 1B | 0 | 0 | 706 | 0 | 0 | N/A | N/A | N/A | N/A | 39428532 | 96 | 124.6753 | 0% | 0% | 100% | 0% | 0% | 0% | 8930489 | 0 |  | Normal operation schedule
59:00 | 12:00 | -1 | -0.70423 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 22.5468 | 19 | A ONG | 17.3 | 19 | 20 | 47367327 | 914 | 21.936 | 0.914 | 1.3 | 1.3 | 1B | 0 | 0 | 706 | 0 | 0 | N/A | N/A | N/A | N/A | 39428648 | 116 | 126.9147 | 0% | 0% | 100% | 0% | 0% | 0% | 8930489 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 0 | 0 | 30 | 21.1268 | Automatic - Pressure Setting | 19.7183 | 21.1268 | 25.3521 | 19 | A ONG | 17.5 | 18 | 18 | 47368100 | 773 | 18.552 | 0.773 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 696 | N/A | N/A | N/A | N/A | 39428756 | 108 | 139.7154 | 0% | 0% | 0% | 0% | 0% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 26.7606 | 28.169 | 32.3944 | 18 | A ONG | 17.3 | 24 | 24 | 47369001 | 901 | 21.624 | 0.901 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39428884 | 128 | 142.0644 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 26.7606 | 28.169 | 32.3944 | 18 | A ONG | 16.9 | 22 | 22 | 47370050 | 1049 | 25.176 | 1.049 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429052 | 168 | 160.1525 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.7 | 22 | 20 | 47370992 | 942 | 22.608 | 0.942 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429228 | 176 | 186.8365 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.7 | 22 | 23 | 47371887 | 895 | 21.48 | 0.895 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429396 | 168 | 187.7095 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.7 | 22 | 22 | 47372861 | 974 | 23.376 | 0.974 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429568 | 172 | 176.5914 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.6 | 22 | 21 | 47373746 | 885 | 21.24 | 0.885 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429740 | 172 | 194.3503 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.6 | 22 | 22 | 47374680 | 934 | 22.416 | 0.934 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39429924 | 184 | 197.0021 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 0 | 0 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 18 | A ONG | 16.1 | 22 | 22 | 47375576 | 896 | 21.504 | 0.896 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 845 | N/A | N/A | N/A | N/A | 39430084 | 160 | 178.5714 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 2 | 1.4085 | 40 | 28.169 | Automatic - Pressure Setting | 24.6479 | 26.0563 | 30.2817 | 14 | A ONG | 12.6 | 19 | 38 | 47376567 | 991 | 23.784 | 0.991 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 715 | N/A | N/A | N/A | N/A | 39430276 | 192 | 193.7437 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 40 | 28.169 | Automatic - Pressure Setting | 23.2394 | 24.6479 | 28.8732 | 14 | A ONG | 11.9 | 21 | 36 | 47377480 | 913 | 21.912 | 0.913 | 1.3 | 1.3 | 1B | 0 | 0 | 0 | 0 | 715 | N/A | N/A | N/A | N/A | 39430400 | 124 | 135.816 | 0% | 0% | 0% | 0% | 100% | 0% | 8930489 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 60 | 42.2535 | Automatic - Pressure Setting | 37.3239 | 38.7324 | 42.9577 | 14 | A ONG | 11.5 | 119 | 106 | 47378882 | 1402 | 33.648 | 1.402 | 2 | 2 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39430636 | 236 | 168.331 | 0% | 0% | 100% | 0% | 100% | 25% | 8931175 | 686 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 45.7917 | 42656 | 42656 | 42.656 | 42.656 | [13 empty] | 6752 | 158.2896 | [6 empty] | 686 | 686 | 1.0567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Target Discharge Pressure 55psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
TARGET DISCHARGE PRESSURE 51 PSI @ 5:01 AM AS PER SCHEDULE
Schedule of Operations for 2.2 realignment
TARGET DISCHARGE PRESSURE SET TO 30 PSI @ 7:01 AM AS PER SCHEDULE
BP3 - STOP @ 7:00 AM AS PER SCHEDULE
BP3 - STARTED @ 12:20 PM DUE TO PREVENTIVE MAINTENANCE
BP1 - STOP @ 12:22 PM DUE TO PREVENTIVE MAINTENANCE
ADDITIONAL 10psi TO THE DISCHARGE PRESSURE @ 1PM AS PER ALVIN CRUZ (SPM)
XCV1 - OPENNED @ 11:01 PM (25%)
BACK TO NORMAL OPERATION AS PER ALVIN CRUZ (SPM), DISCHARGE PRESSURE SET TO 66psi 12AM
INCREASE 2B TO MEET THE DISCHARGE PRESSURE 66psi
BP1 - START @ 11:50 PM

## AUG 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26616 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47378882 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39430636 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8931175 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 107 | 98 | 47383334 | 4452 | 106.848 | 4.452 | 3.3 | 3.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39431540 | 904 | 203.0548 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 1261 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 103 | 47387618 | 4284 | 102.816 | 4.284 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39432413 | 873 | 203.7815 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 100 | 47391740 | 4122 | 98.928 | 4.122 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39433286 | 873 | 211.7904 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 110 | 101 | 47395868 | 4128 | 99.072 | 4.128 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39434157 | 871 | 210.9981 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 2 | 1.4085 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 47399994 | 4126 | 99.024 | 4.126 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39435040 | 883 | 214.0087 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 47.8989 | 19 | A ONG | 13.1 | 105 | 101 | 47404246 | 4252 | 102.048 | 4.252 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39435908 | 868 | 204.1392 | 0% | 0% | 100% | 0% | 100% | 0% | 8932436 | 0 | 0.93 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 0 | 0 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 16.7 | 124 | 115 | 47409219 | 4973 | 119.352 | 4.973 | 3.5 | 3.5 | 3B+1S | 0 | 1001 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39437140 | 1232 | 247.7378 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | -1 | -0.70423 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 17.3 | 123 | 112 | 47413939 | 4720 | 113.28 | 4.72 | 3.8 | 3.8 | 3B+1S | 0 | 1001 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39438332 | 1192 | 252.5424 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | -1 | -0.70423 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 18.4 | 124 | 108 | 47418659 | 4720 | 113.28 | 4.72 | 4.1 | 4.1 | 3B+1S | 0 | 952 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39439524 | 1192 | 252.5424 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | -1 | -0.70423 | 73 | 51.4085 | Automatic - Pressure Setting | 50 | 51.4085 | 52.8285 | 19 | A ONG | 17.7 | 126 | 120 | 47423678 | 5019 | 120.456 | 5.019 | 4.2 | 7.6 | 3B+1S | 0 | 952 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39440564 | 1040 | 207.2126 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 | 1.06 | Normal operation schedule
58:00 | 11:00 | 0 | 0 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 17.7 | 137 | 131 | 47428674 | 4996 | 119.904 | 4.996 | 4.3 | 6.9 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39441936 | 1372 | 274.6197 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Normal operation schedule
59:00 | 12:00 | 0 | 0 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 17.3 | 136 | 120 | 47434288 | 5614 | 134.736 | 5.614 | 4.3 | 4.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39443220 | 1284 | 228.7139 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 0 | 0 | 71 | 50 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 19 | A ONG | 17.5 | 137 | 133 | 47439706 | 5418 | 130.032 | 5.418 | 4.3 | 4.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39444452 | 1232 | 227.3902 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 1 | 0.70423 | 71 | 50 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 17.3 | 136 | 132 | 47445095 | 5389 | 129.336 | 5.389 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39445632 | 1180 | 218.9646 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 2 | 1.4085 | 71 | 50 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.9 | 136 | 129 | 47450479 | 5384 | 129.216 | 5.384 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39446844 | 1212 | 225.1114 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 2 | 1.4085 | 71 | 50 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.7 | 136 | 138 | 47456035 | 5556 | 133.344 | 5.556 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39448084 | 1240 | 223.1821 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 71 | 50 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.7 | 137 | 133 | 47461480 | 5445 | 130.68 | 5.445 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39449308 | 1224 | 224.7934 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 137 | 137 | 47467003 | 5523 | 132.552 | 5.523 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39450556 | 1248 | 225.9641 | 0% | 0% | 100% | 100% | 100% | 0% | 8932436 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 132 | 47472908 | 5905 | 141.72 | 5.905 | 4.3 | 4.3 | 3B+1S | 0 | 1179 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39451892 | 1336 | 226.2489 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 134 | 47477960 | 5052 | 121.248 | 5.052 | 4.3 | 4.3 | 3B+1S | 0 | 1179 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39453036 | 1144 | 226.445 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 134 | 133 | 47483531 | 5571 | 133.704 | 5.571 | 4.3 | 4.3 | 3B+1S | 0 | 1179 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39454300 | 1264 | 226.8892 | 0% | 100% | 100% | 100% | 100% | 0% | 8932436 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 110 | 47488780 | 5249 | 125.976 | 5.249 | 4.3 | 4.3 | 2B+1S | 0 | 1179 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39455476 | 1176 | 224.0427 | 0% | 100% | 100% | 0% | 100% | 0% | 8932436 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 107 | 47493142 | 4362 | 104.688 | 4.362 | 4.9 | 4.9 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39456372 | 896 | 205.4104 | 0% | 0% | 100% | 0% | 100% | 35% | 8933059 | 623 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 100 | 47497413 | 4271 | 102.504 | 4.271 | 5.7 | 5.7 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39457252 | 880 | 206.0407 | 0% | 0% | 100% | 0% | 100% | 35% | 8933825 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.875 | 118531 | 118531 | 118.531 | 118.531 | [13 empty] | 26616 | 224.5489 | [6 empty] | 2650 | 2650 | 1.0533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 1:00 AM,WATER ELEVATION (3.3M)
BP2 - START @ 6:00 AM
SP2 - STARTED @ 6:01 AM
XCV4 - OPENNED @ 6:05 AM FOR BOOSTER REFILLING
XCV4 - CLOSED @ 10:41 AM (4.M)
SP2 - CLOSED @ 10:42 AM
SP2 ATART@6:27PM AS PER ALVIN CRUZ (SPM) FOR REDUCING WATER LEVEL UP TO 1.3
XC2 - OPENNED @ 10:01 PM w/ 35%

## AUG 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27124 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47497413 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39457252 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8933825 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 101 | 47501428 | 4015 | 96.36 | 4.015 | 6.7 | 6.7 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39458040 | 788 | 196.264 | 0% | 0% | 100% | 0% | 100% | 45% | 8934798 | 973 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 99 | 47505446 | 4018 | 96.432 | 4.018 | 7.8 | 7.8 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39458831 | 791 | 196.8641 | 0% | 0% | 100% | 0% | 100% | 45% | 8935776 | 978 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 103 | 47509464 | 4018 | 96.432 | 4.018 | 8.6 | 8.6 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39459624 | 793 | 197.3619 | 0% | 0% | 100% | 0% | 100% | 45% | 8936753 | 977 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 100 | 47513481 | 4017 | 96.408 | 4.017 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39460414 | 790 | 196.6642 | 0% | 0% | 100% | 0% | 100% | 45% | 8937732 | 979 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 102 | 47517500 | 4019 | 96.456 | 4.019 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39461204 | 790 | 196.5663 | 0% | 0% | 100% | 0% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 123 | 47522228 | 4728 | 113.472 | 4.728 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39462048 | 844 | 178.511 | 0% | 0% | 100% | 0% | 100% | 0% | 8937732 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 145 | 47528412 | 6184 | 148.416 | 6.184 | 9.2 | 9.2 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39463412 | 1364 | 220.5692 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 47534629 | 6217 | 149.208 | 6.217 | 8.4 | 8.4 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39464820 | 1408 | 226.4758 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 150 | 47540861 | 6232 | 149.568 | 6.232 | 7.7 | 7.7 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39466204 | 1384 | 222.0796 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 153 | 47547077 | 6216 | 149.184 | 6.216 | 7 | 7 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39467585 | 1381 | 222.1686 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 47553230 | 6153 | 147.672 | 6.153 | 6.2 | 6.9 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39468940 | 1355 | 220.2178 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 164 | 47559344 | 6114 | 146.736 | 6.114 | 5.6 | 5.6 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39470356 | 1416 | 231.5996 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 47565312 | 5968 | 143.232 | 5.968 | 5.1 | 5.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39471716 | 1360 | 227.882 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 152 | 47570844 | 5532 | 132.768 | 5.532 | 4.8 | 4.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39472976 | 1260 | 227.7657 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 47576496 | 5652 | 135.648 | 5.652 | 4.5 | 4.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39474284 | 1308 | 231.4225 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 47582117 | 5621 | 134.904 | 5.621 | 4.3 | 4.3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39475596 | 1312 | 233.4104 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 130 | 47587745 | 5628 | 135.072 | 5.628 | 3.9 | 3.9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39476900 | 1304 | 231.6986 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 47593302 | 5557 | 133.368 | 5.557 | 3.7 | 3.7 | 3B+1S | 0 | 1004 | 1187 | 1187 | 1187 | N/A | N/A | N/A | N/A | 39478204 | 1304 | 234.659 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 131 | 47598795 | 5493 | 131.832 | 5.493 | 3.7 | 3.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39479516 | 1312 | 238.8494 | 0% | 100% | 100% | 100% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 105 | 126 | 47603939 | 5144 | 123.456 | 5.144 | 3 | 3 | 2B+1S | 0 | 1115 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39480588 | 1072 | 208.3981 | 0% | 100% | 100% | 0% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 104 | 122 | 47608974 | 5035 | 120.84 | 5.035 | 2.1 | 2.1 | 2B+1S | 0 | 1117 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39481636 | 1048 | 208.143 | 0% | 100% | 100% | 0% | 100% | 0% | 8937732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 121 | 47614143 | 5169 | 124.056 | 5.169 | 1.3 | 1.3 | 2B+1S | 0 | 1116 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39482748 | 1112 | 215.1287 | 0% | 100% | 100% | 0% | 100% | 0% | 8937732 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 150 | 96 | 47618225 | 4082 | 97.968 | 4.082 | 2.9 | 2.9 | 2B | 0 | 0 | 1158 | 0 | 1157 | N/A | N/A | N/A | N/A | 39483572 | 824 | 201.8618 | 0% | 0% | 100% | 0% | 100% | 55% | 8939589 | 1857 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 144 | 97 | 47622181 | 3956 | 94.944 | 3.956 | 5.2 | 5.2 | 2B | 0 | 0 | 1157 | 0 | 1157 | N/A | N/A | N/A | N/A | 39484376 | 804 | 203.2356 | 0% | 0% | 100% | 0% | 100% | 55% | 8941590 | 2001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.3333 | 124768 | 124768 | 124.768 | 124.768 | [13 empty] | 27124 | 217.3955 | [6 empty] | 7765 | 7765 | 1.1083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (45%)
XCV1 CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 13, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (55%)

## AUG 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47622181 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39484376 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8941590 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 137 | 87 | 47626066 | 3885 | 93.24 | 3.885 | 6.9 | 6.9 | 2B | 0 | 0 | 1117 | 0 | 1116 | N/A | N/A | N/A | N/A | 39485172 | 796 | 204.8906 | 0% | 0% | 100% | 0% | 100% | 60% | 8943321 | 1731 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 122 | 47629724 | 3658 | 87.792 | 3.658 | 8.7 | 8.7 | 2B | 0 | 0 | 1117 | 0 | 1116 | N/A | N/A | N/A | N/A | 39485884 | 712 | 194.6419 | 0% | 0% | 100% | 0% | 100% | 60% | 8944996 | 1675 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 103 | 102 | 47633552 | 3828 | 91.872 | 3.828 | 9.5 | 9.5 | 2B | 0 | 0 | 1086 | 0 | 1087 | N/A | N/A | N/A | N/A | 39486572 | 688 | 179.7283 | 0% | 0% | 100% | 0% | 100% | 60% | 8946198 | 1202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 108 | 110 | 47637937 | 4385 | 105.24 | 4.385 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1087 | N/A | N/A | N/A | N/A | 39487284 | 712 | 162.3717 | 0% | 0% | 100% | 0% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 112 | 47642549 | 4612 | 110.688 | 4.612 | 9.5 | 9.5 | 2B | 0 | 0 | 1087 | 0 | 1186 | N/A | N/A | N/A | N/A | 39488004 | 720 | 156.1145 | 0% | 0% | 100% | 0% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 126 | 47647401 | 4852 | 116.448 | 4.852 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39488872 | 868 | 178.8953 | 0% | 0% | 100% | 0% | 100% | 0% | 8946198 | 0 | 1.35 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 153 | 47653956 | 6555 | 157.32 | 6.555 | 9.4 | 9.4 | 3B+1S | 0 | 1167 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39490308 | 1436 | 219.0694 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 154 | 47660607 | 6651 | 159.624 | 6.651 | 8.4 | 8.4 | 3B+1S | 0 | 1169 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39491812 | 1504 | 226.1314 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 148 | 47666668 | 6061 | 145.464 | 6.061 | 7.5 | 7.5 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39493196 | 1384 | 228.3452 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 47672704 | 6036 | 144.864 | 6.036 | 6.8 | 7 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39494556 | 1360 | 225.3148 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 139 | 47678553 | 5849 | 140.376 | 5.849 | 6.2 | 6.9 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39495892 | 1336 | 228.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 136 | 47684426 | 5873 | 140.952 | 5.873 | 5.5 | 5.6 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39497252 | 1360 | 231.5682 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 137 | 47690328 | 5902 | 141.648 | 5.902 | 4.9 | 4.9 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39498620 | 1368 | 231.7858 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 123 | 124 | 47695818 | 5490 | 131.76 | 5.49 | 4.5 | 4.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39499928 | 1308 | 238.2514 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 122 | 47701027 | 5209 | 125.016 | 5.209 | 4.4 | 4.4 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39501204 | 1276 | 244.9606 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 120 | 47706020 | 4993 | 119.832 | 4.993 | 4.3 | 4.3 | 3B+1S | 0 | 1012 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39502468 | 1264 | 253.1544 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 138 | 47711300 | 5280 | 126.72 | 5.28 | 4.2 | 4.2 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39503748 | 1280 | 242.4242 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 131 | 47716830 | 5530 | 132.72 | 5.53 | 3.8 | 3.8 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39505060 | 1312 | 237.2514 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 122 | 47722228 | 5398 | 129.552 | 5.398 | 3.5 | 3.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39506340 | 1280 | 237.1249 | 0% | 100% | 100% | 100% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 101 | 120 | 47727545 | 5317 | 127.608 | 5.317 | 2.9 | 2.9 | 2B+1S | 0 | 1136 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39507540 | 1200 | 225.6912 | 0% | 100% | 100% | 0% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 101 | 121 | 47732473 | 4928 | 118.272 | 4.928 | 2.1 | 2.1 | 2B+1S | 0 | 1136 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39508580 | 1040 | 211.039 | 0% | 100% | 100% | 0% | 100% | 0% | 8946198 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 121 | 47737521 | 5048 | 121.152 | 5.048 | 1.3 | 1.3 | 2B+1S | 0 | 1136 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39509684 | 1104 | 218.7005 | 0% | 100% | 100% | 0% | 100% | 0% | 8946198 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 91 | 47741450 | 3929 | 94.296 | 3.929 | 2.7 | 2.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39510544 | 860 | 218.8852 | 0% | 0% | 100% | 0% | 100% | 0% | 8947778 | 1580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 83 | 47744972 | 3522 | 84.528 | 3.522 | 5 | 5 | 2B | 0 | 0 | 1096 | 0 | 1096 | N/A | N/A | N/A | N/A | 39511236 | 692 | 196.4793 | 0% | 0% | 100% | 0% | 100% | 0% | 8949698 | 1920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.4167 | 122791 | 122791 | 122.791 | 122.791 | [13 empty] | 26860 | 218.7457 | [6 empty] | 8108 | 8108 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (60%)
XCV1 CLOSED @ 2:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 15, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:20 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27432 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47744972 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39511236 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8949698 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 81 | 47748383 | 3411 | 81.864 | 3.411 | 7 | 7 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39511908 | 672 | 197.0097 | 0% | 0% | 100% | 0% | 100% | 50% | 8950916 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 89 | 47752000 | 3617 | 86.808 | 3.617 | 8.6 | 8.6 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39512589 | 681 | 188.2776 | 0% | 0% | 100% | 0% | 100% | 56% | 8952137 | 1221 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 90 | 47755620 | 3620 | 86.88 | 3.62 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39513270 | 681 | 188.1215 | 0% | 0% | 100% | 0% | 100% | 56% | 8953357 | 1220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 93 | 47759243 | 3623 | 86.952 | 3.623 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39513952 | 682 | 188.2418 | 0% | 0% | 100% | 0% | 100% | 56% | 8954578 | 1221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 98 | 47762864 | 3621 | 86.904 | 3.621 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39514636 | 684 | 188.8981 | 0% | 0% | 100% | 0% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 106 | 91 | 47767069 | 4205 | 100.92 | 4.205 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39515356 | 720 | 171.2247 | 0% | 0% | 100% | 0% | 100% | 0% | 8954578 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 1434 | 145 | 47772990 | 5921 | 142.104 | 5.921 | 9.5 | 9.5 | 3B+1S | 0 | 1117 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39516644 | 1288 | 217.5308 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 133 | 148 | 47779631 | 6641 | 159.384 | 6.641 | 8.8 | 8.8 | 3B+1S | 0 | 1117 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39518108 | 1464 | 220.4487 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 132 | 150 | 47785570 | 5939 | 142.536 | 5.939 | 7.8 | 7.8 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39519476 | 1368 | 230.3418 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 127 | 148 | 47791990 | 6420 | 154.08 | 6.42 | 6.9 | 7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39520932 | 1456 | 226.7913 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 | 152 | 47798231 | 6241 | 149.784 | 6.241 | 5.8 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39522372 | 1440 | 230.7323 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 127 | 148 | 47804627 | 6396 | 153.504 | 6.396 | 4.7 | 5.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39523856 | 1484 | 232.02 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 125 | 143 | 47810640 | 6013 | 144.312 | 6.013 | 3.6 | 3.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39525260 | 1404 | 233.4941 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 128 | 141 | 47816602 | 5962 | 143.088 | 5.962 | 2.8 | 2.8 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39526620 | 1360 | 228.1114 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 | 144 | 47822372 | 5770 | 138.48 | 5.77 | 2.3 | 2.3 | 3B+1S | 0 | 1174 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39527972 | 1352 | 234.3154 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 130 | 47828149 | 5777 | 138.648 | 5.777 | 1.7 | 1.7 | 3B+1S | 0 | 1164 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39529316 | 1344 | 232.6467 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 | 131 | 47833724 | 5575 | 133.8 | 5.575 | 1.5 | 1.5 | 3B+1S | 0 | 1124 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39530620 | 1304 | 233.9013 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.7 | 134 | 131 | 47839378 | 5654 | 135.696 | 5.654 | 1.3 | 1.3 | 3B+1S | 0 | 993 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39531940 | 1320 | 233.463 | 0% | 100% | 100% | 100% | 100% | 0% | 8954578 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 135 | 137 | 47844960 | 5582 | 133.968 | 5.582 | 1.3 | 1.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39533184 | 1244 | 222.8592 | 0% | 0% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 135 | 132 | 47850441 | 5481 | 131.544 | 5.481 | 1.3 | 1.3 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39534412 | 1228 | 224.0467 | 0% | 0% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 134 | 131 | 47856053 | 5612 | 134.688 | 5.612 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39535684 | 1272 | 226.6572 | 0% | 0% | 100% | 100% | 100% | 0% | 8954578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 131 | 129 | 47861408 | 5355 | 128.52 | 5.355 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39536888 | 1204 | 224.8366 | 0% | 0% | 100% | 100% | 100% | 0% | 8954578 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 64 | 45.0704 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 14 | A ONG | 11.9 | 141 | 101 | 47865726 | 4318 | 103.632 | 4.318 | 2.4 | 2.4 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39537796 | 908 | 210.2825 | 0% | 0% | 100% | 0% | 100% | 50% | 8955863 | 1285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 102 | 47870037 | 4311 | 103.464 | 4.311 | 4 | 4 | 2B | 0 | 0 | 1157 | 0 | 1167 | N/A | N/A | N/A | N/A | 39538668 | 872 | 202.2733 | 0% | 0% | 100% | 0% | 100% | 50% | 8957351 | 1488 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.375 | 125065 | 125065 | 125.065 | 125.065 | [13 empty] | 27432 | 219.3419 | [6 empty] | 7653 | 7653 | 1.0683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (56%)
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 8am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 15, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE UNREACH THE SET OF 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE DUE TO LOW OF DISCHARGE
SP2 - STOPPED @ 6:00PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
BP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (50%)

## AUG 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27628 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47870037 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39538668 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8957351 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 93 | 47874159 | 4122 | 98.928 | 4.122 | 5.7 | 5.7 | 2B | 0 | 0 | 1107 | 0 | 1157 | N/A | N/A | N/A | N/A | 39539500 | 832 | 201.8438 | 0% | 0% | 100% | 0% | 100% | 55% | 8958758 | 1407 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 115 | 47877905 | 3746 | 89.904 | 3.746 | 7.1 | 7.1 | 2B | 0 | 0 | 1107 | 0 | 1096 | N/A | N/A | N/A | N/A | 39540228 | 728 | 194.3406 | 0% | 0% | 100% | 0% | 100% | 55% | 8960226 | 1468 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 94 | 47881666 | 3761 | 90.264 | 3.761 | 8.6 | 8.6 | 2B | 0 | 0 | 1108 | 0 | 1096 | N/A | N/A | N/A | N/A | 39540924 | 696 | 185.0572 | 0% | 0% | 100% | 0% | 100% | 55% | 8961676 | 1450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 91 | 90 | 47885384 | 3718 | 89.232 | 3.718 | 9.8 | 9.8 | 2B | 0 | 0 | 1048 | 0 | 1046 | N/A | N/A | N/A | N/A | 39541580 | 656 | 176.4389 | 0% | 0% | 100% | 0% | 100% | 55% | 8962639 | 963 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 99 | 47889273 | 3889 | 93.336 | 3.889 | 9.8 | 9.8 | 2B | 0 | 0 | 1048 | 0 | 1077 | N/A | N/A | N/A | N/A | 39542228 | 648 | 166.6238 | 0% | 0% | 100% | 0% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 117 | 47894032 | 4759 | 114.216 | 4.759 | 9.8 | 9.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39543148 | 920 | 193.3179 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 130 | 47899654 | 5622 | 134.928 | 5.622 | 9.8 | 9.8 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39544332 | 1184 | 210.6012 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 139 | 47905957 | 6303 | 151.272 | 6.303 | 9.3 | 9.3 | 3B+1S | 0 | 1116 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39545756 | 1424 | 225.9242 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 145 | 47912194 | 6237 | 149.688 | 6.237 | 8.6 | 8.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39547156 | 1400 | 224.4669 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 | 149 | 47918363 | 6169 | 148.056 | 6.169 | 7.6 | 7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39548564 | 1408 | 228.238 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 | 149 | 47924767 | 6404 | 153.696 | 6.404 | 6.5 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39550028 | 1464 | 228.6071 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 127 | 147 | 47930969 | 6202 | 148.848 | 6.202 | 5.5 | 5.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39551460 | 1432 | 230.8933 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 19 | A ONG | 17.5 | 126 | 142 | 47936991 | 6022 | 144.528 | 6.022 | 4.5 | 4.5 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39552868 | 1408 | 233.8094 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 17.3 | 124 | 140 | 47943063 | 6072 | 145.728 | 6.072 | 3.4 | 3.4 | 3B+1S | 0 | 1166 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39554260 | 1392 | 229.249 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.9 | 122 | 139 | 47948976 | 5913 | 141.912 | 5.913 | 2.6 | 2.6 | 3B+1S | 0 | 1166 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39555658 | 1398 | 236.4282 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 122 | 138 | 47954827 | 5851 | 140.424 | 5.851 | 1.7 | 1.7 | 3B+1S | 0 | 1166 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39557060 | 1402 | 239.6172 | 0% | 100% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 135 | 135 | 47960568 | 5741 | 137.784 | 5.741 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39558428 | 1368 | 238.286 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 136 | 133 | 47965994 | 5426 | 130.224 | 5.426 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39559636 | 1208 | 222.6318 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 135 | 132 | 47971489 | 5495 | 131.88 | 5.495 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39560864 | 1228 | 223.4759 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 134 | 133 | 47976965 | 5476 | 131.424 | 5.476 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39562094 | 1230 | 224.6165 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 132 | 124 | 47982551 | 5586 | 134.064 | 5.586 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39563348 | 1254 | 224.4898 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 132 | 47987962 | 5411 | 129.864 | 5.411 | 1.3 | 1.3 | 3B | 0 | 0 | 1107 | 1185 | 1096 | N/A | N/A | N/A | N/A | 39564556 | 1208 | 223.2489 | 0% | 0% | 100% | 100% | 100% | 0% | 8962639 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 100 | 47992116 | 4154 | 99.696 | 4.154 | 2.2 | 2.2 | 2B | 0 | 0 | 1187 | 0 | 1186 | N/A | N/A | N/A | N/A | 39565412 | 856 | 206.0664 | 0% | 0% | 100% | 0% | 100% | 45% | 8963910 | 1271 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 141 | 101 | 47996355 | 4239 | 101.736 | 4.239 | 3.6 | 3.6 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39566296 | 884 | 208.5397 | 0% | 0% | 100% | 0% | 100% | 45% | 8965394 | 1484 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.6667 | 126318 | 126318 | 126.318 | 126.318 | [13 empty] | 27628 | 218.7178 | [6 empty] | 8043 | 8043 | 1.165 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (55%)
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 10am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 17, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
SP2 - STOPPED @ 4:50PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE UNREACH THE SET OF 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE DUE TO LOW OF DISCHARGE
BP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (45%)

## AUG 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27780 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 47996355 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39566296 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8965394 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 89 | 48000520 | 4165 | 99.96 | 4.165 | 5.5 | 5.5 | 2B | 0 | 0 | 1117 | 0 | 1115 | N/A | N/A | N/A | N/A | 39567140 | 844 | 202.6411 | 0% | 0% | 100% | 0% | 100% | 55% | 8967075 | 1681 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 92 | 48004344 | 3824 | 91.776 | 3.824 | 7.3 | 7.3 | 2B | 0 | 0 | 1118 | 0 | 1116 | N/A | N/A | N/A | N/A | 39567888 | 748 | 195.6067 | 0% | 0% | 100% | 0% | 100% | 55% | 8968735 | 1660 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 90 | 48007710 | 3366 | 80.784 | 3.366 | 8.7 | 8.7 | 2B | 0 | 0 | 1087 | 0 | 1096 | N/A | N/A | N/A | N/A | 39568524 | 636 | 188.9483 | 0% | 0% | 100% | 0% | 100% | 55% | 8970136 | 1401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 92 | 48011553 | 3843 | 92.232 | 3.843 | 9.7 | 9.7 | 2B | 0 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 39569216 | 692 | 180.0677 | 0% | 0% | 100% | 0% | 100% | 55% | 8970900 | 764 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 101 | 48015597 | 4044 | 97.056 | 4.044 | 9.7 | 9.7 | 2B | 0 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 39569860 | 644 | 159.2483 | 0% | 0% | 100% | 0% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 118 | 48020586 | 4989 | 119.736 | 4.989 | 9.7 | 9.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39570804 | 944 | 189.2163 | 0% | 0% | 100% | 0% | 100% | 0% | 8970900 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 141 | 48026748 | 6162 | 147.888 | 6.162 | 9 | 9 | 3B+1S | 0 | 1087 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39572180 | 1376 | 223.3041 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 153 | 48032977 | 6229 | 149.496 | 6.229 | 8.1 | 8.1 | 3B+1S | 0 | 1157 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39573588 | 1408 | 226.0395 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 18.4 | 130 | 146 | 48039328 | 6351 | 152.424 | 6.351 | 7.2 | 7.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39575036 | 1448 | 227.9956 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 126 | 149 | 48045685 | 6357 | 152.568 | 6.357 | 6 | 7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39576508 | 1472 | 231.5558 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 126 | 145 | 48051713 | 6028 | 144.672 | 6.028 | 5 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39577912 | 1404 | 232.9131 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 125 | 149 | 48057935 | 6222 | 149.328 | 6.222 | 3.8 | 5.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39579380 | 1468 | 235.937 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 128 | 145 | 48063842 | 5907 | 141.768 | 5.907 | 3.2 | 3.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39580756 | 1376 | 232.944 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 136 | 48069390 | 5548 | 133.152 | 5.548 | 2.6 | 2.6 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39582020 | 1264 | 227.8298 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 48075124 | 5734 | 137.616 | 5.734 | 2.1 | 2.1 | 3B+1S | 0 | 1062 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39583372 | 1352 | 235.7865 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 48080749 | 5625 | 135 | 5.625 | 1.9 | 1.9 | 3B+1S | 0 | 1032 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39584700 | 1328 | 236.0889 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 48086290 | 5541 | 132.984 | 5.541 | 1.6 | 1.6 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39586012 | 1312 | 236.7804 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 132 | 48092028 | 5738 | 137.712 | 5.738 | 1.4 | 1.4 | 3B+1S | 0 | 1033 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39587344 | 1332 | 232.1366 | 0% | 100% | 100% | 100% | 100% | 0% | 8970900 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 135 | 132 | 48097516 | 5488 | 131.712 | 5.488 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39588604 | 1260 | 229.5918 | 0% | 0% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 133 | 135 | 48103047 | 5531 | 132.744 | 5.531 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39589860 | 1256 | 227.0837 | 0% | 0% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 133 | 129 | 48108551 | 5504 | 132.096 | 5.504 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39591116 | 1256 | 228.1977 | 0% | 0% | 100% | 100% | 100% | 0% | 8970900 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 126 | 48113873 | 5322 | 127.728 | 5.322 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39592348 | 1232 | 231.4919 | 0% | 0% | 100% | 100% | 100% | 0% | 8970900 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 140 | 98 | 48118045 | 4172 | 100.128 | 4.172 | 2.5 | 2.5 | 2B | 0 | 0 | 1147 | 0 | 1187 | N/A | N/A | N/A | N/A | 39593248 | 900 | 215.7239 | 0% | 0% | 100% | 0% | 100% | 45% | 8972201 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 91 | 48122050 | 4005 | 96.12 | 4.005 | 4.2 | 4.2 | 2B | 0 | 0 | 1107 | 0 | 1096 | N/A | N/A | N/A | N/A | 39594076 | 828 | 206.7416 | 0% | 0% | 100% | 0% | 100% | 45% | 8973782 | 1581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.5833 | 125695 | 125695 | 125.695 | 125.695 | [13 empty] | 27780 | 221.0112 | [6 empty] | 8388 | 8388 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (55%)
XCV1 CLOSED @ 3:30 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 9:00am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
SP2 - STOPPED @ 6:15PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE UNREACH THE SET OF 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE DUE TO LOW OF DISCHARGE
BP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (45%)

## AUG 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27400 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48122050 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39594076 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8973782 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 84 | 48125818 | 3768 | 90.432 | 3.768 | 6.2 | 6.2 | 2B | 0 | 0 | 1077 | 0 | 1066 | N/A | N/A | N/A | N/A | 39594792 | 716 | 190.0212 | 0% | 0% | 100% | 0% | 100% | 50% | 8975619 | 1837 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 48129257 | 3439 | 82.536 | 3.439 | 7.9 | 7.9 | 2B | 0 | 0 | 1077 | 0 | 1066 | N/A | N/A | N/A | N/A | 39595428 | 636 | 184.9375 | 0% | 0% | 100% | 0% | 100% | 50% | 8977284 | 1665 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 86 | 48132954 | 3697 | 88.728 | 3.697 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1066 | N/A | N/A | N/A | N/A | 39596100 | 672 | 181.769 | 0% | 0% | 100% | 0% | 100% | 50% | 8978771 | 1487 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 97 | 48136711 | 3757 | 90.168 | 3.757 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1066 | N/A | N/A | N/A | N/A | 39596764 | 664 | 176.7368 | 0% | 0% | 100% | 0% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 117 | 48140806 | 4095 | 98.28 | 4.095 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1066 | N/A | N/A | N/A | N/A | 39597444 | 680 | 166.0562 | 0% | 0% | 100% | 0% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 114 | 48145826 | 5020 | 120.48 | 5.02 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39598396 | 952 | 189.6414 | 0% | 0% | 100% | 0% | 100% | 0% | 8978771 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 142 | 48151970 | 6144 | 147.456 | 6.144 | 9 | 9 | 3B+1S | 0 | 1135 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39599792 | 1396 | 227.2135 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 148 | 48158198 | 6228 | 149.472 | 6.228 | 8 | 8 | 3B+1S | 0 | 1135 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39601224 | 1432 | 229.9294 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 125 | 148 | 48164477 | 6279 | 150.696 | 6.279 | 7.1 | 7.1 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39602660 | 1436 | 228.6988 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 125 | 145 | 48170777 | 6300 | 151.2 | 6.3 | 5.9 | 7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39604120 | 1460 | 231.746 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 | 0.97 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 126 | 143 | 48176877 | 6100 | 146.4 | 6.1 | 5 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39605552 | 1432 | 234.7541 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 124 | 145 | 48182668 | 5791 | 138.984 | 5.791 | 4.1 | 5.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39606908 | 1356 | 234.1564 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 19 | A ONG | 17.5 | 128 | 140 | 48188459 | 5791 | 138.984 | 5.791 | 3.8 | 3.8 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39608264 | 1356 | 234.1564 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 17.3 | 130 | 130 | 48194250 | 5791 | 138.984 | 5.791 | 2.7 | 2.7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39609620 | 1356 | 234.1564 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.9 | 128 | 134 | 48199761 | 5511 | 132.264 | 5.511 | 2.3 | 2.3 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39610932 | 1312 | 238.0693 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 128 | 133 | 48205467 | 5706 | 136.944 | 5.706 | 2 | 2 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39612292 | 1360 | 238.3456 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 80 | 56.338 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 126 | 131 | 48211070 | 5603 | 134.472 | 5.603 | 1.7 | 1.7 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39613596 | 1304 | 232.7325 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 133 | 128 | 48216310 | 5240 | 125.76 | 5.24 | 1.3 | 1.3 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39614908 | 1312 | 250.3817 | 0% | 100% | 100% | 100% | 100% | 0% | 8978771 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 48221779 | 5469 | 131.256 | 5.469 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39616160 | 1252 | 228.9267 | 0% | 0% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 133 | 48227161 | 5382 | 129.168 | 5.382 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39617396 | 1236 | 229.6544 | 0% | 0% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 132 | 131 | 48232517 | 5356 | 128.544 | 5.356 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39618620 | 1224 | 228.5288 | 0% | 0% | 100% | 100% | 100% | 0% | 8978771 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 139 | 48237815 | 5298 | 127.152 | 5.298 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1135 | N/A | N/A | N/A | N/A | 39619852 | 1232 | 232.5406 | 0% | 0% | 100% | 100% | 100% | 0% | 8978771 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 100 | 48241953 | 4138 | 99.312 | 4.138 | 2.5 | 2.5 | 2B | 0 | 0 | 1187 | 0 | 1136 | N/A | N/A | N/A | N/A | 39620720 | 868 | 209.7632 | 0% | 0% | 100% | 0% | 100% | 40% | 8980073 | 1302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 91 | 48245844 | 3891 | 93.384 | 3.891 | 4.2 | 4.2 | 2B | 0 | 0 | 1127 | 0 | 1105 | N/A | N/A | N/A | N/A | 39621476 | 756 | 194.2945 | 0% | 0% | 100% | 0% | 100% | 40% | 8981600 | 1527 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.2917 | 123794 | 123794 | 123.794 | 123.794 | [13 empty] | 27400 | 221.3354 | [6 empty] | 7818 | 7818 | 1.025 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (50%)
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 9:00am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 18, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
SP2 - STOPPED @ 6:01 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE UNREACH THE SET OF 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE DUE TO LOW OF DISCHARGE
BP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## AUG 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27048 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48245844 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39621476 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8981600 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 91 | 48249448 | 3604 | 86.496 | 3.604 | 5.8 | 5.8 | 2B | 0 | 0 | 1097 | 0 | 1086 | N/A | N/A | N/A | N/A | 39622160 | 684 | 189.7891 | 0% | 0% | 100% | 0% | 100% | 45% | 8983141 | 1541 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 86 | 48253156 | 3708 | 88.992 | 3.708 | 7.4 | 7.4 | 2B | 0 | 0 | 1057 | 0 | 1066 | N/A | N/A | N/A | N/A | 39622852 | 692 | 186.6235 | 0% | 0% | 100% | 0% | 100% | 45% | 8984729 | 1588 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 87 | 48256597 | 3441 | 82.584 | 3.441 | 9 | 9 | 2B | 0 | 0 | 1056 | 0 | 1065 | N/A | N/A | N/A | N/A | 39623468 | 616 | 179.0177 | 0% | 0% | 100% | 0% | 100% | 45% | 8986191 | 1462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 90 | 48260205 | 3608 | 86.592 | 3.608 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1065 | N/A | N/A | N/A | N/A | 39624108 | 640 | 177.3836 | 0% | 0% | 100% | 0% | 100% | 45% | 8987493 | 1302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 105 | 48264333 | 4128 | 99.072 | 4.128 | 9.5 | 9.5 | 2B | 0 | 0 | 1057 | 0 | 1116 | N/A | N/A | N/A | N/A | 39624780 | 672 | 162.7907 | 0% | 0% | 100% | 0% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 123 | 124 | 48269295 | 4962 | 119.088 | 4.962 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39625716 | 936 | 188.6336 | 0% | 0% | 100% | 0% | 100% | 0% | 8987493 | 0 | 0.96 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 145 | 48275337 | 6042 | 145.008 | 6.042 | 9.5 | 9.5 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39627080 | 1364 | 225.7531 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 152 | 48281566 | 6229 | 149.496 | 6.229 | 9 | 9 | 3B+1S | 0 | 1158 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39628496 | 1416 | 227.3238 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 144 | 48287854 | 6288 | 150.912 | 6.288 | 8.1 | 8.1 | 3B+1S | 0 | 1158 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39629932 | 1436 | 228.3715 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 127 | 149 | 48294176 | 6322 | 151.728 | 6.322 | 6.7 | 7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39631356 | 1424 | 225.2452 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 126 | 146 | 48300070 | 5894 | 141.456 | 5.894 | 6 | 6.9 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39632772 | 1416 | 240.2443 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.3 | 124 | 155 | 48306478 | 6408 | 153.792 | 6.408 | 4.9 | 5.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39634244 | 1472 | 229.7129 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 19 | A ONG | 17.5 | 122 | 152 | 48312469 | 5991 | 143.784 | 5.991 | 3.7 | 3.7 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39635692 | 1448 | 241.6959 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 138 | 48317840 | 5371 | 128.904 | 5.371 | 3.3 | 3.3 | 3B+1S | 0 | 1065 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39636924 | 1232 | 229.38 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 | 1.46 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 129 | 48323481 | 5641 | 135.384 | 5.641 | 2.9 | 2.9 | 3B+1S | 0 | 1065 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39638252 | 1328 | 235.4193 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 48328893 | 5412 | 129.888 | 5.412 | 2.6 | 2.6 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39639548 | 1296 | 239.4678 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 48334523 | 5630 | 135.12 | 5.63 | 2.4 | 2.4 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39640900 | 1352 | 240.1421 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 48339975 | 5452 | 130.848 | 5.452 | 2.1 | 2.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39642196 | 1296 | 237.7109 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 135 | 48345523 | 5548 | 133.152 | 5.548 | 1.9 | 1.9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39643532 | 1336 | 240.8075 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 133 | 48350891 | 5368 | 128.832 | 5.368 | 1.7 | 1.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39644824 | 1292 | 240.6855 | 0% | 100% | 100% | 100% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 154 | 48355846 | 4955 | 118.92 | 4.955 | 1.3 | 1.3 | 2B+1S | 0 | 996 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39645908 | 1084 | 218.7689 | 0% | 100% | 100% | 0% | 100% | 0% | 8987493 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 108 | 48360648 | 4802 | 115.248 | 4.802 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39646840 | 932 | 194.0858 | 0% | 0% | 100% | 0% | 100% | 0% | 8987493 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 102 | 48364806 | 4158 | 99.792 | 4.158 | 2.3 | 2.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39647724 | 884 | 212.6022 | 0% | 0% | 100% | 0% | 100% | 40% | 8988696 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 93 | 48368746 | 3940 | 94.56 | 3.94 | 3.7 | 3.7 | 2B | 0 | 0 | 1117 | 0 | 1116 | N/A | N/A | N/A | N/A | 39648524 | 800 | 203.0457 | 0% | 0% | 100% | 0% | 100% | 40% | 8990079 | 1383 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.4167 | 122902 | 122902 | 122.902 | 122.902 | [13 empty] | 27048 | 220.0778 | [6 empty] | 8479 | 8479 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 10:00am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 20, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 9:01 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE UNREACH THE SET OF 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE DUE TO LOW OF DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## AUG 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26896 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48368746 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39648524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8990079 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 88 | 48372455 | 3709 | 89.016 | 3.709 | 5.4 | 5.4 | 2B | 0 | 0 | 1117 | 0 | 1116 | N/A | N/A | N/A | N/A | 39649256 | 732 | 197.3578 | 0% | 0% | 100% | 0% | 100% | 45% | 8991626 | 1547 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 112 | 48376040 | 3585 | 86.04 | 3.585 | 7 | 7 | 2B | 0 | 0 | 1077 | 0 | 1087 | N/A | N/A | N/A | N/A | 39649916 | 660 | 184.1004 | 0% | 0% | 100% | 0% | 100% | 45% | 8993152 | 1526 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 89 | 48381001 | 4961 | 119.064 | 4.961 | 8.4 | 8.4 | 2B | 0 | 0 | 1077 | 0 | 1087 | N/A | N/A | N/A | N/A | 39650823 | 907 | 182.826 | 0% | 0% | 100% | 0% | 100% | 45% | 8995100 | 1948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 86 | 48383368 | 2367 | 56.808 | 2.367 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1006 | N/A | N/A | N/A | N/A | 39651236 | 413 | 174.4825 | 0% | 0% | 100% | 0% | 100% | 45% | 8995433 | 333 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 103 | 48387479 | 4111 | 98.664 | 4.111 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1187 | N/A | N/A | N/A | N/A | 39651928 | 692 | 168.3289 | 0% | 0% | 100% | 0% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 118 | 48392156 | 4677 | 112.248 | 4.677 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39652800 | 872 | 186.4443 | 0% | 0% | 100% | 0% | 100% | 0% | 8995433 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 150 | 48398484 | 6328 | 151.872 | 6.328 | 8.9 | 8.9 | 3B+1S | 0 | 1107 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39654212 | 1412 | 223.1353 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 48404739 | 6255 | 150.12 | 6.255 | 8 | 8 | 3B+1S | 0 | 1108 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39655620 | 1408 | 225.0999 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 128 | 149 | 48410952 | 6213 | 149.112 | 6.213 | 7.2 | 7.2 | 3B+1S | 0 | 1108 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39657028 | 1408 | 226.6216 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 127 | 145 | 48417124 | 6172 | 148.128 | 6.172 | 6.2 | 6.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39658452 | 1424 | 230.7194 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 | 1.42 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 128 | 140 | 48423179 | 6055 | 145.32 | 6.055 | 5.3 | 5.3 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39659852 | 1400 | 231.2139 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.3 | 131 | 138 | 48429146 | 5967 | 143.208 | 5.967 | 4.7 | 4.7 | 3B+1S | 0 | 1056 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39661228 | 1376 | 230.6016 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 132 | 48434877 | 5731 | 137.544 | 5.731 | 4.3 | 4.3 | 3B+1S | 0 | 1024 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39662556 | 1328 | 231.7222 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 135 | 48440189 | 5312 | 127.488 | 5.312 | 4 | 4 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39663808 | 1252 | 235.6928 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 130 | 48445703 | 5514 | 132.336 | 5.514 | 3.8 | 3.8 | 3B+1S | 0 | 1024 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39665116 | 1308 | 237.2144 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 130 | 48450972 | 5269 | 126.456 | 5.269 | 3.7 | 3.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39666380 | 1264 | 239.8937 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 129 | 48456541 | 5569 | 133.656 | 5.569 | 3.7 | 3.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39667716 | 1336 | 239.8994 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 129 | 48461887 | 5346 | 128.304 | 5.346 | 3.6 | 3.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39668984 | 1268 | 237.1867 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 48467540 | 5653 | 135.672 | 5.653 | 3.6 | 3.6 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39670324 | 1340 | 237.0423 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 132 | 48473051 | 5511 | 132.264 | 5.511 | 3.5 | 3.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39671628 | 1304 | 236.6177 | 0% | 100% | 100% | 100% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 103 | 126 | 48478202 | 5151 | 123.624 | 5.151 | 2.7 | 2.7 | 2B+1S | 0 | 1128 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39672724 | 1096 | 212.7742 | 0% | 100% | 100% | 0% | 100% | 0% | 8995433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 123 | 48483258 | 5056 | 121.344 | 5.056 | 1.9 | 1.9 | 2B+1S | 0 | 1056 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39673798 | 1074 | 212.4209 | 0% | 100% | 100% | 0% | 100% | 0% | 8995433 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 101 | 48487456 | 4198 | 100.752 | 4.198 | 2.8 | 2.8 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39674668 | 870 | 207.2415 | 0% | 0% | 100% | 0% | 100% | 35% | 8996526 | 1093 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 94 | 48491458 | 4002 | 96.048 | 4.002 | 4.4 | 4.4 | 2B | 0 | 0 | 1117 | 0 | 1097 | N/A | N/A | N/A | N/A | 39675420 | 752 | 187.906 | 0% | 0% | 100% | 0% | 100% | 35% | 8997893 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.2083 | 122712 | 122712 | 122.712 | 122.712 | [13 empty] | 26896 | 219.1799 | [6 empty] | 7814 | 7814 | 1.2183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 CLOSED @ 3:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 10:00am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 21, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
XCV1 -OPENED @ 10:01 PM (35%)

## AUG 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26360 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48491458 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39675420 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 8997893 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 92 | 48495068 | 3610 | 86.64 | 3.61 | 5.8 | 5.8 | 2B | 0 | 0 | 1097 | 0 | 1077 | N/A | N/A | N/A | N/A | 39676092 | 672 | 186.1496 | 0% | 0% | 100% | 0% | 100% | 40% | 8999227 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 48498754 | 3686 | 88.464 | 3.686 | 7.2 | 7.2 | 2B | 0 | 0 | 1097 | 0 | 1076 | N/A | N/A | N/A | N/A | 39676768 | 676 | 183.3966 | 0% | 0% | 100% | 0% | 100% | 40% | 9000587 | 1360 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 87 | 48502528 | 3774 | 90.576 | 3.774 | 8.5 | 8.5 | 2B | 0 | 0 | 1076 | 0 | 1066 | N/A | N/A | N/A | N/A | 39677436 | 668 | 177.0005 | 0% | 0% | 100% | 0% | 100% | 40% | 9001915 | 1328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 48506239 | 3711 | 89.064 | 3.711 | 9.7 | 9.7 | 2B | 0 | 0 | 1047 | 0 | 1047 | N/A | N/A | N/A | N/A | 39678076 | 640 | 172.4603 | 0% | 0% | 100% | 0% | 100% | 40% | 9002937 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 99 | 48510157 | 3918 | 94.032 | 3.918 | 9.7 | 9.7 | 2B | 0 | 0 | 1027 | 0 | 1016 | N/A | N/A | N/A | N/A | 39678676 | 600 | 153.1394 | 0% | 0% | 100% | 0% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 113 | 48514889 | 4732 | 113.568 | 4.732 | 9.7 | 9.7 | 2B | 0 | 0 | 1188 | 0 | 1137 | N/A | N/A | N/A | N/A | 39679556 | 880 | 185.9679 | 0% | 0% | 100% | 0% | 100% | 0% | 9002937 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 137 | 48520553 | 5664 | 135.936 | 5.664 | 9.7 | 9.7 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39680712 | 1156 | 204.096 | 0% | 0% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 48526507 | 5954 | 142.896 | 5.954 | 9.6 | 9.6 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39682024 | 1312 | 220.3561 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 153 | 48532669 | 6162 | 147.888 | 6.162 | 9 | 9 | 3B+1S | 0 | 1097 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39683400 | 1376 | 223.3041 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 147 | 48538929 | 6260 | 150.24 | 6.26 | 8.2 | 8.2 | 3B+1S | 0 | 1097 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39684796 | 1396 | 223.0032 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 | 0.94 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 150 | 48545176 | 6247 | 149.928 | 6.247 | 7.2 | 7.2 | 3B+1S | 0 | 1148 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39686220 | 1424 | 227.9494 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 144 | 48551366 | 6190 | 148.56 | 6.19 | 6.3 | 6.3 | 3B+1S | 0 | 1148 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39687690 | 1470 | 237.4798 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 124 | 139 | 48557344 | 5978 | 143.472 | 5.978 | 5.3 | 5.3 | 3B+1S | 0 | 1148 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39689044 | 1354 | 226.4972 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 139 | 48562926 | 5582 | 133.968 | 5.582 | 4.6 | 4.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39690360 | 1316 | 235.7578 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 140 | 48568341 | 5415 | 129.96 | 5.415 | 3.6 | 3.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39691532 | 1172 | 216.4358 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 133 | 48573835 | 5494 | 131.856 | 5.494 | 3.2 | 3.2 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39692820 | 1288 | 234.4376 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 48579631 | 5796 | 139.104 | 5.796 | 2.8 | 2.8 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39694188 | 1368 | 236.0248 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 48585162 | 5531 | 132.744 | 5.531 | 2.6 | 2.6 | 3B+1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39695472 | 1284 | 232.1461 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 143 | 48591161 | 5999 | 143.976 | 5.999 | 2.2 | 2.2 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39696852 | 1380 | 230.0383 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 137 | 48596828 | 5667 | 136.008 | 5.667 | 2 | 2 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39698156 | 1304 | 230.1041 | 0% | 100% | 100% | 100% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 48602319 | 5491 | 131.784 | 5.491 | 1.5 | 1.5 | 2B+1S | 0 | 1046 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39699260 | 1104 | 201.0563 | 0% | 100% | 100% | 0% | 100% | 0% | 9002937 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 115 | 48607233 | 4914 | 117.936 | 4.914 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39700192 | 932 | 189.6622 | 0% | 0% | 100% | 0% | 100% | 0% | 9002937 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 108 | 48611598 | 4365 | 104.76 | 4.365 | 2.2 | 2.2 | 2B | 0 | 0 | 1117 | 0 | 1148 | N/A | N/A | N/A | N/A | 39701036 | 844 | 193.3562 | 0% | 0% | 100% | 0% | 100% | 35% | 9003923 | 986 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 101 | 48615666 | 4068 | 97.632 | 4.068 | 3.3 | 3.3 | 2B | 0 | 0 | 1117 | 0 | 1147 | N/A | N/A | N/A | N/A | 39701780 | 744 | 182.8909 | 0% | 0% | 100% | 0% | 100% | 35% | 9004988 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0833 | 124208 | 124208 | 124.208 | 124.208 | [13 empty] | 26360 | 212.2247 | [6 empty] | 7095 | 7095 | 1.1417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV1 CLOSED @ 3:45 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:29 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
all motors fullspeed @ 10:00am, cannot reach the normal target discharge pressure.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 22, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
MERALCO POWER FLUCTUATION @9:20PM / RESUME @9:30PM NORMAL OPERATION
SP2 - STOPPED @ 9:20 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## AUG 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25930 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48615666 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39701780 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9004988 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 98 | 48619987 | 4321 | 103.704 | 4.321 | 4.9 | 4.9 | 2B | 0 | 0 | 1077 | 0 | 1097 | N/A | N/A | N/A | N/A | 39702556 | 776 | 179.5881 | 0% | 0% | 100% | 0% | 100% | 45% | 9006514 | 1526 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 93 | 48623987 | 4000 | 96 | 4 | 6.4 | 6.4 | 2B | 0 | 0 | 1046 | 0 | 1057 | N/A | N/A | N/A | N/A | 39703252 | 696 | 174 | 0% | 0% | 100% | 0% | 100% | 45% | 9007944 | 1430 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 93 | 48627635 | 3648 | 87.552 | 3.648 | 7.7 | 7.7 | 2B | 0 | 0 | 1044 | 0 | 1057 | N/A | N/A | N/A | N/A | 39703856 | 604 | 165.5702 | 0% | 0% | 100% | 0% | 100% | 45% | 9009193 | 1249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 92 | 48631528 | 3893 | 93.432 | 3.893 | 9.1 | 9.1 | 2B | 0 | 0 | 1046 | 0 | 1057 | N/A | N/A | N/A | N/A | 39704500 | 644 | 165.4251 | 0% | 0% | 100% | 0% | 100% | 45% | 9010474 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 141 | 48635533 | 4005 | 96.12 | 4.005 | 9.7 | 9.7 | 2B | 0 | 0 | 1047 | 0 | 1057 | N/A | N/A | N/A | N/A | 39705140 | 640 | 159.8002 | 0% | 0% | 100% | 0% | 100% | 45% | 9010967 | 493 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 121 | 48640136 | 4603 | 110.472 | 4.603 | 9.7 | 9.7 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39705884 | 744 | 161.6337 | 0% | 0% | 100% | 0% | 100% | 0% | 9010967 | 0 | 0.99 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 137 | 48645539 | 5403 | 129.672 | 5.403 | 9.7 | 9.7 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39706980 | 1096 | 202.8503 | 0% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 149 | 146 | 48651411 | 5872 | 140.928 | 5.872 | 9.7 | 9.7 | 3B | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39708196 | 1216 | 207.0845 | 0% | 100% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 48657554 | 6143 | 147.432 | 6.143 | 9.3 | 9.3 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39709580 | 1384 | 225.2971 | 0% | 100% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 48663539 | 5985 | 143.64 | 5.985 | 8.7 | 8.2 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39710884 | 1304 | 217.878 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 142 | 48669670 | 6131 | 147.144 | 6.131 | 8.1 | 7.2 | 3B+1S | 1107 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39712308 | 1424 | 232.2623 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 48676082 | 6412 | 153.888 | 6.412 | 7.2 | 7.2 | 3B+1S | 1107 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39713740 | 1432 | 223.3313 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 148 | 48681832 | 5750 | 138 | 5.75 | 6.6 | 6.6 | 3B+1S | 1056 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39715092 | 1352 | 235.1304 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 48687713 | 5881 | 141.144 | 5.881 | 6.1 | 6.1 | 3B+1S | 1056 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39716412 | 1320 | 224.4516 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 | 1.37 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 144 | 48693589 | 5876 | 141.024 | 5.876 | 5.7 | 5.7 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39717760 | 1348 | 229.4078 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 138 | 48699300 | 5711 | 137.064 | 5.711 | 5.3 | 5.3 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39719092 | 1332 | 233.2341 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 48705015 | 5715 | 137.16 | 5.715 | 4.9 | 4.9 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39720420 | 1328 | 232.371 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 48710749 | 5734 | 137.616 | 5.734 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39721744 | 1324 | 230.9034 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 134 | 48716420 | 5671 | 136.104 | 5.671 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 39723036 | 1292 | 227.8258 | 100% | 0% | 100% | 100% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 126 | 48721755 | 5335 | 128.04 | 5.335 | 3.3 | 3.3 | 2B+1S | 1096 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39724124 | 1088 | 203.9363 | 100% | 0% | 100% | 0% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 48727017 | 5262 | 126.288 | 5.262 | 2.7 | 2.7 | 2B+1S | 1056 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39725180 | 1056 | 200.6842 | 100% | 0% | 100% | 0% | 100% | 0% | 9010967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 121 | 48732169 | 5152 | 123.648 | 5.152 | 2.3 | 2.3 | 2B+1S | 1056 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39726256 | 1076 | 208.8509 | 100% | 0% | 100% | 0% | 100% | 0% | 9010967 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 97 | 48736224 | 4055 | 97.32 | 4.055 | 3.5 | 3.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39727000 | 744 | 183.4772 | 0% | 0% | 100% | 0% | 100% | 45% | 9012290 | 1323 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 101 | 48740173 | 3949 | 94.776 | 3.949 | 5.1 | 5.1 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39727710 | 710 | 179.7924 | 0% | 0% | 100% | 0% | 100% | 45% | 9013658 | 1368 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 127.0833 | 124507 | 124507 | 124.507 | 124.507 | [13 empty] | 25930 | 208.2614 | [6 empty] | 8670 | 8670 | 1.1317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:29 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 STOPPED @ 10:11 AM DUE TO TEST RUNNING OF SP1
SP1 -START @ 10:12 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 23, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (45%)

## AUG 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25950 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48740173 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39727710 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9013658 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 94 | 48744122 | 3949 | 94.776 | 3.949 | 6.5 | 6.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39728420 | 710 | 179.7924 | 0% | 0% | 100% | 0% | 100% | 45% | 9015027 | 1369 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 94 | 48748090 | 3968 | 95.232 | 3.968 | 7.8 | 7.8 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39729140 | 720 | 181.4516 | 0% | 0% | 100% | 0% | 100% | 45% | 9016275 | 1248 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 102 | 48752213 | 4123 | 98.952 | 4.123 | 8.9 | 8.9 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39729880 | 740 | 179.481 | 0% | 0% | 100% | 0% | 100% | 45% | 9017435 | 1160 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 100 | 48756336 | 4123 | 98.952 | 4.123 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39730620 | 740 | 179.481 | 0% | 0% | 100% | 0% | 100% | 45% | 9017995 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 109 | 48760609 | 4273 | 102.552 | 4.273 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39731340 | 720 | 168.4999 | 0% | 0% | 100% | 0% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 129 | 48764882 | 4273 | 102.552 | 4.273 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 39732060 | 720 | 168.4999 | 0% | 0% | 100% | 0% | 100% | 0% | 9017995 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 143 | 48770527 | 5645 | 135.48 | 5.645 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39733212 | 1152 | 204.0744 | 0% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 48776419 | 5892 | 141.408 | 5.892 | 9.5 | 9.5 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39734476 | 1264 | 214.5282 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 149 | 48782723 | 6304 | 151.296 | 6.304 | 8.9 | 8.9 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39735876 | 1400 | 222.0812 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 156 | 48788894 | 6171 | 148.104 | 6.171 | 8.4 | 8.2 | 3B+1S | 1118 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39737244 | 1368 | 221.6821 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 | 0.88 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 149 | 48795076 | 6182 | 148.368 | 6.182 | 7.3 | 7.2 | 3B+1S | 1158 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39738630 | 1386 | 224.1993 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 146 | 48801259 | 6183 | 148.392 | 6.183 | 6.4 | 6.4 | 3B+1S | 1158 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39740016 | 1386 | 224.163 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 145 | 48807335 | 6076 | 145.824 | 6.076 | 5.5 | 5.5 | 3B+1S | 1158 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39741396 | 1380 | 227.1231 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 139 | 48813284 | 5949 | 142.776 | 5.949 | 4.9 | 4.9 | 3B+1S | 1065 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39742724 | 1328 | 223.2308 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 133 | 48819003 | 5719 | 137.256 | 5.719 | 4.3 | 4.3 | 3B+1S | 1056 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39744028 | 1304 | 228.0119 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 137 | 48824683 | 5680 | 136.32 | 5.68 | 3.8 | 3.8 | 3B+1S | 1056 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39745324 | 1296 | 228.169 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 48830329 | 5646 | 135.504 | 5.646 | 3.4 | 3.4 | 3B+1S | 1056 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39746620 | 1296 | 229.543 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 133 | 48835911 | 5582 | 133.968 | 5.582 | 3 | 3 | 3B+1S | 1056 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39747904 | 1284 | 230.0251 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 48841464 | 5553 | 133.272 | 5.553 | 2.7 | 2.7 | 3B+1S | 1065 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39749180 | 1276 | 229.7857 | 100% | 0% | 100% | 100% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 125 | 48846939 | 5475 | 131.4 | 5.475 | 2 | 2 | 2B+1S | 1097 | 0 | 1168 | 0 | 1168 | N/A | N/A | N/A | N/A | 39750268 | 1088 | 198.7215 | 100% | 0% | 100% | 0% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 125 | 48852109 | 5170 | 124.08 | 5.17 | 1.4 | 1.4 | 2B+1S | 1097 | 0 | 1168 | 0 | 1168 | N/A | N/A | N/A | N/A | 39751284 | 1016 | 196.5184 | 100% | 0% | 100% | 0% | 100% | 0% | 9017995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 110 | 48857190 | 5081 | 121.944 | 5.081 | 1.3 | 1.3 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39752272 | 988 | 194.4499 | 0% | 0% | 100% | 0% | 100% | 0% | 9017995 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 95 | 48861216 | 4026 | 96.624 | 4.026 | 2.5 | 2.5 | 2B | 0 | 0 | 1087 | 0 | 1057 | N/A | N/A | N/A | N/A | 39752972 | 700 | 173.8698 | 0% | 0% | 100% | 0% | 100% | 40% | 9019272 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 95 | 48865233 | 4017 | 96.408 | 4.017 | 4.3 | 4.3 | 2B | 0 | 0 | 1087 | 0 | 1057 | N/A | N/A | N/A | N/A | 39753660 | 688 | 171.2721 | 0% | 0% | 100% | 0% | 100% | 40% | 9020688 | 1416 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.0833 | 125060 | 125060 | 125.06 | 125.06 | [13 empty] | 25950 | 207.5004 | [6 empty] | 7030 | 7030 | 1.0617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:39 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP1 - FAULT @ 10:01 AM DUE TO OVER VOLTAGE, RESTART @ 10:03AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 24, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 9:01 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (40%)

## AUG 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25984 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48865233 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39753660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9020688 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 98 | 48869005 | 3772 | 90.528 | 3.772 | 5.3 | 5.3 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39754290 | 630 | 167.0201 | 0% | 0% | 100% | 0% | 100% | 40% | 9021898 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 100 | 48872778 | 3773 | 90.552 | 3.773 | 6.7 | 6.7 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39754920 | 630 | 166.9759 | 0% | 0% | 100% | 0% | 100% | 45% | 9023108 | 1210 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 48876550 | 3772 | 90.528 | 3.772 | 8.1 | 8.1 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39755550 | 630 | 167.0201 | 0% | 0% | 100% | 0% | 100% | 45% | 9024320 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 129 | 93 | 48880323 | 3773 | 90.552 | 3.773 | 9 | 9 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39756180 | 630 | 166.9759 | 0% | 0% | 100% | 0% | 100% | 45% | 9025531 | 1211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 108 | 48884661 | 4338 | 104.112 | 4.338 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39756836 | 656 | 151.2218 | 0% | 0% | 100% | 0% | 100% | 45% | 9026162 | 631 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 132 | 118 | 48889624 | 4963 | 119.112 | 4.963 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1057 | N/A | N/A | N/A | N/A | 39757628 | 792 | 159.5809 | 0% | 0% | 100% | 0% | 100% | 0% | 9026162 | 0 | 0.99 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 48895589 | 5965 | 143.16 | 5.965 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1107 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39758936 | 1308 | 219.2791 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 151 | 48901826 | 6237 | 149.688 | 6.237 | 8.7 | 8.7 | 3B+1S | 1056 | 0 | 1166 | 1187 | 1167 | N/A | N/A | N/A | N/A | 39760324 | 1388 | 222.5429 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 48908254 | 6428 | 154.272 | 6.428 | 8.3 | 8.3 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39761724 | 1400 | 217.7971 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 48914229 | 5975 | 143.4 | 5.975 | 7.6 | 8.3 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39763044 | 1320 | 220.9205 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 | 1.34 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 48920576 | 6347 | 152.328 | 6.347 | 7 | 7.6 | 3B+1S | 1056 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39764480 | 1436 | 226.2486 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 48926815 | 6239 | 149.736 | 6.239 | 6.5 | 6.5 | 3B+1S | 1055 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39765856 | 1376 | 220.5482 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 48932591 | 5776 | 138.624 | 5.776 | 6 | 6 | 3B+1S | 1055 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39767188 | 1332 | 230.6094 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 137 | 48938058 | 5467 | 131.208 | 5.467 | 5.6 | 5.6 | 3B+1S | 1034 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39768452 | 1264 | 231.2054 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 132 | 48943668 | 5610 | 134.64 | 5.61 | 5.2 | 5.2 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39769756 | 1304 | 232.4421 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 130 | 48949245 | 5577 | 133.848 | 5.577 | 5 | 5 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39771076 | 1320 | 236.6864 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 48954890 | 5645 | 135.48 | 5.645 | 4.7 | 4.7 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39772388 | 1312 | 232.4181 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 48960551 | 5661 | 135.864 | 5.661 | 4.4 | 4.4 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39773700 | 1312 | 231.7612 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 48966339 | 5788 | 138.912 | 5.788 | 4.1 | 4.1 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39775044 | 1344 | 232.2046 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 125 | 48971728 | 5389 | 129.336 | 5.389 | 3.5 | 3.5 | 2B+1S | 1066 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39776148 | 1104 | 204.8618 | 100% | 0% | 100% | 100% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 126 | 48976927 | 5199 | 124.776 | 5.199 | 2.9 | 2.9 | 2B+1S | 1066 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39777180 | 1032 | 198.4997 | 100% | 0% | 100% | 0% | 100% | 0% | 9026162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 112 | 48982157 | 5230 | 125.52 | 5.23 | 2.4 | 2.4 | 2B+1S | 1066 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39778252 | 1072 | 204.9713 | 100% | 0% | 100% | 0% | 100% | 0% | 9026162 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 98 | 48986310 | 4153 | 99.672 | 4.153 | 3.3 | 3.3 | 2B | 0 | 0 | 1057 | 0 | 1087 | N/A | N/A | N/A | N/A | 39778972 | 720 | 173.3686 | 0% | 0% | 100% | 0% | 100% | 40% | 9027248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 91 | 48990207 | 3897 | 93.528 | 3.897 | 4.7 | 4.7 | 2B | 0 | 0 | 1057 | 0 | 1087 | N/A | N/A | N/A | N/A | 39779644 | 672 | 172.4403 | 0% | 0% | 100% | 0% | 100% | 40% | 9028557 | 1309 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.875 | 124974 | 124974 | 124.974 | 124.974 | [13 empty] | 25984 | 207.9152 | [6 empty] | 7869 | 6783 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP1 - FAULT @ 10:01 AM DUE TO OVER VOLTAGE, RESTART @ 10:03AM, NORMAL OPERATION
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 25, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:01 PM DUE TO PARAMETER CAPACITY OF 2.4 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (40%)

## AUG 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26784 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 48990207 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39779644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9028557 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 93 | 48993877 | 3670 | 88.08 | 3.67 | 5.8 | 5.8 | 2B | 0 | 0 | 1016 | 0 | 1048 | N/A | N/A | N/A | N/A | 39780238 | 594 | 161.8529 | 0% | 0% | 100% | 0% | 100% | 40% | 9029769 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 48997539 | 3662 | 87.888 | 3.662 | 7.3 | 7.3 | 2B | 0 | 0 | 1016 | 0 | 1048 | N/A | N/A | N/A | N/A | 39780837 | 599 | 163.5718 | 0% | 0% | 100% | 0% | 100% | 40% | 9030979 | 1210 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 49001205 | 3666 | 87.984 | 3.666 | 8.6 | 8.6 | 2B | 0 | 0 | 1016 | 0 | 1048 | N/A | N/A | N/A | N/A | 39781436 | 599 | 163.3933 | 0% | 0% | 100% | 0% | 100% | 40% | 9032206 | 1227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 92 | 49005058 | 3853 | 92.472 | 3.853 | 9.5 | 9.5 | 2B | 0 | 0 | 1016 | 0 | 1048 | N/A | N/A | N/A | N/A | 39782048 | 612 | 158.8373 | 0% | 0% | 100% | 0% | 100% | 40% | 9033282 | 1076 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 101 | 49009210 | 4152 | 99.648 | 4.152 | 9.5 | 9.5 | 2B | 0 | 0 | 1016 | 0 | 1048 | N/A | N/A | N/A | N/A | 39782668 | 620 | 149.3256 | 0% | 0% | 100% | 0% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 132 | 49014140 | 4930 | 118.32 | 4.93 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1048 | N/A | N/A | N/A | N/A | 39783620 | 952 | 193.1034 | 0% | 0% | 100% | 0% | 100% | 0% | 9033282 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 146 | 49020619 | 6479 | 155.496 | 6.479 | 9.3 | 9.3 | 3B+1S | 1045 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39785000 | 1380 | 212.9958 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 156 | 49026853 | 6234 | 149.616 | 6.234 | 8.6 | 8.6 | 3B+1S | 1087 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39786380 | 1380 | 221.3667 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 49033342 | 6489 | 155.736 | 6.489 | 7.9 | 7.9 | 3B+1S | 1127 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39787804 | 1424 | 219.4483 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 145 | 49039414 | 6072 | 145.728 | 6.072 | 7 | 8.2 | 3B+1S | 1127 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39789208 | 1404 | 231.2253 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 | 1.11 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 150 | 49045630 | 6216 | 149.184 | 6.216 | 6.4 | 7.2 | 3B+1S | 1157 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39790636 | 1428 | 229.7297 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 146 | 49051861 | 6231 | 149.544 | 6.231 | 5.2 | 5.2 | 3B+1S | 1158 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39792068 | 1432 | 229.8186 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 144 | 49058038 | 6177 | 148.248 | 6.177 | 4.4 | 4.4 | 3B+1S | 1158 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39793480 | 1412 | 228.5899 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 123 | 140 | 49063463 | 5425 | 130.2 | 5.425 | 3.4 | 3.4 | 3B+1S | 1157 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39794856 | 1376 | 253.6406 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 131 | 49068993 | 5530 | 132.72 | 5.53 | 3.1 | 3.1 | 3B+1S | 1023 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39796088 | 1232 | 222.7848 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 49074433 | 5440 | 130.56 | 5.44 | 3.1 | 3.1 | 3B+1S | 1023 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39797388 | 1300 | 238.9706 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 136 | 49080019 | 5586 | 134.064 | 5.586 | 2.9 | 2.9 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39798720 | 1332 | 238.4533 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 49085701 | 5682 | 136.368 | 5.682 | 2.6 | 2.6 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39800052 | 1332 | 234.4245 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 49091399 | 5698 | 136.752 | 5.698 | 2.3 | 2.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39801372 | 1320 | 231.6602 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 135 | 49097003 | 5604 | 134.496 | 5.604 | 2.1 | 2.1 | 2B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39802692 | 1320 | 235.546 | 100% | 0% | 100% | 100% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 137 | 49102311 | 5308 | 127.392 | 5.308 | 1.6 | 1.6 | 2B+1S | 1045 | 0 | 1187 |  | 1187 | N/A | N/A | N/A | N/A | 39803722 | 1030 | 194.0467 | 100% | 0% | 100% | 0% | 100% | 0% | 9033282 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 118 | 49107580 | 5269 | 126.456 | 5.269 | 1.3 | 1.3 | 2B+1S | 1044 | 0 | 1187 |  | 1187 | N/A | N/A | N/A | N/A | 39804844 | 1122 | 212.9436 | 100% | 0% | 100% | 0% | 100% | 0% | 9033282 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 101 | 49111940 | 4360 | 104.64 | 4.36 | 1.9 | 1.9 | 2B | 0 | 0 | 1097 |  | 1107 | N/A | N/A | N/A | N/A | 39805700 | 856 | 196.3303 | 0% | 0% | 100% | 0% | 100% | 35% | 9034191 | 909 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 92 | 49116010 | 4070 | 97.68 | 4.07 | 3.2 | 3.2 | 2B | 0 | 0 | 1037 |  | 1057 | N/A | N/A | N/A | N/A | 39806428 | 728 | 178.8698 | 0% | 0% | 100% | 0% | 100% | 35% | 9035388 | 1197 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.25 | 125803 | 125803 | 125.803 | 125.803 | [13 empty] | 26784 | 212.9043 | [6 empty] | 6831 | 6831 | 1.165 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 CLOSED @ 3:51 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 26, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)

## AUG 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26948 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49116010 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39806428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9035388 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 120 | 49119803 | 3793 | 91.032 | 3.793 | 4.8 | 4.8 | 2B | 0 | 0 | 1036 | 0 | 1057 | N/A | N/A | N/A | N/A | 39807068 | 640 | 168.7319 | 0% | 0% | 100% | 0% | 100% | 40% | 9036802 | 1414 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 49123216 | 3413 | 81.912 | 3.413 | 6.1 | 6.1 | 2B | 0 | 0 | 1037 | 0 | 1056 | N/A | N/A | N/A | N/A | 39807656 | 588 | 172.2824 | 0% | 0% | 100% | 0% | 100% | 40% | 9038087 | 1285 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 87 | 49126867 | 3651 | 87.624 | 3.651 | 7.4 | 7.4 | 2B | 0 | 0 | 1016 | 0 | 1026 | N/A | N/A | N/A | N/A | 39808244 | 588 | 161.0518 | 0% | 0% | 100% | 0% | 100% | 40% | 9039439 | 1352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 94 | 49130534 | 3667 | 88.008 | 3.667 | 8.9 | 8.9 | 2B | 0 | 0 | 1017 | 0 | 1028 | N/A | N/A | N/A | N/A | 39808828 | 584 | 159.2582 | 0% | 0% | 100% | 0% | 100% | 40% | 9040788 | 1349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 106 | 49134728 | 4194 | 100.656 | 4.194 | 9.6 | 9.6 | 2B | 0 | 0 | 1016 | 0 | 1027 | N/A | N/A | N/A | N/A | 39809448 | 620 | 147.8302 | 0% | 0% | 100% | 0% | 100% | 40% | 9041314 | 526 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 123 | 132 | 49139771 | 5043 | 121.032 | 5.043 | 9.6 | 9.6 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39810316 | 868 | 172.1198 | 0% | 0% | 100% | 0% | 100% | 0% | 9041314 | 0 | 0.92 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 151 | 49145973 | 6202 | 148.848 | 6.202 | 9.2 | 9.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39811684 | 1368 | 220.574 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 49152224 | 6251 | 150.024 | 6.251 | 8.4 | 8.4 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39813084 | 1400 | 223.9642 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 141 | 49158562 | 6338 | 152.112 | 6.338 | 7.5 | 7.5 | 3B+1S | 1126 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39814516 | 1432 | 225.9388 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 49164800 | 6238 | 149.712 | 6.238 | 6.6 | 8.2 | 3B+1S | 1127 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39815948 | 1432 | 229.5608 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 148 | 49171064 | 6264 | 150.336 | 6.264 | 5.9 | 7.2 | 3B+1S | 1166 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39817356 | 1408 | 224.7765 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 146 | 49177228 | 6164 | 147.936 | 6.164 | 4.9 | 4.9 | 3B+1S | 1166 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39818764 | 1408 | 228.4231 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 141 | 49182920 | 5692 | 136.608 | 5.692 | 3.8 | 3.8 | 3B+1S | 1085 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39820104 | 1340 | 235.4181 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 136 | 49188641 | 5721 | 137.304 | 5.721 | 3.4 | 3.4 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39821460 | 1356 | 237.0215 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 49194264 | 5623 | 134.952 | 5.623 | 3.2 | 3.2 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39822788 | 1328 | 236.1729 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 134 | 49199843 | 5579 | 133.896 | 5.579 | 2.9 | 2.9 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39824108 | 1320 | 236.6015 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 49205405 | 5562 | 133.488 | 5.562 | 2.7 | 2.7 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39825420 | 1312 | 235.8864 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 137 | 49211042 | 5637 | 135.288 | 5.637 | 2.4 | 2.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39826752 | 1332 | 236.2959 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 49216671 | 5629 | 135.096 | 5.629 | 2.1 | 2.1 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39828068 | 1316 | 233.7893 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 136 | 49222285 | 5614 | 134.736 | 5.614 | 1.9 | 1.9 | 2B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39829388 | 1320 | 235.1265 | 100% | 0% | 100% | 100% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 133 | 132 | 49227740 | 5455 | 130.92 | 5.455 | 1.7 | 1.7 | 2B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39830684 | 1296 | 237.5802 | 100% | 0% | 100% | 0% | 100% | 0% | 9041314 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 145 | 49233146 | 5406 | 129.744 | 5.406 | 1.3 | 1.3 | 2B+1S | 1066 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39831808 | 1124 | 207.9171 | 100% | 0% | 100% | 0% | 100% | 0% | 9041314 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 107 | 49237558 | 4412 | 105.888 | 4.412 | 2 | 2 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39832668 | 860 | 194.9229 | 0% | 0% | 100% | 0% | 100% | 35% | 9042272 | 958 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 95 | 49241445 | 3887 | 93.288 | 3.887 | 3.2 | 3.2 | 2B | 0 | 0 | 1097 | 0 | 1146 | N/A | N/A | N/A | N/A | 39833376 | 708 | 182.1456 | 0% | 0% | 100% | 0% | 100% | 35% | 9043420 | 1148 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 128.2917 | 125435 | 125435 | 125.435 | 125.435 | [13 empty] | 26948 | 214.8364 | [6 empty] | 8032 | 8032 | 1.0733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV1 CLOSED @ 4:25 AM,WATER ELEVATION (9.6M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 27, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)

## AUG 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26588 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49241445 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39833376 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9043420 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 93 | 49245256 | 3811 | 91.464 | 3.811 | 4.9 | 4.9 | 2B | 0 | 0 | 1097 | 0 | 1046 | N/A | N/A | N/A | N/A | 39834044 | 668 | 175.2821 | 0% | 0% | 100% | 0% | 100% | 43% | 9044964 | 1544 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 92 | 49249117 | 3861 | 92.664 | 3.861 | 6.4 | 6.4 | 2B | 0 | 0 | 1097 | 0 | 1047 | N/A | N/A | N/A | N/A | 39834716 | 672 | 174.0482 | 0% | 0% | 100% | 0% | 100% | 43% | 9046434 | 1470 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 86 | 49252719 | 3602 | 86.448 | 3.602 | 8 | 8 | 2B | 0 | 0 | 1027 | 0 | 1006 | N/A | N/A | N/A | N/A | 39835296 | 580 | 161.0217 | 0% | 0% | 100% | 0% | 100% | 43% | 9047889 | 1455 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 94 | 49256327 | 3608 | 86.592 | 3.608 | 9.4 | 9.4 | 2B | 0 | 0 | 1026 | 0 | 1007 | N/A | N/A | N/A | N/A | 39835860 | 564 | 156.3193 | 0% | 0% | 100% | 0% | 100% | 43% | 9049248 | 1359 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 409 | 49260503 | 4176 | 100.224 | 4.176 | 9.7 | 9.7 | 2B | 0 | 0 | 1006 | 0 | 1117 | N/A | N/A | N/A | N/A | 39836476 | 616 | 147.5096 | 0% | 0% | 100% | 0% | 100% | 43% | 9049391 | 143 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 125 | 49265711 | 5208 | 124.992 | 5.208 | 9.7 | 9.7 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 39837388 | 912 | 175.1152 | 0% | 0% | 100% | 0% | 100% | 0% | 9049391 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 49271908 | 6197 | 148.728 | 6.197 | 9.3 | 9.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39838748 | 1360 | 219.461 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 49278140 | 6232 | 149.568 | 6.232 | 8.7 | 8.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39840140 | 1392 | 223.3633 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 156 | 49284359 | 6219 | 149.256 | 6.219 | 8 | 8 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39841524 | 1384 | 222.5438 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 170 | 49290609 | 6250 | 150 | 6.25 | 7.2 | 8.2 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39842921 | 1397 | 223.52 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 49296774 | 6165 | 147.96 | 6.165 | 6.4 | 7.2 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39844320 | 1399 | 226.9262 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 139 | 49302830 | 6056 | 145.344 | 6.056 | 5.7 | 5.7 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39845696 | 1376 | 227.2127 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 141 | 49308767 | 5937 | 142.488 | 5.937 | 5.2 | 5.2 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39847056 | 1360 | 229.0719 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 49314451 | 5684 | 136.416 | 5.684 | 4.8 | 4.8 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39848364 | 1308 | 230.1196 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 137 | 49320146 | 5695 | 136.68 | 5.695 | 4.4 | 4.4 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39849684 | 1320 | 231.7823 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 49325775 | 5629 | 135.096 | 5.629 | 4 | 4 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39851004 | 1320 | 234.4999 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 49331545 | 5770 | 138.48 | 5.77 | 3.6 | 3.6 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39852344 | 1340 | 232.2357 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 49337207 | 5662 | 135.888 | 5.662 | 3.3 | 3.3 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39853660 | 1316 | 232.4267 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 49343026 | 5819 | 139.656 | 5.819 | 2.9 | 2.9 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39854996 | 1336 | 229.5927 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 129 | 49348662 | 5636 | 135.264 | 5.636 | 2.7 | 2.7 | 2B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39856324 | 1328 | 235.6281 | 100% | 0% | 100% | 100% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 49354030 | 5368 | 128.832 | 5.368 | 2 | 2 | 2B+1S | 1044 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39857404 | 1080 | 201.1923 | 100% | 0% | 100% | 0% | 100% | 0% | 9049391 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 119 | 49359126 | 5096 | 122.304 | 5.096 | 1.5 | 1.5 | 2B+1S | 1074 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39858456 | 1052 | 206.4364 | 100% | 0% | 100% | 0% | 100% | 0% | 9049391 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 115 | 49363366 | 4240 | 101.76 | 4.24 | 2.4 | 2.4 | 2B | 0 | 0 | 1107 | 0 | 1096 | N/A | N/A | N/A | N/A | 39859236 | 780 | 183.9623 | 0% | 0% | 100% | 0% | 100% | 35% | 9050382 | 991 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 93 | 49367458 | 4092 | 98.208 | 4.092 | 3.6 | 3.6 | 2B | 0 | 0 | 1076 | 0 | 1027 | N/A | N/A | N/A | N/A | 39859964 | 728 | 177.9081 | 0% | 0% | 100% | 0% | 100% | 35% | 9051606 | 1224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 139.1667 | 126013 | 126013 | 126.013 | 126.013 | [13 empty] | 26588 | 210.9941 | [6 empty] | 8186 | 8186 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (43%)
XCV1 CLOSED @ 4:05 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 28, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)

## AUG 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26320 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49367458 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39859964 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9051606 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 115 | 49371066 | 3608 | 86.592 | 3.608 | 5.1 | 5.1 | 2B | 0 | 0 | 1077 | 0 | 1026 | N/A | N/A | N/A | N/A | 39860576 | 612 | 169.6231 | 0% | 0% | 100% | 0% | 100% | 42% | 9052998 | 1392 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 89 | 49375010 | 3944 | 94.656 | 3.944 | 6.7 | 6.7 | 2B | 0 | 0 | 1077 | 0 | 1026 | N/A | N/A | N/A | N/A | 39861252 | 676 | 171.3996 | 0% | 0% | 100% | 0% | 100% | 42% | 9054482 | 1484 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 121 | 49378436 | 3426 | 82.224 | 3.426 | 7.9 | 7.9 | 2B | 0 | 0 | 1037 | 0 | 1007 | N/A | N/A | N/A | N/A | 39861820 | 568 | 165.791 | 0% | 0% | 100% | 0% | 100% | 42% | 9055686 | 1204 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 89 | 49382129 | 3693 | 88.632 | 3.693 | 9.3 | 9.3 | 2B | 0 | 0 | 1037 | 0 | 1006 | N/A | N/A | N/A | N/A | 39862404 | 584 | 158.137 | 0% | 0% | 100% | 0% | 100% | 42% | 9057040 | 1354 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 103 | 49386193 | 4064 | 97.536 | 4.064 | 9.7 | 9.7 | 2B | 0 | 0 | 1006 | 0 | 1006 | N/A | N/A | N/A | N/A | 39862984 | 580 | 142.7165 | 0% | 0% | 100% | 0% | 100% | 42% | 9057181 | 141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 125 | 49391235 | 5042 | 121.008 | 5.042 | 9.7 | 9.7 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39863852 | 868 | 172.1539 | 0% | 0% | 100% | 0% | 100% | 0% | 9057181 | 0 | 1.38 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 147 | 49397340 | 6105 | 146.52 | 6.105 | 9.2 | 9.2 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39865164 | 1312 | 214.9058 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 49403738 | 6398 | 153.552 | 6.398 | 8.5 | 8.5 | 3B+1S | 1116 | 0 | 1186 | 1185 | 1145 | N/A | N/A | N/A | N/A | 39866564 | 1400 | 218.8184 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 49409867 | 6129 | 147.096 | 6.129 | 7.7 | 7.7 | 3B+1S | 1116 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39867948 | 1384 | 225.8117 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 146 | 49416066 | 6199 | 148.776 | 6.199 | 6.9 | 8.2 | 3B+1S | 1116 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39869348 | 1400 | 225.8429 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 | 1.4 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 49422248 | 6182 | 148.368 | 6.182 | 6 | 7.2 | 3B+1S | 1137 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39870756 | 1408 | 227.758 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 114 | 49428385 | 6137 | 147.288 | 6.137 | 5.1 | 5.1 | 3B+1S | 1136 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39872180 | 1424 | 232.0352 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 49434387 | 6002 | 144.048 | 6.002 | 4.5 | 4.5 | 3B+1S | 1044 | 0 | 1186 | 1185 | 1185 | N/A | N/A | N/A | N/A | 39873580 | 1400 | 233.2556 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 135 | 49440126 | 5739 | 137.736 | 5.739 | 4 | 4 | 3B+1S | 1044 | 0 | 1156 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39874912 | 1332 | 232.0962 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 130 | 49445648 | 5522 | 132.528 | 5.522 | 3.6 | 3.6 | 3B+1S | 1043 | 0 | 1156 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39876204 | 1292 | 233.9732 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 49451166 | 5518 | 132.432 | 5.518 | 3.3 | 3.3 | 3B+1S | 1043 | 0 | 1156 | 1185 | 1186 | N/A | N/A | N/A | N/A | 39877484 | 1280 | 231.9681 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 49456745 | 5579 | 133.896 | 5.579 | 3 | 3 | 3B+1S | 1045 | 0 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39878764 | 1280 | 229.4318 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 49462404 | 5659 | 135.816 | 5.659 | 2.7 | 2.7 | 3B+1S | 1043 | 0 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39880076 | 1312 | 231.8431 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 49467920 | 5516 | 132.384 | 5.516 | 2.4 | 2.4 | 3B+1S | 1044 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 39881332 | 1256 | 227.7012 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 49473327 | 5407 | 129.768 | 5.407 | 2.1 | 2.1 | 2B+1S | 1044 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 39882580 | 1248 | 230.8119 | 100% | 0% | 100% | 100% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 128 | 49478455 | 5128 | 123.072 | 5.128 | 1.7 | 1.7 | 2B+1S | 1044 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39883644 | 1064 | 207.4883 | 100% | 0% | 100% | 0% | 100% | 0% | 9057181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 120 | 49483471 | 5016 | 120.384 | 5.016 | 1.3 | 1.3 | 2B+1S | 1044 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39884668 | 1024 | 204.1467 | 100% | 0% | 100% | 0% | 100% | 0% | 9057181 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 110 | 49488020 | 4549 | 109.176 | 4.549 | 2.1 | 2.1 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39885588 | 920 | 202.2423 | 0% | 0% | 100% | 0% | 100% | 35% | 9058053 | 872 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 94 | 49491950 | 3930 | 94.32 | 3.93 | 3.5 | 3.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 39886284 | 696 | 177.0992 | 0% | 0% | 100% | 0% | 100% | 35% | 9059254 | 1201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.2917 | 124492 | 124492 | 124.492 | 124.492 | [13 empty] | 26320 | 211.4192 | [6 empty] | 7648 | 7648 | 1.1883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (42%)
XCV1 CLOSED @ 4:05 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 29, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)

## AUG 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ALEXANDER CABREROS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49491950 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39886284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9059254 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 88 | 49495863 | 3913 | 93.912 | 3.913 | 4.8 | 4.8 | 2B | 0 | 0 | 1026 | 0 | 1046 | N/A | N/A | N/A | N/A | 39886980 | 696 | 177.8686 | 0% | 0% | 100% | 0% | 100% | 40% | 9060698 | 1444 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 91 | 49499475 | 3612 | 86.688 | 3.612 | 6.3 | 6.3 | 2B | 0 | 0 | 1026 | 0 | 1046 | N/A | N/A | N/A | N/A | 39887580 | 600 | 166.113 | 0% | 0% | 100% | 0% | 100% | 40% | 9062107 | 1409 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 88 | 49503134 | 3659 | 87.816 | 3.659 | 7.8 | 7.8 | 2B | 0 | 0 | 1026 | 0 | 1046 | N/A | N/A | N/A | N/A | 39888180 | 600 | 163.9792 | 0% | 0% | 100% | 0% | 100% | 40% | 9063452 | 1345 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 90 | 49506788 | 3654 | 87.696 | 3.654 | 9 | 9 | 2B | 0 | 0 | 1026 | 0 | 1047 | N/A | N/A | N/A | N/A | 39888788 | 608 | 166.393 | 0% | 0% | 100% | 0% | 100% | 40% | 9064679 | 1227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 101 | 49510827 | 4039 | 96.936 | 4.039 | 9.6 | 9.6 | 2B | 0 | 0 | 1006 | 0 | 1006 | N/A | N/A | N/A | N/A | 39889396 | 608 | 150.5323 | 0% | 0% | 100% | 0% | 100% | 40% | 9065081 | 402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 110 | 49515466 | 4639 | 111.336 | 4.639 | 9.6 | 9.6 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39890236 | 840 | 181.0735 | 0% | 0% | 100% | 0% | 100% | 0% | 9065081 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 146 | 49521540 | 6074 | 145.776 | 6.074 | 9.5 | 9.5 | 3B+1S | 0 | 1087 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39891540 | 1304 | 214.6855 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 150 | 49527949 | 6409 | 153.816 | 6.409 | 8.6 | 8.6 | 3B+1S | 0 | 1138 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39892928 | 1388 | 216.5704 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 49534025 | 6076 | 145.824 | 6.076 | 7.7 | 7.7 | 3B+1S | 0 | 1138 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39894316 | 1388 | 228.4398 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 129 | 151 | 49540443 | 6418 | 154.032 | 6.418 | 6.7 | 8.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39895776 | 1460 | 227.4852 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 129 | 151 | 49546749 | 6306 | 151.344 | 6.306 | 5.7 | 7.2 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39897236 | 1460 | 231.5255 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 127 | 151 | 49553104 | 6355 | 152.52 | 6.355 | 4.6 | 4.6 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39898716 | 1480 | 232.8875 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 19 | A ONG | 17.5 | 129 | 143 | 49559210 | 6106 | 146.544 | 6.106 | 3.5 | 3.5 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39900156 | 1440 | 235.8336 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 144 | 49565031 | 5821 | 139.704 | 5.821 | 2.8 | 2.8 | 3B+1S | 0 | 1188 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39901516 | 1360 | 233.6368 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 138 | 49570808 | 5777 | 138.648 | 5.777 | 2.4 | 2.4 | 3B+1S | 0 | 1056 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39902836 | 1320 | 228.4923 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 49576509 | 5701 | 136.824 | 5.701 | 2.2 | 2.2 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39904156 | 1320 | 231.5383 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 49581974 | 5465 | 131.16 | 5.465 | 2.1 | 2.1 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39905452 | 1296 | 237.1455 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 135 | 49587463 | 5489 | 131.736 | 5.489 | 2.1 | 2.1 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39906756 | 1304 | 237.566 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 150 | 49592904 | 5441 | 130.584 | 5.441 | 2 | 2 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39908052 | 1296 | 238.1915 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 133 | 49598409 | 5505 | 132.12 | 5.505 | 1.9 | 1.9 | 3B+1S | 0 | 1009 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39909356 | 1304 | 236.8756 | 0% | 100% | 100% | 100% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 121 | 49603538 | 5129 | 123.096 | 5.129 | 1.7 | 1.7 | 2B+1S | 0 | 1036 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39910404 | 1048 | 204.3283 | 0% | 100% | 100% | 0% | 100% | 0% | 9065081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 111 | 49608616 | 5078 | 121.872 | 5.078 | 1.4 | 1.4 | 2B+1S | 0 | 1036 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39911460 | 1056 | 207.9559 | 0% | 100% | 100% | 0% | 100% | 0% | 9065081 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 97 | 49612703 | 4087 | 98.088 | 4.087 | 2.7 | 2.7 | 2B | 0 | 0 | 1087 | 0 | 1077 | N/A | N/A | N/A | N/A | 39912192 | 732 | 179.1045 | 0% | 0% | 100% | 0% | 100% | 40% | 9066317 | 1236 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 94 | 49616707 | 4004 | 96.096 | 4.004 | 4.5 | 4.5 | 2B | 0 | 0 | 1087 | 0 | 1077 | N/A | N/A | N/A | N/A | 39912884 | 692 | 172.8272 | 0% | 0% | 100% | 0% | 100% | 40% | 9067767 | 1450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.7083 | 124757 | 124757 | 124.757 | 124.757 | [13 empty] | 26600 | 213.2145 | [6 empty] | 8513 | 8513 | 1.0283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV1 CLOSED @ 4:18 AM,WATER ELEVATION (9.6M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:50 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
NOTE: ALL MOTORS FULLSPEED UNABLE TO REACH THE TARGET DISC. PRESS.
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 30, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:00 PM
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (40%)

## AUG 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26260 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49616707 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39912884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9067767 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 99 | 49620575 | 3868 | 92.832 | 3.868 | 6.5 | 6.5 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39913572 | 688 | 177.8697 | 0% | 0% | 100% | 0% | 100% | 45% | 9069057 | 1290 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 101 | 49624443 | 3868 | 92.832 | 3.868 | 7.8 | 7.8 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39914260 | 688 | 177.8697 | 0% | 0% | 100% | 0% | 100% | 45% | 9070350 | 1293 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 112 | 96 | 49628312 | 3869 | 92.856 | 3.869 | 8.9 | 8.9 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39914948 | 688 | 177.8237 | 0% | 0% | 100% | 0% | 100% | 45% | 9071637 | 1287 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 100 | 49632180 | 3868 | 92.832 | 3.868 | 9.5 | 9.5 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39915636 | 688 | 177.8697 | 0% | 0% | 100% | 0% | 100% | 45% | 9072903 | 1266 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 112 | 49636625 | 4445 | 106.68 | 4.445 | 9.5 | 9.5 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39916356 | 720 | 161.9798 | 0% | 0% | 100% | 0% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 115 | 49641070 | 4445 | 106.68 | 4.445 | 9.5 | 9.5 | 2B | 0 | 0 | 1086 | 0 | 1076 | N/A | N/A | N/A | N/A | 39917076 | 720 | 161.9798 | 0% | 0% | 100% | 0% | 100% | 0% | 9072903 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 138 | 49646777 | 5707 | 136.968 | 5.707 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1165 | N/A | N/A | N/A | N/A | 39918244 | 1168 | 204.6609 | 0% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 49652985 | 6208 | 148.992 | 6.208 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39919536 | 1292 | 208.1186 | 0% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 153 | 49659085 | 6100 | 146.4 | 6.1 | 8.9 | 8.9 | 3B+1S | 1065 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39920910 | 1374 | 225.2459 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 153 | 49665185 | 6100 | 146.4 | 6.1 | 8.4 | 8.2 | 3B+1S | 1065 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39922284 | 1374 | 225.2459 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 | 0.98 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 152 | 49671578 | 6393 | 153.432 | 6.393 | 7.6 | 7.2 | 3B+1S | 1157 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39923708 | 1424 | 222.7436 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 149 | 49677841 | 6263 | 150.312 | 6.263 | 6.7 | 6.7 | 3B+1S | 1156 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39925116 | 1408 | 224.8124 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 144 | 49683952 | 6111 | 146.664 | 6.111 | 5.4 | 5.4 | 3B+1S | 1156 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39926580 | 1464 | 239.568 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 139 | 49689732 | 5780 | 138.72 | 5.78 | 4.9 | 4.9 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39927900 | 1320 | 228.3737 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 137 | 49695403 | 5671 | 136.104 | 5.671 | 4.4 | 4.4 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39929236 | 1336 | 235.5846 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 49701420 | 6017 | 144.408 | 6.017 | 3.9 | 3.9 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39930628 | 1392 | 231.3445 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 49706946 | 5526 | 132.624 | 5.526 | 3.4 | 3.4 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39931916 | 1288 | 233.08 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 138 | 49712961 | 6015 | 144.36 | 6.015 | 3 | 3 | 3B+1S | 1054 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39933332 | 1416 | 235.4115 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 131 | 49718513 | 5552 | 133.248 | 5.552 | 2.6 | 2.6 | 3B+1S | 1054 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 39934580 | 1248 | 224.7839 | 100% | 0% | 100% | 100% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 122 | 49723644 | 5131 | 123.144 | 5.131 | 2.1 | 2.1 | 2B+1S | 1054 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 39935660 | 1080 | 210.4853 | 100% | 0% | 100% | 0% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 120 | 49728701 | 5057 | 121.368 | 5.057 | 1.6 | 1.6 | 2B+1S | 1045 | 0 | 1167 | 0 | 1167 | N/A | N/A | N/A | N/A | 39936668 | 1008 | 199.3277 | 100% | 0% | 100% | 0% | 100% | 0% | 9072903 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 108 | 116 | 49733746 | 5045 | 121.08 | 5.045 | 1.3 | 1.3 | 2B+1S | 1045 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 39937660 | 992 | 196.6303 | 100% | 0% | 100% | 0% | 100% | 0% | 9072903 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 105 | 49737408 | 3662 | 87.888 | 3.662 | 2.2 | 2.2 | 2B | 0 | 0 | 1117 | 0 | 1137 | N/A | N/A | N/A | N/A | 39938432 | 772 | 210.8138 | 0% | 0% | 100% | 0% | 100% | 40% | 9074143 | 1240 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 102 | 49741836 | 4428 | 106.272 | 4.428 | 3.6 | 3.6 | 2B | 0 | 0 | 1087 | 0 | 1117 | N/A | N/A | N/A | N/A | 39939144 | 712 | 160.7949 | 0% | 0% | 100% | 0% | 100% | 40% | 9075500 | 1357 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 126.6667 | 125129 | 125129 | 125.129 | 125.129 | [13 empty] | 26260 | 209.8634 | [6 empty] | 7733 | 7733 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (AUG 31, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:00 PM
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## AUG 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ALEXANDER CABREROS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-08-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+1S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26856 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 49741836 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 39939144 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9075500 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 49745957 | 4121 | 98.904 | 4.121 | 5.3 | 5.3 | 2B | 0 | 0 | 1086 | 0 | 1117 | N/A | N/A | N/A | N/A | 39939908 | 764 | 185.3919 | 0% | 0% | 100% | 0% | 100% | 45% | 9076954 | 1454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 90 | 49749736 | 3779 | 90.696 | 3.779 | 6.7 | 6.7 | 2B | 0 | 0 | 1036 | 0 | 1087 | N/A | N/A | N/A | N/A | 39940572 | 664 | 175.7079 | 0% | 0% | 100% | 0% | 100% | 45% | 9078393 | 1439 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 86 | 49753536 | 3800 | 91.2 | 3.8 | 8.2 | 8.2 | 2B | 0 | 0 | 1027 | 0 | 1037 | N/A | N/A | N/A | N/A | 39941224 | 652 | 171.5789 | 0% | 0% | 100% | 0% | 100% | 45% | 9079804 | 1411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 94 | 49757103 | 3567 | 85.608 | 3.567 | 9.6 | 9.6 | 2B | 0 | 0 | 1026 | 0 | 1036 | N/A | N/A | N/A | N/A | 39941804 | 580 | 162.6016 | 0% | 0% | 100% | 0% | 100% | 45% | 9081079 | 1275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 95 | 49761083 | 3980 | 95.52 | 3.98 | 9.6 | 9.6 | 2B | 0 | 0 | 996 | 0 | 1007 | N/A | N/A | N/A | N/A | 39942384 | 580 | 145.7286 | 0% | 0% | 100% | 0% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 114 | 49765691 | 4608 | 110.592 | 4.608 | 9.7 | 9.7 | 2B | 0 | 0 | 1076 | 0 | 1117 | N/A | N/A | N/A | N/A | 39943112 | 728 | 157.9861 | 0% | 0% | 100% | 0% | 100% | 0% | 9081079 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 138 | 49771176 | 5485 | 131.64 | 5.485 | 9.7 | 9.7 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39944228 | 1116 | 203.464 | 0% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 150 | 49777370 | 6194 | 148.656 | 6.194 | 9.5 | 9.5 | 3B+1S | 1045 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39945564 | 1336 | 215.6926 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 49783449 | 6079 | 145.896 | 6.079 | 8.8 | 8.8 | 3B+1S | 1067 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39946940 | 1376 | 226.353 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 49789956 | 6507 | 156.168 | 6.507 | 8.2 | 8.2 | 3B+1S | 1135 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39948372 | 1432 | 220.0707 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 151 | 49796305 | 6349 | 152.376 | 6.349 | 7.3 | 7.2 | 3B+1S | 1136 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39949812 | 1440 | 226.8074 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 148 | 49802335 | 6030 | 144.72 | 6.03 | 6.2 | 6.2 | 3B+1S | 1175 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39951228 | 1416 | 234.8259 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 145 | 49808544 | 6209 | 149.016 | 6.209 | 5.4 | 5.4 | 3B+1S | 1175 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 39952644 | 1416 | 228.056 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 49814206 | 5662 | 135.888 | 5.662 | 4.7 | 4.7 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39953956 | 1312 | 231.7202 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 141 | 49820086 | 5880 | 141.12 | 5.88 | 4.1 | 4.1 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39955316 | 1360 | 231.2925 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 49825908 | 5822 | 139.728 | 5.822 | 3.5 | 3.5 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39956672 | 1356 | 232.9097 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 49831692 | 5784 | 138.816 | 5.784 | 3 | 3 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39958020 | 1348 | 233.0567 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 138 | 49837455 | 5763 | 138.312 | 5.763 | 2.6 | 2.6 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39959368 | 1348 | 233.906 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 138 | 49843258 | 5803 | 139.272 | 5.803 | 2.1 | 2.1 | 3B+1S | 1063 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39960724 | 1356 | 233.6722 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 136 | 49848957 | 5699 | 136.776 | 5.699 | 1.7 | 1.7 | 3B+1S | 1043 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39962044 | 1320 | 231.6196 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 143 | 49854480 | 5523 | 132.552 | 5.523 | 1.4 | 1.4 | 3B+1S | 1043 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 39963332 | 1288 | 233.2066 | 100% | 0% | 100% | 100% | 100% | 0% | 9081079 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 114 | 49859663 | 5183 | 124.392 | 5.183 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 39964412 | 1080 | 208.3735 | 100% | 0% | 100% | 0% | 100% | 0% | 9081079 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 100 | 49863937 | 4274 | 102.576 | 4.274 | 2.2 | 2.2 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 39965228 | 816 | 190.9219 | 0% | 0% | 100% | 0% | 100% | 40% | 9082246 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 98 | 49868083 | 4146 | 99.504 | 4.146 | 3.7 | 3.7 | 2B | 0 | 0 | 1127 | 0 | 1127 | N/A | N/A | N/A | N/A | 39966000 | 772 | 186.2036 | 0% | 0% | 100% | 0% | 100% | 40% | 9083523 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.9583 | 126247 | 126247 | 126.247 | 126.247 | [13 empty] | 26856 | 212.7258 | [6 empty] | 8023 | 8023 | 1.0917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Edmundo Llagas Jr (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.Edmundo Llagas Jr (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 CLOSED @ 3:53 AM,WATER ELEVATION (9.6M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (SEPT 1, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 9:30 PM
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)