## OCT 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24976 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 53545034 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40732252 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9305842 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 108 | 67 | 53547825 | 2791 | 66.984 | 2.791 | 5.9 | 5.9 | 1B | 0 | 0 | 0 | 0 | 1009 | N/A | N/A | N/A | N/A | 40732584 | 332 | 118.9538 | 0% | 0% | 0% | 0% | 100% | 30% | 9307497 | 1655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 107 | 65 | 53550542 | 2717 | 65.208 | 2.717 | 7.6 | 7.6 | 1B | 0 | 0 | 0 | 0 | 1009 | N/A | N/A | N/A | N/A | 40732916 | 332 | 122.1936 | 0% | 0% | 0% | 0% | 100% | 30% | 9309125 | 1628 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 96 | 53554661 | 4119 | 98.856 | 4.119 | 9 | 9 | 2B | 0 | 0 | 1008 | 0 | 1008 | N/A | N/A | N/A | N/A | 40733500 | 584 | 141.782 | 0% | 0% | 100% | 0% | 100% | 30% | 9310422 | 1297 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 97 | 53558653 | 3992 | 95.808 | 3.992 | 9.5 | 9.5 | 2B | 0 | 0 | 1008 | 0 | 1008 | N/A | N/A | N/A | N/A | 40734100 | 600 | 150.3006 | 0% | 0% | 100% | 0% | 100% | 30% | 9310884 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 101 | 53562649 | 3996 | 95.904 | 3.996 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 0 | 1047 | N/A | N/A | N/A | N/A | 40734676 | 576 | 144.1441 | 0% | 0% | 100% | 0% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 124 | 53567712 | 5063 | 121.512 | 5.063 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 40735592 | 916 | 180.9204 | 0% | 0% | 100% | 0% | 100% | 0% | 9310884 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 53573687 | 5975 | 143.4 | 5.975 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40736936 | 1344 | 224.9372 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 53579756 | 6069 | 145.656 | 6.069 | 8.6 | 8.6 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40738300 | 1364 | 224.7487 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 53585864 | 6108 | 146.592 | 6.108 | 8.1 | 8.1 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40739684 | 1384 | 226.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 53591973 | 6109 | 146.616 | 6.109 | 7.5 | 7.5 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40741052 | 1368 | 223.9319 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 147 | 53597961 | 5988 | 143.712 | 5.988 | 7 | 7 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40742416 | 1364 | 227.7889 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 144 | 53603886 | 5925 | 142.2 | 5.925 | 6.3 | 6.3 | 3B+1S | 0 | 1098 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40743796 | 1380 | 232.9114 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 139 | 53609806 | 5920 | 142.08 | 5.92 | 5.7 | 5.7 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40745164 | 1368 | 231.0811 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 133 | 53615488 | 5682 | 136.368 | 5.682 | 5.3 | 5.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40746476 | 1312 | 230.9046 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 133 | 53621025 | 5537 | 132.888 | 5.537 | 5 | 5 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40747764 | 1288 | 232.6169 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 128 | 53626483 | 5458 | 130.992 | 5.458 | 4.8 | 4.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 40749060 | 1296 | 237.4496 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 53632016 | 5533 | 132.792 | 5.533 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40750372 | 1312 | 237.1227 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 129 | 53637399 | 5383 | 129.192 | 5.383 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 40751636 | 1264 | 234.8133 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 132 | 53643019 | 5620 | 134.88 | 5.62 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 40752948 | 1312 | 233.452 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 132 | 53648383 | 5364 | 128.736 | 5.364 | 4 | 4 | 3B+1S | 0 | 983 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 40754236 | 1288 | 240.1193 | 0% | 100% | 100% | 100% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 117 | 53653305 | 4922 | 118.128 | 4.922 | 3.5 | 3.5 | 2B+1S | 0 | 1006 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40755252 | 1016 | 206.4202 | 0% | 100% | 100% | 0% | 100% | 0% | 9310884 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 106 | 53658143 | 4838 | 116.112 | 4.838 | 3.3 | 3.3 | 2B+1S | 0 | 995 | 1147 | 0 | 1188 | N/A | N/A | N/A | N/A | 40756236 | 984 | 203.3898 | 0% | 100% | 100% | 0% | 100% | 0% | 9310884 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 78 | 53661523 | 3380 | 81.12 | 3.38 | 4.5 | 4.5 | 1B | 0 | 0 | 0 | 0 | 1188 | N/A | N/A | N/A | N/A | 40756772 | 536 | 158.5799 | 0% | 0% | 0% | 0% | 100% | 25% | 9312051 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 30 | 21.1268 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 100 | 80 | 53664637 | 3114 | 74.736 | 3.114 | 5.8 | 5.8 | 1B | 0 | 0 | 0 | 0 | 1138 | N/A | N/A | N/A | N/A | 40757228 | 456 | 146.4355 | 0% | 0% | 0% | 0% | 100% | 25% | 9313309 | 1258 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.2083 | 119603 | 119603 | 119.603 | 119.603 | [12 empty] | 24976 | 24976 | 208.8242 | [6 empty] | 7467 | 7467 | 1.1467 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:01 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (SEPT 8, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP2 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 10:00 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24464 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 53664637 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40757228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9313309 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 105 | 68 | 53667325 | 2688 | 64.512 | 2.688 | 7.3 | 7.3 | 1B | 0 | 0 | 0 | 0 | 987 | N/A | N/A | N/A | N/A | 40757544 | 316 | 117.5595 | 0% | 0% | 0% | 0% | 100% | 30% | 9314900 | 1591 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 103 | 64 | 53670063 | 2738 | 65.712 | 2.738 | 9 | 9 | 1B | 0 | 0 | 0 | 0 | 967 | N/A | N/A | N/A | N/A | 40757852 | 308 | 112.4909 | 0% | 0% | 0% | 0% | 100% | 30% | 9316460 | 1560 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 93 | 92 | 53674013 | 3950 | 94.8 | 3.95 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 957 | N/A | N/A | N/A | N/A | 40758412 | 560 | 141.7722 | 0% | 0% | 100% | 0% | 100% | 30% | 9317208 | 748 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 95 | 53677924 | 3911 | 93.864 | 3.911 | 9.5 | 9.5 | 2B | 0 | 0 | 950 | 0 | 957 | N/A | N/A | N/A | N/A | 40758924 | 512 | 130.9128 | 0% | 0% | 100% | 0% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 103 | 53681973 | 4049 | 97.176 | 4.049 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1058 | N/A | N/A | N/A | N/A | 40759484 | 560 | 138.3058 | 0% | 0% | 100% | 0% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 212 | 53686601 | 4628 | 111.072 | 4.628 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40760296 | 812 | 175.4538 | 0% | 0% | 100% | 0% | 100% | 0% | 9317208 | 0 | 1.15 | Normal operation schedule | Error - General | E | FIDEL A. RAMOS / PAUL LABIAN
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 137 | 53692489 | 5888 | 141.312 | 5.888 | 9.5 | 9.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40761596 | 1300 | 220.788 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 53697941 | 5452 | 130.848 | 5.452 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40762788 | 1192 | 218.6354 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 53704060 | 6119 | 146.856 | 6.119 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40764172 | 1384 | 226.1807 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 143 | 53710199 | 6139 | 147.336 | 6.139 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40765540 | 1368 | 222.8376 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 | 1.07 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 53716424 | 6225 | 149.4 | 6.225 | 7.6 | 7.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40766948 | 1408 | 226.1847 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 53722435 | 6011 | 144.264 | 6.011 | 7 | 7 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40768284 | 1336 | 222.2592 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 53728443 | 6008 | 144.192 | 6.008 | 6.4 | 6.4 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40769660 | 1376 | 229.028 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 139 | 53734607 | 6164 | 147.936 | 6.164 | 5.7 | 5.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40771092 | 1432 | 232.3167 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 53740225 | 5618 | 134.832 | 5.618 | 5.2 | 5.2 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40772404 | 1312 | 233.5351 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 131 | 53745946 | 5721 | 137.304 | 5.721 | 4.8 | 4.8 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40773748 | 1344 | 234.924 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 144 | 53751803 | 5857 | 140.568 | 5.857 | 4.4 | 4.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40775112 | 1364 | 232.8837 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 53757081 | 5278 | 126.672 | 5.278 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1157 | N/A | N/A | N/A | N/A | 40776332 | 1220 | 231.1482 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 130 | 53762554 | 5473 | 131.352 | 5.473 | 3.8 | 3.8 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1157 | N/A | N/A | N/A | N/A | 40777620 | 1288 | 235.3371 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 126 | 53768035 | 5481 | 131.544 | 5.481 | 3.6 | 3.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1136 | N/A | N/A | N/A | N/A | 40778908 | 1288 | 234.9936 | 100% | 0% | 100% | 100% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 103 | 111 | 53773109 | 5074 | 121.776 | 5.074 | 3.1 | 3.1 | 2B+1S | 1047 | 0 | 1188 | 0 | 1178 | N/A | N/A | N/A | N/A | 40779972 | 1064 | 209.6965 | 100% | 0% | 100% | 0% | 100% | 0% | 9317208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 97 | 92 | 53777081 | 3972 | 95.328 | 3.972 | 2.9 | 2.9 | 2B+1S | 965 | 0 | 1188 | 0 | 976 | N/A | N/A | N/A | N/A | 40780772 | 800 | 201.4099 | 100% | 0% | 100% | 0% | 100% | 0% | 9317208 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 25 | 17.6056 | 64 | 45.0704 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 14 | A ONG | 11.9 | 104 | 76 | 53780447 | 3366 | 80.784 | 3.366 | 3.8 | 3.8 | 1B | 0 | 0 | 0 | 0 | 965 | N/A | N/A | N/A | N/A | 40781308 | 536 | 159.2395 | 0% | 0% | 0% | 0% | 100% | 25% | 9318134 | 926 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 30 | 21.1268 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 97 | 66 | 53783431 | 2984 | 71.616 | 2.984 | 5 | 5 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 40781692 | 384 | 128.6863 | 0% | 0% | 0% | 0% | 100% | 25% | 9319234 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.75 | 118794 | 118794 | 118.794 | 118.794 | [12 empty] | 24464 | 24464 | 205.9363 | [6 empty] | 5925 | 5925 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:15 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (SEPT 8, 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO EXCESS CAPACITY
SP1 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 10:00 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY / FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25664 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 53783431 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40781692 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9319234 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 102 | 69 | 53786159 | 2728 | 65.472 | 2.728 | 6.4 | 6.4 | 1B | 0 | 0 | 987 | 0 | 0 | N/A | N/A | N/A | N/A | 40782012 | 320 | 117.3021 | 0% | 0% | 100% | 0% | 0% | 30% | 9320652 | 1418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 30 | 21.1268 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 101 | 91 | 53788849 | 2690 | 64.56 | 2.69 | 7.9 | 7.9 | 1B | 0 | 0 | 967 | 0 | 0 | N/A | N/A | N/A | N/A | 40782308 | 296 | 110.0372 | 0% | 0% | 100% | 0% | 0% | 30% | 9322111 | 1459 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 94 | 53792936 | 4087 | 98.088 | 4.087 | 9.2 | 9.2 | 2B | 0 | 0 | 948 | 0 | 947 | N/A | N/A | N/A | N/A | 40782844 | 536 | 131.1475 | 0% | 0% | 100% | 0% | 100% | 30% | 9323314 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 89 | 53796727 | 3791 | 90.984 | 3.791 | 9.6 | 9.6 | 2B | 0 | 0 | 967 | 0 | 947 | N/A | N/A | N/A | N/A | 40783340 | 496 | 130.8362 | 0% | 0% | 100% | 0% | 100% | 30% | 9323573 | 259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 96 | 53800723 | 3996 | 95.904 | 3.996 | 9.6 | 9.6 | 2B | 0 | 0 | 988 | 0 | 957 | N/A | N/A | N/A | N/A | 40783880 | 540 | 135.1351 | 0% | 0% | 100% | 0% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 128 | 53805533 | 4810 | 115.44 | 4.81 | 9.6 | 9.6 | 2B | 0 | 0 | 1188 | 0 | 1168 | N/A | N/A | N/A | N/A | 40784692 | 812 | 168.815 | 0% | 0% | 100% | 0% | 100% | 0% | 9323573 | 0 | 1.01 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 53811336 | 5803 | 139.272 | 5.803 | 9.5 | 9.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40785968 | 1276 | 219.8863 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 53817513 | 6177 | 148.248 | 6.177 | 8.9 | 8.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40787348 | 1380 | 223.4094 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 53824185 | 6672 | 160.128 | 6.672 | 8.3 | 8.3 | 3B+1S | 0 | 1168 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40788844 | 1496 | 224.2206 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 150 | 53830174 | 5989 | 143.736 | 5.989 | 7.3 | 7.3 | 3B+1S | 0 | 1169 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40790206 | 1362 | 227.4169 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 152 | 53836995 | 6821 | 163.704 | 6.821 | 6.1 | 6.1 | 3B+1S | 0 | 1138 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40791756 | 1550 | 227.2394 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 152 | 53843097 | 6102 | 146.448 | 6.102 | 5.4 | 5.4 | 3B+1S | 0 | 1180 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40793156 | 1400 | 229.433 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 53849197 | 6100 | 146.4 | 6.1 | 4.3 | 4.3 | 3B+1S | 0 | 1129 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40794596 | 1440 | 236.0656 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 143 | 53855304 | 6107 | 146.568 | 6.107 | 3.2 | 3.2 | 3B+1S | 0 | 1129 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40796044 | 1448 | 237.105 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 138 | 53861090 | 5786 | 138.864 | 5.786 | 2.7 | 2.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40797396 | 1352 | 233.6675 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 53866881 | 5791 | 138.984 | 5.791 | 2.3 | 2.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40798748 | 1352 | 233.4657 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 53872570 | 5689 | 136.536 | 5.689 | 1.9 | 1.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40800092 | 1344 | 236.2454 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 53878192 | 5622 | 134.928 | 5.622 | 1.7 | 1.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40801412 | 1320 | 234.7919 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 53883834 | 5642 | 135.408 | 5.642 | 1.6 | 1.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40802732 | 1320 | 233.9596 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 136 | 53889376 | 5542 | 133.008 | 5.542 | 1.5 | 1.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40804048 | 1316 | 237.4594 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 122 | 53894647 | 5271 | 126.504 | 5.271 | 1.5 | 1.5 | 3B+1S | 0 | 995 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40805332 | 1284 | 243.597 | 0% | 100% | 100% | 100% | 100% | 0% | 9323573 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 | 97 | 53899131 | 4484 | 107.616 | 4.484 | 1.5 | 1.5 | 3B | 0 | 0 | 1016 | 1185 | 1016 | N/A | N/A | N/A | N/A | 40806380 | 1048 | 233.7199 | 0% | 0% | 100% | 100% | 100% | 0% | 9323573 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 89 | 53902754 | 3623 | 86.952 | 3.623 | 2.4 | 2.4 | 2B | 0 | 0 | 988 | 0 | 997 | N/A | N/A | N/A | N/A | 40806964 | 584 | 161.1924 | 0% | 0% | 100% | 0% | 100% | 25% | 9324622 | 1049 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 103 | 72 | 53905837 | 3083 | 73.992 | 3.083 | 3.7 | 3.7 | 1B | 0 | 0 | 0 | 0 | 1018 | N/A | N/A | N/A | N/A | 40807356 | 392 | 127.1489 | 0% | 0% | 0% | 0% | 100% | 25% | 9325881 | 1259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.2917 | 122406 | 122406 | 122.406 | 122.406 | [12 empty] | 25664 | 25664 | 209.6629 | [6 empty] | 6647 | 6647 | 1.1433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:15 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 3 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:01 PM DUE TO LOW WATER LEVEL
BP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24844 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 53905837 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40807356 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9325881 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 26 | 18.3099 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 109 | 64 | 53908659 | 2822 | 67.728 | 2.822 | 5.2 | 5.2 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 40807696 | 340 | 120.4819 | 0% | 0% | 0% | 0% | 100% | 30% | 9327244 | 1363 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 106 | 71 | 53911441 | 2782 | 66.768 | 2.782 | 6.8 | 6.8 | 1B | 0 | 0 | 0 | 0 | 978 | N/A | N/A | N/A | N/A | 40808024 | 328 | 117.9008 | 0% | 0% | 0% | 0% | 100% | 30% | 9328859 | 1615 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 111 | 53915071 | 3630 | 87.12 | 3.63 | 8.3 | 8.3 | 2B | 0 | 0 | 957 | 0 | 1169 | N/A | N/A | N/A | N/A | 40808548 | 524 | 144.3526 | 0% | 0% | 100% | 0% | 100% | 30% | 9330189 | 1330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 96 | 53919136 | 4065 | 97.56 | 4.065 | 9.1 | 9.1 | 2B | 0 | 0 | 956 | 0 | 1158 | N/A | N/A | N/A | N/A | 40809228 | 680 | 167.2817 | 0% | 0% | 100% | 0% | 100% | 30% | 9330885 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 96 | 53923223 | 4087 | 98.088 | 4.087 | 9.6 | 9.6 | 2B | 0 | 0 | 957 | 0 | 1098 | N/A | N/A | N/A | N/A | 40809900 | 672 | 164.4238 | 0% | 0% | 100% | 0% | 100% | 30% | 9331261 | 376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 120 | 53927810 | 4587 | 110.088 | 4.587 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 1098 | N/A | N/A | N/A | N/A | 40810688 | 788 | 171.7898 | 0% | 0% | 100% | 0% | 100% | 0% | 9331261 | 0 | 1.13 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 138 | 53933431 | 5621 | 134.904 | 5.621 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40811912 | 1224 | 217.7548 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 135 | 53939544 | 6113 | 146.712 | 6.113 | 8.6 | 8.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40813236 | 1324 | 216.5876 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 144 | 53945573 | 6029 | 144.696 | 6.029 | 7.7 | 7.7 | 3B+1S | 1159 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40814564 | 1328 | 220.2687 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 53951700 | 6127 | 147.048 | 6.127 | 6.7 | 6.7 | 3B+1S | 1049 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40815932 | 1368 | 223.274 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 | 1.35 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 53957923 | 6223 | 149.352 | 6.223 | 6 | 6 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40817332 | 1400 | 224.9719 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 146 | 53963946 | 6023 | 144.552 | 6.023 | 5.4 | 5.4 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40818716 | 1384 | 229.7858 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 53969877 | 5931 | 142.344 | 5.931 | 4.7 | 4.7 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40820092 | 1376 | 232.0013 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 141 | 53975639 | 5762 | 138.288 | 5.762 | 4.3 | 4.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40821436 | 1344 | 233.2523 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 135 | 53981406 | 5767 | 138.408 | 5.767 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40822780 | 1344 | 233.0501 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 53987025 | 5619 | 134.856 | 5.619 | 3.4 | 3.4 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40824108 | 1328 | 236.341 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 130 | 53992670 | 5645 | 135.48 | 5.645 | 3.2 | 3.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40825440 | 1332 | 235.961 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 53998173 | 5503 | 132.072 | 5.503 | 3 | 3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40826748 | 1308 | 237.6885 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 130 | 54003895 | 5722 | 137.328 | 5.722 | 2.9 | 2.9 | 3B+1S | 985 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40828108 | 1360 | 237.6791 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 131 | 54009076 | 5181 | 124.344 | 5.181 | 2.8 | 2.8 | 3B+1S | 904 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40829352 | 1244 | 240.1081 | 100% | 0% | 100% | 100% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 106 | 112 | 54014132 | 5056 | 121.344 | 5.056 | 2.6 | 2.6 | 2B+1S | 1035 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 40830408 | 1056 | 208.8608 | 100% | 0% | 100% | 0% | 100% | 0% | 9331261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 21 | 14.7887 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 101 | 92 | 54018513 | 4381 | 105.144 | 4.381 | 2.5 | 2.5 | 2B+1S | 954 | 0 | 1188 | 0 | 1047 | N/A | N/A | N/A | N/A | 40831324 | 916 | 209.0847 | 100% | 0% | 100% | 0% | 100% | 0% | 9331261 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 109 | 85 | 54022046 | 3533 | 84.792 | 3.533 | 3.3 | 3.3 | 2B | 0 | 0 | 960 | 0 | 950 | N/A | N/A | N/A | N/A | 40831884 | 560 | 158.5055 | 0% | 0% | 100% | 0% | 100% | 25% | 9332152 | 891 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 31 | 21.831 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 94 | 63 | 54024802 | 2756 | 66.144 | 2.756 | 4.6 | 4.6 | 1B | 0 | 0 | 967 | 0 | 0 | N/A | N/A | N/A | N/A | 40832200 | 316 | 114.6589 | 0% | 0% | 100% | 0% | 0% | 25% | 9333303 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.25 | 118965 | 118965 | 118.965 | 118.965 | [12 empty] | 24844 | 24844 | 208.8345 | [6 empty] | 7422 | 7422 | 1.2633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:15 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 3 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24632 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54024802 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40832200 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9333303 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 95 | 60 | 54027391 | 2589 | 62.136 | 2.589 | 6.2 | 6.2 | 1B | 0 | 0 | 967 | 0 | 0 | N/A | N/A | N/A | N/A | 40832500 | 300 | 115.8749 | 0% | 0% | 100% | 0% | 0% | 30% | 9334752 | 1449 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 110 | 76 | 54030036 | 2645 | 63.48 | 2.645 | 7.7 | 7.7 | 1B | 0 | 0 | 1068 | 0 | 0 | N/A | N/A | N/A | N/A | 40832792 | 292 | 110.397 | 0% | 0% | 100% | 0% | 0% | 30% | 9336247 | 1495 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 85 | 54033957 | 3921 | 94.104 | 3.921 | 9 | 9 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 40833348 | 556 | 141.8006 | 0% | 0% | 100% | 0% | 100% | 30% | 9337421 | 1174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 88 | 54037602 | 3645 | 87.48 | 3.645 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 40833844 | 496 | 136.0768 | 0% | 0% | 100% | 0% | 100% | 30% | 9338014 | 593 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 108 | 54041703 | 4101 | 98.424 | 4.101 | 9.5 | 9.5 | 2B | 0 | 0 | 1158 | 0 | 1038 | N/A | N/A | N/A | N/A | 40834420 | 576 | 140.4535 | 0% | 0% | 100% | 0% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 124 | 54046589 | 4886 | 117.264 | 4.886 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 40835292 | 872 | 178.4691 | 0% | 0% | 100% | 0% | 100% | 0% | 9338014 | 0 | 1.14 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 143 | 54052507 | 5918 | 142.032 | 5.918 | 9.5 | 9.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40836616 | 1324 | 223.7242 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 54058623 | 6116 | 146.784 | 6.116 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40838012 | 1396 | 228.2538 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 54064780 | 6157 | 147.768 | 6.157 | 7.8 | 7.8 | 3B+1S | 0 | 1078 | 1189 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40839395 | 1383 | 224.6224 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 54070982 | 6202 | 148.848 | 6.202 | 7.1 | 7.1 | 3B+1S | 0 | 1078 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40840820 | 1425 | 229.7646 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 | 1.1 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 143 | 54077382 | 6400 | 153.6 | 6.4 | 6.4 | 6.4 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40842252 | 1432 | 223.75 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 54083212 | 5830 | 139.92 | 5.83 | 5.6 | 5.6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40843620 | 1368 | 234.6484 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 141 | 54089113 | 5901 | 141.624 | 5.901 | 4.9 | 4.9 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40844980 | 1360 | 230.4694 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 54094903 | 5790 | 138.96 | 5.79 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40846340 | 1360 | 234.8877 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 130 | 54100439 | 5536 | 132.864 | 5.536 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40847652 | 1312 | 236.9942 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 54105961 | 5522 | 132.528 | 5.522 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40848972 | 1320 | 239.0438 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 131 | 54111512 | 5551 | 133.224 | 5.551 | 4 | 4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40850292 | 1320 | 237.795 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 54116996 | 5484 | 131.616 | 5.484 | 3.8 | 3.8 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40851588 | 1296 | 236.3239 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 120 | 54122656 | 5660 | 135.84 | 5.66 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40852924 | 1336 | 236.0424 | 0% | 100% | 100% | 100% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 128 | 54128129 | 5473 | 131.352 | 5.473 | 2.8 | 2.8 | 2B+1S | 0 | 1150 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40854072 | 1148 | 209.757 | 0% | 100% | 100% | 0% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 102 | 115 | 54133253 | 5124 | 122.976 | 5.124 | 1.9 | 1.9 | 2B+1S | 0 | 1148 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40855148 | 1076 | 209.9922 | 0% | 100% | 100% | 0% | 100% | 0% | 9338014 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 94 | 99 | 54137573 | 4320 | 103.68 | 4.32 | 1.8 | 1.8 | 2B+1S | 0 | 964 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 40855976 | 828 | 191.6667 | 0% | 100% | 100% | 0% | 100% | 0% | 9338014 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 118 | 82 | 54141147 | 3574 | 85.776 | 3.574 | 3 | 3 | 2B | 0 | 0 | 957 | 0 | 968 | N/A | N/A | N/A | N/A | 40856504 | 528 | 147.7336 | 0% | 0% | 100% | 0% | 100% | 25% | 9339240 | 1226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 33 | 23.2394 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 100 | 68 | 54143813 | 2666 | 63.984 | 2.666 | 4.5 | 4.5 | 1B | 0 | 0 | 0 | 0 | 1038 | N/A | N/A | N/A | N/A | 40856832 | 328 | 123.0308 | 0% | 0% | 0% | 0% | 100% | 25% | 9340625 | 1385 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.6667 | 119011 | 119011 | 119.011 | 119.011 | [12 empty] | 24632 | 24632 | 206.9725 | [6 empty] | 7322 | 7322 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (30%)
BP3 - STARTED @ 2:10 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 6 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25001 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54143813 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40856832 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9340625 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 101 | 71 | 54146443 | 2630 | 63.12 | 2.63 | 6.3 | 6.3 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 40857152 | 320 | 121.673 | 0% | 0% | 0% | 0% | 100% | 30% | 9342190 | 1565 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 29 | 20.4225 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 102 | 62 | 54149079 | 2636 | 63.264 | 2.636 | 7.6 | 7.6 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 40857484 | 332 | 125.9484 | 0% | 0% | 0% | 0% | 100% | 30% | 9343765 | 1575 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR/PAUL LABIAN
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 99 | 95 | 54152959 | 3880 | 93.12 | 3.88 | 9.2 | 9.2 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 40858054 | 570 | 146.9072 | 0% | 0% | 100% | 0% | 100% | 30% | 9345330 | 1565 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 94 | 54156847 | 3888 | 93.312 | 3.888 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 40858628 | 574 | 147.6337 | 0% | 0% | 100% | 0% | 100% | 30% | 9345538 | 208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 103 | 54160930 | 4083 | 97.992 | 4.083 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1078 | N/A | N/A | N/A | N/A | 40859236 | 608 | 148.9101 | 0% | 0% | 100% | 0% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 122 | 54165790 | 4860 | 116.64 | 4.86 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 40860148 | 912 | 187.6543 | 0% | 0% | 100% | 0% | 100% | 0% | 9345538 | 0 | 1.04 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 140 | 54171870 | 6080 | 145.92 | 6.08 | 9.2 | 9.2 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40861516 | 1368 | 225 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 145 | 54177883 | 6013 | 144.312 | 6.013 | 8.4 | 8.4 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40862896 | 1380 | 229.5027 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 147 | 54183983 | 6100 | 146.4 | 6.1 | 7.6 | 7.6 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40864308 | 1412 | 231.4754 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 54190113 | 6130 | 147.12 | 6.13 | 6.9 | 6.9 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40865716 | 1408 | 229.69 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 | 1.45 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 54196212 | 6099 | 146.376 | 6.099 | 6.3 | 6.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40867100 | 1384 | 226.9224 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 138 | 54202143 | 5931 | 142.344 | 5.931 | 5.8 | 5.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 40868464 | 1364 | 229.9781 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 136 | 54207867 | 5724 | 137.376 | 5.724 | 5.2 | 5.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40869826 | 1362 | 237.9455 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 133 | 54213483 | 5616 | 134.784 | 5.616 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40871156 | 1330 | 236.8234 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 131 | 54218997 | 5514 | 132.336 | 5.514 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40872488 | 1332 | 241.5669 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 126 | 54224334 | 5337 | 128.088 | 5.337 | 4.5 | 4.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40873792 | 1304 | 244.332 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 54229734 | 5400 | 129.6 | 5.4 | 4.3 | 4.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40875096 | 1304 | 241.4815 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 54235422 | 5688 | 136.512 | 5.688 | 3.9 | 3.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40876452 | 1356 | 238.3966 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 136 | 54240913 | 5491 | 131.784 | 5.491 | 3.6 | 3.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40877764 | 1312 | 238.9364 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 130 | 54246390 | 5477 | 131.448 | 5.477 | 3.4 | 3.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40879064 | 1300 | 237.3562 | 100% | 0% | 100% | 100% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 106 | 113 | 54251345 | 4955 | 118.92 | 4.955 | 2.7 | 2.7 | 2B+1S | 1016 | 0 | 1187 | 0 | 1186 | N/A | N/A | N/A | N/A | 40880136 | 1072 | 216.3471 | 100% | 0% | 100% | 0% | 100% | 0% | 9345538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 92 | 94 | 54255472 | 4127 | 99.048 | 4.127 | 2.5 | 2.5 | 2B+1S | 1016 | 0 | 1067 | 0 | 1047 | N/A | N/A | N/A | N/A | 40880940 | 804 | 194.8146 | 100% | 0% | 100% | 0% | 100% | 0% | 9345538 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 85 | 54259013 | 3541 | 84.984 | 3.541 | 3.6 | 3.6 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 40881508 | 568 | 160.4067 | 0% | 0% | 100% | 0% | 100% | 25% | 9346707 | 1169 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 101 | 81 | 54261783 | 2770 | 66.48 | 2.77 | 4.9 | 4.9 | 1B | 0 | 0 | 997 | 0 | 0 | N/A | N/A | N/A | N/A | 40881833 | 325 | 117.3285 | 0% | 0% | 0% | 0% | 100% | 25% | 9348017 | 1310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.3333 | 117970 | 117970 | 117.97 | 117.97 | [12 empty] | 25001 | 25001 | 211.9268 | [6 empty] | 7392 | 7392 | 1.205 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:01 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 7 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY / PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25183 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54261783 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40881833 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9348017 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 31 | 21.831 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 100 | 71 | 54264555 | 2772 | 66.528 | 2.772 | 7 | 7 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 40882151 | 318 | 114.7186 | 0% | 0% | 0% | 0% | 100% | 30% | 9349334 | 1317 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 30 | 21.1268 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 97 | 65 | 54267343 | 2788 | 66.912 | 2.788 | 8.3 | 8.3 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 40882468 | 317 | 113.7016 | 0% | 0% | 0% | 0% | 100% | 30% | 9350645 | 1311 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 99 | 54271503 | 4160 | 99.84 | 4.16 | 9.1 | 9.1 | 2B | 0 | 0 | 997 | 0 | 998 | N/A | N/A | N/A | N/A | 40883016 | 548 | 131.7308 | 0% | 0% | 100% | 0% | 100% | 30% | 9352102 | 1457 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 98 | 54275573 | 4070 | 97.68 | 4.07 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 998 | N/A | N/A | N/A | N/A | 40883586 | 570 | 140.0491 | 0% | 0% | 100% | 0% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 100 | 54279660 | 4087 | 98.088 | 4.087 | 9.5 | 9.5 | 2B | 0 | 0 | 1038 | 0 | 1038 | N/A | N/A | N/A | N/A | 40884176 | 590 | 144.3602 | 0% | 0% | 100% | 0% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 54284736 | 5076 | 121.824 | 5.076 | 9.5 | 9.5 | 2B | 0 | 0 | 1186 | 0 | 1186 | N/A | N/A | N/A | N/A | 40885092 | 916 | 180.4571 | 0% | 0% | 100% | 0% | 100% | 0% | 9352102 | 0 | 1.24 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 54290826 | 6090 | 146.16 | 6.09 | 9.1 | 9.1 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 40886444 | 1352 | 222.0033 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 149 | 54297060 | 6234 | 149.616 | 6.234 | 8.3 | 8.3 | 3B+1S |  | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40887856 | 1412 | 226.4998 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 54303292 | 6232 | 149.568 | 6.232 | 7.5 | 7.5 | 3B+1S |  | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40889264 | 1408 | 225.9307 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 151 | 54309508 | 6216 | 149.184 | 6.216 | 6.8 | 6.8 | 3B+1S |  | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40890668 | 1404 | 225.8687 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 54315723 | 6215 | 149.16 | 6.215 | 6.1 | 6.1 | 3B+1S |  | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40892068 | 1400 | 225.2615 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 54321773 | 6050 | 145.2 | 6.05 | 5.4 | 5.4 | 3B+1S |  | 1099 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40893444 | 1376 | 227.438 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 139 | 54327671 | 5898 | 141.552 | 5.898 | 4.7 | 4.7 | 3B+1S |  | 1077 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40894820 | 1376 | 233.2994 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 54333492 | 5821 | 139.704 | 5.821 | 4.2 | 4.2 | 3B+1S |  | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40896172 | 1352 | 232.2625 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 54339152 | 5660 | 135.84 | 5.66 | 3.7 | 3.7 | 3B+1S |  | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40897500 | 1328 | 234.629 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 54344673 | 5521 | 132.504 | 5.521 | 3.6 | 3.6 | 3B+1S |  | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40898812 | 1312 | 237.6381 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 54350213 | 5540 | 132.96 | 5.54 | 3.6 | 3.6 | 3B+1S |  | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40900140 | 1328 | 239.7112 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 54355751 | 5538 | 132.912 | 5.538 | 3.5 | 3.5 | 3B+1S |  | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40901436 | 1296 | 234.0195 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 54361395 | 5644 | 135.456 | 5.644 | 3.3 | 3.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40902756 | 1320 | 233.8767 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 129 | 54366934 | 5539 | 132.936 | 5.539 | 3.1 | 3.1 | 3B+1S | 0 | 1004 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 40904040 | 1284 | 231.8108 | 0% | 100% | 100% | 100% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 123 | 54372079 | 5145 | 123.48 | 5.145 | 2.6 | 2.6 | 2B+1S | 0 | 1068 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 40905108 | 1068 | 207.5802 | 0% | 100% | 100% | 0% | 100% | 0% | 9352102 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 117 | 54377134 | 5055 | 121.32 | 5.055 | 2.1 | 2.1 | 2B | 0 | 1015 | 1157 | 0 | 1158 | N/A | N/A | N/A | N/A | 40906104 | 996 | 197.0326 | 0% | 100% | 100% |  |  | 0% | 9352102 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 85 | 54380995 | 3861 | 92.664 | 3.861 | 3.2 | 3.2 | 2B | 0 | 0 | 998 | 0 | 998 | N/A | N/A | N/A | N/A | 40906692 | 588 | 152.2922 | 0% | 0% |  |  |  | 25% | 9353410 | 1308 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 29 | 20.4225 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 101 | 70 | 54383816 | 2821 | 67.704 | 2.821 | 4.8 | 4.8 | 1B | 0 | 0 | 0 | 0 | 998 | N/A | N/A | N/A | N/A | 40907016 | 324 | 114.8529 | 0% | 0% |  |  |  | 25% | 9354725 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.5417 | 122033 | 122033 | 122.033 | 122.033 | [12 empty] | 25183 | 25183 | 206.3622 | [6 empty] | 6708 | 6708 | 1.255 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP3 - STARTED @ 2:01 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 8 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR/PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR/PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25024 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54383816 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40907016 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9354725 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 101 | 77 | 54386500 | 2684 | 64.416 | 2.684 | 6.3 | 6.3 | 1B | 0 | 0 | 0 | 0 | 1007 | N/A | N/A | N/A | N/A | 40907316 | 300 | 111.7735 | 0% | 0% | 0% | 0% | 100% | 30% | 9356178 | 1453 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 23 | 16.1972 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 100 | 75 | 54389100 | 2600 | 62.4 | 2.6 | 8.1 | 8.1 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 40907646 | 330 | 126.9231 | 0% | 0% | 0% | 0% | 100% | 30% | 9357628 | 1450 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR/PAUL LABIAN
50:00 | 3:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 110 | 92 | 54393117 | 4017 | 96.408 | 4.017 | 9.2 | 9.2 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 40908172 | 526 | 130.9435 | 0% | 0% | 100% | 0% | 100% | 30% | 9359084 | 1456 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 108 | 54397091 | 3974 | 95.376 | 3.974 | 9.5 | 9.5 | 2B | 0 | 0 | 1007 | 0 | 1007 | N/A | N/A | N/A | N/A | 40908732 | 560 | 140.916 | 0% | 0% | 100% | 0% | 100% | 30% | 9359435 | 351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 103 | 54401085 | 3994 | 95.856 | 3.994 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1048 | N/A | N/A | N/A | N/A | 40909300 | 568 | 142.2133 | 0% | 0% | 100% | 0% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 54406220 | 5135 | 123.24 | 5.135 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 40910244 | 944 | 183.8364 | 0% | 0% | 100% | 0% | 100% | 0% | 9359435 | 0 | 1.15 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 148 | 54412308 | 6088 | 146.112 | 6.088 | 9.1 | 9.1 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40911612 | 1368 | 224.7043 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 54418558 | 6250 | 150 | 6.25 | 8.4 | 8.4 | 3B+1S | 1076 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40913016 | 1404 | 224.64 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 54424734 | 6176 | 148.224 | 6.176 | 7.6 | 7.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40914408 | 1392 | 225.3886 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 54431052 | 6318 | 151.632 | 6.318 | 6.9 | 6.9 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40915828 | 1420 | 224.7547 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 | 1.17 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 155 | 54437193 | 6141 | 147.384 | 6.141 | 6.2 | 6.2 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40917212 | 1384 | 225.3705 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 143 | 54443196 | 6003 | 144.072 | 6.003 | 5.6 | 5.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40918604 | 1392 | 231.8841 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 137 | 54448913 | 5717 | 137.208 | 5.717 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40919940 | 1336 | 233.689 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 138 | 54454659 | 5746 | 137.904 | 5.746 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40921284 | 1344 | 233.9018 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 157 | 54460247 | 5588 | 134.112 | 5.588 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40922614 | 1330 | 238.01 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 54465745 | 5498 | 131.952 | 5.498 | 4.1 | 4.1 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40923916 | 1302 | 236.8134 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 150 | 54471278 | 5533 | 132.792 | 5.533 | 3.9 | 3.9 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40925228 | 1312 | 237.1227 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 54476899 | 5621 | 134.904 | 5.621 | 3.7 | 3.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40926548 | 1320 | 234.8337 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 127 | 54482466 | 5567 | 133.608 | 5.567 | 3.3 | 3.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40927868 | 1320 | 237.1116 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 107 | 129 | 54487886 | 5420 | 130.08 | 5.42 | 2.5 | 2.5 | 2B+1S | 1148 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 40929020 | 1152 | 212.5461 | 100% | 0% | 100% | 100% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 127 | 54493123 | 5237 | 125.688 | 5.237 | 1.7 | 1.7 | 2B+1S | 1148 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 40930108 | 1088 | 207.7525 | 100% | 0% | 100% | 0% | 100% | 0% | 9359435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 112 | 54498089 | 4966 | 119.184 | 4.966 | 1.4 | 1.4 | 2B+1S | 1045 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 40931076 | 968 | 194.9255 | 100% | 0% | 100% | 0% | 100% | 0% | 9359435 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 90 | 54502003 | 3914 | 93.936 | 3.914 | 2.3 | 2.3 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 40931700 | 624 | 159.4277 | 0% | 0% | 100% | 0% | 100% | 25% | 9360554 | 1119 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 30 | 21.1268 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 103 | 61 | 54504895 | 2892 | 69.408 | 2.892 | 3.7 | 3.7 | 1B | 0 | 0 | 0 | 0 | 998 | N/A | N/A | N/A | N/A | 40932040 | 340 | 117.5657 | 0% | 0% | 0% | 0% | 100% | 25% | 9361888 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.5417 | 121079 | 121079 | 121.079 | 121.079 | [12 empty] | 25024 | 25024 | 206.675 | [6 empty] | 7163 | 7163 | 1.13 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:01 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:21 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 9 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25148 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54504895 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40932040 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9361888 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 115 | 68 | 54507732 | 2837 | 68.088 | 2.837 | 5.6 | 5.6 | 1B | 0 | 0 | 0 | 0 | 998 | N/A | N/A | N/A | N/A | 40932368 | 328 | 115.6151 | 0% | 0% | 0% | 0% | 100% | 30% | 9363614 | 1726 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 122 | 79 | 54510967 | 3235 | 77.64 | 3.235 | 7.2 | 7.2 | 1B | 0 | 0 | 0 | 0 | 1148 | N/A | N/A | N/A | N/A | 40932772 | 404 | 124.8841 | 0% | 0% | 0% | 0% | 100% | 30% | 9365192 | 1578 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 93 | 54514956 | 3989 | 95.736 | 3.989 | 8.7 | 8.7 | 2B | 0 | 0 | 967 | 0 | 998 | N/A | N/A | N/A | N/A | 40933332 | 560 | 140.3861 | 0% | 0% | 100% | 0% | 100% | 30% | 9366564 | 1372 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 90 | 54518781 | 3825 | 91.8 | 3.825 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 0 | 987 | N/A | N/A | N/A | N/A | 40933876 | 544 | 142.2222 | 0% | 0% | 100% | 0% | 100% | 30% | 9367162 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 105 | 54522819 | 4038 | 96.912 | 4.038 | 9.5 | 9.5 | 2B | 0 | 0 | 1058 | 0 | 1078 | N/A | N/A | N/A | N/A | 40934460 | 584 | 144.6261 | 0% | 0% | 100% | 0% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 54527773 | 4954 | 118.896 | 4.954 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40935340 | 880 | 177.6342 | 0% | 0% | 100% | 0% | 100% | 0% | 9367162 | 0 | 1.23 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 150 | 54533903 | 6130 | 147.12 | 6.13 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40936708 | 1368 | 223.1648 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 148 | 54540079 | 6176 | 148.224 | 6.176 | 8.3 | 8.3 | 3B+1S | 0 | 1099 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40938092 | 1384 | 224.0933 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 145 | 54546293 | 6214 | 149.136 | 6.214 | 7.5 | 7.5 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40939500 | 1408 | 226.5851 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 54552505 | 6212 | 149.088 | 6.212 | 6.8 | 6.8 | 3B+1S | 0 | 1078 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40940904 | 1404 | 226.0142 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 | 1.32 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 54558722 | 6217 | 149.208 | 6.217 | 6.1 | 6.1 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40942308 | 1404 | 225.8324 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 121 | 54564731 | 6009 | 144.216 | 6.009 | 5.4 | 5.4 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40943684 | 1376 | 228.9898 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 114 | 54570624 | 5893 | 141.432 | 5.893 | 4.7 | 4.7 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40945060 | 1376 | 233.4974 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 139 | 54576444 | 5820 | 139.68 | 5.82 | 4.1 | 4.1 | 3B+1S | 0 | 1076 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40946416 | 1356 | 232.9897 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 145 | 54582147 | 5703 | 136.872 | 5.703 | 3.6 | 3.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40947748 | 1332 | 233.5613 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 54587780 | 5633 | 135.192 | 5.633 | 3.4 | 3.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40949068 | 1320 | 234.3334 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 133 | 54593399 | 5619 | 134.856 | 5.619 | 3 | 3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40950384 | 1316 | 234.2054 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 54599087 | 5688 | 136.512 | 5.688 | 2.7 | 2.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40951728 | 1344 | 236.2869 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 54604543 | 5456 | 130.944 | 5.456 | 2.5 | 2.5 | 3B+1S | 0 | 1025 | 1185 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40953020 | 1292 | 236.8035 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 1354 | 54609905 | 5362 | 128.688 | 5.362 | 2.3 | 2.3 | 3B+1S | 0 | 986 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40954292 | 1272 | 237.2249 | 0% | 100% | 100% | 100% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 106 | 125 | 54615074 | 5169 | 124.056 | 5.169 | 1.8 | 1.8 | 2B+1S | 0 | 1119 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40955380 | 1088 | 210.4856 | 0% | 100% | 100% | 0% | 100% | 0% | 9367162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 20 | 14.0845 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 97 | 54619591 | 4517 | 108.408 | 4.517 | 1.6 | 1.6 | 2B+1S | 0 | 995 | 1187 | 0 | 1007 | N/A | N/A | N/A | N/A | 40956284 | 904 | 200.1328 | 0% | 100% | 100% | 0% | 100% | 0% | 9367162 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 108 | 77 | 54623330 | 3739 | 89.736 | 3.739 | 2.4 | 2.4 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 40956860 | 576 | 154.0519 | 0% | 0% | 100% | 0% | 100% | 25% | 9368048 | 886 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 92 | 66 | 54626032 | 2702 | 64.848 | 2.702 | 3.5 | 3.5 | 1B | 0 | 0 | 1028 | 0 | 0 | N/A | N/A | N/A | N/A | 40957188 | 328 | 121.3916 | 0% | 0% | 100% | 0% | 0% | 25% | 9369084 | 1036 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 169.2917 | 121137 | 121137 | 121.137 | 121.137 | [12 empty] | 25148 | 25148 | 207.5997 | [6 empty] | 7196 | 7196 | 1.1967 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (30%)
BP1 - STARTED @ 2:01 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 10 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25264 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54626032 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40957188 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9369084 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 99 | 65 | 54628733 | 2701 | 64.824 | 2.701 | 5 | 5 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 40957516 | 328 | 121.4365 | 0% | 0% | 100% | 0% | 0% | 30% | 9370435 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 99 | 63 | 54631410 | 2677 | 64.248 | 2.677 | 6.5 | 6.5 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 40957848 | 332 | 124.0194 | 0% | 0% | 100% | 0% | 0% | 30% | 9371859 | 1424 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 104 | 54635159 | 3749 | 89.976 | 3.749 | 7.7 | 7.7 | 2B | 0 | 0 | 1139 | 0 | 957 | N/A | N/A | N/A | N/A | 40958428 | 580 | 154.7079 | 0% | 0% | 100% | 0% | 100% | 30% | 9373124 | 1265 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 93 | 54639281 | 4122 | 98.928 | 4.122 | 9.1 | 9.1 | 2B | 0 | 0 | 1027 | 0 | 957 | N/A | N/A | N/A | N/A | 40959052 | 624 | 151.3828 | 0% | 0% | 100% | 0% | 100% | 30% | 9374367 | 1243 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 70 | 54643076 | 3795 | 91.08 | 3.795 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 0 | 967 | N/A | N/A | N/A | N/A | 40959608 | 556 | 146.5086 | 0% | 0% | 100% | 0% | 100% | 30% | 9374787 | 420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 54647599 | 4523 | 108.552 | 4.523 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40960348 | 740 | 163.6082 | 0% | 0% | 100% | 0% | 100% | 0% | 9374787 | 0 | 1.17 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 131 | 54653792 | 6193 | 148.632 | 6.193 | 9.4 | 9.4 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40961692 | 1344 | 217.0192 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 54660115 | 6323 | 151.752 | 6.323 | 8.7 | 8.7 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40963104 | 1412 | 223.3117 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 54666384 | 6269 | 150.456 | 6.269 | 7.9 | 7.9 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40964504 | 1400 | 223.3211 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 54672513 | 6129 | 147.096 | 6.129 | 7.1 | 7.1 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40965884 | 1380 | 225.1591 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 145 | 54678866 | 6353 | 152.472 | 6.353 | 6.3 | 6.3 | 3B+1S | 1118 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40967312 | 1428 | 224.7757 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 146 | 54684879 | 6013 | 144.312 | 6.013 | 5.4 | 5.4 | 3B+1S | 1119 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40968632 | 1320 | 219.5244 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 148 | 54691187 | 6308 | 151.392 | 6.308 | 4.6 | 4.6 | 3B+1S | 1099 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40970132 | 1500 | 237.7933 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 54697172 | 5985 | 143.64 | 5.985 | 3.8 | 3.8 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40971512 | 1380 | 230.5764 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 54702950 | 5778 | 138.672 | 5.778 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40972852 | 1340 | 231.9142 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 54708730 | 5780 | 138.72 | 5.78 | 3.1 | 3.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40974144 | 1292 | 223.5294 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 54714477 | 5747 | 137.928 | 5.747 | 2.7 | 2.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40975524 | 1380 | 240.1253 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 131 | 54720173 | 5696 | 136.704 | 5.696 | 2.5 | 2.5 | 3B+1S | 986 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40976852 | 1328 | 233.1461 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 54725744 | 5571 | 133.704 | 5.571 | 2.4 | 2.4 | 3B+1S | 986 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40978156 | 1304 | 234.0693 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 130 | 54731249 | 5505 | 132.12 | 5.505 | 2.3 | 2.3 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40979460 | 1304 | 236.8756 | 100% | 0% | 100% | 100% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 101 | 111 | 54736414 | 5165 | 123.96 | 5.165 | 1.6 | 1.6 | 2B+1S | 1097 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 40980564 | 1104 | 213.7464 | 100% | 0% | 100% | 0% | 100% | 0% | 9374787 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 100 | 98 | 54740444 | 4030 | 96.72 | 4.03 | 1.5 | 1.5 | 2B+1S | 953 | 0 | 1007 | 0 | 1187 | N/A | N/A | N/A | N/A | 40981412 | 848 | 210.4218 | 100% | 0% | 100% | 0% | 100% | 0% | 9374787 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 90 | 54744294 | 3850 | 92.4 | 3.85 | 2.7 | 2.7 | 2B | 0 | 0 | 956 | 0 | 1129 | N/A | N/A | N/A | N/A | 40982092 | 680 | 176.6234 | 0% | 0% | 100% | 0% | 100% | 30% | 9376163 | 1376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 112 | 66 | 54747183 | 2889 | 69.336 | 2.889 | 4.8 | 4.8 | 1B | 0 | 0 | 956 | 0 | 0 | N/A | N/A | N/A | N/A | 40982452 | 360 | 124.6106 | 0% | 0% | 100% | 0% | 100% | 30% | 9377886 | 1723 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 118.25 | 121151 | 121151 | 121.151 | 121.151 | [12 empty] | 25264 | 25264 | 208.5332 | [6 empty] | 8802 | 8802 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (30%)
BP3 - STARTED @ 2:25 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 10 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24800 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54747183 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 40982452 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9377886 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 23 | 16.1972 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 114 | 64 | 54749847 | 2664 | 63.936 | 2.664 | 6.6 | 6.6 | 1B | 0 | 0 | 0 | 0 | 998 | N/A | N/A | N/A | N/A | 40982776 | 324 | 121.6216 | 0% | 0% | 0% | 0% | 100% | 35% | 9379840 | 1954 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 117 | 62 | 54752537 | 2690 | 64.56 | 2.69 | 8.6 | 8.6 | 1B | 0 | 0 | 0 | 0 | 978 | N/A | N/A | N/A | N/A | 40983096 | 320 | 118.9591 | 0% | 0% | 0% | 0% | 100% | 35% | 9381795 | 1955 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 26 | 18.3099 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 102 | 102 | 54756732 | 4195 | 100.68 | 4.195 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 1078 | N/A | N/A | N/A | N/A | 40983716 | 620 | 147.795 | 0% | 0% | 100% | 0% | 100% | 35% | 9382719 | 924 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 54760632 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 40984244 | 528 | 135.3846 | 0% | 0% | 100% | 0% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 102 | 54764589 | 3957 | 94.968 | 3.957 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 998 | N/A | N/A | N/A | N/A | 40984820 | 576 | 145.5648 | 0% | 0% | 100% | 0% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 117 | 54769298 | 4709 | 113.016 | 4.709 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 40985616 | 796 | 169.038 | 0% | 0% | 100% | 0% | 100% | 0% | 9382719 | 0 | 1.07 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 142 | 54775086 | 5788 | 138.912 | 5.788 | 9.5 | 9.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40986836 | 1220 | 210.7809 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 54781207 | 6121 | 146.904 | 6.121 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40988204 | 1368 | 223.4929 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 54787460 | 6253 | 150.072 | 6.253 | 8.5 | 8.5 | 3B+1S | 0 | 1058 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40989588 | 1384 | 221.3338 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 54793754 | 6294 | 151.056 | 6.294 | 7.8 | 7.8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40990980 | 1392 | 221.163 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 | 1.37 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 54799980 | 6226 | 149.424 | 6.226 | 7.1 | 7.1 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 40992380 | 1400 | 224.8635 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 54806115 | 6135 | 147.24 | 6.135 | 6.4 | 6.4 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40993776 | 1396 | 227.5469 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 131 | 54812013 | 5898 | 141.552 | 5.898 | 5.7 | 5.7 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40995148 | 1372 | 232.6212 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 137 | 54817858 | 5845 | 140.28 | 5.845 | 5 | 5 | 3B+1S | 0 | 1078 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40996516 | 1368 | 234.0462 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 138 | 54823647 | 5789 | 138.936 | 5.789 | 4.4 | 4.4 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 40997884 | 1368 | 236.3102 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 140 | 54829491 | 5844 | 140.256 | 5.844 | 3.6 | 3.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40999260 | 1376 | 235.4552 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 143 | 54835274 | 5783 | 138.792 | 5.783 | 3.1 | 3.1 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41000600 | 1340 | 231.7136 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 138 | 54841073 | 5799 | 139.176 | 5.799 | 2.6 | 2.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41001956 | 1356 | 233.8334 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 128 | 54846573 | 5500 | 132 | 5.5 | 2.4 | 2.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1158 | N/A | N/A | N/A | N/A | 41003256 | 1300 | 236.3636 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 145 | 54852356 | 5783 | 138.792 | 5.783 | 2 | 2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 41004608 | 1352 | 233.7887 | 0% | 100% | 100% | 100% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 93 | 98 | 54857014 | 4658 | 111.792 | 4.658 | 1.6 | 1.6 | 2B+1S | 0 | 1014 | 1188 | 0 | 1048 | N/A | N/A | N/A | N/A | 41005572 | 964 | 206.9558 | 0% | 100% | 100% | 0% | 100% | 0% | 9382719 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 22 | 15.493 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 94 | 108 | 54861196 | 4182 | 100.368 | 4.182 | 1.5 | 1.5 | 2B+1S | 0 | 955 | 1138 | 0 | 957 | N/A | N/A | N/A | N/A | 41006412 | 840 | 200.8608 | 0% | 100% | 100% | 0% | 100% | 0% | 9382719 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 81 | 54864603 | 3407 | 81.768 | 3.407 | 2.7 | 2.7 | 2B | 0 | 0 | 957 | 0 | 958 | N/A | N/A | N/A | N/A | 41006932 | 520 | 152.6269 | 0% | 0% | 100% | 0% | 100% | 30% | 9383942 | 1223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 29 | 20.4225 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 102 | 66 | 54867305 | 2702 | 64.848 | 2.702 | 4.4 | 4.4 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 41007252 | 320 | 118.4308 | 0% | 0% | 100% | 0% | 0% | 30% | 9385462 | 1520 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 119.0833 | 120122 | 120122 | 120.122 | 120.122 | [12 empty] | 24800 | 24800 | 206.4568 | [6 empty] | 7576 | 7576 | 1.18 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (35%)
BP1 - STARTED @ 2:10 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 10 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25056 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54867305 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41007252 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9385462 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 106 | 60 | 54869963 | 2658 | 63.792 | 2.658 | 6.4 | 6.4 | 1B | 0 | 0 | 998 | 0 | 0 | N/A | N/A | N/A | N/A | 41007580 | 328 | 123.4011 | 0% | 0% | 100% | 0% | 0% | 35% | 9387342 | 1880 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 111 | 69 | 54872535 | 2572 | 61.728 | 2.572 | 8.2 | 8.2 | 1B | 0 | 0 | 987 | 0 | 0 | N/A | N/A | N/A | N/A | 41007892 | 312 | 121.3064 | 0% | 0% | 100% | 0% | 0% | 35% | 9389120 | 1778 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR/PAUL LABIAN
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 54876483 | 3948 | 94.752 | 3.948 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41008500 | 608 | 154.002 | 0% | 0% | 100% | 0% | 100% | 35% | 9390475 | 1355 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 54880256 | 3773 | 90.552 | 3.773 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 958 | N/A | N/A | N/A | N/A | 41008996 | 496 | 131.4604 | 0% | 0% | 100% | 0% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 105 | 54884512 | 4256 | 102.144 | 4.256 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1078 | N/A | N/A | N/A | N/A | 41009628 | 632 | 148.4962 | 0% | 0% | 100% | 0% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 119 | 54889254 | 4742 | 113.808 | 4.742 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41010484 | 856 | 180.5146 | 0% | 0% | 100% | 0% | 100% | 0% | 9390475 | 0 | 1.24 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 54895443 | 6189 | 148.536 | 6.189 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41011844 | 1360 | 219.7447 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 150 | 54901713 | 6270 | 150.48 | 6.27 | 8.5 | 8.5 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41013244 | 1400 | 223.2855 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 149 | 54908003 | 6290 | 150.96 | 6.29 | 7.7 | 7.7 | 3B+1S | 1128 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41014660 | 1416 | 225.1192 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 54914322 | 6319 | 151.656 | 6.319 | 6.8 | 6.8 | 3B+1S | 1098 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41016084 | 1424 | 225.3521 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 | 1.06 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 54920605 | 6283 | 150.792 | 6.283 | 6 | 6 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41017492 | 1408 | 224.0968 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 54926743 | 6138 | 147.312 | 6.138 | 5.4 | 5.4 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41018892 | 1400 | 228.0873 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 142 | 54932622 | 5879 | 141.096 | 5.879 | 4.7 | 4.7 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41020256 | 1364 | 232.0122 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 54938434 | 5812 | 139.488 | 5.812 | 3.9 | 3.9 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41021620 | 1364 | 234.6869 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 137 | 54944246 | 5812 | 139.488 | 5.812 | 3.4 | 3.4 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41022989 | 1369 | 235.5471 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 54949561 | 5315 | 127.56 | 5.315 | 3.1 | 3.1 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41024132 | 1143 | 215.0517 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 54955211 | 5650 | 135.6 | 5.65 | 2.7 | 2.7 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41025460 | 1328 | 235.0442 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 123 | 130 | 54961134 | 5923 | 142.152 | 5.923 | 2.4 | 2.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41026852 | 1392 | 235.016 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 54966643 | 5509 | 132.216 | 5.509 | 2.2 | 2.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41028164 | 1312 | 238.1557 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 131 | 54972226 | 5583 | 133.992 | 5.583 | 2.1 | 2.1 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41029500 | 1336 | 239.2979 | 100% | 0% | 100% | 100% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 105 | 116 | 54977276 | 5050 | 121.2 | 5.05 | 1.6 | 1.6 | 2B+1S | 1047 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41030544 | 1044 | 206.7327 | 100% | 0% | 100% | 0% | 100% | 0% | 9390475 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 97 | 98 | 54981603 | 4327 | 103.848 | 4.327 | 1.5 | 1.5 | 2B+1S | 954 | 0 | 966 | 0 | 1108 | N/A | N/A | N/A | N/A | 41031420 | 876 | 202.4497 | 100% | 0% | 100% | 0% | 100% | 0% | 9390475 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 112 | 54985124 | 3521 | 84.504 | 3.521 | 2.5 | 2.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41031956 | 536 | 152.2295 | 0% | 0% | 100% | 0% | 100% | 25% | 9391539 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 24 | 16.9014 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 98 | 69 | 54988084 | 2960 | 71.04 | 2.96 | 3.8 | 3.8 | 1B | 0 | 0 | 0 | 0 | 1018 | N/A | N/A | N/A | N/A | 41032308 | 352 | 118.9189 | 0% | 0% | 0% | 0% | 100% | 25% | 9392824 | 1285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.75 | 120779 | 120779 | 120.779 | 120.779 | [12 empty] | 25056 | 25056 | 207.4533 | [6 empty] | 7362 | 7362 | 1.175 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (35%)
BP3 - STARTED @ 2:10 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 12 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25088 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 54988084 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41032308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9392824 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 23 | 16.1972 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 115 | 66 | 54990777 | 2693 | 64.632 | 2.693 | 5.8 | 5.8 | 1B | 0 | 0 | 0 | 0 | 1017 | N/A | N/A | N/A | N/A | 41032652 | 344 | 127.7386 | 0% | 0% | 0% | 0% | 100% | 35% | 9394811 | 1987 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 24 | 16.9014 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 116 | 69 | 54993634 | 2857 | 68.568 | 2.857 | 8.1 | 8.1 | 1B | 0 | 0 | 0 | 0 | 968 | N/A | N/A | N/A | N/A | 41033004 | 352 | 123.2062 | 0% | 0% | 0% | 0% | 100% | 35% | 9396900 | 2089 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR/PAUL LABIAN
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 54997473 | 3839 | 92.136 | 3.839 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 1089 | N/A | N/A | N/A | N/A | 41033388 | 384 | 100.026 | 0% | 0% | 100% | 0% | 100% | 35% | 9398317 | 1417 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 96 | 55001356 | 3883 | 93.192 | 3.883 | 9.5 | 9.5 | 2B | 0 | 0 | 988 | 0 | 1058 | N/A | N/A | N/A | N/A | 41034136 | 748 | 192.6346 | 0% | 0% | 100% | 0% | 100% | 35% | 9398341 | 24 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 106 | 55005573 | 4217 | 101.208 | 4.217 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 0 | 1099 | N/A | N/A | N/A | N/A | 41034814 | 678 | 160.7778 | 0% | 0% | 100% | 0% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 120 | 55010283 | 4710 | 113.04 | 4.71 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41035652 | 838 | 177.9193 | 0% | 0% | 100% | 0% | 100% | 0% | 9398341 | 0 | 1.4 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 149 | 55016324 | 6041 | 144.984 | 6.041 | 9.3 | 9.3 | 3B+1S | 0 | 1099 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41036996 | 1344 | 222.4797 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 146 | 55022647 | 6323 | 151.752 | 6.323 | 8.5 | 8.5 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41038474 | 1478 | 233.7498 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 149 | 55028771 | 6124 | 146.976 | 6.124 | 7.7 | 7.7 | 3B+1S | 0 | 1108 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41039812 | 1338 | 218.4847 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 55034981 | 6210 | 149.04 | 6.21 | 6.9 | 6.9 | 3B+1S | 0 | 1108 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41041224 | 1412 | 227.3752 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 | 1.27 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 55041073 | 6092 | 146.208 | 6.092 | 6.1 | 6.1 | 3B+1S | 0 | 1107 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41042614 | 1390 | 228.1681 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 139 | 55047196 | 6123 | 146.952 | 6.123 | 5.5 | 5.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41044004 | 1390 | 227.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 107 | 55053057 | 5861 | 140.664 | 5.861 | 4.9 | 4.9 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41045368 | 1364 | 232.7248 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 135 | 55058916 | 5859 | 140.616 | 5.859 | 4.3 | 4.3 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41046732 | 1364 | 232.8042 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 126 | 55064663 | 5747 | 137.928 | 5.747 | 3.8 | 3.8 | 3B+1S | 0 | 1065 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41048092 | 1360 | 236.6452 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 55070294 | 5631 | 135.144 | 5.631 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41049428 | 1336 | 237.258 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 55075873 | 5579 | 133.896 | 5.579 | 3.3 | 3.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41050756 | 1328 | 238.0355 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 55081413 | 5540 | 132.96 | 5.54 | 3.2 | 3.2 | 3B+1S | 0 | 995 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41052060 | 1304 | 235.3791 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 127 | 55086554 | 5141 | 123.384 | 5.141 | 3.1 | 3.1 | 3B+1S | 0 | 994 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41053284 | 1224 | 238.086 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 126 | 55092024 | 5470 | 131.28 | 5.47 | 3 | 3 | 3B+1S | 0 | 955 | 1186 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41054596 | 1312 | 239.8537 | 0% | 100% | 100% | 100% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 105 | 102 | 55096963 | 4939 | 118.536 | 4.939 | 2.6 | 2.6 | 2B+1S | 0 | 995 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41055652 | 1056 | 213.8085 | 0% | 100% | 100% | 0% | 100% | 0% | 9398341 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 97 | 105 | 55101137 | 4174 | 100.176 | 4.174 | 2.5 | 2.5 | 2B+1S | 0 | 955 | 1108 | 0 | 1047 | N/A | N/A | N/A | N/A | 41056484 | 832 | 199.3292 | 0% | 100% | 100% | 0% | 100% | 0% | 9398341 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 112 | 106 | 55104954 | 3817 | 91.608 | 3.817 | 3.6 | 3.6 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41057056 | 572 | 149.8559 | 0% | 0% | 100% | 0% | 100% | 25% | 9399325 | 984 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 31 | 21.831 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 94 | 64 | 55107617 | 2663 | 63.912 | 2.663 | 4.9 | 4.9 | 1B | 0 | 0 | 1038 | 0 | 0 | N/A | N/A | N/A | N/A | 41057396 | 340 | 127.6756 | 0% | 0% | 100% | 0% | 0% | 25% | 9400462 | 1137 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 117.9167 | 119533 | 119533 | 119.533 | 119.533 | [12 empty] | 25088 | 25088 | 209.8835 | [6 empty] | 7638 | 7638 | 1.1933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (35%)
BP1 - STARTED @ 2:10 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 13 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25360 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55107617 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41057396 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9400462 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 106 | 62 | 55110205 | 2588 | 62.112 | 2.588 | 6.7 | 6.7 | 1B | 0 | 0 | 1068 | 0 | 0 | N/A | N/A | N/A | N/A | 41057768 | 372 | 143.7403 | 0% | 0% | 100% | 0% | 0% | 35% | 9402221 | 1759 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 106 | 71 | 55112813 | 2608 | 62.592 | 2.608 | 8.5 | 8.5 | 1B | 0 | 0 | 1008 | 0 | 0 | N/A | N/A | N/A | N/A | 41058128 | 360 | 138.0368 | 0% | 0% | 100% | 0% | 0% | 35% | 9403992 | 1771 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 90 | 94 | 55117032 | 4219 | 101.256 | 4.219 | 9.5 | 9.5 | 2B | 0 | 0 | 958 | 0 | 958 | N/A | N/A | N/A | N/A | 41058762 | 634 | 150.2726 | 0% | 0% | 100% | 0% | 100% | 35% | 9405265 | 1273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 92 | 55120728 | 3696 | 88.704 | 3.696 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 0 | 967 | N/A | N/A | N/A | N/A | 41059232 | 470 | 127.1645 | 0% | 0% | 100% | 0% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 136 | 55124845 | 4117 | 98.808 | 4.117 | 9.5 | 9.5 | 2B | 0 | 0 | 1080 | 0 | 1017 | N/A | N/A | N/A | N/A | 41059844 | 612 | 148.6519 | 0% | 0% | 100% | 0% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 125 | 55130035 | 5190 | 124.56 | 5.19 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41060780 | 936 | 180.3468 | 0% | 0% | 100% | 0% | 100% | 0% | 9405265 | 0 | 1.47 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 149 | 55135960 | 5925 | 142.2 | 5.925 | 9.4 | 9.4 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41062104 | 1324 | 223.4599 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 152 | 55142168 | 6208 | 148.992 | 6.208 | 8.6 | 8.6 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41063508 | 1404 | 226.1598 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 55148440 | 6272 | 150.528 | 6.272 | 7.7 | 7.7 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41064916 | 1408 | 224.4898 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 155 | 55154647 | 6207 | 148.968 | 6.207 | 6.9 | 6.9 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41066316 | 1400 | 225.5518 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 | 1.29 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 55160874 | 6227 | 149.448 | 6.227 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41067716 | 1400 | 224.8274 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 151 | 55166864 | 5990 | 143.76 | 5.99 | 5.7 | 5.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41069080 | 1364 | 227.7129 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 135 | 55172640 | 5776 | 138.624 | 5.776 | 5.2 | 5.2 | 3B+1S | 1046 |  | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41070412 | 1332 | 230.6094 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 133 | 55178386 | 5746 | 137.904 | 5.746 | 4.8 | 4.8 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41071756 | 1344 | 233.9018 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 55184006 | 5620 | 134.88 | 5.62 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41073076 | 1320 | 234.8754 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 55189586 | 5580 | 133.92 | 5.58 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41074396 | 1320 | 236.5591 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 55195233 | 5647 | 135.528 | 5.647 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41075716 | 1320 | 233.7524 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 55200956 | 5723 | 137.352 | 5.723 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41077044 | 1328 | 232.0461 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 55206686 | 5730 | 137.52 | 5.73 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41078372 | 1328 | 231.7627 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 55212292 | 5606 | 134.544 | 5.606 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41079668 | 1296 | 231.1809 | 100% | 0% | 100% | 100% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 105 | 127 | 55217673 | 5381 | 129.144 | 5.381 | 2 | 2 | 2B+1S | 1179 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41080824 | 1156 | 214.83 | 100% | 0% | 100% | 0% | 100% | 0% | 9405265 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 107 | 55222603 | 4930 | 118.32 | 4.93 | 1.6 | 1.6 | 2B+1S | 1023 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 41081796 | 972 | 197.1602 | 100% | 0% | 0% | 100% | 100% | 0% | 9405265 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 104 | 82 | 55226039 | 3436 | 82.464 | 3.436 | 2.5 | 2.5 | 2B | 0 | 0 | 986 | 0 | 896 | N/A | N/A | N/A | N/A | 41082372 | 576 | 167.6368 | 0% | 0% | 100% | 0% | 100% | 25% | 9406221 | 956 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 22 | 15.493 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 95 | 69 | 55229099 | 3060 | 73.44 | 3.06 | 3.8 | 3.8 | 1B | 0 | 0 | 0 | 0 | 1008 | N/A | N/A | N/A | N/A | 41082756 | 384 | 125.4902 | 0% | 0% | 0% | 0% | 100% | 25% | 9407544 | 1323 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.3333 | 121482 | 121482 | 121.482 | 121.482 | [12 empty] | 25360 | 25360 | 208.7552 | [6 empty] | 7082 | 7082 | 1.2267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (35%)
BP3 - STARTED @ 2:00 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 14 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
BP2 - START @ 9:10 PM DUE TO MODIFICATION ON SCALING BOARD OF MOV DRIVE
BP1 - STOPPED @ 9:11 PM DUE TO MODIFICATION ON SCALING BOARD OF MOV DRIVE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 10:01 PM DUE TO MODIFICATION ON SCALING BOARD OF MOV DRIVE
BP1 - START @ 10:02 PM DUE TO MODIFICATION ON SCALING BOARD OF MOV DRIVE
BP3 - START @ 10:45PM DUE TO MODIFICATION ON SCALING BOARD OF MOV DRIVE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25248 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55229099 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41082756 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9407544 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 21 | 14.7887 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 113 | 63 | 55231659 | 2560 | 61.44 | 2.56 | 5.8 | 5.8 | 1B | 0 | 0 | 0 | 0 | 1027 | N/A | N/A | N/A | N/A | 41083084 | 328 | 128.125 | 0% | 0% | 0% | 0% | 100% | 35% | 9409408 | 1864 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 22 | 15.493 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 114 | 70 | 55234634 | 2975 | 71.4 | 2.975 | 8.1 | 8.1 | 1B | 0 | 0 | 0 | 0 | 1030 | N/A | N/A | N/A | N/A | 41083492 | 408 | 137.1429 | 0% | 0% | 0% | 0% | 100% | 35% | 9411551 | 2143 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 93 | 55238493 | 3859 | 92.616 | 3.859 | 9.5 | 9.5 | 2B | 0 | 0 | 980 | 0 | 1028 | N/A | N/A | N/A | N/A | 41084100 | 608 | 157.5538 | 0% | 0% | 100% | 0% | 100% | 35% | 9412866 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 96 | 55242465 | 3972 | 95.328 | 3.972 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 1017 | N/A | N/A | N/A | N/A | 41084684 | 584 | 147.0292 | 0% | 0% | 100% | 0% | 100% | 35% | 9412894 | 28 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 119 | 115 | 55246534 | 4069 | 97.656 | 4.069 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1128 | N/A | N/A | N/A | N/A | 41085276 | 592 | 145.4903 | 0% | 0% | 100% | 0% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 119 | 55251632 | 5098 | 122.352 | 5.098 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41086220 | 944 | 185.1707 | 0% | 0% | 100% | 0% | 100% | 0% | 9412894 | 0 | 1.13 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 55257803 | 6171 | 148.104 | 6.171 | 9.1 | 9.1 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41087596 | 1376 | 222.9784 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 152 | 55264066 | 6263 | 150.312 | 6.263 | 8.3 | 8.3 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41089014 | 1418 | 226.4091 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 55270381 | 6315 | 151.56 | 6.315 | 7.5 | 7.5 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41090424 | 1410 | 223.2779 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 152 | 55276694 | 6313 | 151.512 | 6.313 | 6.6 | 6.6 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41091844 | 1420 | 224.9327 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 156 | 55282934 | 6240 | 149.76 | 6.24 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41093236 | 1392 | 223.0769 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 55288932 | 5998 | 143.952 | 5.998 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41094612 | 1376 | 229.4098 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 131 | 55294765 | 5833 | 139.992 | 5.833 | 5 | 5 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41095972 | 1360 | 233.1562 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 134 | 55300427 | 5662 | 135.888 | 5.662 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41097300 | 1328 | 234.5461 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 130 | 55305823 | 5396 | 129.504 | 5.396 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41098572 | 1272 | 235.7302 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 130 | 55311481 | 5658 | 135.792 | 5.658 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41099892 | 1320 | 233.298 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 55317106 | 5625 | 135 | 5.625 | 4.1 | 4.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41101208 | 1316 | 233.9556 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 55322746 | 5640 | 135.36 | 5.64 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41102528 | 1320 | 234.0426 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 55328346 | 5600 | 134.4 | 5.6 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41103852 | 1324 | 236.4286 | 0% | 100% | 100% | 100% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 107 | 162 | 55333863 | 5517 | 132.408 | 5.517 | 2.7 | 2.7 | 2B+1S | 0 | 1189 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 41105028 | 1176 | 213.1593 | 0% | 100% | 100% | 0% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 117 | 55339092 | 5229 | 125.496 | 5.229 | 1.7 | 1.7 | 2B+1S | 0 | 1077 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41106124 | 1096 | 209.6003 | 0% | 100% | 100% | 0% | 100% | 0% | 9412894 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 26 | 18.3099 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 107 | 55343601 | 4509 | 108.216 | 4.509 | 1.6 | 1.6 | 2B+1S | 0 | 955 | 1187 | 0 | 987 | N/A | N/A | N/A | N/A | 41107024 | 900 | 199.6008 | 0% | 100% | 100% | 0% | 100% | 0% | 9412894 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 25 | 17.6056 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 88 | 55347564 | 3963 | 95.112 | 3.963 | 2.5 | 2.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41107620 | 596 | 150.3911 | 0% | 0% | 100% | 0% | 100% | 25% | 9413811 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 30 | 21.1268 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 98 | 73 | 55350553 | 2989 | 71.736 | 2.989 | 3.7 | 3.7 | 1B | 0 | 0 | 1048 | 0 | 0 | N/A | N/A | N/A | N/A | 41108004 | 384 | 128.4711 | 0% | 0% | 100% | 0% | 0% | 25% | 9414925 | 1114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.25 | 121454 | 121454 | 121.454 | 121.454 | [12 empty] | 25248 | 25248 | 207.8812 | [6 empty] | 7381 | 7381 | 1.105 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (35%)
BP1 - STARTED @ 2:00 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 15 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25516 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55350553 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41108004 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9414925 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 23 | 16.1972 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 111 | 66 | 55353284 | 2731 | 65.544 | 2.731 | 5.5 | 5.5 | 1B | 0 | 0 | 1088 | 0 | 0 | N/A | N/A | N/A | N/A | 41108380 | 376 | 137.6785 | 0% | 0% | 100% | 0% | 0% | 35% | 9416608 | 1683 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 109 | 68 | 55356153 | 2869 | 68.856 | 2.869 | 7.3 | 7.3 | 1B | 0 | 0 | 1048 | 0 | 0 | N/A | N/A | N/A | N/A | 41108764 | 384 | 133.8445 | 0% | 0% | 100% | 0% | 0% | 35% | 9418396 | 1788 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 96 | 55360257 | 4104 | 98.496 | 4.104 | 8.8 | 8.8 | 2B | 0 | 0 | 988 | 0 | 988 | N/A | N/A | N/A | N/A | 41109324 | 560 | 136.4522 | 0% | 0% | 100% | 0% | 100% | 35% | 9419755 | 1359 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 96 | 55364193 | 3936 | 94.464 | 3.936 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 41109892 | 568 | 144.3089 | 0% | 0% | 100% | 0% | 100% | 35% | 9420435 | 680 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 102 | 55368581 | 4388 | 105.312 | 4.388 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 0 | 1097 | N/A | N/A | N/A | N/A | 41110516 | 624 | 142.206 | 0% | 0% | 100% | 0% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 109 | 55373242 | 4661 | 111.864 | 4.661 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41111388 | 872 | 187.0843 | 0% | 0% | 100% | 0% | 100% | 0% | 9420435 | 0 | 0.96 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 145 | 55379339 | 6097 | 146.328 | 6.097 | 8.8 | 8.8 | 3B+1S | 1129 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41112764 | 1376 | 225.6848 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 151 | 55385807 | 6468 | 155.232 | 6.468 | 7.9 | 7.9 | 3B+1S | 1129 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41114240 | 1476 | 228.2004 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 55391974 | 6167 | 148.008 | 6.167 | 7 | 7 | 3B+1S | 1129 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41115632 | 1392 | 225.7175 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 55398294 | 6320 | 151.68 | 6.32 | 6.2 | 6.2 | 3B+1S | 1129 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41117072 | 1440 | 227.8481 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 | 1.08 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 154 | 55404650 | 6356 | 152.544 | 6.356 | 5.3 | 5.3 | 3B+1S | 1129 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41118508 | 1436 | 225.9283 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 157 | 55410904 | 6254 | 150.096 | 6.254 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41119908 | 1400 | 223.8567 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 55416901 | 5997 | 143.928 | 5.997 | 4.3 | 4.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41121268 | 1360 | 226.7801 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 55422734 | 5833 | 139.992 | 5.833 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41122628 | 1360 | 233.1562 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 134 | 55428886 | 6152 | 147.648 | 6.152 | 3.6 | 3.6 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41124052 | 1424 | 231.4694 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 55434386 | 5500 | 132 | 5.5 | 3.5 | 3.5 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41125340 | 1288 | 234.1818 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 55440012 | 5626 | 135.024 | 5.626 | 3.4 | 3.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41126656 | 1316 | 233.914 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 55445423 | 5411 | 129.864 | 5.411 | 3.1 | 3.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41127920 | 1264 | 233.5982 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 55451013 | 5590 | 134.16 | 5.59 | 3 | 3 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41129248 | 1328 | 237.5671 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 131 | 55456426 | 5413 | 129.912 | 5.413 | 2.9 | 2.9 | 2B+1S | 975 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41130536 | 1288 | 237.9457 | 100% | 0% | 100% | 100% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 104 | 114 | 55461581 | 5155 | 123.72 | 5.155 | 2.4 | 2.4 | 2B+1S | 1076 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41131640 | 1104 | 214.161 | 100% | 0% | 100% | 0% | 100% | 0% | 9420435 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 109 | 55466185 | 4604 | 110.496 | 4.604 | 2.3 | 2.3 | 2B+1S | 985 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41132616 | 976 | 211.9896 | 100% | 0% | 100% | 0% | 100% | 0% | 9420435 | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 83 | 55469806 | 3621 | 86.904 | 3.621 | 3.2 | 3.2 | 2B | 0 | 0 | 947 | 0 | 947 | N/A | N/A | N/A | N/A | 41133156 | 540 | 149.1301 | 0% | 0% | 100% | 0% | 100% | 25% | 9421398 | 963 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 27 | 19.0141 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 101 | 65 | 55472768 | 2962 | 71.088 | 2.962 | 4.6 | 4.6 | 1B | 0 | 0 | 0 | 0 | 1028 | N/A | N/A | N/A | N/A | 41133520 | 364 | 122.8899 | 0% | 0% | 0% | 0% | 100% | 25% | 9422692 | 1294 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.4167 | 122215 | 122215 | 122.215 | 122.215 | [12 empty] | 25516 | 25516 | 208.7796 | [6 empty] | 7767 | 7767 | 1.025 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (35%)
BP3 - STARTED @ 2:00 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 16 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)
BP1- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25092 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55472768 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41133520 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9422692 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 22 | 15.493 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 115 | 72 | 55475561 | 2793 | 67.032 | 2.793 | 6 | 6 | 1B | 0 | 0 | 0 | 0 | 1048 | N/A | N/A | N/A | N/A | 41133884 | 364 | 130.3258 | 0% | 0% | 0% | 0% | 100% | 35% | 9424211 | 1519 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 22 | 15.493 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 126 | 80 | 55478761 | 3200 | 76.8 | 3.2 | 7.9 | 7.9 | 1B | 0 | 0 | 0 | 0 | 1188 | N/A | N/A | N/A | N/A | 41134324 | 440 | 137.5 | 0% | 0% | 0% | 0% | 100% | 35% | 9425987 | 1776 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 97 | 55482751 | 3990 | 95.76 | 3.99 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 0 | 988 | N/A | N/A | N/A | N/A | 41134908 | 584 | 146.3659 | 0% | 0% | 100% | 0% | 100% | 35% | 9427340 | 1353 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 91 | 55486674 | 3923 | 94.152 | 3.923 | 9.5 | 9.5 | 2B | 0 | 0 | 948 | 0 | 947 | N/A | N/A | N/A | N/A | 41135428 | 520 | 132.5516 | 0% | 0% | 100% | 0% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 100 | 55490701 | 4027 | 96.648 | 4.027 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 0 | 1008 | N/A | N/A | N/A | N/A | 41135980 | 552 | 137.0747 | 0% | 0% | 100% | 0% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 117 | 55495698 | 4997 | 119.928 | 4.997 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41136880 | 900 | 180.1081 | 0% | 0% | 100% | 0% | 100% | 0% | 9427340 | 0 | 1.18 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 55501654 | 5956 | 142.944 | 5.956 | 9.3 | 9.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41138204 | 1324 | 222.2968 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 140 | 55508022 | 6368 | 152.832 | 6.368 | 8.7 | 8.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41139612 | 1408 | 221.1055 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 151 | 55514327 | 6305 | 151.32 | 6.305 | 8 | 8 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41141020 | 1408 | 223.3148 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 153 | 55520679 | 6352 | 152.448 | 6.352 | 7.3 | 7.3 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41142428 | 1408 | 221.6625 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 154 | 55526996 | 6317 | 151.608 | 6.317 | 6.6 | 6.6 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41143824 | 1396 | 220.991 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 55533319 | 6323 | 151.752 | 6.323 | 5.9 | 5.9 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41145228 | 1404 | 222.0465 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 146 | 55539484 | 6165 | 147.96 | 6.165 | 5.4 | 5.4 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41146608 | 1380 | 223.8443 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 55545775 | 6291 | 150.984 | 6.291 | 4.6 | 4.6 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41148052 | 1444 | 229.5343 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 55551555 | 5780 | 138.72 | 5.78 | 4.3 | 4.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41149372 | 1320 | 228.3737 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 55557405 | 5850 | 140.4 | 5.85 | 3.9 | 3.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41150708 | 1336 | 228.3761 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 55563171 | 5766 | 138.384 | 5.766 | 3.5 | 3.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41152036 | 1328 | 230.3156 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 55568886 | 5715 | 137.16 | 5.715 | 3.3 | 3.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41153356 | 1320 | 230.9711 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 133 | 55574442 | 5556 | 133.344 | 5.556 | 3.2 | 3.2 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41154668 | 1312 | 236.1411 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 127 | 55579841 | 5399 | 129.576 | 5.399 | 3.1 | 3.1 | 3B+1S | 0 | 995 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41155912 | 1244 | 230.413 | 0% | 100% | 100% | 100% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 101 | 112 | 55584964 | 5123 | 122.952 | 5.123 | 2.5 | 2.5 | 2B+1S | 0 | 1035 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41156972 | 1060 | 206.91 | 0% | 100% | 100% | 0% | 100% | 0% | 9427340 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 23 | 16.1972 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 99 | 98 | 55589221 | 4257 | 102.168 | 4.257 | 2.4 | 2.4 | 2B+1S | 0 | 965 | 1037 | 0 | 1027 | N/A | N/A | N/A | N/A | 41157760 | 788 | 185.1069 | 0% | 100% | 100% | 0% | 100% | 0% | 9427340 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 110 | 86 | 55592952 | 3731 | 89.544 | 3.731 | 3.2 | 3.2 | 2B | 0 | 0 | 947 | 0 | 947 | N/A | N/A | N/A | N/A | 41158284 | 524 | 140.4449 | 0% | 0% | 100% | 0% | 100% | 25% | 9428228 | 888 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 28 | 19.7183 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A ONG | 11.5 | 94 | 68 | 55595851 | 2899 | 69.576 | 2.899 | 4.4 | 4.4 | 1B | 0 | 0 | 997 | 0 | 0 | N/A | N/A | N/A | N/A | 41158612 | 328 | 113.1425 | 0% | 0% | 100% | 0% | 0% | 25% | 9429296 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.2917 | 123083 | 123083 | 123.083 | 123.083 | [12 empty] | 25092 | 25092 | 203.8624 | [6 empty] | 6604 | 6604 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (35%)
BP1 - STARTED @ 2:00 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV1 CLOSED @ 2:47 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 17 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)
BP3- STOPPED @ 11:01 PM DUE TO OPERATION ADJUSTMENT TARGET PREASSURE 56psi

## OCT 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24456 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55595851 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41158612 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9429296 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 24 | 16.9014 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.4 | 109 | 67 | 55598644 | 2793 | 67.032 | 2.793 | 6.1 | 6.1 | 1B | 0 | 0 | 1018 | 0 | 0 | N/A | N/A | N/A | N/A | 41158940 | 328 | 117.4364 | 0% | 0% | 100% | 0% | 0% | 35% | 9431037 | 1741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 25 | 17.6056 | 56 | 39.4366 | Automatic - Pressure Setting | 34.507 | 35.9155 | 40.1408 | 14 | A.ONG | 11.2 | 109 | 66 | 55601387 | 2743 | 65.832 | 2.743 | 7.9 | 7.9 | 1B | 0 | 0 | 1019 | 0 | 0 | N/A | N/A | N/A | N/A | 41159268 | 328 | 119.5771 | 0% | 0% | 100% | 0% | 0% | 35% | 9432711 | 1674 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 109 | 55605147 | 3760 | 90.24 | 3.76 | 9.3 | 9.3 | 2B | 0 | 0 | 1028 | 0 | 1038 | N/A | N/A | N/A | N/A | 41159800 | 532 | 141.4894 | 0% | 0% | 100% | 0% | 100% | 35% | 9434079 | 1368 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 96 | 55609219 | 4072 | 97.728 | 4.072 | 9.7 | 9.7 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41160340 | 540 | 132.613 | 0% | 0% | 100% | 0% | 100% | 35% | 9434310 | 231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 98 | 55613167 | 3948 | 94.752 | 3.948 | 9.7 | 9.7 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 41160868 | 528 | 133.7386 | 0% | 0% | 100% | 0% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 113 | 105 | 55617647 | 4480 | 107.52 | 4.48 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 0 | 1046 | N/A | N/A | N/A | N/A | 41161556 | 688 | 153.5714 | 0% | 0% | 100% | 0% | 100% | 0% | 9434310 | 0 | 1.11 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 134 | 55623179 | 5532 | 132.768 | 5.532 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 41162672 | 1116 | 201.7354 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 55629207 | 6028 | 144.672 | 6.028 | 9.1 | 9.1 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41163964 | 1292 | 214.3331 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 151 | 55635321 | 6114 | 146.736 | 6.114 | 8.8 | 8.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41165308 | 1344 | 219.8234 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 152 | 55641609 | 6288 | 150.912 | 6.288 | 8.2 | 8.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41166700 | 1392 | 221.374 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 55647885 | 6276 | 150.624 | 6.276 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41168084 | 1384 | 220.5226 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 151 | 55654136 | 6251 | 150.024 | 6.251 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41169464 | 1380 | 220.7647 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 142 | 142 | 55660425 | 6289 | 150.936 | 6.289 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41170852 | 1388 | 220.7028 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 14 | 9.8592 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 140 | 142 | 55666503 | 6078 | 145.872 | 6.078 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41172164 | 1312 | 215.8605 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 17 | 11.9718 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 121 | 55672461 | 5958 | 142.992 | 5.958 | 6.4 | 6.4 | 3B+1S | 1007 | 0 | 1117 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41173348 | 1184 | 198.7244 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 55678281 | 5820 | 139.68 | 5.82 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 41174628 | 1280 | 219.9313 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 55684209 | 5928 | 142.272 | 5.928 | 5.9 | 5.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41175984 | 1356 | 228.7449 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 55690203 | 5994 | 143.856 | 5.994 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1158 | 1185 | 1157 | N/A | N/A | N/A | N/A | 41177316 | 1332 | 222.2222 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 137 | 55695634 | 5431 | 130.344 | 5.431 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 41178516 | 1200 | 220.9538 | 100% | 0% | 100% | 100% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 131 | 55701144 | 5510 | 132.24 | 5.51 | 4.6 | 4.6 | 3B+1S | 1138 | 0 | 1178 | 0 | 1178 | N/A | N/A | N/A | N/A | 41179576 | 1060 | 192.3775 | 100% | 0% | 100% | 0% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 130 | 55706467 | 5323 | 127.752 | 5.323 | 3.6 | 3.6 | 2B+1S | 1119 | 0 | 1117 | 0 | 1178 | N/A | N/A | N/A | N/A | 41180644 | 1068 | 200.6387 | 100% | 0% | 100% | 0% | 100% | 0% | 9434310 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 121 | 55711825 | 5358 | 128.592 | 5.358 | 2.9 | 2.9 | 2B+1S | 1046 | 0 | 1138 | 0 | 1138 | N/A | N/A | N/A | N/A | 41181696 | 1052 | 196.3419 | 100% | 0% | 100% | 0% | 100% | 0% | 9434310 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 98 | 55716256 | 4431 | 106.344 | 4.431 | 3.5 | 3.5 | 2B | 0 | 0 | 1058 | 0 | 1058 | N/A | N/A | N/A | N/A | 41182440 | 744 | 167.9079 | 0% | 0% | 100% | 0% | 100% | 25% | 9435035 | 725 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 115 | 91 | 55720216 | 3960 | 95.04 | 3.96 | 4.5 | 4.5 | 2B | 0 | 0 | 1007 | 0 | 997 | N/A | N/A | N/A | N/A | 41183068 | 628 | 158.5859 | 0% | 0% | 100% | 0% | 100% | 25% | 9435845 | 810 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123 | 124365 | 124365 | 124.365 | 124.365 | [12 empty] | 24456 | 24456 | 196.647 | [6 empty] | 6549 | 6549 | 1.1833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (35%)
BP3 - STARTED @ 2:25 AM DUE TO THE NORMAL TARGET DISCHARGE PRESSURE 66psi
XCV2 CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 17 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)

## OCT 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55720216 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41183068 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9435845 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 93 | 55724156 | 3940 | 94.56 | 3.94 | 5.8 | 5.8 | 2B | 0 | 0 | 1037 | 0 | 1037 | N/A | N/A | N/A | N/A | 41183668 | 600 | 152.2843 | 0% | 0% | 100% | 0% | 100% | 35% | 9437150 | 1305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 89 | 55727843 | 3687 | 88.488 | 3.687 | 7 | 7 | 2B | 0 | 0 | 1017 | 0 | 1028 | N/A | N/A | N/A | N/A | 41184260 | 592 | 160.5641 | 0% | 0% | 100% | 0% | 100% | 35% | 9438266 | 1116 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 88 | 55731555 | 3712 | 89.088 | 3.712 | 8.2 | 8.2 | 2B | 0 | 0 | 1007 | 0 | 997 | N/A | N/A | N/A | N/A | 41184836 | 576 | 155.1724 | 0% | 0% | 100% | 0% | 100% | 35% | 9439466 | 1200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 91 | 55735382 | 3827 | 91.848 | 3.827 | 9.4 | 9.4 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 41185416 | 580 | 151.5547 | 0% | 0% | 100% | 0% | 100% | 35% | 9440624 | 1158 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 96 | 55739312 | 3930 | 94.32 | 3.93 | 9.5 | 9.5 | 2B | 0 | 0 | 968 | 0 | 967 | N/A | N/A | N/A | N/A | 41185964 | 548 | 139.4402 | 0% | 0% | 100% | 0% | 100% | 35% | 9440912 | 288 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 115 | 55743899 | 4587 | 110.088 | 4.587 | 9.5 | 9.5 | 2B | 0 | 0 | 1128 | 0 | 1118 | N/A | N/A | N/A | N/A | 41186704 | 740 | 161.3255 | 0% | 0% | 100% | 0% | 100% | 0% | 9440912 | 0 | 1.05 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 55749663 | 5764 | 138.336 | 5.764 | 9.5 | 9.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41187956 | 1252 | 217.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 55755789 | 6126 | 147.024 | 6.126 | 9.1 | 9.1 | 3B+1S | 0 | 1058 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41189324 | 1368 | 223.3105 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 55762043 | 6254 | 150.096 | 6.254 | 8.4 | 8.4 | 3B+1S | 0 | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41190728 | 1404 | 224.4963 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 55768193 | 6150 | 147.6 | 6.15 | 7.7 | 7.7 | 3B+1S | 0 | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41192108 | 1380 | 224.3902 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 155 | 55774543 | 6350 | 152.4 | 6.35 | 6.9 | 6.9 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41193532 | 1424 | 224.252 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 149 | 55780701 | 6158 | 147.792 | 6.158 | 6.2 | 6.2 | 3B+1S | 0 | 1107 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41194932 | 1400 | 227.3465 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 142 | 55786796 | 6095 | 146.28 | 6.095 | 5.4 | 5.4 | 3B+1S | 0 | 1098 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41196340 | 1408 | 231.009 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 137 | 55792704 | 5908 | 141.792 | 5.908 | 4.7 | 4.7 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41197724 | 1384 | 234.2586 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 140 | 55798526 | 5822 | 139.728 | 5.822 | 4 | 4 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41199092 | 1368 | 234.9708 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 141 | 55804285 | 5759 | 138.216 | 5.759 | 3.4 | 3.4 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41200456 | 1364 | 236.8467 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 141 | 55810065 | 5780 | 138.72 | 5.78 | 2.9 | 2.9 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41201804 | 1348 | 233.218 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 55815712 | 5647 | 135.528 | 5.647 | 2.6 | 2.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41203116 | 1312 | 232.3358 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 55821423 | 5711 | 137.064 | 5.711 | 2.5 | 2.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41204468 | 1352 | 236.7361 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 128 | 55826987 | 5564 | 133.536 | 5.564 | 2.4 | 2.4 | 3B+1S | 0 | 1005 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 41205752 | 1284 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 125 | 124 | 55832374 | 5387 | 129.288 | 5.387 | 2.3 | 2.3 | 3B+1S | 0 | 1005 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 41206996 | 1244 | 230.9263 | 0% | 100% | 100% | 100% | 100% | 0% | 9440912 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 120 | 55837276 | 4902 | 117.648 | 4.902 | 1.9 | 1.9 | 2B+1S | 0 | 1045 | 1178 | 0 | 1178 | N/A | N/A | N/A | N/A | 41208004 | 1008 | 205.6304 | 0% | 100% | 100% | 0% | 100% | 0% | 9440912 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 115 | 91 | 55841471 | 4195 | 100.68 | 4.195 | 2.7 | 2.7 | 2B | 0 | 0 | 1037 | 0 | 1017 | N/A | N/A | N/A | N/A | 41208708 | 704 | 167.8188 | 0% | 0% | 100% | 0% | 100% | 35% | 9441697 | 785 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 88 | 55845244 | 3773 | 90.552 | 3.773 | 3.8 | 3.8 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 41209300 | 592 | 156.9043 | 0% | 0% | 100% | 0% | 100% | 35% | 9442785 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 124.125 | 125028 | 125028 | 125.028 | 125.028 | [12 empty] | 26232 | 26232 | 209.809 | [6 empty] | 6940 | 6940 | 1.0383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (35%)
XCV1 CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 17 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)

## OCT 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/ PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26952 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55845244 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41209300 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9442785 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 88 | 55848879 | 3635 | 87.24 | 3.635 | 5.7 | 5.7 | 2B | 0 | 0 | 1027 | 0 | 1026 | N/A | N/A | N/A | N/A | 41209890 | 590 | 162.3109 | 0% | 0% | 100% | 0% | 100% | 40% | 9444175 | 1390 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 86 | 55852519 | 3640 | 87.36 | 3.64 | 6.9 | 6.9 | 2B | 0 | 0 | 1027 | 0 | 1026 | N/A | N/A | N/A | N/A | 41210485 | 595 | 163.4615 | 0% | 0% | 100% | 0% | 100% | 40% | 9445569 | 1394 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 86 | 55856166 | 3647 | 87.528 | 3.647 | 8.3 | 8.3 | 2B | 0 | 0 | 1027 | 0 | 1026 | N/A | N/A | N/A | N/A | 41211084 | 599 | 164.2446 | 0% | 0% | 100% | 0% | 100% | 40% | 9446968 | 1399 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 87 | 55859769 | 3603 | 86.472 | 3.603 | 9.3 | 9.3 | 2B | 0 | 0 | 1008 | 0 | 1007 | N/A | N/A | N/A | N/A | 41211652 | 568 | 157.6464 | 0% | 0% | 100% | 0% | 100% | 40% | 9447942 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 99 | 55863783 | 4014 | 96.336 | 4.014 | 9.5 | 9.5 | 2B | 0 | 0 | 1028 | 0 | 1027 | N/A | N/A | N/A | N/A | 41212268 | 616 | 153.4629 | 0% | 0% | 100% | 0% | 100% | 40% | 9448215 | 273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 | 135 | 55868599 | 4816 | 115.584 | 4.816 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41213220 | 952 | 197.6744 | 0% | 0% | 100% | 0% | 100% | 0% | 9448215 | 0 | 1.07 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 138 | 55874469 | 5870 | 140.88 | 5.87 | 9.3 | 9.3 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41214572 | 1352 | 230.3237 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 55880457 | 5988 | 143.712 | 5.988 | 8.6 | 8.6 | 3B+1S | 1057 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41215956 | 1384 | 231.1289 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 55886577 | 6120 | 146.88 | 6.12 | 7.8 | 7.8 | 3B+1S | 1119 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41217372 | 1416 | 231.3725 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 55892797 | 6220 | 149.28 | 6.22 | 6.9 | 6.9 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41218796 | 1424 | 228.9389 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 | 1.27 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 55899019 | 6222 | 149.328 | 6.222 | 6.1 | 6.1 | 3B+1S | 1118 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41220228 | 1432 | 230.1511 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 148 | 55905107 | 6088 | 146.112 | 6.088 | 5.3 | 5.3 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41221636 | 1408 | 231.2746 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 55911135 | 6028 | 144.672 | 6.028 | 4.6 | 4.6 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41223044 | 1408 | 233.5766 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 55916902 | 5767 | 138.408 | 5.767 | 3.8 | 3.8 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41224420 | 1376 | 238.5989 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 55922594 | 5692 | 136.608 | 5.692 | 3.3 | 3.3 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41225788 | 1368 | 240.3373 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 131 | 55928166 | 5572 | 133.728 | 5.572 | 2.9 | 2.9 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41227124 | 1336 | 239.7703 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 133 | 55933797 | 5631 | 135.144 | 5.631 | 2.5 | 2.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41228476 | 1352 | 240.0994 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 131 | 55939251 | 5454 | 130.896 | 5.454 | 2.1 | 2.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41229784 | 1308 | 239.824 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 55944760 | 5509 | 132.216 | 5.509 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41231104 | 1320 | 239.6079 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 131 | 55950913 | 6153 | 147.672 | 6.153 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41232420 | 1316 | 213.8794 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 | 122 | 55955583 | 4670 | 112.08 | 4.67 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41233748 | 1328 | 284.3683 | 100% | 0% | 100% | 100% | 100% | 0% | 9448215 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 118 | 55960422 | 4839 | 116.136 | 4.839 | 1.4 | 1.4 | 2B+1S | 1015 | 0 | 1188 |  | 1187 | N/A | N/A | N/A | N/A | 41234768 | 1020 | 210.7874 | 100% | 0% | 100% | 0% | 100% | 0% | 9448215 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 99 | 55964793 | 4371 | 104.904 | 4.371 | 1.9 | 1.9 | 2B | 0 | 0 | 1088 |  | 1087 | N/A | N/A | N/A | N/A | 41235596 | 828 | 189.4303 | 0% | 0% | 100% |  | 100% | 25% | 9448801 | 586 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 114 | 88 | 55968672 | 3879 | 93.096 | 3.879 | 2.7 | 2.7 | 2B | 0 | 0 | 1018 |  | 1017 | N/A | N/A | N/A | N/A | 41236252 | 656 | 169.1158 | 0% | 0% | 100% | 0% | 100% | 25% | 9449556 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.75 | 123428 | 123428 | 123.428 | 123.428 | [12 empty] | 26952 | 26952 | 218.3621 | [6 empty] | 6771 | 6771 | 1.1167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (40%)
XCV2 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 20 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)

## OCT 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26776 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 55968672 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41236252 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9449556 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 88 | 55972456 | 3784 | 90.816 | 3.784 | 4 | 4 | 2B | 0 | 0 | 1047 | 0 | 1047 | N/A | N/A | N/A | N/A | 41236884 | 632 | 167.019 | 0% | 0% | 100% | 0% | 100% | 45% | 9450751 | 1195 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 85 | 55975804 | 3348 | 80.352 | 3.348 | 5.5 | 5.5 | 2B | 0 | 0 | 1047 | 0 | 10547 | N/A | N/A | N/A | N/A | 41237480 | 596 | 178.0167 | 0% | 0% | 100% | 0% | 100% | 45% | 9452196 | 1445 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 83 | 55979358 | 3554 | 85.296 | 3.554 | 7.2 | 7.2 | 2B | 0 | 0 | 1037 | 0 | 1037 | N/A | N/A | N/A | N/A | 41238108 | 628 | 176.7023 | 0% | 0% | 100% | 0% | 100% | 45% | 9453747 | 1551 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 89 | 55982913 | 3555 | 85.32 | 3.555 | 8.6 | 8.6 | 2B | 0 | 0 | 1037 | 0 | 1037 | N/A | N/A | N/A | N/A | 41238716 | 608 | 171.0267 | 0% | 0% | 100% | 0% | 100% | 45% | 9455196 | 1449 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 121 | 101 | 55986746 | 3833 | 91.992 | 3.833 | 9.4 | 9.4 | 2B | 0 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 41239356 | 640 | 166.971 | 0% | 0% | 100% | 0% | 100% | 45% | 9455890 | 694 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 118 | 55991553 | 4807 | 115.368 | 4.807 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41240256 | 900 | 187.227 | 0% | 0% | 100% | 0% | 100% | 45% | 9456037 | 147 | 1.2 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 144 | 55997520 | 5967 | 143.208 | 5.967 | 9 | 9 | 3B+1S | 0 | 1119 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41241620 | 1364 | 228.5906 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 147 | 56003884 | 6364 | 152.736 | 6.364 | 8.1 | 8.1 | 3B+1S | 0 | 1118 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41243092 | 1472 | 231.3011 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 145 | 56009758 | 5874 | 140.976 | 5.874 | 7.1 | 7.1 | 3B+1S | 0 | 1168 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41244468 | 1376 | 234.2526 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 149 | 56016083 | 6325 | 151.8 | 6.325 | 6.1 | 6.1 | 3B+1S | 0 | 1189 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41245956 | 1488 | 235.2569 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 | 1.09 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 151 | 56022276 | 6193 | 148.632 | 6.193 | 5.2 | 5.2 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41247404 | 1448 | 233.8124 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 56028376 | 6100 | 146.4 | 6.1 | 4.2 | 4.2 | 3B+1S | 0 | 1187 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41248852 | 1448 | 237.377 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 136 | 56034326 | 5950 | 142.8 | 5.95 | 3.3 | 3.3 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41250276 | 1424 | 239.3277 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 134 | 56040143 | 5817 | 139.608 | 5.817 | 2.6 | 2.6 | 3B+1S | 0 | 1107 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41251668 | 1392 | 239.2986 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 56045773 | 5630 | 135.12 | 5.63 | 2.1 | 2.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41253012 | 1344 | 238.7211 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 56051343 | 5570 | 133.68 | 5.57 | 1.8 | 1.8 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41254344 | 1332 | 239.1382 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 56056993 | 5650 | 135.6 | 5.65 | 1.5 | 1.5 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41255692 | 1348 | 238.5841 | 0% | 100% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 135 | 56062607 | 5614 | 134.736 | 5.614 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41256996 | 1304 | 232.2765 | 0% | 0% | 100% | 100% | 100% | 0% | 9456037 | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 131 | 56068027 | 5420 | 130.08 | 5.42 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41258244 | 1248 | 230.2583 | 0% | 0% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 118 | 56073339 | 5312 | 127.488 | 5.312 | 1.3 | 1.3 | 3B | 0 | 0 | 1157 | 1185 | 1147 | N/A | N/A | N/A | N/A | 41259460 | 1216 | 228.9157 | 0% | 0% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 | 125 | 56078532 | 5193 | 124.632 | 5.193 | 1.3 | 1.3 | 3B | 0 | 0 | 1157 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41260648 | 1188 | 228.7695 | 0% | 0% | 100% | 100% | 100% | 0% | 9456037 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 112 | 56083652 | 5120 | 122.88 | 5.12 | 1.3 | 1.3 | 3B | 0 | 0 | 1057 | 1185 | 1047 | N/A | N/A | N/A | N/A | 41261756 | 1108 | 216.4062 | 0% | 0% | 100% | 100% | 100% | 0% | 9456037 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 110 | 89 | 56087426 | 3774 | 90.576 | 3.774 | 2.2 | 2.2 | 2B | 0 | 0 | 1058 | 0 | 1047 | N/A | N/A | N/A | N/A | 41262436 | 680 | 180.1802 | 0% | 0% | 100% | 0% | 100% | 25% | 9456862 | 825 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 106 | 81 | 56090924 | 3498 | 83.952 | 3.498 | 3.1 | 3.1 | 2B | 0 | 0 | 998 | 0 | 997 | N/A | N/A | N/A | N/A | 41263028 | 592 | 169.2396 | 0% | 0% | 100% | 0% | 100% | 25% | 9457927 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 122252 | 122.252 | 122.252 | [13 empty] | 26776 | 219.023 | [6 empty] | 8371 | 8371 | 1.1067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (45%)
XCV2 CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 22 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
SP1 - STOPPED @ 5:30 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)

## OCT 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26004 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56090924 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41263028 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9457927 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 79 | 56094196 | 3272 | 78.528 | 3.272 | 4.9 | 4.9 | 2B | 0 | 0 | 1027 | 0 | 1026 | N/A | N/A | N/A | N/A | 41263584 | 556 | 169.9267 | 0% | 0% | 100% | 0% | 100% | 45% | 9459599 | 1672 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 80 | 56097463 | 3267 | 78.408 | 3.267 | 6.5 | 6.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41264148 | 564 | 172.6354 | 0% | 0% | 100% | 0% | 100% | 45% | 9461192 | 1593 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 56101165 | 3702 | 88.848 | 3.702 | 8 | 8 | 2B | 0 | 0 | 1047 | 0 | 1047 | N/A | N/A | N/A | N/A | 41264760 | 612 | 165.316 | 0% | 0% | 100% | 0% | 100% | 45% | 9462570 | 1378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 132 | 94 | 56104916 | 3751 | 90.024 | 3.751 | 9.3 | 9.3 | 2B | 0 | 0 | 1037 | 0 | 1037 | N/A | N/A | N/A | N/A | 41265376 | 616 | 164.2229 | 0% | 0% | 100% | 0% | 100% | 45% | 9463902 | 1332 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 109 | 56108956 | 4040 | 96.96 | 4.04 | 9.8 | 9.8 | 2B | 0 | 0 | 1128 | 0 | 1128 | N/A | N/A | N/A | N/A | 41266020 | 644 | 159.4059 | 0% | 0% | 100% | 0% | 100% | 45% | 9464288 | 386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 127 | 56114022 | 5066 | 121.584 | 5.066 | 9.8 | 9.8 | 2B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41266948 | 928 | 183.182 | 0% | 0% | 100% | 0% | 100% | 45% | 9464288 | 0 | 1.17 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 148 | 56120146 | 6124 | 146.976 | 6.124 | 9.3 | 9.3 | 3B+1S | 1078 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41268340 | 1392 | 227.3024 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 56126265 | 6119 | 146.856 | 6.119 | 8.6 | 8.6 | 3B+1S | 1068 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41269740 | 1400 | 228.7956 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 56132427 | 6162 | 147.888 | 6.162 | 7.8 | 7.8 | 3B+1S | 1068 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41271132 | 1392 | 225.9007 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 56138519 | 6092 | 146.208 | 6.092 | 7.2 | 7.2 | 3B+1S | 1058 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41272540 | 1408 | 231.1228 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 | 1.07 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 56144793 | 6274 | 150.576 | 6.274 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41273932 | 1392 | 221.868 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 141 | 56150796 | 6003 | 144.072 | 6.003 | 6.1 | 6.1 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41275292 | 1360 | 226.5534 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 139 | 56156634 | 5838 | 140.112 | 5.838 | 5.8 | 5.8 | 3B+1S | 1008 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41276636 | 1344 | 230.2158 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 130 | 56162244 | 5610 | 134.64 | 5.61 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41277964 | 1328 | 236.7201 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 131 | 56167592 | 5348 | 128.352 | 5.348 | 5.4 | 5.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41279236 | 1272 | 237.8459 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 129 | 56172994 | 5402 | 129.648 | 5.402 | 5.3 | 5.3 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41280540 | 1304 | 241.3921 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 56178449 | 5455 | 130.92 | 5.455 | 5.2 | 5.2 | 3B+1S | 995 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41281844 | 1304 | 239.0467 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 56184076 | 5627 | 135.048 | 5.627 | 5 | 5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41283176 | 1332 | 236.7158 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 56189714 | 5638 | 135.312 | 5.638 | 4.7 | 4.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41284512 | 1336 | 236.9635 | 100% | 0% | 100% | 100% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 109 | 121 | 56194913 | 5199 | 124.776 | 5.199 | 3.9 | 3.9 | 2B+1S | 1099 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41285604 | 1092 | 210.0404 | 100% | 0% | 100% | 0% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 125 | 56200134 | 5221 | 125.304 | 5.221 | 3 | 3 | 2B+1S | 1098 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 41286676 | 1072 | 205.3247 | 100% | 0% | 100% | 0% | 100% | 0% | 9464288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 122 | 56205412 | 5278 | 126.672 | 5.278 | 2.3 | 2.3 | 2B+1S | 1089 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41287772 | 1096 | 207.6544 | 100% | 0% | 100% | 0% | 100% | 0% | 9464288 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 88 | 56209314 | 3902 | 93.648 | 3.902 | 3.1 | 3.1 | 2B | 0 | 0 | 1018 | 0 | 1017 | N/A | N/A | N/A | N/A | 41288468 | 696 | 178.3701 | 0% | 0% | 100% | 0% | 100% | 30% | 9465170 | 882 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 83 | 56212773 | 3459 | 83.016 | 3.459 | 4.4 | 4.4 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41289032 | 564 | 163.0529 | 0% | 0% | 100% | 0% | 100% | 30% | 9466213 | 1043 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121849 | 121.849 | 121.849 | [13 empty] | 26004 | 213.4117 | [6 empty] | 8286 | 8286 | 1.1217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:01 AM (40%)
XCV1 CLOSED @ 4:18 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 22 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26212 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56212773 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41289032 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9466213 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 78 | 56216157 | 3384 | 81.216 | 3.384 | 6.3 | 6.3 | 2B | 0 | 0 | 996 | 0 | 997 | N/A | N/A | N/A | N/A | 41289596 | 564 | 166.6667 | 0% | 0% | 100% | 0% | 100% | 45% | 9468084 | 1871 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 76 | 56219413 | 3256 | 78.144 | 3.256 | 8.1 | 8.1 | 2B | 0 | 0 | 997 | 0 | 996 | N/A | N/A | N/A | N/A | 41290132 | 536 | 164.6192 | 0% | 0% | 100% | 0% | 100% | 45% | 9469850 | 1766 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 75 | 56222401 | 2988 | 71.712 | 2.988 | 9.8 | 9.8 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 41290612 | 480 | 160.6426 | 0% | 0% | 100% | 0% | 100% | 45% | 9471425 | 1575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 93 | 56226024 | 3623 | 86.952 | 3.623 | 9.8 | 9.8 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41291124 | 512 | 141.3193 | 0% | 0% | 100% | 0% | 100% | 45% | 9471464 | 39 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 104 | 56230046 | 4022 | 96.528 | 4.022 | 9.8 | 9.8 | 2B | 0 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 41291772 | 648 | 161.1139 | 0% | 0% | 100% | 0% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 121 | 56234903 | 4857 | 116.568 | 4.857 | 9.8 | 9.8 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41292660 | 888 | 182.8289 | 0% | 0% | 100% | 0% | 100% | 0% | 9471464 | 0 | 1.09 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 129 | 142 | 56240750 | 5847 | 140.328 | 5.847 | 9.3 | 9.3 | 3B+1S | 0 | 1069 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41294004 | 1344 | 229.8615 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 56246850 | 6100 | 146.4 | 6.1 | 8.5 | 8.5 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41295412 | 1408 | 230.8197 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 56252989 | 6139 | 147.336 | 6.139 | 7.7 | 7.7 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41296812 | 1400 | 228.0502 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 56259235 | 6246 | 149.904 | 6.246 | 6.9 | 6.9 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41298244 | 1432 | 229.2667 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 | 1.36 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 56265385 | 6150 | 147.6 | 6.15 | 6.2 | 6.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41299652 | 1408 | 228.9431 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 56271280 | 5895 | 141.48 | 5.895 | 5.7 | 5.7 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41300992 | 1340 | 227.3113 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 139 | 56277219 | 5939 | 142.536 | 5.939 | 5.2 | 5.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41302388 | 1396 | 235.0564 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 132 | 56282956 | 5737 | 137.688 | 5.737 | 4.7 | 4.7 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41303740 | 1352 | 235.6632 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 133 | 56288683 | 5727 | 137.448 | 5.727 | 4.2 | 4.2 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41305100 | 1360 | 237.4716 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 130 | 56294352 | 5669 | 136.056 | 5.669 | 3.6 | 3.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41306444 | 1344 | 237.0788 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 56300226 | 5874 | 140.976 | 5.874 | 3.2 | 3.2 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41307856 | 1412 | 240.3813 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 126 | 56305664 | 5438 | 130.512 | 5.438 | 2.9 | 2.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41309144 | 1288 | 236.8518 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 129 | 56311263 | 5599 | 134.376 | 5.599 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41310484 | 1340 | 239.3285 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 131 | 56316404 | 5141 | 123.384 | 5.141 | 2.6 | 2.6 | 2B+1S | 0 | 955 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41311732 | 1248 | 242.7543 | 0% | 100% | 100% | 100% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 105 | 124 | 56320896 | 4492 | 107.808 | 4.492 | 2 | 2 | 2B+1S | 0 | 1150 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41312715 | 983 | 218.8335 | 0% | 100% | 100% | 0% | 100% | 0% | 9471464 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 107 | 56326472 | 5576 | 133.824 | 5.576 | 1.3 | 1.3 | 2B+1S | 0 | 996 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41313900 | 1185 | 212.5179 | 0% | 100% | 100% | 0% | 100% | 0% | 9471464 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 105 | 56330267 | 3795 | 91.08 | 3.795 | 2.5 | 2.5 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 41314644 | 744 | 196.0474 | 0% | 0% | 100% | 0% | 100% | 35% | 9472790 | 1326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 82 | 56333757 | 3490 | 83.76 | 3.49 | 3.9 | 3.9 | 2B | 0 | 0 | 1018 | 0 | 996 | N/A | N/A | N/A | N/A | 41315244 | 600 | 171.9198 | 0% | 0% | 100% | 0% | 100% | 35% | 9474244 | 1454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 120984 | 120.984 | 120.984 | [13 empty] | 26212 | 216.6567 | [6 empty] | 8031 | 8031 | 1.2017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (45%)
XCV2 CLOSED @ 3:00 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 22 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## OCT 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY / FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25752 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56333757 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41315244 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9474244 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 65 | 56336950 | 3193 | 76.632 | 3.193 | 5.9 | 5.9 | 2B | 0 | 0 | 997 | 0 | 1017 | N/A | N/A | N/A | N/A | 41315792 | 548 | 171.6254 | 0% | 0% | 100% | 0% | 100% | 45% | 9476145 | 1901 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 74 | 56340065 | 3115 | 74.76 | 3.115 | 7.8 | 7.8 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41316332 | 540 | 173.3547 | 0% | 0% | 100% | 0% | 100% | 45% | 9478021 | 1876 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 88 | 56343675 | 3610 | 86.64 | 3.61 | 9.7 | 9.7 | 2B | 0 | 0 | 997 | 0 | 1017 | N/A | N/A | N/A | N/A | 41316904 | 572 | 158.4488 | 0% | 0% | 100% | 0% | 100% | 45% | 9479521 | 1500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 86 | 56347332 | 3657 | 87.768 | 3.657 | 9.7 | 9.7 | 2B | 0 | 0 | 977 | 0 | 967 | N/A | N/A | N/A | N/A | 41317432 | 528 | 144.3806 | 0% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 94 | 56351163 | 3831 | 91.944 | 3.831 | 9.7 | 9.7 | 2B | 0 | 0 | 977 | 0 | 978 | N/A | N/A | N/A | N/A | 41317972 | 540 | 140.9554 | 0% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 122 | 56355746 | 4583 | 109.992 | 4.583 | 9.7 | 9.7 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41318700 | 728 | 158.8479 | 0% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 | 1.03 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 138 | 56361598 | 5852 | 140.448 | 5.852 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41320012 | 1312 | 224.1969 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 56367723 | 6125 | 147 | 6.125 | 8.9 | 8.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41321392 | 1380 | 225.3061 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 56373887 | 6164 | 147.936 | 6.164 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41322776 | 1384 | 224.5295 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 159 | 56380099 | 6212 | 149.088 | 6.212 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41324172 | 1396 | 224.7263 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 | 1.28 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 56386276 | 6177 | 148.248 | 6.177 | 7 | 7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41325556 | 1384 | 224.057 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 56392430 | 6154 | 147.696 | 6.154 | 6.5 | 6.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41326944 | 1388 | 225.5444 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 142 | 56398338 | 5908 | 141.792 | 5.908 | 6.1 | 6.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41328311 | 1367 | 231.3812 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 56404139 | 5801 | 139.224 | 5.801 | 5.6 | 5.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41329652 | 1341 | 231.167 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 56409821 | 5682 | 136.368 | 5.682 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41330944 | 1292 | 227.3847 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 135 | 56415561 | 5740 | 137.76 | 5.74 | 4.9 | 4.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41332340 | 1396 | 243.2056 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 142 | 56421351 | 5790 | 138.96 | 5.79 | 4.2 | 4.2 | 3B+1S | 1079 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41333708 | 1368 | 236.2694 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 125 | 56427008 | 5657 | 135.768 | 5.657 | 3.6 | 3.6 | 3B+1S | 1030 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41335044 | 1336 | 236.1676 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 56432504 | 5496 | 131.904 | 5.496 | 3.3 | 3.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41336348 | 1304 | 237.2635 | 100% | 0% | 100% | 100% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 107 | 130 | 56437804 | 5300 | 127.2 | 5.3 | 2.5 | 2.5 | 2B+1S | 1139 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41337476 | 1128 | 212.8302 | 100% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 106 | 120 | 56442890 | 5086 | 122.064 | 5.086 | 1.7 | 1.7 | 2B+1S | 1118 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41338548 | 1072 | 210.7747 | 100% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 109 | 56447761 | 4871 | 116.904 | 4.871 | 1.3 | 1.3 | 2B+1S | 965 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41339572 | 1024 | 210.2238 | 100% | 0% | 100% | 0% | 100% | 0% | 9479521 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 85 | 56451644 | 3883 | 93.192 | 3.883 | 2.2 | 2.2 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 41340308 | 736 | 189.5442 | 0% | 0% | 0% | 100% | 100% | 35% | 9480705 | 1184 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 117 | 87 | 56455284 | 3640 | 87.36 | 3.64 | 3.6 | 3.6 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 41340996 | 688 | 189.011 | 0% | 0% | 0% | 100% | 100% | 35% | 9482009 | 1304 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121527 | 121.527 | 121.527 | [13 empty] | 25752 | 211.9035 | [6 empty] | 7765 | 7765 | 1.195 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:01 AM (45%)
XCV2 CLOSED @ 3:00 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:17 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 24 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)
MAINTENANCE TEAM ARRIVED @ 7:20PM FOR MONTHLY PREVENTIVE MAINTENANCE.
BP2 - STARTED @ 10:01 PM DUE TO PREVENTIVE MAINTENANCE
BP1 - STOPPED @ 10:02 PM DUE TO PREVENTIVE MAINTENANCE
SP2 - STARTED @ 11:30 PM DUE TO PREVENTIVE MAINTENANCE
SP2 - STOPPED @ 11:40 PM DUE TO PREVENTIVE MAINTENANCE
BP3 - STOPPED @ 12:20 AM DUE TO PREVENTIVE MAINTENANCE
BP1 - STARTED @ 12:21 AM DUE TO PREVENTIVE MAINTENANCE
BP3 - STARTED @ 2:20 AM DUE TO PREVENTIVE MAINTENANCE
BP2 - STOPPED @ 2:21 AM DUE TO PREVENTIVE MAINTENANCE

## OCT 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25820 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56455284 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41340996 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9482009 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 84 | 56458808 | 3524 | 84.576 | 3.524 | 5.5 | 5.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 41341680 | 684 | 194.0976 | 0% | 0% | 100% | 100% | 0% | 45% | 9483691 | 1682 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 87 | 56462114 | 3306 | 79.344 | 3.306 | 7.3 | 7.3 | 2B | 0 | 0 | 886 | 1185 | 0 | N/A | N/A | N/A | N/A | 41342328 | 648 | 196.0073 | 0% | 0% | 100% | 100% | 0% | 45% | 9485352 | 1661 | 1.42 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 87 | 56465957 | 3843 | 92.232 | 3.843 | 8.7 | 8.7 | 2B | 0 | 0 | 1007 | 0 | 1007 | N/A | N/A | N/A | N/A | 41342968 | 640 | 166.5366 | 0% | 0% | 100% | 0% | 100% | 45% | 9486737 | 1385 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 89 | 56469667 | 3710 | 89.04 | 3.71 | 9.8 | 9.8 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41343524 | 556 | 149.8652 | 0% | 0% | 100% | 0% | 100% | 45% | 9487650 | 913 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 117 | 56473906 | 4239 | 101.736 | 4.239 | 9.8 | 9.8 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41344120 | 596 | 140.5992 | 0% | 0% | 100% | 0% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 56478276 | 4370 | 104.88 | 4.37 | 9.8 | 9.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41344836 | 716 | 163.8444 | 0% | 0% | 100% | 0% | 100% | 0% | 9487650 | 0 | 1.09 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 139 | 56484022 | 5746 | 137.904 | 5.746 | 9.7 | 9.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41346076 | 1240 | 215.8023 | 0% | 0% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 143 | 56489983 | 5961 | 143.064 | 5.961 | 9.7 | 9.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41347356 | 1280 | 214.7291 | 0% | 0% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 151 | 56496205 | 6222 | 149.328 | 6.222 | 9.2 | 9.2 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41348748 | 1392 | 223.7223 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 56502513 | 6308 | 151.392 | 6.308 | 8.4 | 8.4 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41350176 | 1428 | 226.3792 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 | 1.05 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 56508791 | 6278 | 150.672 | 6.278 | 7.6 | 7.6 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41351592 | 1416 | 225.5495 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 56515088 | 6297 | 151.128 | 6.297 | 6.8 | 6.8 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41353024 | 1432 | 227.4099 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 146 | 56521215 | 6127 | 147.048 | 6.127 | 6.3 | 6.3 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41354412 | 1388 | 226.5383 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 56527071 | 5856 | 140.544 | 5.856 | 5.9 | 5.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41355764 | 1352 | 230.8743 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 140 | 56532890 | 5819 | 139.656 | 5.819 | 5.3 | 5.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41357132 | 1368 | 235.0919 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 56538559 | 5669 | 136.056 | 5.669 | 4.9 | 4.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41358464 | 1332 | 234.9621 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 56544310 | 5751 | 138.024 | 5.751 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41359816 | 1352 | 235.0895 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 133 | 56550146 | 5836 | 140.064 | 5.836 | 3.9 | 3.9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41361184 | 1368 | 234.4071 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 134 | 56555643 | 5497 | 131.928 | 5.497 | 3.7 | 3.7 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41362476 | 1292 | 235.0373 | 0% | 100% | 100% | 100% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 127 | 56561003 | 5360 | 128.64 | 5.36 | 3.1 | 3.1 | 2B+1S | 0 | 1099 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41363580 | 1104 | 205.9701 | 0% | 100% | 100% | 0% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 119 | 56566315 | 5312 | 127.488 | 5.312 | 2.4 | 2.4 | 2B+1S | 0 | 1056 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41364664 | 1084 | 204.0663 | 0% | 100% | 100% | 0% | 100% | 0% | 9487650 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 101 | 56571198 | 4883 | 117.192 | 4.883 | 2.1 | 2.1 | 2B+1S | 0 | 955 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 41365656 | 992 | 203.1538 | 0% | 100% | 100% | 0% | 100% | 0% | 9487650 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 87 | 56574826 | 3628 | 87.072 | 3.628 | 3.1 | 3.1 | 2B | 0 | 0 | 996 | 0 | 997 | N/A | N/A | N/A | N/A | 41366276 | 620 | 170.8931 | 0% | 0% | 100% | 0% | 100% | 30% | 9488702 | 1052 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 110 | 80 | 56578314 | 3488 | 83.712 | 3.488 | 4.5 | 4.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41366816 | 540 | 154.8165 | 0% | 0% | 100% | 0% | 100% | 30% | 9489928 | 1226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123030 | 123.03 | 123.03 | [13 empty] | 25820 | 209.8675 | [6 empty] | 7919 | 7919 | 1.1783 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2 CLOSED @ 3:40 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 25 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## OCT 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25956 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56578314 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41366816 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9489928 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 115 | 76 | 56581542 | 3228 | 77.472 | 3.228 | 6.2 | 6.2 | 2B | 0 | 0 | 987 | 0 | 978 | N/A | N/A | N/A | N/A | 41367332 | 516 | 159.8513 | 0% | 0% | 100% | 0% | 100% | 40% | 9491659 | 1731 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 56584952 | 3410 | 81.84 | 3.41 | 7.8 | 7.8 | 2B | 0 | 0 | 1037 | 0 | 1038 | N/A | N/A | N/A | N/A | 41367880 | 548 | 160.7038 | 0% | 0% | 100% | 0% | 100% | 40% | 9493190 | 1531 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR/PAUL LABIAN
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 86 | 56589021 | 4069 | 97.656 | 4.069 | 9.1 | 9.1 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41368435 | 555 | 136.3971 | 0% | 0% | 100% | 0% | 100% | 40% | 9494553 | 1363 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 91 | 56593060 | 4039 | 96.936 | 4.039 | 9.8 | 9.8 | 2B | 0 | 0 | 977 | 0 | 957 | N/A | N/A | N/A | N/A | 41369104 | 669 | 165.6351 | 0% | 0% | 100% | 0% | 100% | 40% | 9494924 | 371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 103 | 56596405 | 3345 | 80.28 | 3.345 | 9.8 | 9.8 | 2B | 0 | 0 | 988 | 0 | 988 | N/A | N/A | N/A | N/A | 41369596 | 492 | 147.0852 | 0% | 0% | 100% | 0% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 128 | 56601282 | 4877 | 117.048 | 4.877 | 9.8 | 9.8 | 2B | 0 | 0 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 41370420 | 824 | 168.9563 | 0% | 0% | 100% | 0% | 100% | 0% | 9494924 | 0 | 1.3 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 56607305 | 6023 | 144.552 | 6.023 | 9.5 | 9.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41371756 | 1336 | 221.8164 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 56613447 | 6142 | 147.408 | 6.142 | 9 | 9 | 3B+1S | 1048 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41373132 | 1376 | 224.0313 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 56619703 | 6256 | 150.144 | 6.256 | 8.2 | 8.2 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41374536 | 1404 | 224.4246 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 155 | 56626053 | 6350 | 152.4 | 6.35 | 7.5 | 7.5 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41375964 | 1428 | 224.8819 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 56632302 | 6249 | 149.976 | 6.249 | 6.7 | 6.7 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41377372 | 1408 | 225.3161 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 56638529 | 6227 | 149.448 | 6.227 | 6 | 6 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41378780 | 1408 | 226.1121 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 144 | 56644654 | 6125 | 147 | 6.125 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41380164 | 1384 | 225.9592 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 56650519 | 5865 | 140.76 | 5.865 | 5 | 5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41381516 | 1352 | 230.52 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 56656260 | 5741 | 137.784 | 5.741 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41382868 | 1352 | 235.499 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 56661944 | 5684 | 136.416 | 5.684 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41384192 | 1324 | 232.9346 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 56667760 | 5816 | 139.584 | 5.816 | 4 | 4 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41385548 | 1356 | 233.1499 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 56673652 | 5892 | 141.408 | 5.892 | 3.4 | 3.4 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41386920 | 1372 | 232.8581 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 131 | 56679273 | 5621 | 134.904 | 5.621 | 3.2 | 3.2 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41388244 | 1324 | 235.5453 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 133 | 56684871 | 5598 | 134.352 | 5.598 | 3 | 3 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41389532 | 1288 | 230.0822 | 100% | 0% | 100% | 100% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 125 | 56690186 | 5315 | 127.56 | 5.315 | 2.3 | 2.3 | 2B+1S | 1087 | 0 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 41390628 | 1096 | 206.2088 | 100% | 0% | 100% | 0% | 100% | 0% | 9494924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 105 | 120 | 56695117 | 4931 | 118.344 | 4.931 | 1.9 | 1.9 | 2B+1S | 1025 | 0 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 41391636 | 1008 | 204.421 | 100% | 0% | 100% | 0% | 100% | 0% | 9494924 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 87 | 56698857 | 3740 | 89.76 | 3.74 | 2.9 | 2.9 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 41392248 | 612 | 163.6364 | 0% | 0% | 100% | 0% | 100% | 30% | 9496110 | 1186 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 87 | 56702331 | 3474 | 83.376 | 3.474 | 4.3 | 4.3 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 41392772 | 524 | 150.8348 | 0% | 0% | 100% | 0% | 100% | 30% | 9497166 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124017 | 124.017 | 124.017 | [13 empty] | 25956 | 209.2939 | [6 empty] | 7238 | 7238 | 1.17 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1 CLOSED @ 3:22 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 26 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR/PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56702331 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41392772 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9497166 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 113 | 85 | 56705709 | 3378 | 81.072 | 3.378 | 5.5 | 5.5 | 2B | 0 | 0 | 978 | 0 | 957 | N/A | N/A | N/A | N/A | 41393282 | 510 | 150.9769 | 0% | 0% | 100% | 0% | 100% | 35% | 9498481 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 78 | 56709090 | 3381 | 81.144 | 3.381 | 7 | 7 | 2B | 0 | 0 | 978 | 0 | 957 | N/A | N/A | N/A | N/A | 41393797 | 515 | 152.3218 | 0% | 0% | 100% | 0% | 100% | 35% | 9499798 | 1317 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 83 | 56712475 | 3385 | 81.24 | 3.385 | 8.4 | 8.4 | 2B | 0 | 0 | 978 | 0 | 957 | N/A | N/A | N/A | N/A | 41394308 | 511 | 150.9601 | 0% | 0% | 100% | 0% | 100% | 35% | 9501117 | 1319 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 92 | 56716171 | 3696 | 88.704 | 3.696 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 0 | 957 | N/A | N/A | N/A | N/A | 41394820 | 512 | 138.5281 | 0% | 0% | 100% | 0% | 100% | 35% | 9502166 | 1049 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 103 | 56720085 | 3914 | 93.936 | 3.914 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41395348 | 528 | 134.9004 | 0% | 0% | 100% | 0% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 143 | 141 | 56725103 | 5018 | 120.432 | 5.018 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41396284 | 936 | 186.5285 | 0% | 0% | 100% |  | 100% | 0% | 9502166 | 0 | 1.09 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 147 | 56731242 | 6139 | 147.336 | 6.139 | 9.1 | 9.1 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41397652 | 1368 | 222.8376 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 56737431 | 6189 | 148.536 | 6.189 | 8.3 | 8.3 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41399060 | 1408 | 227.5004 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 152 | 56743691 | 6260 | 150.24 | 6.26 | 7.5 | 7.5 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41400484 | 1424 | 227.476 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 175 | 56749941 | 6250 | 150 | 6.25 | 6.8 | 6.8 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41401900 | 1416 | 226.56 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 | 1.41 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 56756225 | 6284 | 150.816 | 6.284 | 6 | 6 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41403308 | 1408 | 224.0611 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 56762480 | 6255 | 150.12 | 6.255 | 5.3 | 5.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41404724 | 1416 | 226.3789 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 145 | 56768597 | 6117 | 146.808 | 6.117 | 4.7 | 4.7 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41406116 | 1392 | 227.5625 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 134 | 56774410 | 5813 | 139.512 | 5.813 | 4.1 | 4.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41407484 | 1368 | 235.3346 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 56780041 | 5631 | 135.144 | 5.631 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41408808 | 1324 | 235.127 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 56785649 | 5608 | 134.592 | 5.608 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41410124 | 1316 | 234.6648 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 141 | 56791350 | 5701 | 136.824 | 5.701 | 3.4 | 3.4 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41411460 | 1336 | 234.3449 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 56797175 | 5825 | 139.8 | 5.825 | 3 | 3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41412820 | 1360 | 233.4764 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 134 | 56802750 | 5575 | 133.8 | 5.575 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41414132 | 1312 | 235.3363 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 132 | 56808260 | 5510 | 132.24 | 5.51 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41415444 | 1312 | 238.1125 | 0% | 100% | 100% | 100% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 130 | 56813546 | 5286 | 126.864 | 5.286 | 2.2 | 2.2 | 2B+1S | 0 | 1087 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41416548 | 1104 | 208.8536 | 0% | 100% | 100% | 0% | 100% | 0% | 9502166 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 119 | 56818749 | 5203 | 124.872 | 5.203 | 1.7 | 1.7 | 2B+1S | 0 | 994 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41417612 | 1064 | 204.4974 | 0% | 100% | 100% | 0% | 100% | 0% | 9502166 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 119 | 88 | 56822916 | 4167 | 100.008 | 4.167 | 2.6 | 2.6 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41418372 | 760 | 182.3854 | 0% | 0% | 100% | 0% | 100% | 30% | 9503245 | 1079 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 82 | 56826337 | 3421 | 82.104 | 3.421 | 3.9 | 3.9 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 41418908 | 536 | 156.6793 | 0% | 0% | 100% | 0% | 100% | 33% | 9504415 | 1170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124006 | 124.006 | 124.006 | [13 empty] | 26136 | 210.764 | [6 empty] | 7249 | 7249 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (35%)
XCV2 CLOSED @ 3:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 27 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## OCT 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25664 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56826337 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41418908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9504415 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 77 | 56829477 | 3140 | 75.36 | 3.14 | 5.6 | 5.6 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41419420 | 512 | 163.0573 | 0% | 0% | 100% | 0% | 100% | 41% | 9505988 | 1573 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 80 | 56832912 | 3435 | 82.44 | 3.435 | 7.4 | 7.4 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 41419980 | 560 | 163.0277 | 0% | 0% | 100% | 0% | 100% | 41% | 9507693 | 1705 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 82 | 56836554 | 3642 | 87.408 | 3.642 | 8.7 | 8.7 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 41420585 | 605 | 166.1175 | 0% | 0% | 100% | 0% | 100% | 41% | 9509363 | 1670 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 56840448 | 3894 | 93.456 | 3.894 | 9.8 | 9.8 | 2B | 0 | 0 | 1018 | 0 | 1018 | N/A | N/A | N/A | N/A | 41421140 | 555 | 142.527 | 0% | 0% | 100% | 0% | 100% | 41% | 9510093 | 730 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 101 | 56844396 | 3948 | 94.752 | 3.948 | 9.8 | 9.8 | 2B | 0 | 0 | 1008 | 0 | 1008 | N/A | N/A | N/A | N/A | 41421716 | 576 | 145.8967 | 0% | 0% | 100% | 0% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 120 | 56849180 | 4784 | 114.816 | 4.784 | 9.8 | 9.8 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41422560 | 844 | 176.4214 | 0% | 0% | 100% | 0% | 100% | 0% | 9510093 | 0 | 1.05 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 150 | 56855205 | 6025 | 144.6 | 6.025 | 9.5 | 9.5 | 3B+1S | 1099 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41423900 | 1340 | 222.4066 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 151 | 56861493 | 6288 | 150.912 | 6.288 | 8.7 | 8.7 | 3B+1S | 1099 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41425320 | 1420 | 225.827 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 56867807 | 6314 | 151.536 | 6.314 | 7.8 | 7.8 | 3B+1S | 1099 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41426740 | 1420 | 224.8971 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 56874060 | 6253 | 150.072 | 6.253 | 7.1 | 7.1 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41428148 | 1408 | 225.1719 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 | 1.32 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 56880381 | 6321 | 151.704 | 6.321 | 6.3 | 6.3 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41429572 | 1424 | 225.2808 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 56886512 | 6131 | 147.144 | 6.131 | 5.7 | 5.7 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41430960 | 1388 | 226.3905 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 56892635 | 6123 | 146.952 | 6.123 | 5.2 | 5.2 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41432336 | 1376 | 224.7264 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 56898375 | 5740 | 137.76 | 5.74 | 4.8 | 4.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41433660 | 1324 | 230.662 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 139 | 56904120 | 5745 | 137.88 | 5.745 | 4.4 | 4.4 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41434984 | 1324 | 230.4613 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 132 | 56909748 | 5628 | 135.072 | 5.628 | 3.9 | 3.9 | 3B+1S | 1046 | 0 | 1168 | 1185 | 1147 | N/A | N/A | N/A | N/A | 41436276 | 1292 | 229.5665 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 56915538 | 5790 | 138.96 | 5.79 | 3.4 | 3.4 | 3B+1S | 1046 | 0 | 1167 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41437596 | 1320 | 227.9793 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 56921268 | 5730 | 137.52 | 5.73 | 3 | 3 | 3B+1S | 1047 | 0 | 1166 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41438916 | 1320 | 230.3665 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 132 | 56926828 | 5560 | 133.44 | 5.56 | 2.7 | 2.7 | 3B+1S | 1004 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 41440212 | 1296 | 233.0935 | 100% | 0% | 100% | 100% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 127 | 56932075 | 5247 | 125.928 | 5.247 | 2.1 | 2.1 | 3B+1S | 1088 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41441288 | 1076 | 205.0696 | 100% | 0% | 100% | 0% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 147 | 56937367 | 5292 | 127.008 | 5.292 | 1.4 | 1.4 | 2B+1S | 1087 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41442360 | 1072 | 202.5699 | 100% | 0% | 100% | 0% | 100% | 0% | 9510093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 105 | 56942426 | 5059 | 121.416 | 5.059 | 1.3 | 1.3 | 2B+1S | 965 | 0 | 1158 | 0 | 1158 | N/A | N/A | N/A | N/A | 41443392 | 1032 | 203.9929 | 100% | 0% | 100% | 0% | 100% | 0% | 9510093 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 111 | 83 | 56946235 | 3809 | 91.416 | 3.809 | 2.1 | 2.1 | 2B | 0 | 0 | 1017 | 0 | 997 | N/A | N/A | N/A | N/A | 41444064 | 672 | 176.4243 | 0% | 0% | 100% | 0% | 100% | 30% | 9511117 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 80 | 56949593 | 3358 | 80.592 | 3.358 | 3.1 | 3.1 | 2B | 0 | 0 | 978 | 0 | 978 | N/A | N/A | N/A | N/A | 41444572 | 508 | 151.2805 | 0% | 0% | 100% | 0% | 100% | 30% | 9512137 | 1020 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123256 | 123.256 | 123.256 | [13 empty] | 25664 | 208.217 | [6 empty] | 7722 | 7722 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (41%)
XCV1 CLOSED @ 3:50 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 29 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25492 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 56949593 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41444572 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9512137 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 77 | 56952994 | 3401 | 81.624 | 3.401 | 5 | 5 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 41445108 | 536 | 157.6007 | 0% | 0% | 100% | 0% | 100% | 40% | 9513795 | 1658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 78 | 56956147 | 3153 | 75.672 | 3.153 | 6.5 | 6.5 | 2B | 0 | 0 | 967 | 0 | 967 | N/A | N/A | N/A | N/A | 41445600 | 492 | 156.0419 | 0% | 0% | 100% | 0% | 100% | 40% | 9515353 | 1558 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 56959896 | 3749 | 89.976 | 3.749 | 8 | 8 | 2B | 0 | 0 | 997 | 0 | 996 | N/A | N/A | N/A | N/A | 41446172 | 572 | 152.574 | 0% | 0% | 100% | 0% | 100% | 40% | 9516730 | 1377 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 91 | 56963284 | 3388 | 81.312 | 3.388 | 9.2 | 9.2 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 41446676 | 504 | 148.7603 | 0% | 0% | 100% | 0% | 100% | 40% | 9517991 | 1261 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 121 | 56967536 | 4252 | 102.048 | 4.252 | 9.8 | 9.8 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 41447276 | 600 | 141.1101 | 0% | 0% | 100% | 0% | 100% | 40% | 9518486 | 495 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 56972596 | 5060 | 121.44 | 5.06 | 9.8 | 9.8 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 41448172 | 896 | 177.0751 | 0% | 0% | 100% | 0% | 100% | 0% | 9518486 | 0 | 1.07 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 151 | 56978548 | 5952 | 142.848 | 5.952 | 9.4 | 9.4 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41449492 | 1320 | 221.7742 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 56984786 | 6238 | 149.712 | 6.238 | 8.9 | 8.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41450884 | 1392 | 223.1484 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 152 | 56990949 | 6163 | 147.912 | 6.163 | 8.2 | 8.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41452260 | 1376 | 223.2679 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 56997240 | 6291 | 150.984 | 6.291 | 7.6 | 7.6 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41453676 | 1416 | 225.0835 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 57003391 | 6151 | 147.624 | 6.151 | 7.1 | 7.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41455052 | 1376 | 223.7035 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 57009649 | 6258 | 150.192 | 6.258 | 6.6 | 6.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41456451 | 1399 | 223.5539 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 57015507 | 5858 | 140.592 | 5.858 | 6.2 | 6.2 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41457796 | 1345 | 229.6005 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 135 | 57021281 | 5774 | 138.576 | 5.774 | 5.9 | 5.9 | 3B+1S | 0 | 995 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41459124 | 1328 | 229.9965 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 130 | 57027013 | 5732 | 137.568 | 5.732 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41460452 | 1328 | 231.6818 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 57032631 | 5618 | 134.832 | 5.618 | 5.5 | 5.5 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41461772 | 1320 | 234.9591 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 57038257 | 5626 | 135.024 | 5.626 | 5.3 | 5.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41463100 | 1328 | 236.0469 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 133 | 57043887 | 5630 | 135.12 | 5.63 | 5 | 5 | 3B+1S | 0 | 996 | 1178 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41464404 | 1304 | 231.6163 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 57049454 | 5567 | 133.608 | 5.567 | 4.8 | 4.8 | 3B+1S | 0 | 994 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 41465692 | 1288 | 231.3634 | 0% | 100% | 100% | 100% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 57054743 | 5289 | 126.936 | 5.289 | 4.2 | 4.2 | 2B+1S | 0 | 1068 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41466780 | 1088 | 205.71 | 0% | 100% | 100% | 0% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 122 | 57059944 | 5201 | 124.824 | 5.201 | 3.4 | 3.4 | 2B+1S | 0 | 1067 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41467852 | 1072 | 206.1142 | 0% | 100% | 100% | 0% | 100% | 0% | 9518486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 117 | 57065193 | 5249 | 125.976 | 5.249 | 2.8 | 2.8 | 2B+1S | 0 | 1056 | 1118 | 0 | 1117 | N/A | N/A | N/A | N/A | 41468884 | 1032 | 196.6089 | 0% | 100% | 100% | 0% | 100% | 0% | 9518486 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 116 | 85 | 57068962 | 3769 | 90.456 | 3.769 | 3.6 | 3.6 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41469528 | 644 | 170.8676 | 0% | 0% | 100% | 0% | 100% | 30% | 9519508 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 116 | 87 | 57072477 | 3515 | 84.36 | 3.515 | 5 | 5 | 2B | 0 | 0 | 967 | 0 | 967 | N/A | N/A | N/A | N/A | 41470064 | 536 | 152.4893 | 0% | 0% | 100% | 0% | 100% | 30% | 9520726 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 122884 | 122.884 | 122.884 | [13 empty] | 25492 | 207.4477 | [6 empty] | 8589 | 8589 | 1.175 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2 CLOSED @ 4:17 AM,WATER ELEVATION (9.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 29 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## OCT 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25960 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 57072477 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41470064 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9520726 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 118 | 78 | 57075813 | 3336 | 80.064 | 3.336 | 6.6 | 6.6 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 41470592 | 528 | 158.2734 | 0% | 0% | 100% | 0% | 100% | 40% | 9522297 | 1571 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 94 | 57079215 | 3402 | 81.648 | 3.402 | 8.1 | 8.1 | 2B | 0 | 0 | 1037 | 0 | 1038 | N/A | N/A | N/A | N/A | 41471116 | 524 | 154.027 | 0% | 0% | 100% | 0% | 100% | 40% | 9523753 | 1456 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 91 | 57082634 | 3419 | 82.056 | 3.419 | 9.7 | 9.7 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 41471652 | 536 | 156.771 | 0% | 0% | 100% | 0% | 100% | 40% | 9525130 | 1377 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 91 | 57086793 | 4159 | 99.816 | 4.159 | 9.7 | 9.7 | 2B | 0 | 0 | 947 | 0 | 948 | N/A | N/A | N/A | N/A | 41472220 | 568 | 136.5713 | 0% | 0% | 100% | 0% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 101 | 57090614 | 3821 | 91.704 | 3.821 | 9.7 | 9.7 | 2B | 0 | 0 | 1017 | 0 | 1018 | N/A | N/A | N/A | N/A | 41472772 | 552 | 144.4648 | 0% | 0% | 100% | 0% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 57095431 | 4817 | 115.608 | 4.817 | 9.7 | 9.7 | 2B | 0 | 0 | 1190 | 0 | 1190 | N/A | N/A | N/A | N/A | 41473600 | 828 | 171.8912 | 0% | 0% | 100% | 0% | 100% | 0% | 9525130 | 0 | 0.98 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 57101404 | 5973 | 143.352 | 5.973 | 9.4 | 9.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41474937 | 1337 | 223.8406 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 151 | 57107624 | 6220 | 149.28 | 6.22 | 8.8 | 8.8 | 3B+1S | 1099 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41476324 | 1387 | 222.9904 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 57113916 | 6292 | 151.008 | 6.292 | 8 | 8 | 3B+1S | 1099 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41477740 | 1416 | 225.0477 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 57120359 | 6443 | 154.632 | 6.443 | 7.2 | 7.2 | 3B+1S | 1098 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41479180 | 1440 | 223.4984 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 | 1.29 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 57126616 | 6257 | 150.168 | 6.257 | 6.4 | 6.4 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41480588 | 1408 | 225.028 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 57132861 | 6245 | 149.88 | 6.245 | 5.7 | 5.7 | 3B+1S | 1098 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41482004 | 1416 | 226.7414 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 57138871 | 6010 | 144.24 | 6.01 | 5 | 5 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41483580 | 1576 | 262.2296 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 133 | 57144871 | 6000 | 144 | 6 | 4.6 | 4.6 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41484764 | 1184 | 197.3333 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 133 | 57150609 | 5738 | 137.712 | 5.738 | 4 | 4 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 41486116 | 1352 | 235.6222 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 135 | 57156327 | 5718 | 137.232 | 5.718 | 3.6 | 3.6 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41487460 | 1344 | 235.0472 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 57162059 | 5732 | 137.568 | 5.732 | 3.2 | 3.2 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41488808 | 1348 | 235.171 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 57167734 | 5675 | 136.2 | 5.675 | 2.9 | 2.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41490112 | 1304 | 229.7797 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 57173396 | 5662 | 135.888 | 5.662 | 2.8 | 2.8 | 3B+1S | 994 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41491452 | 1340 | 236.6655 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 124 | 57178676 | 5280 | 126.72 | 5.28 | 2.7 | 2.7 | 2B+1S | 954 | 0 | 1148 | 1185 | 1136 | N/A | N/A | N/A | N/A | 41492688 | 1236 | 234.0909 | 100% | 0% | 100% | 100% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 123 | 57183963 | 5287 | 126.888 | 5.287 | 2.4 | 2.4 | 2B+1S | 1078 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 41493788 | 1100 | 208.0575 | 100% | 0% | 100% | 0% | 100% | 0% | 9525130 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 116 | 57188889 | 4926 | 118.224 | 4.926 | 2 | 2 | 2B+1S | 995 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41494796 | 1008 | 204.6285 | 100% | 0% | 100% | 0% | 100% | 0% | 9525130 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 85 | 57192691 | 3802 | 91.248 | 3.802 | 2.7 | 2.7 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 41495452 | 656 | 172.5408 | 0% | 0% | 100% | 0% | 100% | 30% | 9525924 | 794 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 109 | 84 | 57196294 | 3603 | 86.472 | 3.603 | 3.8 | 3.8 | 2B | 0 | 0 | 988 | 0 | 987 | N/A | N/A | N/A | N/A | 41496024 | 572 | 158.7566 | 0% | 0% | 100% | 0% | 100% | 30% | 9526982 | 1058 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123817 | 123.817 | 123.817 | [13 empty] | 25960 | 209.6643 | [6 empty] | 6256 | 6256 | 1.1533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1 CLOSED @ 3:00 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 30 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-10-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25584 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 57196294 |  |  |  |  | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 41496024 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9526982 |  | mg /l |  | Automatic - i2O | AI
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 58 | 57199708 | 3414 | 81.936 | 3.414 | 5.4 | 5.4 | 2B | 0 | 0 | 997 | 0 | 998 | N/A | N/A | N/A | N/A | 41496588 | 564 | 165.2021 | 0% | 0% | 100% | 0% | 100% | 40% | 9528354 | 1372 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 105 | 57203030 | 3322 | 79.728 | 3.322 | 6.8 | 6.8 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 41497116 | 528 | 158.9404 | 0% | 0% | 100% | 0% | 100% | 40% | 9529824 | 1470 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 86 | 57206813 | 3783 | 90.792 | 3.783 | 8.3 | 8.3 | 2B | 0 | 0 | 1007 | 0 | 1008 | N/A | N/A | N/A | N/A | 41497708 | 592 | 156.4896 | 0% | 0% | 100% | 0% | 100% | 40% | 9531052 | 1228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 90 | 57210493 | 3680 | 88.32 | 3.68 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 1007 | N/A | N/A | N/A | N/A | 41498268 | 560 | 152.1739 | 0% | 0% | 100% | 0% | 100% | 40% | 9532364 | 1312 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 95 | 57214436 | 3943 | 94.632 | 3.943 | 9.8 | 9.8 | 2B | 0 | 0 | 1027 | 0 | 1038 | N/A | N/A | N/A | N/A | 41498836 | 568 | 144.0528 | 0% | 0% | 100% | 0% | 100% | 40% | 9532485 | 121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / PAUL LABIAN
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 121 | 57219412 | 4976 | 119.424 | 4.976 | 9.8 | 9.8 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 41499692 | 856 | 172.0257 | 0% | 0% | 100% | 0% | 100% | 0% | 9532485 | 0 | 1.02 | Normal operation schedule | Error - General | E | GLITTERS SY / FIDEL RAMOS
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 139 | 57224928 | 5516 | 132.384 | 5.516 | 9.8 | 9.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41500900 | 1208 | 218.9993 | 0% | 0% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / PAUL LABIAN
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 57231036 | 6108 | 146.592 | 6.108 | 9.4 | 9.4 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41502260 | 1360 | 222.6588 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 57237298 | 6262 | 150.288 | 6.262 | 8.7 | 8.7 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41503660 | 1400 | 223.5707 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 57243607 | 6309 | 151.416 | 6.309 | 8 | 8 | 3B+1S | 0 | 1079 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41505140 | 1480 | 234.5855 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 | 1.37 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 57249935 | 6328 | 151.872 | 6.328 | 7.3 | 7.3 | 3B+1S | 0 | 1079 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41506484 | 1344 | 212.3894 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 57256228 | 6293 | 151.032 | 6.293 | 6.6 | 6.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1887 | N/A | N/A | N/A | N/A | 41507908 | 1424 | 226.2832 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 145 | 57262357 | 6129 | 147.096 | 6.129 | 6 | 6 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41509300 | 1392 | 227.117 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 57268307 | 5950 | 142.8 | 5.95 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41510664 | 1364 | 229.2437 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 143 | 57274189 | 5882 | 141.168 | 5.882 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41512024 | 1360 | 231.2139 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 57279987 | 5798 | 139.152 | 5.798 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41513364 | 1340 | 231.1142 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 57285652 | 5665 | 135.96 | 5.665 | 4.3 | 4.3 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41514700 | 1336 | 235.8341 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 57291350 | 5698 | 136.752 | 5.698 | 4 | 4 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41516032 | 1332 | 233.7662 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 57296952 | 5602 | 134.448 | 5.602 | 3.8 | 3.8 | 3B+1S | 0 | 994 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 41517348 | 1316 | 234.9161 | 0% | 100% | 100% | 100% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 126 | 57302175 | 5223 | 125.352 | 5.223 | 3.2 | 3.2 | 2B+1S | 0 | 1037 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 41518412 | 1064 | 203.7143 | 0% | 100% | 100% | 0% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 121 | 57307349 | 5174 | 124.176 | 5.174 | 2.7 | 2.7 | 2B+1S | 0 | 1037 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 41519460 | 1048 | 202.5512 | 0% | 100% | 100% | 0% | 100% | 0% | 9532485 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 114 | 57312310 | 4961 | 119.064 | 4.961 | 2.4 | 2.4 | 2B+1S | 0 | 994 | 1186 | 0 | 1188 | N/A | N/A | N/A | N/A | 41520476 | 1016 | 204.7974 | 0% | 100% | 100% | 0% | 100% | 0% | 9532485 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 113 | 86 | 57316014 | 3704 | 88.896 | 3.704 | 3.3 | 3.3 | 2B | 0 | 0 | 1007 | 0 | 1007 | N/A | N/A | N/A | N/A | 41521076 | 600 | 161.987 | 0% | 0% | 100% | 0% | 100% | 30% | 9533523 | 1038 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 111 | 83 | 57319504 | 3490 | 83.76 | 3.49 | 4.8 | 4.8 | 2B | 0 | 0 | 987 | 0 | 977 | N/A | N/A | N/A | N/A | 41521608 | 532 | 152.4355 | 0% | 0% | 100% | 0% | 100% | 30% | 9534669 | 1146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123210 | 123.21 | 123.21 | [13 empty] | 25584 | 207.6455 | [6 empty] | 7687 | 7687 | 1.1633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2 CLOSED @ 3:00 AM,WATER ELEVATION (9.7M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (OCT 31 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)