## DEC 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25820 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61063157 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42297860 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9747887 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 85 | 61066608 | 3451 | 82.824 | 3.451 | 5.5 | 5.5 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 42298404 | 544 | 157.6355 | 0% | 0% | 100% | 0% | 100% | 30% | 9749275 | 1388 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 87 | 61070168 | 3560 | 85.44 | 3.56 | 7.1 | 7.1 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 42298944 | 540 | 151.6854 | 0% | 0% | 100% | 0% | 100% | 30% | 9750555 | 1280 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 88 | 61073732 | 3564 | 85.536 | 3.564 | 8.7 | 8.7 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 42299490 | 546 | 153.1987 | 0% | 0% | 100% | 0% | 100% | 30% | 9751842 | 1287 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 90 | 61077300 | 3568 | 85.632 | 3.568 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 42300044 | 554 | 155.2691 | 0% | 0% | 100% | 0% | 100% | 30% | 9753138 | 1296 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 103 | 61081493 | 4193 | 100.632 | 4.193 | 9.5 | 9.5 | 2B | 0 | 0 | 1077 | 0 | 1078 | N/A | N/A | N/A | N/A | 42300688 | 644 | 153.5893 | 0% | 0% | 100% | 0% | 100% | 30% | 9753148 | 10 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 61086509 | 5016 | 120.384 | 5.016 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42301628 | 940 | 187.4003 | 0% | 0% | 100% | 0% | 100% | 0% | 9753148 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 147 | 61092530 | 6021 | 144.504 | 6.021 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42302992 | 1364 | 226.5404 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 61098690 | 6160 | 147.84 | 6.16 | 8.4 | 8.4 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42304384 | 1392 | 225.974 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 61104892 | 6202 | 148.848 | 6.202 | 7.6 | 7.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42305788 | 1404 | 226.3786 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 153 | 61111160 | 6268 | 150.432 | 6.268 | 6.8 | 6.8 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42307204 | 1416 | 225.9094 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 61117321 | 6161 | 147.864 | 6.161 | 6 | 6 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42308608 | 1404 | 227.8851 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 159 | 61123546 | 6225 | 149.4 | 6.225 | 5.3 | 5.3 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42310028 | 1420 | 228.1124 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 145 | 61129470 | 5924 | 142.176 | 5.924 | 4.8 | 4.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42311400 | 1372 | 231.6003 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 137 | 61135176 | 5706 | 136.944 | 5.706 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42312720 | 1320 | 231.3354 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 134 | 61140958 | 5782 | 138.768 | 5.782 | 4.5 | 4.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42314064 | 1344 | 232.4455 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 61146526 | 5568 | 133.632 | 5.568 | 4.4 | 4.4 | 3B+1S | 993 | 0 | 1158 | 1185 | 1158 | N/A | N/A | N/A | N/A | 42315340 | 1276 | 229.1667 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 61152100 | 5574 | 133.776 | 5.574 | 4.3 | 4.3 | 3B+1S | 1036 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42316612 | 1272 | 228.2024 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 132 | 61157717 | 5617 | 134.808 | 5.617 | 4.1 | 4.1 | 3B+1S | 1015 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42317860 | 1248 | 222.1827 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 138 | 61163253 | 5536 | 132.864 | 5.536 | 3.7 | 3.7 | 3B+1S | 1015 |  | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42319120 | 1260 | 227.6012 | 100% | 0% | 100% | 100% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 128 | 61168522 | 5269 | 126.456 | 5.269 | 3.1 | 3.1 | 2B+1S | 1087 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42320200 | 1080 | 204.9725 | 100% | 0% | 100% | 0% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 108 | 131 | 61173763 | 5241 | 125.784 | 5.241 | 2.4 | 2.4 | 2B+1S | 1099 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42321276 | 1076 | 205.3043 | 100% | 0% | 100% | 0% | 100% | 0% | 9753148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 121 | 61178876 | 5113 | 122.712 | 5.113 | 1.7 | 1.7 | 2B+1S | 1056 | 0 | 1168 | 0 | 1168 | N/A | N/A | N/A | N/A | 42322304 | 1028 | 201.0561 | 100% | 0% | 100% | 0% | 100% | 0% | 9753148 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 99 | 61183006 | 4130 | 99.12 | 4.13 | 2.4 | 2.4 | 2B | 0 | 0 | 1066 | 0 | 1168 | N/A | N/A | N/A | N/A | 42323036 | 732 | 177.2397 | 0% | 0% | 100% | 0% | 100% | 30% | 9753983 | 835 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 91 | 61186958 | 3952 | 94.848 | 3.952 | 3.4 | 3.4 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 42323680 | 644 | 162.9555 | 0% | 0% | 100% | 0% | 100% | 30% | 9754968 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 125.0833 | 123801 | 123801 | 123.801 | 123.801 | [12 empty] | 25820 | 25820 | 208.5605 | [6 empty] | 7081 | 7081 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (35%)
XCV1- CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 01 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## DEC 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26492 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61186958 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42323680 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9754968 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 87 | 61190817 | 3859 | 92.616 | 3.859 | 5 | 5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 42324292 | 612 | 158.5903 | 0% | 0% | 100% | 0% | 100% | 35% | 9756330 | 1362 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 91 | 61194337 | 3520 | 84.48 | 3.52 | 6.3 | 6.3 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 42324828 | 536 | 152.2727 | 0% | 0% | 100% | 0% | 100% | 35% | 9757633 | 1303 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 85 | 61197774 | 3437 | 82.488 | 3.437 | 7.5 | 7.5 | 2B | 0 | 0 | 977 | 0 | 977 | N/A | N/A | N/A | N/A | 42325340 | 512 | 148.9671 | 0% | 0% | 100% | 0% | 100% | 35% | 9758838 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 91 | 61201485 | 3711 | 89.064 | 3.711 | 8.8 | 8.8 | 2B | 0 | 0 | 998 | 0 | 998 | N/A | N/A | N/A | N/A | 42325896 | 556 | 149.8248 | 0% | 0% | 100% | 0% | 100% | 35% | 9759972 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 106 | 61205533 | 4048 | 97.152 | 4.048 | 9.5 | 9.5 | 2B | 0 | 0 | 1088 | 0 | 1088 | N/A | N/A | N/A | N/A | 42326528 | 632 | 156.1265 | 0% | 0% | 100% | 0% | 100% | 35% | 9760625 | 653 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 61210516 | 4983 | 119.592 | 4.983 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42327432 | 904 | 181.4168 | 0% | 0% | 100% | 0% | 100% | 0% | 9760625 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 128 | 147 | 61216611 | 6095 | 146.28 | 6.095 | 8.8 | 8.8 | 3B+1S | 0 | 1118 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42328820 | 1388 | 227.7276 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 149 | 61222742 | 6131 | 147.144 | 6.131 | 8 | 8 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42330236 | 1416 | 230.9574 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 61228921 | 6179 | 148.296 | 6.179 | 7.2 | 7.2 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42331652 | 1416 | 229.1633 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 61235134 | 6213 | 149.112 | 6.213 | 6.5 | 6.5 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42333072 | 1420 | 228.553 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 | 1.25 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 61241306 | 6172 | 148.128 | 6.172 | 5.8 | 5.8 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42334472 | 1400 | 226.8308 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 61247423 | 6117 | 146.808 | 6.117 | 5 | 5 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42335864 | 1392 | 227.5625 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 8 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 139 | 61253468 | 6045 | 145.08 | 6.045 | 4.5 | 4.5 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42337268 | 1404 | 232.2581 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 61259169 | 5701 | 136.824 | 5.701 | 4.1 | 4.1 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42338588 | 1320 | 231.5383 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 135 | 61264922 | 5753 | 138.072 | 5.753 | 3.9 | 3.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42339928 | 1340 | 232.922 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 135 | 61270632 | 5710 | 137.04 | 5.71 | 3.8 | 3.8 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42341260 | 1332 | 233.275 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 61276460 | 5828 | 139.872 | 5.828 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42342604 | 1344 | 230.6108 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 61282232 | 5772 | 138.528 | 5.772 | 3.5 | 3.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42343932 | 1328 | 230.0762 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 61287867 | 5635 | 135.24 | 5.635 | 3.3 | 3.3 | 3B+1S | 0 | 1014 | 1167 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42345260 | 1328 | 235.6699 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 131 | 61293447 | 5580 | 133.92 | 5.58 | 3 | 3 | 3B+1S | 0 | 1025 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42346536 | 1276 | 228.6738 | 0% | 100% | 100% | 100% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 129 | 61298741 | 5294 | 127.056 | 5.294 | 2.4 | 2.4 | 2B+1S | 0 | 1099 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 42347628 | 1092 | 206.2713 | 0% | 100% | 100% | 0% | 100% | 0% | 9760625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 111 | 61304048 | 5307 | 127.368 | 5.307 | 1.7 | 1.7 | 2B+1S | 0 | 965 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42348728 | 1100 | 207.2734 | 0% | 100% | 100% | 0% | 100% | 0% | 9760625 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 89 | 61308194 | 4146 | 99.504 | 4.146 | 2.7 | 2.7 | 2B | 0 | 0 | 1078 | 0 | 1047 | N/A | N/A | N/A | N/A | 42349548 | 820 | 197.781 | 0% | 0% | 100% | 0% | 100% | 35% | 9761740 | 1115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 88 | 61311886 | 3692 | 88.608 | 3.692 | 4.2 | 4.2 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 42350172 | 624 | 169.0141 | 0% | 0% | 100% | 0% | 100% | 35% | 9763091 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.7917 | 124928 | 124928 | 124.928 | 124.928 | [12 empty] | 26492 | 26492 | 212.0581 | [6 empty] | 8123 | 8123 | 1.2183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (35%)
XCV2- CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 02 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## DEC 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26384 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61311886 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42350172 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9763091 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 85 | 61315423 | 3537 | 84.888 | 3.537 | 5.9 | 5.9 | 2B | 0 | 0 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 42350756 | 584 | 165.1117 | 0% | 0% | 100% | 0% | 100% | 40% | 9764651 | 1560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 80 | 61318907 | 3484 | 83.616 | 3.484 | 7.6 | 7.6 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 42351316 | 560 | 160.7348 | 0% | 0% | 100% | 0% | 100% | 40% | 9766292 | 1641 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 84 | 61322299 | 3392 | 81.408 | 3.392 | 9.2 | 9.2 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 42351836 | 520 | 153.3019 | 0% | 0% | 100% | 0% | 100% | 40% | 9767872 | 1580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 92 | 61325836 | 3537 | 84.888 | 3.537 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 978 | N/A | N/A | N/A | N/A | 42352332 | 496 | 140.2318 | 0% | 0% | 100% | 0% | 100% | 40% | 9768074 | 202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 109 | 61329965 | 4129 | 99.096 | 4.129 | 9.5 | 9.5 | 2B | 0 | 0 | 1088 | 0 | 1088 | N/A | N/A | N/A | N/A | 42352948 | 616 | 149.1887 | 0% | 0% | 100% | 0% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 61335059 | 5094 | 122.256 | 5.094 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42353884 | 936 | 183.7456 | 0% | 0% | 100% | 0% | 100% | 0% | 9768074 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 147 | 61341111 | 6052 | 145.248 | 6.052 | 9.1 | 9.1 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42355244 | 1360 | 224.7191 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 61347210 | 6099 | 146.376 | 6.099 | 8.4 | 8.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42356628 | 1384 | 226.9224 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 61353384 | 6174 | 148.176 | 6.174 | 7.7 | 7.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42358016 | 1388 | 224.8137 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 153 | 61359494 | 6110 | 146.64 | 6.11 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42359344 | 1328 | 217.3486 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 61365575 | 6081 | 145.944 | 6.081 | 6.6 | 6.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42360754 | 1410 | 231.8698 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 140 | 61371638 | 6063 | 145.512 | 6.063 | 6.1 | 6.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42362141 | 1387 | 228.7646 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 61377530 | 5892 | 141.408 | 5.892 | 5.7 | 5.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42363488 | 1347 | 228.6151 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 134 | 61383305 | 5775 | 138.6 | 5.775 | 5.4 | 5.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42364828 | 1340 | 232.0346 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 61389036 | 5731 | 137.544 | 5.731 | 5.1 | 5.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42366168 | 1340 | 233.8161 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 61394735 | 5699 | 136.776 | 5.699 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42367500 | 1332 | 233.7252 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 61400489 | 5754 | 138.096 | 5.754 | 4.6 | 4.6 | 3B+1S | 1044 | 0 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42368836 | 1336 | 232.1863 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 139 | 61406227 | 5738 | 137.712 | 5.738 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42370188 | 1352 | 235.6222 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 138 | 61412172 | 5945 | 142.68 | 5.945 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42371552 | 1364 | 229.4365 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 136 | 61417729 | 5557 | 133.368 | 5.557 | 3.4 | 3.4 | 2B+1S | 1025 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42372832 | 1280 | 230.3401 | 100% | 0% | 100% | 100% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 126 | 61423104 | 5375 | 129 | 5.375 | 2.6 | 2.6 | 2B+1S | 1138 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42373948 | 1116 | 207.6279 | 100% | 0% | 100% | 0% | 100% | 0% | 9768074 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 118 | 61428746 | 5642 | 135.408 | 5.642 | 1.9 | 1.9 | 2B+1S | 1066 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42375116 | 1168 | 207.0188 | 100% | 0% | 100% | 0% | 100% | 0% | 9768074 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 99 | 61432758 | 4012 | 96.288 | 4.012 | 2.7 | 2.7 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 42375860 | 744 | 185.4437 | 0% | 0% | 0% | 100% | 100% | 35% | 9769026 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 93 | 61436768 | 4010 | 96.24 | 4.01 | 4 | 4 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42376556 | 696 | 173.5661 | 0% | 0% | 100% | 100% | 0% | 35% | 9770248 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 123.9583 | 124882 | 124882 | 124.882 | 124.882 | [12 empty] | 26384 | 26384 | 211.2714 | [6 empty] | 7157 | 7157 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 03 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)
PREVENTIVE MAINTENANCE OF ALL UNITS (SP2,BP1,BP2,BP3)
BP1 - STOP @10:01 PM
BP2 - START @ 10:02 PM
BP1 - START @ 11:30 PM
BP3 - STOP @ 111:31 PM
BP3 - START @12:00 AM
BP2 - STOP @ 12:01 AM

## DEC 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27088 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61436768 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42376556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9770248 |  | mg /l |  | Automatic - i2O | AI | ALEXANDER CABREROS
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 90 | 61440402 | 3634 | 87.216 | 3.634 | 5.7 | 5.7 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 42377156 | 600 | 165.1073 | 0% | 0% | 100% | 0% | 100% | 40% | 9771755 | 1507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 86 | 61444160 | 3758 | 90.192 | 3.758 | 7.2 | 7.2 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 42377748 | 592 | 157.5306 | 0% | 0% | 100% | 0% | 100% | 40% | 9773308 | 1553 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 84 | 61447775 | 3615 | 86.76 | 3.615 | 8.6 | 8.6 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 42378308 | 560 | 154.9101 | 0% | 0% | 100% | 0% | 100% | 40% | 9774684 | 1376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 89 | 61451314 | 3539 | 84.936 | 3.539 | 9.5 | 9.5 | 2B | 0 | 0 | 978 | 0 | 977 | N/A | N/A | N/A | N/A | 42378852 | 544 | 153.7157 | 0% | 0% | 100% | 0% | 100% | 40% | 9775601 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 103 | 61455504 | 4190 | 100.56 | 4.19 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 42379476 | 624 | 148.926 | 0% | 0% | 100% | 0% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 114 | 61460039 | 4535 | 108.84 | 4.535 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42380364 | 888 | 195.8104 | 0% | 0% | 100% | 0% | 100% | 0% | 9775601 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 124 | 141 | 61465914 | 5875 | 141 | 5.875 | 9 | 9 | 3B+1S | 0 | 1147 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42381740 | 1376 | 234.2128 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 145 | 61471932 | 6018 | 144.432 | 6.018 | 8 | 8 | 3B+1S | 0 | 1148 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42383180 | 1440 | 239.2822 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 141 | 61477915 | 5983 | 143.592 | 5.983 | 7 | 7 | 3B+1S | 0 | 1149 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42384612 | 1432 | 239.3448 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 142 | 61483909 | 5994 | 143.856 | 5.994 | 6 | 6 | 3B+1S | 0 | 1148 | 1187 | 1158 | 1186 | N/A | N/A | N/A | N/A | 42386036 | 1424 | 237.5709 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 142 | 61489887 | 5978 | 143.472 | 5.978 | 5.1 | 5.1 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42387460 | 1424 | 238.2068 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 141 | 61495833 | 5946 | 142.704 | 5.946 | 4.3 | 4.3 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42388860 | 1400 | 235.4524 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 136 | 61501670 | 5837 | 140.088 | 5.837 | 3.4 | 3.4 | 3B+1S | 0 | 1097 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42390256 | 1396 | 239.164 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 133 | 61507281 | 5611 | 134.664 | 5.611 | 2.8 | 2.8 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42391600 | 1344 | 239.5295 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 61512846 | 5565 | 133.56 | 5.565 | 2.7 | 2.7 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42392924 | 1324 | 237.9155 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 61518278 | 5432 | 130.368 | 5.432 | 2.6 | 2.6 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42394256 | 1332 | 245.2135 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 131 | 61523933 | 5655 | 135.72 | 5.655 | 2.4 | 2.4 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42395572 | 1316 | 232.7144 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 61529547 | 5614 | 134.736 | 5.614 | 2.2 | 2.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42396924 | 1352 | 240.8265 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 61534941 | 5394 | 129.456 | 5.394 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42398212 | 1288 | 238.7838 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 129 | 61540341 | 5400 | 129.6 | 5.4 | 2 | 2 | 3B+1S | 0 | 984 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42399532 | 1320 | 244.4444 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 124 | 61545546 | 5205 | 124.92 | 5.205 | 1.9 | 1.9 | 3B+1S | 0 | 1016 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42400816 | 1284 | 246.6859 | 0% | 100% | 100% | 100% | 100% | 0% | 9775601 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 117 | 61550574 | 5028 | 120.672 | 5.028 | 1.3 | 1.3 | 2B+1S | 0 | 1107 | 1186 | 0 | 1187 | N/A | N/A | N/A | N/A | 42401924 | 1108 | 220.366 | 0% | 100% | 100% | 0% | 100% | 0% | 9775601 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 100 | 61554756 | 4182 | 100.368 | 4.182 | 2.1 | 2.1 | 2B | 0 | 0 | 1167 | 0 | 1168 | N/A | N/A | N/A | N/A | 42402820 | 896 | 214.2516 | 0% | 0% | 100% | 0% | 100% | 35% | 9776598 | 997 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 113 | 61558828 | 4072 | 97.728 | 4.072 | 3.4 | 3.4 | 2B | 0 | 0 | 1138 | 0 | 1138 | N/A | N/A | N/A | N/A | 42403644 | 824 | 202.3576 | 0% | 0% | 100% | 0% | 100% | 35% | 9777830 | 1232 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122.2083 | 122060 | 122060 | 122.06 | 122.06 | [12 empty] | 27088 | 27088 | 221.9236 | [6 empty] | 7582 | 7582 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 3:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 04 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## DEC 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27504 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61558828 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42403644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9777830 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 92 | 61562703 | 3875 | 93 | 3.875 | 5.1 | 5.1 | 2B | 0 | 0 | 1107 | 0 | 1107 | N/A | N/A | N/A | N/A | 42404404 | 760 | 196.129 | 0% | 0% | 100% | 0% | 100% | 40% | 9779326 | 1496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 89 | 61566453 | 3750 | 90 | 3.75 | 6.8 | 6.8 | 2B | 0 | 0 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 42405108 | 704 | 187.7333 | 0% | 0% | 100% | 0% | 100% | 40% | 9780876 | 1550 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 87 | 61570264 | 3811 | 91.464 | 3.811 | 8.3 | 8.3 | 2B | 0 | 0 | 1067 | 0 | 1067 | N/A | N/A | N/A | N/A | 42405812 | 704 | 184.7284 | 0% | 0% | 100% | 0% | 100% | 40% | 9782278 | 1402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 86 | 61573826 | 3562 | 85.488 | 3.562 | 9.2 | 9.2 | 2B | 0 | 0 | 1067 | 0 | 1067 | N/A | N/A | N/A | N/A | 42406460 | 648 | 181.9203 | 0% | 0% | 100% | 0% | 100% | 40% | 9783157 | 879 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 100 | 61577695 | 3869 | 92.856 | 3.869 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 0 | 1067 | N/A | N/A | N/A | N/A | 42407156 | 696 | 179.8914 | 0% | 0% | 100% | 0% | 100% | 40% | 9783572 | 415 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 114 | 61582366 | 4671 | 112.104 | 4.671 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42408056 | 900 | 192.6782 | 0% | 0% | 100% | 0% | 100% | 0% | 9783572 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 139 | 61587899 | 5533 | 132.792 | 5.533 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42409332 | 1276 | 230.6163 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 140 | 61593761 | 5862 | 140.688 | 5.862 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42410700 | 1368 | 233.3675 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 141 | 61599639 | 5878 | 141.072 | 5.878 | 8.2 | 8.2 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42412100 | 1400 | 238.1763 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 145 | 61605639 | 6000 | 144 | 6 | 7.3 | 7.3 | 3B+1S | 1119 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42413512 | 1412 | 235.3333 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 143 | 61611696 | 6057 | 145.368 | 6.057 | 6.3 | 6.3 | 3B+1S | 1139 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42414936 | 1424 | 235.0999 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 142 | 61617798 | 6102 | 146.448 | 6.102 | 5.4 | 5.4 | 3B+1S | 1119 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42416364 | 1428 | 234.0216 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 140 | 61623622 | 5824 | 139.776 | 5.824 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42417748 | 1384 | 237.6374 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 135 | 61629264 | 5642 | 135.408 | 5.642 | 4.2 | 4.2 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42419092 | 1344 | 238.2134 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 134 | 61634952 | 5688 | 136.512 | 5.688 | 3.6 | 3.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42420436 | 1344 | 236.2869 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 131 | 61640541 | 5589 | 134.136 | 5.589 | 3.2 | 3.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42421764 | 1328 | 237.6096 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 131 | 61646079 | 5538 | 132.912 | 5.538 | 2.7 | 2.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42423100 | 1336 | 241.2423 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 129 | 61651571 | 5492 | 131.808 | 5.492 | 2.3 | 2.3 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42424444 | 1344 | 244.7196 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 129 | 61656996 | 5425 | 130.2 | 5.425 | 2.1 | 2.1 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42425760 | 1316 | 242.5806 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 130 | 61662376 | 5380 | 129.12 | 5.38 | 1.9 | 1.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42427084 | 1324 | 246.0967 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 122 | 61667642 | 5266 | 126.384 | 5.266 | 1.9 | 1.9 | 3B+1S | 964 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42428384 | 1300 | 246.8667 | 100% | 0% | 100% | 100% | 100% | 0% | 9783572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 105 | 117 | 61672441 | 4799 | 115.176 | 4.799 | 1.7 | 1.7 | 2B+1S | 1057 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42429452 | 1068 | 222.5464 | 100% | 0% | 100% | 0% | 100% | 0% | 9783572 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 95 | 61676835 | 4394 | 105.456 | 4.394 | 2.8 | 2.8 | 2B | 0 | 0 | 1147 | 0 | 1117 | N/A | N/A | N/A | N/A | 42430396 | 944 | 214.8384 | 0% | 0% | 100% | 0% | 100% | 40% | 9784922 | 1350 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 95 | 61680645 | 3810 | 91.44 | 3.81 | 4.3 | 4.3 | 2B | 0 | 0 | 1117 | 0 | 1108 | N/A | N/A | N/A | N/A | 42431148 | 752 | 197.3753 | 0% | 0% | 100% | 0% | 100% | 40% | 9786227 | 1305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.0833 | 121817 | 121817 | 121.817 | 121.817 | [12 empty] | 27504 | 27504 | 225.7813 | [6 empty] | 8397 | 8397 | 1.105 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 4:34 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:36 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 05 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27136 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61680645 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42431148 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9786227 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 113 | 61684467 | 3822 | 91.728 | 3.822 | 5.9 | 5.9 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 42431900 | 752 | 196.7556 | 0% | 0% | 100% | 0% | 100% | 45% | 9787729 | 1502 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 87 | 61688076 | 3609 | 86.616 | 3.609 | 7.4 | 7.4 | 2B | 0 | 0 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 42432580 | 680 | 188.4178 | 0% | 0% | 100% | 0% | 100% | 45% | 9789263 | 1534 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 83 | 61691723 | 3647 | 87.528 | 3.647 | 9.1 | 9.1 | 2B | 0 | 0 | 1047 | 0 | 1047 | N/A | N/A | N/A | N/A | 42433236 | 656 | 179.8739 | 0% | 0% | 100% | 0% | 100% | 45% | 9790838 | 1575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 88 | 61695413 | 3690 | 88.56 | 3.69 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1018 | N/A | N/A | N/A | N/A | 42433850 | 614 | 166.3957 | 0% | 0% | 100% | 0% | 100% | 45% | 9791232 | 394 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 96 | 90 | 61699138 | 3725 | 89.4 | 3.725 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1038 | N/A | N/A | N/A | N/A | 42434460 | 610 | 163.7584 | 0% | 0% | 100% | 0% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 116 | 111 | 61703670 | 4532 | 108.768 | 4.532 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42435316 | 856 | 188.8791 | 0% | 0% | 100% | 0% | 100% | 0% | 9791232 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 137 | 61709132 | 5462 | 131.088 | 5.462 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42436506 | 1190 | 217.8689 | 0% | 0% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 61715023 | 5891 | 141.384 | 5.891 | 9.1 | 9.1 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42437920 | 1414 | 240.0272 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 146 | 61720965 | 5942 | 142.608 | 5.942 | 8.3 | 8.3 | 3B+1S | 0 | 1127 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42439308 | 1388 | 233.5914 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 147 | 61727067 | 6102 | 146.448 | 6.102 | 7.3 | 7.3 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42440752 | 1444 | 236.6437 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 | 1.22 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 139 | 61733056 | 5989 | 143.736 | 5.989 | 6.4 | 6.4 | 3B+1S | 0 | 1129 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42442176 | 1424 | 237.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 144 | 61739059 | 6003 | 144.072 | 6.003 | 5.5 | 5.5 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42443604 | 1428 | 237.8811 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 140 | 61744903 | 5844 | 140.256 | 5.844 | 4.7 | 4.7 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42444996 | 1392 | 238.193 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 132 | 61750568 | 5665 | 135.96 | 5.665 | 4 | 4 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42446348 | 1352 | 238.6584 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 61756233 | 5665 | 135.96 | 5.665 | 3.5 | 3.5 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42447700 | 1352 | 238.6584 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 61761879 | 5646 | 135.504 | 5.646 | 3.2 | 3.2 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42449032 | 1332 | 235.9192 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 148 | 61767509 | 5630 | 135.12 | 5.63 | 2.8 | 2.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42450368 | 1336 | 237.3002 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 133 | 61773086 | 5577 | 133.848 | 5.577 | 2.5 | 2.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42451684 | 1316 | 235.9692 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 128 | 61778512 | 5426 | 130.224 | 5.426 | 2.3 | 2.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42452988 | 1304 | 240.3244 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 61783794 | 5282 | 126.768 | 5.282 | 2.2 | 2.2 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42454288 | 1300 | 246.1189 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 125 | 125 | 61789033 | 5239 | 125.736 | 5.239 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42455588 | 1300 | 248.139 | 0% | 100% | 100% | 100% | 100% | 0% | 9791232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 108 | 61793957 | 4924 | 118.176 | 4.924 | 1.6 | 1.6 | 2B+1S | 0 | 1048 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42456668 | 1080 | 219.3339 | 0% | 100% | 100% | 0% | 100% | 0% | 9791232 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 96 | 61798064 | 4107 | 98.568 | 4.107 | 2.7 | 2.7 | 2B | 0 | 0 | 1147 | 0 | 1148 | N/A | N/A | N/A | N/A | 42457544 | 876 | 213.2944 | 0% | 0% | 100% | 0% | 100% | 40% | 9792573 | 1341 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 90 | 61801838 | 3774 | 90.576 | 3.774 | 4.5 | 4.5 | 2B | 0 | 0 | 1097 | 0 | 1098 | N/A | N/A | N/A | N/A | 42458284 | 740 | 196.0784 | 0% | 0% | 100% | 0% | 100% | 40% | 9794192 | 1619 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 122 | 121193 | 121193 | 121.193 | 121.193 | [12 empty] | 27136 | 27136 | 223.9073 | [6 empty] | 7965 | 7965 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 06 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## DEC 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27344 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61801838 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42458284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9794192 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 86 | 61805742 | 3904 | 93.696 | 3.904 | 6.3 | 6.3 | 2B | 0 | 0 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 42459028 | 744 | 190.5738 | 0% | 0% | 100% | 0% | 100% | 45% | 9796042 | 1850 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 84 | 61809364 | 3622 | 86.928 | 3.622 | 8.4 | 8.4 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 42459688 | 660 | 182.2198 | 0% | 0% | 100% | 0% | 100% | 45% | 9797880 | 1838 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 84 | 82 | 61812556 | 3192 | 76.608 | 3.192 | 9.5 | 9.5 | 2B | 0 | 0 | 987 | 0 | 988 | N/A | N/A | N/A | N/A | 42460236 | 548 | 171.6792 | 0% | 0% | 100% | 0% | 100% | 45% | 9798891 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 91 | 89 | 61816224 | 3668 | 88.032 | 3.668 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1018 | N/A | N/A | N/A | N/A | 42460824 | 588 | 160.3053 | 0% | 0% | 100% | 0% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 107 | 61820167 | 3943 | 94.632 | 3.943 | 9.5 | 9.5 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 42461464 | 640 | 162.313 | 0% | 0% | 100% | 0% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 115 | 61825010 | 4843 | 116.232 | 4.843 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 42462400 | 936 | 193.2686 | 0% | 0% | 100% | 0% | 100% | 0% | 9798891 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 125 | 140 | 61830829 | 5819 | 139.656 | 5.819 | 8.9 | 8.9 | 3B+1S | 1118 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42463768 | 1368 | 235.0919 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 143 | 61836824 | 5995 | 143.88 | 5.995 | 7.9 | 7.9 | 3B+1S | 1149 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42465200 | 1432 | 238.8657 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 142 | 61842867 | 6043 | 145.032 | 6.043 | 6.8 | 6.8 | 3B+1S | 1150 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42466636 | 1436 | 237.6303 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 144 | 61848770 | 5903 | 141.672 | 5.903 | 6 | 6 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42468036 | 1400 | 237.1675 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 | 1.33 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 141 | 61854849 | 6079 | 145.896 | 6.079 | 5 | 5 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42469472 | 1436 | 236.2231 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 142 | 61860752 | 5903 | 141.672 | 5.903 | 4.1 | 4.1 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42470876 | 1404 | 237.8452 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 137 | 61866559 | 5807 | 139.368 | 5.807 | 3.4 | 3.4 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42472252 | 1376 | 236.9554 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 61872233 | 5674 | 136.176 | 5.674 | 2.8 | 2.8 | 3B+1S | 1066 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42473600 | 1348 | 237.5749 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 61877765 | 5532 | 132.768 | 5.532 | 2.6 | 2.6 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42474908 | 1308 | 236.4425 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 61883331 | 5566 | 133.584 | 5.566 | 2.5 | 2.5 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42476216 | 1308 | 234.9982 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 61888942 | 5611 | 134.664 | 5.611 | 2.2 | 2.2 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42477532 | 1316 | 234.5393 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 132 | 61894543 | 5601 | 134.424 | 5.601 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42478860 | 1328 | 237.1005 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 130 | 61900018 | 5475 | 131.4 | 5.475 | 1.8 | 1.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42480184 | 1324 | 241.8265 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 131 | 61905409 | 5391 | 129.384 | 5.391 | 1.7 | 1.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42481500 | 1316 | 244.1106 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 126 | 61910743 | 5334 | 128.016 | 5.334 | 1.6 | 1.6 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42482796 | 1296 | 242.9696 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 118 | 61915796 | 5053 | 121.272 | 5.053 | 1.5 | 1.5 | 3B+1S | 1003 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 42484032 | 1236 | 244.6072 | 100% | 0% | 100% | 100% | 100% | 0% | 9798891 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 140 | 94 | 61920050 | 4254 | 102.096 | 4.254 | 2.9 | 2.9 | 2B | 0 | 0 | 1147 | 0 | 1117 | N/A | N/A | N/A | N/A | 42484936 | 904 | 212.5059 | 0% | 0% | 100% | 0% | 100% | 40% | 9800251 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 91 | 61923879 | 3829 | 91.896 | 3.829 | 5 | 5 | 2B | 0 | 0 | 1077 | 0 | 1057 | N/A | N/A | N/A | N/A | 42485628 | 692 | 180.726 | 0% | 0% | 100% | 0% | 100% | 40% | 9802080 | 1829 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 121.375 | 122041 | 122041 | 122.041 | 122.041 | [12 empty] | 27344 | 27344 | 224.0559 | [6 empty] | 7888 | 7888 | 1.2083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 07 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27224 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 61923879 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42485628 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9802080 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 85 | 61927583 | 3704 | 88.896 | 3.704 | 6.8 | 6.8 | 2B | 0 | 0 | 1017 | 0 | 1018 | N/A | N/A | N/A | N/A | 42486292 | 664 | 179.2657 | 0% | 0% | 100% | 0% | 100% | 43% | 9803811 | 1731 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 83 | 61931121 | 3538 | 84.912 | 3.538 | 8.5 | 8.5 | 2B | 0 | 0 | 1047 | 0 | 1038 | N/A | N/A | N/A | N/A | 42486888 | 596 | 168.4568 | 0% | 0% | 100% | 0% | 100% | 45% | 9805502 | 1691 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 88 | 85 | 61934665 | 3544 | 85.056 | 3.544 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 998 | N/A | N/A | N/A | N/A | 42487492 | 604 | 170.4289 | 0% | 0% | 100% | 0% | 100% | 45% | 9806376 | 874 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 90 | 88 | 61938505 | 3840 | 92.16 | 3.84 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 0 | 1018 | N/A | N/A | N/A | N/A | 42488092 | 600 | 156.25 | 0% | 0% | 100% | 0% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 105 | 61942351 | 3846 | 92.304 | 3.846 | 9.5 | 9.5 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 42488700 | 608 | 158.0863 | 0% | 0% | 100% | 0% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 114 | 61947031 | 4680 | 112.32 | 4.68 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42489620 | 920 | 196.5812 | 0% | 0% | 100% | 0% | 100% | 0% | 9806376 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 126 | 140 | 61952809 | 5778 | 138.672 | 5.778 | 8.8 | 8.8 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42490972 | 1352 | 233.991 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 139 | 61958765 | 5956 | 142.944 | 5.956 | 7.9 | 7.9 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42492396 | 1424 | 239.0866 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 126 | 144 | 61964812 | 6047 | 145.128 | 6.047 | 6.9 | 6.9 | 3B+1S | 0 | 1149 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42493836 | 1440 | 238.1346 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 142 | 61970781 | 5969 | 143.256 | 5.969 | 5.9 | 5.9 | 3B+1S | 0 | 1149 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42495264 | 1428 | 239.2361 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 | 1.31 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 143 | 61976795 | 6014 | 144.336 | 6.014 | 5 | 5 | 3B+1S | 0 | 1149 | 1187 | 1158 | 1187 | N/A | N/A | N/A | N/A | 42496692 | 1428 | 237.446 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 142 | 61982755 | 5960 | 143.04 | 5.96 | 4 | 4 | 3B+1S | 0 | 1147 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42498116 | 1424 | 238.9262 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 133 | 61988478 | 5723 | 137.352 | 5.723 | 3.2 | 3.2 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42499493 | 1377 | 240.6081 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 134 | 61994007 | 5529 | 132.696 | 5.529 | 2.8 | 2.8 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42500824 | 1331 | 240.7307 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 135 | 61999552 | 5545 | 133.08 | 5.545 | 2.6 | 2.6 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42502148 | 1324 | 238.7737 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 131 | 62005076 | 5524 | 132.576 | 5.524 | 2.5 | 2.5 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42503468 | 1320 | 238.9573 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 62010564 | 5488 | 131.712 | 5.488 | 2.4 | 2.4 | 3B+1S | 0 | 1055 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42504796 | 1328 | 241.9825 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 62016146 | 5582 | 133.968 | 5.582 | 2.2 | 2.2 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42506124 | 1328 | 237.9076 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 127 | 62021533 | 5387 | 129.288 | 5.387 | 2.1 | 2.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42507436 | 1312 | 243.5493 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 126 | 62026833 | 5300 | 127.2 | 5.3 | 2 | 2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42508744 | 1308 | 246.7925 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 | 123 | 62032011 | 5178 | 124.272 | 5.178 | 1.9 | 1.9 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42510044 | 1300 | 251.0622 | 0% | 100% | 100% | 100% | 100% | 0% | 9806376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 100 | 112 | 62036830 | 4819 | 115.656 | 4.819 | 1.4 | 1.4 | 2B+1S | 0 | 1077 | 1187 |  | 1187 | N/A | N/A | N/A | N/A | 42511124 | 1080 | 224.1129 | 0% | 100% | 100% |  | 100% | 0% | 9806376 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 97 | 62041046 | 4216 | 101.184 | 4.216 | 2.4 | 2.4 | 2B | 0 | 0 | 1187 |  | 1188 | N/A | N/A | N/A | N/A | 42512032 | 908 | 215.37 | 0% | 0% | 100% | 0% | 100% | 40% | 9807412 | 1036 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 96 | 62045062 | 4016 | 96.384 | 4.016 | 4 | 4 | 2B | 0 | 0 | 1117 |  | 1118 | N/A | N/A | N/A | N/A | 42512852 | 820 | 204.1833 | 0% | 0% | 100% | 0% | 100% | 40% | 9808877 | 1465 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  | 120.4583 | 121183 | 121183 | 121.183 | 121.183 | [12 empty] | 27224 | 27224 | 224.652 | [6 empty] | 6797 | 6797 | 1.2317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (43%)
XCV2- CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 08 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## DEC 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27496 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62045062 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42512852 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9808877 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 88 | 62048769 | 3707 | 88.968 | 3.707 | 5.8 | 5.8 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 42513592 | 740 | 199.6223 | 0% | 0% | 100% | 0% | 100% | 45% | 9810561 | 1684 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 85 | 62052380 | 3611 | 86.664 | 3.611 | 7.6 | 7.6 | 2B | 0 | 0 | 1076 | 0 | 1087 | N/A | N/A | N/A | N/A | 42514292 | 700 | 193.8521 | 0% | 0% | 100% | 0% | 100% | 45% | 9812309 | 1748 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 84 | 62055872 | 3492 | 83.808 | 3.492 | 9.4 | 9.4 | 2B | 0 | 0 | 1048 | 0 | 1048 | N/A | N/A | N/A | N/A | 42514912 | 620 | 177.5487 | 0% | 0% | 100% | 0% | 100% | 45% | 9814038 | 1729 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 91 | 62059603 | 3731 | 89.544 | 3.731 | 9.5 | 9.5 | 2B | 0 | 0 | 1037 | 0 | 1038 | N/A | N/A | N/A | N/A | 42515544 | 632 | 169.3916 | 0% | 0% | 100% | 0% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 104 | 62063710 | 4107 | 98.568 | 4.107 | 9.5 | 9.5 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 42516268 | 724 | 176.2844 | 0% | 0% | 100% | 0% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 115 | 62068407 | 4697 | 112.728 | 4.697 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42517188 | 920 | 195.8697 | 0% | 0% | 100% | 0% | 100% | 0% | 9814038 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 125 | 143 | 62074409 | 6002 | 144.048 | 6.002 | 9 | 9 | 3B+1S | 1149 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42518580 | 1392 | 231.9227 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 142 | 62080276 | 5867 | 140.808 | 5.867 | 8 | 8 | 3B+1S | 1149 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42519984 | 1404 | 239.3046 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 144 | 62086389 | 6113 | 146.712 | 6.113 | 6.8 | 6.8 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42521436 | 1452 | 237.5266 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 145 | 62092361 | 5972 | 143.328 | 5.972 | 5.9 | 5.9 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42522852 | 1416 | 237.1065 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 | 1.26 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 143 | 62098376 | 6015 | 144.36 | 6.015 | 5 | 5 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42524284 | 1432 | 238.0715 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 62104323 | 5947 | 142.728 | 5.947 | 4.3 | 4.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42525692 | 1408 | 236.758 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 62109979 | 5656 | 135.744 | 5.656 | 3.6 | 3.6 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42527044 | 1352 | 239.0382 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 62115669 | 5690 | 136.56 | 5.69 | 3.2 | 3.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42528396 | 1352 | 237.6098 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 62121255 | 5586 | 134.064 | 5.586 | 2.9 | 2.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42529724 | 1328 | 237.7372 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 62126830 | 5575 | 133.8 | 5.575 | 2.8 | 2.8 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42531044 | 1320 | 236.7713 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 62132403 | 5573 | 133.752 | 5.573 | 2.6 | 2.6 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42532380 | 1336 | 239.7273 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 133 | 62137929 | 5526 | 132.624 | 5.526 | 2.3 | 2.3 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42533704 | 1324 | 239.5946 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 133 | 62143400 | 5471 | 131.304 | 5.471 | 2.1 | 2.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42535028 | 1324 | 242.0033 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 128 | 62148756 | 5356 | 128.544 | 5.356 | 2 | 2 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42536340 | 1312 | 244.9589 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 129 | 62154096 | 5340 | 128.16 | 5.34 | 1.9 | 1.9 | 3B+1S | 1004 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42537652 | 1312 | 245.6929 | 100% | 0% | 100% | 100% | 100% | 0% | 9814038 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 97 | 110 | 62159223 | 5127 | 123.048 | 5.127 | 1.3 | 1.3 | 2B+1S | 1128 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42538812 | 1160 | 226.2532 | 100% | 0% | 100% | 0% | 100% | 0% | 9814038 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 91 | 62163109 | 3886 | 93.264 | 3.886 | 2.4 | 2.4 | 2B | 0 | 0 | 1137 | 0 | 1138 | N/A | N/A | N/A | N/A | 42539628 | 816 | 209.9846 | 0% | 0% | 100% | 0% | 100% | 40% | 9815500 | 1462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 85 | 62166772 | 3663 | 87.912 | 3.663 | 4.1 | 4.1 | 2B | 0 | 0 | 1077 | 0 | 1147 | N/A | N/A | N/A | N/A | 42540348 | 720 | 196.5602 | 0% | 0% | 100% | 0% | 100% | 40% | 9817007 | 1507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121710 | 121.71 | 121.71 | [12 empty] | 27496 | 27496 | 225.9141 | [6 empty] | 8130 | 8130 | 1.1717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 09 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27216 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62166772 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42540348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9817007 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 87 | 62170146 | 3374 | 80.976 | 3.374 | 5.9 | 5.9 | 2B | 0 | 0 | 1037 | 0 | 1037 | N/A | N/A | N/A | N/A | 42540978 | 630 | 186.722 | 0% | 0% | 100% | 0% | 100% | 45% | 9818731 | 1724 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 77 | 62173416 | 3270 | 78.48 | 3.27 | 7.7 | 7.7 | 2B | 0 | 0 | 1007 | 0 | 1007 | N/A | N/A | N/A | N/A | 42541556 | 578 | 176.7584 | 0% | 0% | 100% | 0% | 100% | 45% | 9820488 | 1757 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 79 | 62176484 | 3068 | 73.632 | 3.068 | 9.4 | 9.4 | 2B | 0 | 0 | 1007 | 0 | 1007 | N/A | N/A | N/A | N/A | 42542092 | 536 | 174.7066 | 0% | 0% | 100% | 0% | 100% | 45% | 9822144 | 1656 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 94 | 62180496 | 4012 | 96.288 | 4.012 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 42542724 | 632 | 157.5274 | 0% | 0% | 100% | 0% | 100% | 45% | 9822376 | 232 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 106 | 62184536 | 4040 | 96.96 | 4.04 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 0 | 1149 | N/A | N/A | N/A | N/A | 42543424 | 700 | 173.2673 | 0% | 0% | 100% | 0% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 114 | 62189288 | 4752 | 114.048 | 4.752 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 42544348 | 924 | 194.4444 | 0% | 0% | 100% | 0% | 100% | 0% | 9822376 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 125 | 143 | 62195086 | 5798 | 139.152 | 5.798 | 9.1 | 9.1 | 3B+1S | 0 | 1089 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42545708 | 1360 | 234.5636 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 145 | 62201136 | 6050 | 145.2 | 6.05 | 8.2 | 8.2 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42547140 | 1432 | 236.6942 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 126 | 144 | 62207048 | 5912 | 141.888 | 5.912 | 7.2 | 7.2 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42548548 | 1408 | 238.1597 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 145 | 62213112 | 6064 | 145.536 | 6.064 | 6.2 | 6.2 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42549996 | 1448 | 238.7863 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 156 | 62219054 | 5942 | 142.608 | 5.942 | 5.3 | 5.3 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42551404 | 1408 | 236.9573 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 62224930 | 5876 | 141.024 | 5.876 | 4.6 | 4.6 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42552792 | 1388 | 236.2151 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 153 | 62230664 | 5734 | 137.616 | 5.734 | 4.1 | 4.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42554140 | 1348 | 235.0889 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 62236310 | 5646 | 135.504 | 5.646 | 3.5 | 3.5 | 3B+1S | 0 | 1065 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42555488 | 1348 | 238.7531 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 151 | 62241863 | 5553 | 133.272 | 5.553 | 3.2 | 3.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42556816 | 1328 | 239.15 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 133 | 62247344 | 5481 | 131.544 | 5.481 | 3.1 | 3.1 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42558140 | 1324 | 241.5618 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 132 | 62252837 | 5493 | 131.832 | 5.493 | 2.8 | 2.8 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42559456 | 1316 | 239.5776 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 129 | 62258326 | 5489 | 131.736 | 5.489 | 2.6 | 2.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42560784 | 1328 | 241.9384 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 62263741 | 5415 | 129.96 | 5.415 | 2.4 | 2.4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42562108 | 1324 | 244.506 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 129 | 62269158 | 5417 | 130.008 | 5.417 | 2.3 | 2.3 | 3B+1S | 0 | 1004 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42563420 | 1312 | 242.2005 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 125 | 62274481 | 5323 | 127.752 | 5.323 | 2.2 | 2.2 | 3B+1S | 0 | 1005 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42564696 | 1276 | 239.7144 | 0% | 100% | 100% | 100% | 100% | 0% | 9822376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 111 | 62279385 | 4904 | 117.696 | 4.904 | 1.5 | 1.5 | 2B+1S | 0 | 1158 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 42565784 | 1088 | 221.8597 | 0% | 100% | 100% | 0% | 100% | 0% | 9822376 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 102 | 62283756 | 4371 | 104.904 | 4.371 | 2.4 | 2.4 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 42566716 | 932 | 213.2235 | 0% | 0% | 100% | 0% | 100% | 40% | 9823576 | 1200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 97 | 62287853 | 4097 | 98.328 | 4.097 | 3.8 | 3.8 | 2B | 0 | 0 | 1137 | 0 | 1137 | N/A | N/A | N/A | N/A | 42567564 | 848 | 206.9807 | 0% | 0% | 100% | 0% | 100% | 40% | 9824951 | 1375 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121081 | 121.081 | 121.081 | [12 empty] | 27216 | 27216 | 224.7752 | [6 empty] | 7944 | 7944 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:08 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 10 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## DEC 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62287853 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42567564 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9824951 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 94 | 62292064 | 4211 | 101.064 | 4.211 | 5.7 | 5.7 | 2B | 0 | 0 | 1127 | 0 | 1128 | N/A | N/A | N/A | N/A | 42568412 | 848 | 201.3773 | 0% | 0% | 100% | 0% | 100% | 45% | 9826592 | 1641 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 90 | 62295763 | 3699 | 88.776 | 3.699 | 7.2 | 7.2 | 2B | 0 | 0 | 1087 | 0 | 1087 | N/A | N/A | N/A | N/A | 42569120 | 708 | 191.4031 | 0% | 0% | 100% | 0% | 100% | 45% | 9828097 | 1505 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 89 | 62299226 | 3463 | 83.112 | 3.463 | 8.6 | 8.6 | 2B | 0 | 0 | 1088 | 0 | 1088 | N/A | N/A | N/A | N/A | 42569768 | 648 | 187.121 | 0% | 0% | 100% | 0% | 100% | 45% | 9829415 | 1318 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 93 | 62303195 | 3969 | 95.256 | 3.969 | 9.5 | 9.5 | 2B | 0 | 0 | 1088 | 0 | 1088 | N/A | N/A | N/A | N/A | 42570500 | 732 | 184.4293 | 0% | 0% | 100% | 0% | 100% | 45% | 9830226 | 811 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 105 | 62307168 | 3973 | 95.352 | 3.973 | 9.5 | 9.5 | 2B | 0 | 0 | 1147 | 0 | 1148 | N/A | N/A | N/A | N/A | 42571208 | 708 | 178.2029 | 0% | 0% | 100% | 0% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 116 | 62311950 | 4782 | 114.768 | 4.782 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1189 | N/A | N/A | N/A | N/A | 42572140 | 932 | 194.8975 | 0% | 0% | 100% | 0% | 100% | 0% | 9830226 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 125 | 142 | 62317718 | 5768 | 138.432 | 5.768 | 8.7 | 8.7 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42573492 | 1352 | 234.3967 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 146 | 62323705 | 5987 | 143.688 | 5.987 | 7.8 | 7.8 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42574920 | 1428 | 238.5168 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 127 | 145 | 62329750 | 6045 | 145.08 | 6.045 | 6.8 | 6.8 | 3B+1S | 1149 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42576356 | 1436 | 237.5517 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 136 | 62335760 | 6010 | 144.24 | 6.01 | 5.8 | 5.8 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42577768 | 1412 | 234.9418 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 | 1.25 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 143 | 62341736 | 5976 | 143.424 | 5.976 | 4.9 | 4.9 | 3B+1S | 1148 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42579180 | 1412 | 236.2784 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 62347715 | 5979 | 143.496 | 5.979 | 4 | 4 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42580572 | 1392 | 232.8149 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 139 | 62353483 | 5768 | 138.432 | 5.768 | 3.2 | 3.2 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42581928 | 1356 | 235.0902 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 137 | 62359221 | 5738 | 137.712 | 5.738 | 2.6 | 2.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42583284 | 1356 | 236.3193 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 62364765 | 5544 | 133.056 | 5.544 | 2.3 | 2.3 | 3B+1S | 1050 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42584588 | 1304 | 235.2092 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 62370114 | 5349 | 128.376 | 5.349 | 2.1 | 2.1 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42585852 | 1264 | 236.3059 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 62375952 | 5838 | 140.112 | 5.838 | 1.9 | 1.9 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42587220 | 1368 | 234.3268 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 132 | 62381413 | 5461 | 131.064 | 5.461 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42588532 | 1312 | 240.249 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 127 | 62386829 | 5416 | 129.984 | 5.416 | 1.6 | 1.6 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42589836 | 1304 | 240.7681 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 124 | 62392145 | 5316 | 127.584 | 5.316 | 1.5 | 1.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42591132 | 1296 | 243.7923 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 124 | 120 | 62397415 | 5270 | 126.48 | 5.27 | 1.4 | 1.4 | 3B+1S | 995 | 0 | 1176 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42592436 | 1304 | 247.4383 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 120 | 62402586 | 5171 | 124.104 | 5.171 | 1.3 | 1.3 | 2B+1S | 1005 | 0 | 1157 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42593684 | 1248 | 241.346 | 100% | 0% | 100% | 100% | 100% | 0% | 9830226 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 100 | 62407046 | 4460 | 107.04 | 4.46 | 2.3 | 2.3 | 2B | 0 | 0 | 1137 | 1185 | 0 | N/A | N/A | N/A | N/A | 42594640 | 956 | 214.3498 | 0% | 0% | 100% | 0% | 100% | 35% | 9830977 | 751 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 101 | 62411236 | 4190 | 100.56 | 4.19 | 3.3 | 3.3 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 42595444 | 804 | 191.8854 | 0% | 0% | 100% | 0% | 100% | 35% | 9831961 | 984 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123383 | 123.383 | 123.383 | [12 empty] | 27880 | 27880 | 225.9631 | [6 empty] | 7010 | 7010 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 11 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 10:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (35%)
BP2 - STARTED @ 10:30 PM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP3 - STOPPED @ 10:31 PM DUE TO LOW WATER LEVEL

## DEC 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26912 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62411236 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42595444 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9831961 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 95 | 62415031 | 3795 | 91.08 | 3.795 | 4.8 | 4.8 | 2B | 0 | 0 | 1016 | 1185 | 0 | N/A | N/A | N/A | N/A | 42596164 | 720 | 189.7233 | 0% | 0% | 100% | 100% | 0% | 45% | 9833309 | 1348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 88 | 62419040 | 4009 | 96.216 | 4.009 | 6.4 | 6.4 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42596916 | 752 | 187.5779 | 0% | 0% | 100% | 100% | 0% | 45% | 9834911 | 1602 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 87 | 62422756 | 3716 | 89.184 | 3.716 | 8.3 | 8.3 | 2B | 0 | 0 | 887 | 1185 | 0 | N/A | N/A | N/A | N/A | 42597576 | 660 | 177.6103 | 0% | 0% | 100% | 100% | 0% | 45% | 9836702 | 1791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 96 | 62426384 | 3628 | 87.072 | 3.628 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 1185 | 0 | N/A | N/A | N/A | N/A | 42598220 | 644 | 177.5083 | 0% | 0% | 100% | 100% | 0% | 45% | 9837947 | 1245 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 105 | 62430506 | 4122 | 98.928 | 4.122 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 927 | N/A | N/A | N/A | N/A | 42598884 | 664 | 161.0869 | 0% | 0% | 0% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 121 | 62435189 | 4683 | 112.392 | 4.683 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42599708 | 824 | 175.9556 | 0% | 0% | 0% | 100% | 100% | 0% | 9837947 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 62441039 | 5850 | 140.4 | 5.85 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42600964 | 1256 | 214.7009 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 62447170 | 6131 | 147.144 | 6.131 | 8.8 | 8.8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42602332 | 1368 | 223.1284 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 62453367 | 6197 | 148.728 | 6.197 | 8.1 | 8.1 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42603720 | 1388 | 223.9793 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 62459689 | 6322 | 151.728 | 6.322 | 7.3 | 7.3 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42605128 | 1408 | 222.7143 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 | 1.34 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 150 | 62466022 | 6333 | 151.992 | 6.333 | 6.5 | 6.5 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42606560 | 1432 | 226.1172 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 149 | 62472308 | 6286 | 150.864 | 6.286 | 5.6 | 5.6 | 3B+1S | 0 | 1146 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42607996 | 1436 | 228.4442 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 139 | 62478461 | 6153 | 147.672 | 6.153 | 4.7 | 4.7 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42609412 | 1416 | 230.1316 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 141 | 62484546 | 6085 | 146.04 | 6.085 | 4 | 4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42610812 | 1400 | 230.074 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 139 | 62490371 | 5825 | 139.8 | 5.825 | 3.7 | 3.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42612144 | 1332 | 228.6695 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 145 | 62496233 | 5862 | 140.688 | 5.862 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42613476 | 1332 | 227.2262 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 62502077 | 5844 | 140.256 | 5.844 | 3.2 | 3.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42614796 | 1320 | 225.8727 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 134 | 62507832 | 5755 | 138.12 | 5.755 | 3 | 3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42616128 | 1332 | 231.4509 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 130 | 62513406 | 5574 | 133.776 | 5.574 | 2.9 | 2.9 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42617444 | 1316 | 236.0962 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 130 | 62518850 | 5444 | 130.656 | 5.444 | 2.8 | 2.8 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42618684 | 1240 | 227.7737 | 0% | 100% | 100% | 100% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 125 | 62524078 | 5228 | 125.472 | 5.228 | 2.5 | 2.5 | 2B+1S | 0 | 1046 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42619736 | 1052 | 201.2242 | 0% | 100% | 100% | 0% | 100% | 0% | 9837947 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 116 | 62529116 | 5038 | 120.912 | 5.038 | 2.1 | 2.1 | 2B+1S | 0 | 1015 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42620756 | 1020 | 202.4613 | 0% | 100% | 100% | 0% | 100% | 0% | 9837947 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 101 | 62533645 | 4529 | 108.696 | 4.529 | 3.2 | 3.2 | 2B | 0 | 0 | 1037 | 1185 | 0 | N/A | N/A | N/A | N/A | 42621608 | 852 | 188.121 | 0% | 0% | 100% | 100% | 0% | 40% | 9839145 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 100 | 62537836 | 4191 | 100.584 | 4.191 | 4.7 | 4.7 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 42622356 | 748 | 178.4777 | 0% | 0% | 100% | 100% | 0% | 40% | 9840490 | 1345 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126600 | 126.6 | 126.6 | [12 empty] | 25320 | 26912 | 212.575 | [6 empty] | 8529 | 8529 | 1.1817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
BP3 - STARTED @ 4:00 AM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP1 - STOPPED @ 4:01 AM DUE TO CHANGE OPERATION OF BOOSTER
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 12 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 10:00 PM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP3 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
XCV2 -OPENED @ 10:02 PM (40%)

## DEC 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26072 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62537836 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42622356 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9840490 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 95 | 62542013 | 4177 | 100.248 | 4.177 | 6.3 | 6.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 42623108 | 752 | 180.0335 | 0% | 0% | 100% | 100% | 0% | 0% | 9842028 | 1538 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 94 | 62545853 | 3840 | 92.16 | 3.84 | 7.8 | 7.8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42623796 | 688 | 179.1667 | 0% | 0% | 100% | 100% | 0% | 0% | 9843543 | 1515 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 86 | 62549495 | 3642 | 87.408 | 3.642 | 9.4 | 9.4 | 2B | 0 | 0 | 886 | 1185 | 0 | N/A | N/A | N/A | N/A | 42624436 | 640 | 175.7276 | 0% | 0% | 100% | 100% | 0% | 0% | 9845073 | 1530 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 91 | 62553174 | 3679 | 88.296 | 3.679 | 9.5 | 9.5 | 2B | 0 | 0 | 846 | 1185 | 0 | N/A | N/A | N/A | N/A | 42625060 | 624 | 169.6113 | 0% | 0% | 100% | 100% | 0% | 0% | 9845114 | 41 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 95 | 62557082 | 3908 | 93.792 | 3.908 | 9.5 | 9.5 | 2B | 0 | 0 | 867 | 1185 | 0 | N/A | N/A | N/A | N/A | 42625692 | 632 | 161.7195 | 0% | 0% | 100% | 100% | 0% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 121 | 116 | 62561701 | 4619 | 110.856 | 4.619 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 42626460 | 768 | 166.2698 | 0% | 0% | 100% | 100% | 0% | 0% | 9845114 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 141 | 62567328 | 5627 | 135.048 | 5.627 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42627652 | 1192 | 211.8358 | 0% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 140 | 62573228 | 5900 | 141.6 | 5.9 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42628928 | 1276 | 216.2712 | 0% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 150 | 62579429 | 6201 | 148.824 | 6.201 | 9 | 9 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42630304 | 1376 | 221.8997 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 62585659 | 6230 | 149.52 | 6.23 | 8.2 | 8.2 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42631704 | 1400 | 224.7191 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 | 1.31 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 62591899 | 6240 | 149.76 | 6.24 | 7.3 | 7.3 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42633108 | 1404 | 225 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 62598092 | 6193 | 148.632 | 6.193 | 6.6 | 6.6 | 3B+1S | 1098 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42634504 | 1396 | 225.4158 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 62604136 | 6044 | 145.056 | 6.044 | 6 | 6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42635864 | 1360 | 225.0165 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 62610150 | 6014 | 144.336 | 6.014 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42637224 | 1360 | 226.139 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 62616025 | 5875 | 141 | 5.875 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42638552 | 1328 | 226.0426 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 62621874 | 5849 | 140.376 | 5.849 | 4.8 | 4.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42639884 | 1332 | 227.7312 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 62627660 | 5786 | 138.864 | 5.786 | 4.5 | 4.5 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42641196 | 1312 | 226.7542 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 142 | 62633503 | 5843 | 140.232 | 5.843 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42642516 | 1320 | 225.9113 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 131 | 62639220 | 5717 | 137.208 | 5.717 | 3.8 | 3.8 | 3B+1S | 994 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42643840 | 1324 | 231.59 | 100% | 0% | 100% | 100% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 123 | 62644558 | 5338 | 128.112 | 5.338 | 3.3 | 3.3 | 3B+1S | 1046 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42644916 | 1076 | 201.5736 | 100% | 0% | 100% | 0% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 121 | 62649724 | 5166 | 123.984 | 5.166 | 2.8 | 2.8 | 2B+1S | 1027 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42645948 | 1032 | 199.7677 | 100% | 0% | 100% | 0% | 100% | 0% | 9845114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 118 | 62654768 | 5044 | 121.056 | 5.044 | 2.5 | 2.5 | 2B+1S | 1026 | 0 | 1169 | 0 | 1168 | N/A | N/A | N/A | N/A | 42646956 | 1008 | 199.8414 | 100% | 0% | 100% | 0% | 100% | 0% | 9845114 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 100 | 62659170 | 4402 | 105.648 | 4.402 | 3.3 | 3.3 | 2B | 0 | 0 | 1077 | 0 | 1088 | N/A | N/A | N/A | N/A | 42647756 | 800 | 181.7356 | 0% | 0% | 100% | 0% | 100% | 40% | 9846080 | 966 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 98 | 62663238 | 4068 | 97.632 | 4.068 | 4.8 | 4.8 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 42648428 | 672 | 165.1917 | 0% | 0% | 100% | 0% | 100% | 40% | 9847438 | 1358 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125402 | 125.402 | 125.402 | [12 empty] | 26072 | 26072 | 207.9074 | [6 empty] | 6948 | 6948 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 13 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24336 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62663238 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42648428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9847438 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 92 | 62667077 | 3839 | 92.136 | 3.839 | 6.3 | 6.3 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 42649048 | 620 | 161.5004 | 0% | 0% | 100% | 0% | 100% | 45% | 9848816 | 1378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 89 | 62670852 | 3775 | 90.6 | 3.775 | 7.6 | 7.6 | 2B | 0 | 0 | 1027 | 0 | 1028 | N/A | N/A | N/A | N/A | 42649668 | 620 | 164.2384 | 0% | 0% | 100% | 0% | 100% | 45% | 9850801 | 1985 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 62674539 | 3687 | 88.488 | 3.687 | 8.9 | 8.9 | 2B | 0 | 0 | 998 | 0 | 1007 | N/A | N/A | N/A | N/A | 42650268 | 600 | 162.7339 | 0% | 0% | 100% | 0% | 100% | 45% | 9851363 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 93 | 62678341 | 3802 | 91.248 | 3.802 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 947 | N/A | N/A | N/A | N/A | 42650828 | 560 | 147.2909 | 0% | 0% | 100% | 0% | 100% | 45% | 9852075 | 712 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 101 | 62682439 | 4098 | 98.352 | 4.098 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 0 | 1037 | N/A | N/A | N/A | N/A | 42651380 | 552 | 134.6999 | 0% | 0% | 100% | 0% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 62687457 | 5018 | 120.432 | 5.018 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42652244 | 864 | 172.1802 | 0% | 0% | 100% | 0% | 100% | 0% | 9852075 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 62693341 | 5884 | 141.216 | 5.884 | 9.5 | 9.5 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42653524 | 1280 | 217.5391 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 62699546 | 6205 | 148.92 | 6.205 | 8.8 | 8.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42654912 | 1388 | 223.6906 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 150 | 62705737 | 6191 | 148.584 | 6.191 | 8.1 | 8.1 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42656308 | 1396 | 225.4886 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 62711951 | 6214 | 149.136 | 6.214 | 7.3 | 7.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42657692 | 1384 | 222.7229 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 62718072 | 6121 | 146.904 | 6.121 | 6.6 | 6.6 | 3B+1S | 0 | 1049 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42659076 | 1384 | 226.1068 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 62724196 | 6124 | 146.976 | 6.124 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42660452 | 1376 | 224.6897 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 62730199 | 6003 | 144.072 | 6.003 | 5.6 | 5.6 | 3B+1S | 0 | 1049 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42661820 | 1368 | 227.8861 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 62736027 | 5828 | 139.872 | 5.828 | 5.2 | 5.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42663148 | 1328 | 227.8655 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 134 | 62741822 | 5795 | 139.08 | 5.795 | 5 | 5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42664476 | 1328 | 229.1631 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 136 | 62747596 | 5774 | 138.576 | 5.774 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42665804 | 1328 | 229.9965 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 127 | 62753246 | 5650 | 135.6 | 5.65 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42667108 | 1304 | 230.7965 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 134 | 62758842 | 5596 | 134.304 | 5.596 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42668364 | 1256 | 224.446 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 129 | 62764313 | 5471 | 131.304 | 5.471 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42669612 | 1248 | 228.1119 | 0% | 100% | 100% | 100% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 126 | 62769573 | 5260 | 126.24 | 5.26 | 3.9 | 3.9 | 3B+1S | 0 | 1067 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 42670684 | 1072 | 203.8023 | 0% | 100% | 100% | 0% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 127 | 62774818 | 5245 | 125.88 | 5.245 | 3.2 | 3.2 | 2B+1S | 0 | 1087 | 1167 | 0 | 1168 | N/A | N/A | N/A | N/A | 42671748 | 1064 | 202.8599 | 0% | 100% | 100% | 0% | 100% | 0% | 9852075 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 116 | 62779916 | 5098 | 122.352 | 5.098 | 2.6 | 2.6 | 2B+1S | 0 | 1045 | 1168 | 0 | 1168 | N/A | N/A | N/A | N/A | 42672764 | 1016 | 199.2938 | 0% | 100% | 100% | 0% | 100% | 0% | 9852075 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 131 | 62784300 | 4384 | 105.216 | 4.384 | 4.1 | 4.1 | 2B | 0 | 0 | 1080 | 0 | 1080 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 35% | 9853245 | 1170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 94 | 62788320 | 4020 | 96.48 | 4.02 | 5.1 | 5.1 | 2B | 0 | 0 | 1048 | 0 | 1018 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 35% | 9854420 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125082 | 125.082 | 125.082 | [12 empty] | 24336 | 24336 | 194.5604 | [6 empty] | 6982 | 6982 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 14 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)
POWER INTERUPTION @ 10:54 PM
BP1 - STOPPED @ 10: 54 PM
BP3 - STOPPED @ 10: 54 PM
GENERATOR 2 STARTED @ 10:59 PM
BP1 - STARTED @ 11: 02 PM
BP3 - STARTED @ 11:04 PM
NORMAL OPERATION

## DEC 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62788320 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9854420 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 90 | 62791541 | 3221 | 77.304 | 3.221 | 6.8 | 6.8 | 2B | 0 | 0 | 1027 | 0 | 1017 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9855926 | 1506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 87 | 62794827 | 3286 | 78.864 | 3.286 | 8.5 | 8.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9857528 | 1602 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 81 | 88 | 62798622 | 3795 | 91.08 | 3.795 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 947 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9859001 | 1473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 91 | 89 | 62802244 | 3622 | 86.928 | 3.622 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 0 | 947 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 102 | 62806322 | 4078 | 97.872 | 4.078 | 9.5 | 9.5 | 2B | 0 | 0 | 1018 | 0 | 1018 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 62811406 | 5084 | 122.016 | 5.084 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 0% | 9859001 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 138 | 62817352 | 5946 | 142.704 | 5.946 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 62823247 | 5895 | 141.48 | 5.895 | 9.5 | 9.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 62829005 | 5758 | 138.192 | 5.758 | 9.1 | 9.1 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 62835318 | 6313 | 151.512 | 6.313 | 8.7 | 8.7 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 | 1.14
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 62841360 | 6042 | 145.008 | 6.042 | 8.2 | 8.2 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 62847230 | 5870 | 140.88 | 5.87 | 7.9 | 7.9 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 62853079 | 5849 | 140.376 | 5.849 | 7.6 | 7.6 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 62858724 | 5645 | 135.48 | 5.645 | 7.3 | 7.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 133 | 62864388 | 5664 | 135.936 | 5.664 | 7 | 7 | 3B+1S | 1006 | 0 | 1127 | 1185 | 1128 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 129 | 62869969 | 5581 | 133.944 | 5.581 | 6.8 | 6.8 | 3B+1S | 1006 | 0 | 1097 | 1185 | 1095 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 130 | 62875372 | 5403 | 129.672 | 5.403 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 122 | 129 | 62881032 | 5660 | 135.84 | 5.66 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1087 | 1185 | 1015 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 122 | 125 | 62886064 | 5032 | 120.768 | 5.032 | 5.7 | 5.7 | 3B+1S | 1016 | 0 | 1087 | 1185 | 1087 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 127 | 62891473 | 5409 | 129.816 | 5.409 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1086 | 1185 | 1086 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 102 | 120 | 62896710 | 5237 | 125.688 | 5.237 | 4.7 | 4.7 | 2B+1S | 1057 | 0 | 1077 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% |  | 0% | 9859001 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 102 | 116 | 62901596 | 4886 | 117.264 | 4.886 | 4 | 4 | 2B+1S | 1057 | 0 | 1037 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% |  | 0% | 9859001 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 101 | 62905908 | 4312 | 103.488 | 4.312 | 4.8 | 4.8 | 2B | 0 | 0 | 986 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% |  | 35% | 9859793 | 792 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 99 | 62909804 | 3896 | 93.504 | 3.896 | 5.6 | 5.6 | 2B | 0 | 0 | 947 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% |  | 35% | 9860774 | 981 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121484 | 121.484 | 121.484 | [12 empty] | 0 | 0 | 0 | [6 empty] | 6354 | 6354 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (43%)
XCV1- CLOSED @ 2:58 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 15 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## DEC 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 62909804 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9860774 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 117 | 85 | 62913747 | 3943 | 94.632 | 3.943 | 6.7 | 6.7 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 35% | 9861771 | 997 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 89 | 62917498 | 3751 | 90.024 | 3.751 | 8 | 8 | 2B | 0 | 0 | 877 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 35% | 9862282 | 511 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 89 | 62921124 | 3626 | 87.024 | 3.626 | 8.9 | 8.9 | 2B | 0 | 0 | 877 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 35% | 9863895 | 1613 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 93 | 62925004 | 3880 | 93.12 | 3.88 | 9.5 | 9.5 | 2B | 0 | 0 | 877 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 35% | 9864370 | 475 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 101 | 62928994 | 3990 | 95.76 | 3.99 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 102 | 62933747 | 4753 | 114.072 | 4.753 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9864370 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 145 | 62938506 | 4759 | 114.216 | 4.759 | 9.5 | 9.5 | 3B | 0 | 965 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 62944851 | 6345 | 152.28 | 6.345 | 9.4 | 9.4 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 62951160 | 6309 | 151.416 | 6.309 | 8.9 | 8.9 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 62956993 | 5833 | 139.992 | 5.833 | 8.5 | 8.5 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 | 1.2
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 62963004 | 6011 | 144.264 | 6.011 | 8.1 | 8.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 139 | 62969535 | 6531 | 156.744 | 6.531 | 7.6 | 7.6 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 62976002 | 6467 | 155.208 | 6.467 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 112 | 62980909 | 4907 | 117.768 | 4.907 | 6.9 | 6.9 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 62986660 | 5751 | 138.024 | 5.751 | 6.5 | 6.5 | 3B+1S | 0 | 1026 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 62992710 | 6050 | 145.2 | 6.05 | 6.1 | 6.1 | 3B+1S | 0 | 1026 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 137 | 62998067 | 5357 | 128.568 | 5.357 | 5.8 | 5.8 | 3B+1S | 0 | 1026 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 121 | 136 | 63003329 | 5262 | 126.288 | 5.262 | 5.3 | 5.3 | 3B+1S | 0 | 1047 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 120 | 132 | 63008833 | 5504 | 132.096 | 5.504 | 4.7 | 4.7 | 3B+1S | 0 | 1046 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 126 | 63014755 | 5922 | 142.128 | 5.922 | 3.8 | 3.8 | 2B+1S | 0 | 1098 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 0% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 104 | 123 | 63019535 | 4780 | 114.72 | 4.78 | 3.1 | 3.1 | 2B+1S | 0 | 1098 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 0% | 0% | 9864370 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 103 | 115 | 63024824 | 5289 | 126.936 | 5.289 | 2.4 | 2.4 | 2B+1S | 0 | 1097 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 0% | 0% | 9864370 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 96 | 63029486 | 4662 | 111.888 | 4.662 | 3 | 3 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9865351 | 981 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 98 | 63033328 | 3842 | 92.208 | 3.842 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9866518 | 1167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123524 | 123.524 | 123.524 | [12 empty] | 0 | 0 | 0 | [6 empty] | 5744 | 5744 | 1.1783 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (35%)
XCV- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 15 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
GENSET 1 STARTED @5:25PM
GENSET 2 STOPPED @ 5:30PM
ALL PUMP STOP DUE TO GENSET 2 STOPPED
BP2 RESUME TO NORMAL OPERATION 5:32PM
BP3 RESUME TO NORMAL OPERATION @5:34PM
BP1 RESUME TO NORMAL OPERATION @5:36PM
SP2 RESUME TO NORMAL OPERATION @5:38PM
BP3 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP1 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
XCV1 -OPENED @ 10:01 PM (35%)

## DEC 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63033328 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9866518 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 90 | 63037103 | 3775 | 90.6 | 3.775 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9867784 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 63040946 | 3843 | 92.232 | 3.843 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9869185 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 82 | 63044517 | 3571 | 85.704 | 3.571 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 876 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9870581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 63048009 | 3492 | 83.808 | 3.492 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 109 | 63052334 | 4325 | 103.8 | 4.325 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 978 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 128 | 63056963 | 4629 | 111.096 | 4.629 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 63062537 | 5574 | 133.776 | 5.574 | 9.4 | 9.4 | 3B | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 148 | 63068973 | 6436 | 154.464 | 6.436 | 8.9 | 8.9 | 3B+1S | 1099 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 146 | 63075188 | 6215 | 149.16 | 6.215 | 8.1 | 8.1 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 143 | 63080945 | 5757 | 138.168 | 5.757 | 7.4 | 7.4 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 | 1.21
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 63087328 | 6383 | 153.192 | 6.383 | 6.7 | 6.7 | 3B+1S | 1098 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 63093474 | 6146 | 147.504 | 6.146 | 6 | 6 | 3B+1S | 1079 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 142 | 63099361 | 5887 | 141.288 | 5.887 | 5.3 | 5.3 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 63105163 | 5802 | 139.248 | 5.802 | 4.8 | 4.8 | 3B+1S | 1036 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 63111052 | 5889 | 141.336 | 5.889 | 4.6 | 4.6 | 3B+1S | 1014 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 63116863 | 5811 | 139.464 | 5.811 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 63122500 | 5637 | 135.288 | 5.637 | 4 | 4 | 3B+1S | 1036 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 63128203 | 5703 | 136.872 | 5.703 | 3.6 | 3.6 | 3B+1S | 1016 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 135 | 63133990 | 5787 | 138.888 | 5.787 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 121 | 131 | 63139377 | 5387 | 129.288 | 5.387 | 3.1 | 3.1 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 131 | 63144828 | 5451 | 130.824 | 5.451 | 2.8 | 2.8 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 126 | 63149757 | 4929 | 118.296 | 4.929 | 2.5 | 2.5 | 2B+1S | 1015 | 0 | 0 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9871331 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 107 | 63154367 | 4610 | 110.64 | 4.61 | 3.2 | 3.2 | 2B | 0 | 0 | 0 | 1185 | 1057 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9872223 | 892 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 100 | 63158691 | 4324 | 103.776 | 4.324 | 4.5 | 4.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9873389 | 1166 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125363 | 125.363 | 125.363 | [12 empty] | 0 | 0 | 0 | [6 empty] | 6871 | 2058 | 1.16 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 15 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63158691 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9873389 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 87 | 63162664 | 3973 | 95.352 | 3.973 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 927 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9874573 | 1184 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 86 | 63166369 | 3705 | 88.92 | 3.705 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9875810 | 1237 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 82 | 63170003 | 3634 | 87.216 | 3.634 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 877 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9877059 | 1249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 94 | 63173718 | 3715 | 89.16 | 3.715 | 9.4 | 9.4 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9878007 | 948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 101 | 63177943 | 4225 | 101.4 | 4.225 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 109 | 63182447 | 4504 | 108.096 | 4.504 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9878007 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 151 | 63188043 | 5596 | 134.304 | 5.596 | 9.4 | 9.4 | 3B | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 63194135 | 6092 | 146.208 | 6.092 | 8.8 | 8.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 63200219 | 6084 | 146.016 | 6.084 | 8.2 | 8.2 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 63206336 | 6117 | 146.808 | 6.117 | 7.4 | 7.4 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 | 1.16
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 63212462 | 6126 | 147.024 | 6.126 | 6.6 | 6.6 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 63218509 | 6047 | 145.128 | 6.047 | 5.9 | 5.9 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 63224469 | 5960 | 143.04 | 5.96 | 5.3 | 5.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 63230588 | 6119 | 146.856 | 6.119 | 4.9 | 4.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 63236375 | 5787 | 138.888 | 5.787 | 4.5 | 4.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 63242073 | 5698 | 136.752 | 5.698 | 4.1 | 4.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 63247947 | 5874 | 140.976 | 5.874 | 3.6 | 3.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 63253487 | 5540 | 132.96 | 5.54 | 3.4 | 3.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 102 | 63259203 | 5716 | 137.184 | 5.716 | 3.2 | 3.2 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 127 | 63265027 | 5824 | 139.776 | 5.824 | 3.1 | 3.1 | 3B+1S | 0 | 965 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 63269948 | 4921 | 118.104 | 4.921 | 2.8 | 2.8 | 2B+1S | 0 | 1036 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 0% | 100% | 0% | 9878007 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 117 | 63275168 | 5220 | 125.28 | 5.22 | 2.4 | 2.4 | 2B+1S | 0 | 1015 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 0% | 100% | 0% | 9878007 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 105 | 63279846 | 4678 | 112.272 | 4.678 | 3.3 | 3.3 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 40% | 9879356 | 1349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 98 | 63283868 | 4022 | 96.528 | 4.022 | 4.8 | 4.8 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 0% | 100% | 40% | 9880441 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125177 | 125.177 | 125.177 | [12 empty] | 0 | 0 | 0 | [6 empty] | 7052 | 7052 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 18 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)
BP2 - STARTED @ 10:00 PM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP3 - STOPPED @ 10:02 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP1 - STOPPED @ 10:01 PM DUE TO LOW WATER LEVEL
XCV1 -OPENED @ 10:01 PM (35%)

## DEC 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63283868 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9880441 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 113 | 63287831 | 3963 | 95.112 | 3.963 | 6 | 6 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 40% | 9881606 | 1165 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 93 | 63291702 | 3871 | 92.904 | 3.871 | 7.2 | 7.2 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 40% | 9882856 | 1250 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 91 | 63295449 | 3747 | 89.928 | 3.747 | 8.5 | 8.5 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 40% | 9884102 | 1246 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 94 | 63299166 | 3717 | 89.208 | 3.717 | 9.5 | 9.5 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 40% | 9885094 | 992 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 99 | 63303357 | 4191 | 100.584 | 4.191 | 9.5 | 9.5 | 2B | 0 | 0 | 867 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 110 | 63307747 | 4390 | 105.36 | 4.39 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9885094 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 134 | 63313120 | 5373 | 128.952 | 5.373 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1046 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 138 | 63318795 | 5675 | 136.2 | 5.675 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 161 | 63324725 | 5930 | 142.32 | 5.93 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 63330815 | 6090 | 146.16 | 6.09 | 9.3 | 9.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 | 1.16
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 63336863 | 6048 | 145.152 | 6.048 | 9 | 9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 142 | 63342974 | 6111 | 146.664 | 6.111 | 8.6 | 8.6 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 63348817 | 5843 | 140.232 | 5.843 | 8.3 | 8.3 | 3B+1S | 1010 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 63354547 | 5730 | 137.52 | 5.73 | 7.9 | 7.9 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 63360238 | 5691 | 136.584 | 5.691 | 7.6 | 7.6 | 3B+1S | 1005 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 124 | 136 | 63365813 | 5575 | 133.8 | 5.575 | 7.3 | 7.3 | 3B+1S | 1005 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 135 | 63371292 | 5479 | 131.496 | 5.479 | 6.9 | 6.9 | 3B+1S | 1005 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 | 132 | 63376937 | 5645 | 135.48 | 5.645 | 6.5 | 6.5 | 3B+1S | 1007 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 100 | 63382667 | 5730 | 137.52 | 5.73 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 122 | 63388248 | 5581 | 133.944 | 5.581 | 6.1 | 6.1 | 3B+1S | 965 | 0 | 1076 | 1185 | 1077 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 106 | 63393094 | 4846 | 116.304 | 4.846 | 5.8 | 5.8 | 2B+1S | 996 | 0 | 1169 | 0 | 1148 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 0% | 100% | 0% | 9885094 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 121 | 63397976 | 4882 | 117.168 | 4.882 | 5.5 | 5.5 | 2B+1S | 995 | 0 | 1158 | 0 | 1148 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 0% | 100% | 0% | 9885094 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 98 | 63402496 | 4520 | 108.48 | 4.52 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9885852 | 758 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 94 | 63407163 | 4667 | 112.008 | 4.667 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9886910 | 1058 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123295 | 123.295 | 123.295 | [13 empty] | 0 | 0 | [6 empty] | 6469 | 6469 | 1.1633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 9:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 19 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 8:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)
BP2 - STARTED @ 10:00 PM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP1 - STOPPED @ 10:02 PM DUE TO LOW WATER LEVEL

## DEC 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63407163 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9886910 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 94 | 63410628 | 3465 | 83.16 | 3.465 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 927 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9887987 | 1077 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 84 | 87 | 63414662 | 4034 | 96.816 | 4.034 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 796 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9889152 | 1165 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 91 | 63418075 | 3413 | 81.912 | 3.413 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 846 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 92 | 63421543 | 3468 | 83.232 | 3.468 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 846 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 99 | 63425874 | 4331 | 103.944 | 4.331 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 114 | 109 | 63430279 | 4405 | 105.72 | 4.405 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9889152 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 63435627 | 5348 | 128.352 | 5.348 | 9.5 | 9.5 | 3B+1S | 0 | 996 | 1148 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 63441175 | 5548 | 133.152 | 5.548 | 9.3 | 9.3 | 3B+1S | 0 | 996 | 1148 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 63447225 | 6050 | 145.2 | 6.05 | 8.7 | 8.7 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 63453478 | 6253 | 150.072 | 6.253 | 8 | 8 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 | 1.08
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 149 | 63459680 | 6202 | 148.848 | 6.202 | 7.2 | 7.2 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 63465866 | 6186 | 148.464 | 6.186 | 6.5 | 6.5 | 3B+1S | 0 | 1095 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 145 | 63471940 | 6074 | 145.776 | 6.074 | 5.7 | 5.7 | 3B+1S | 0 | 1095 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 146 | 63477996 | 6056 | 145.344 | 6.056 | 5 | 5 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 143 | 63483961 | 5965 | 143.16 | 5.965 | 4.4 | 4.4 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 63489777 | 5816 | 139.584 | 5.816 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 63495430 | 5653 | 135.672 | 5.653 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 63501065 | 5635 | 135.24 | 5.635 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 145 | 63506477 | 5412 | 129.888 | 5.412 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 123 | 63511789 | 5312 | 127.488 | 5.312 | 3.1 | 3.1 | 3B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 0% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 123 | 63516957 | 5168 | 124.032 | 5.168 | 2.5 | 2.5 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 0% | 100% | 100% | 0% | 9889152 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 135 | 63522053 | 5096 | 122.304 | 5.096 | 2.1 | 2.1 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 0% | 100% | 100% | 0% | 9889152 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 102 | 63526815 | 4762 | 114.288 | 4.762 | 2.9 | 2.9 | 2B | 0 | 0 | 0 | 1185 | 1037 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9890074 | 922 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 101 | 63531162 | 4347 | 104.328 | 4.347 | 4.1 | 4.1 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9891237 | 1163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123999 | 123.999 | 123.999 | [13 empty] | 0 | 0 | [6 empty] | 4327 | 4327 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 1:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 19 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:00 PM (35%)

## DEC 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63531162 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9891237 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 120 | 63535113 | 3951 | 94.824 | 3.951 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9892470 | 1233 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 90 | 63539018 | 3905 | 93.72 | 3.905 | 6.9 | 6.9 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9893820 | 1350 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 63542796 | 3778 | 90.672 | 3.778 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9895272 | 1452 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 93 | 63546586 | 3790 | 90.96 | 3.79 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 856 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 40% | 9896296 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 103 | 97 | 63550667 | 4081 | 97.944 | 4.081 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 856 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 122 | 63555496 | 4829 | 115.896 | 4.829 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1118 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 0% | 9896296 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 141 | 63561196 | 5700 | 136.8 | 5.7 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 150 | 63567177 | 5981 | 143.544 | 5.981 | 9.3 | 9.3 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 63573383 | 6206 | 148.944 | 6.206 | 8.4 | 8.4 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 63579603 | 6220 | 149.28 | 6.22 | 7.6 | 7.6 | 3B+1S | 1120 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 | 1.4
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 63585879 | 6276 | 150.624 | 6.276 | 6.7 | 6.7 | 3B+1S | 1117 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 63592148 | 6269 | 150.456 | 6.269 | 5.9 | 5.9 | 3B+1S | 1118 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 149 | 63598262 | 6114 | 146.736 | 6.114 | 5.1 | 5.1 | 3B+1S | 1117 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 147 | 63604458 | 6196 | 148.704 | 6.196 | 4.3 | 4.3 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 63610390 | 5932 | 142.368 | 5.932 | 3.6 | 3.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 63616259 | 5869 | 140.856 | 5.869 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 135 | 63621946 | 5687 | 136.488 | 5.687 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 141 | 63627657 | 5711 | 137.064 | 5.711 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 127 | 63633195 | 5538 | 132.912 | 5.538 | 3 | 3 | 3B+1S | 995 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 127 | 63638502 | 5307 | 127.368 | 5.307 | 2.8 | 2.8 | 2B+1S | 1016 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 124 | 63644041 | 5539 | 132.936 | 5.539 | 2.4 | 2.4 | 2B+1S | 1015 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9896296 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 121 | 63648755 | 4714 | 113.136 | 4.714 | 2.2 | 2.2 | 2B+1S | 1014 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 0% | 100% | 100% | 0% | 9896296 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 96 | 63653033 | 4278 | 102.672 | 4.278 | 2.9 | 2.9 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 30% | 9897087 | 791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 99 | 63657233 | 4200 | 100.8 | 4.2 | 3.8 | 3.8 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 30% | 9897997 | 910 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126071 | 126.071 | 126.071 | [13 empty] | 0 | 0 | [6 empty] | 6760 | 6760 | 1.2217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 21 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (30%)
BP1 - STARTED @ 11:01 PM DUE TO LOW WATER LEVEL

## DEC 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR/PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 0 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63657233 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9897997 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 63661107 | 3874 | 92.976 | 3.874 | 5.4 | 5.4 | 2B | 0 | 0 | 987 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9899366 | 1369 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 63665057 | 3950 | 94.8 | 3.95 | 7 | 7 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9900865 | 1499 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 83 | 63668906 | 3849 | 92.376 | 3.849 | 8.6 | 8.6 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9902396 | 1531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 98 | 63672822 | 3916 | 93.984 | 3.916 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9903225 | 829 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 97 | 63676858 | 4036 | 96.864 | 4.036 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 123 | 120 | 63681658 | 4800 | 115.2 | 4.8 | 9.5 | 9.5 | 2B | 0 | 0 | 1138 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9903225 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 63687418 | 5760 | 138.24 | 5.76 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 63693339 | 5921 | 142.104 | 5.921 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 63699494 | 6155 | 147.72 | 6.155 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 63705692 | 6198 | 148.752 | 6.198 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 | 1.36
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 63711979 | 6287 | 150.888 | 6.287 | 7.2 | 7.2 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 154 | 63718111 | 6132 | 147.168 | 6.132 | 6.5 | 6.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 147 | 63724207 | 6096 | 146.304 | 6.096 | 5.9 | 5.9 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 63730221 | 6014 | 144.336 | 6.014 | 5.3 | 5.3 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 146 | 63736222 | 6001 | 144.024 | 6.001 | 4.8 | 4.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 63742134 | 5912 | 141.888 | 5.912 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 134 | 63747872 | 5738 | 137.712 | 5.738 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 140 | 63753541 | 5669 | 136.056 | 5.669 | 3.9 | 3.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 63759210 | 5669 | 136.056 | 5.669 | 3.7 | 3.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 127 | 63764724 | 5514 | 132.336 | 5.514 | 3.2 | 3.2 | 2B+1S | 0 | 1078 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% |  | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 63769922 | 5198 | 124.752 | 5.198 | 2.6 | 2.6 | 2B+1S | 0 | 1078 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% |  | 0% | 9903225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 117 | 63775047 | 5125 | 123 | 5.125 | 2.1 | 2.1 | 2B+1S | 0 | 1078 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 100% | 100% | 100% |  | 0% | 9903225 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 102 | 63779413 | 4366 | 104.784 | 4.366 | 2.9 | 2.9 | 2B | 0 | 0 | 1057 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% |  | 40% | 9904166 | 941 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 152 | 63783526 | 4113 | 98.712 | 4.113 | 4.4 | 4.4 | 2B | 0 | 0 | 977 | 1185 |  | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% |  | 40% | 9905500 | 1334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126293 | 126.293 | 126.293 | [13 empty] | 0 | 0 | [6 empty] | 7503 | 7503 | 1.2067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 22 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## DEC 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 10368 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63783526 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42672764 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9905500 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 91 | 63787483 | 3957 | 94.968 | 3.957 | 5.7 | 5.7 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9906673 | 1173 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 63791260 | 3777 | 90.648 | 3.777 | 6.9 | 6.9 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9907913 | 1240 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 88 | 63795307 | 4047 | 97.128 | 4.047 | 8.5 | 8.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9909289 | 1376 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 91 | 63798728 | 3421 | 82.104 | 3.421 | 9.3 | 9.3 | 2B | 0 | 0 | 915 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9910208 | 919 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 95 | 63802740 | 4012 | 96.288 | 4.012 | 9.5 | 9.5 | 2B | 0 | 0 | 846 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 116 | 63807333 | 4593 | 110.232 | 4.593 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9910208 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 141 | 63812988 | 5655 | 135.72 | 5.655 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 63819012 | 6024 | 144.576 | 6.024 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 63825019 | 6007 | 144.168 | 6.007 | 8.9 | 8.9 | 3B+1S | 1008 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 149 | 63831214 | 6195 | 148.68 | 6.195 | 8.4 | 8.4 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 | 1.36
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 63837420 | 6206 | 148.944 | 6.206 | 7.6 | 7.6 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 63843808 | 6388 | 153.312 | 6.388 | 6.8 | 6.8 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 147 | 63850332 | 6524 | 156.576 | 6.524 | 6 | 6 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 63855460 | 5128 | 123.072 | 5.128 | 5.4 | 5.4 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42672764 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 142 | 149 | 63860687 | 5227 | 125.448 | 5.227 | 5 | 5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42673884 | 1120 | 214.272 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 63866012 | 5325 | 127.8 | 5.325 | 4.7 | 4.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42675004 | 1120 | 210.3286 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 63871245 | 5233 | 125.592 | 5.233 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42676108 | 1104 | 210.9689 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 129 | 63876436 | 5191 | 124.584 | 5.191 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 42677308 | 1200 | 231.1693 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 128 | 63881921 | 5485 | 131.64 | 5.485 | 4 | 4 | 3B+1S | 1015 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 42678563 | 1255 | 228.8058 | 100% | 0% | 100% | 100% | 100% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 131 | 63887550 | 5629 | 135.096 | 5.629 | 3.5 | 3.5 | 2B+1S | 1046 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 42679652 | 1089 | 193.4624 | 100% | 0% | 100% | 100% | 0% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 116 | 63893123 | 5573 | 133.752 | 5.573 | 2.9 | 2.9 | 2B+1S | 1046 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 42680816 | 1164 | 208.8642 | 100% | 0% | 100% | 100% | 0% | 0% | 9910208 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 120 | 63897645 | 4522 | 108.528 | 4.522 | 2.5 | 2.5 | 2B+1S | 1046 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 42681565 | 749 | 165.6347 | 100% | 0% | 100% | 100% | 0% | 0% | 9910208 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 105 | 63901706 | 4061 | 97.464 | 4.061 | 3.3 | 3.3 | 2B |  | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 42682396 | 831 | 204.6294 | 0% | 0% | 100% | 100% | 0% | 40% | 9911413 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 98 | 63905852 | 4146 | 99.504 | 4.146 | 4.6 | 4.6 | 2B |  | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 42683132 | 736 | 177.5205 | 0% | 0% | 100% | 100% | 0% | 40% | 9912525 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 122326 | 122.326 | 122.326 | [12 empty] | 10368 | 10368 | 84.7571 | [6 empty] | 7025 | 7025 | 1.225 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 23 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
GENSET OPERATION ALL BOOSTER STOP @ 2:42 PM
START READING IN MERALCO ( ATS ) @ 4:00 PM
MERALCO OPERATION ALL BOOSTER START
BP2 START @ 3:02 PM
BP1 START @ 3:04 PM
BP3 START @ 3:06 PM
SP1 START @ 3:08 PM
ALL BOOSTER RESUME TO NORMAL CONDITION @ 3:10 PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## DEC 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25568 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 63905852 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42683132 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9912525 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 93 | 63909888 | 4036 | 96.864 | 4.036 | 5.6 | 5.6 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 42683844 | 712 | 176.4123 | 0% | 0% | 100% | 100% | 0% | 0% | 9913586 | 1061 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 90 | 63913921 | 4033 | 96.792 | 4.033 | 7 | 7 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42684556 | 712 | 176.5435 | 0% | 0% | 100% | 100% | 0% | 0% | 9914774 | 1188 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 63917705 | 3784 | 90.816 | 3.784 | 8.2 | 8.2 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42685216 | 660 | 174.4186 | 0% | 0% | 100% | 100% | 0% | 0% | 9915952 | 1178 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 122 | 96 | 63921491 | 3786 | 90.864 | 3.786 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42685868 | 652 | 172.2134 | 0% | 0% | 100% | 100% | 0% | 0% | 9917114 | 1162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 120 | 102 | 63925721 | 4230 | 101.52 | 4.23 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42686528 | 660 | 156.0284 | 0% | 0% | 100% | 100% | 0% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 21 | 14.7887 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 111 | 63929956 | 4235 | 101.64 | 4.235 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 42687200 | 672 | 158.6777 | 0% | 0% | 100% | 100% | 0% | 0% | 9917114 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 121 | 135 | 63935461 | 5505 | 132.12 | 5.505 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1158 | N/A | N/A | N/A | N/A | 42688308 | 1108 | 201.2716 | 0% | 0% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 139 | 63941264 | 5803 | 139.272 | 5.803 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42689572 | 1264 | 217.8184 | 0% | 0% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 134 | 63947300 | 6036 | 144.864 | 6.036 | 9.2 | 9.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42690932 | 1360 | 225.3148 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 132 | 63953402 | 6102 | 146.448 | 6.102 | 8.6 | 8.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42692311 | 1379 | 225.9915 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 | 1.29
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 63959451 | 6049 | 145.176 | 6.049 | 8 | 8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42693676 | 1365 | 225.6571 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 150 | 63965573 | 6122 | 146.928 | 6.122 | 7.4 | 7.4 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42695056 | 1380 | 225.4165 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 63971515 | 5942 | 142.608 | 5.942 | 6.9 | 6.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42696412 | 1356 | 228.206 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 63977548 | 6033 | 144.792 | 6.033 | 6.4 | 6.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42697754 | 1342 | 222.4432 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 139 | 63983230 | 5682 | 136.368 | 5.682 | 6 | 6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42699076 | 1322 | 232.6646 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 63989144 | 5914 | 141.936 | 5.914 | 5.6 | 5.6 | 3B+1S | 0 | 1036 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42700440 | 1364 | 230.6392 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 135 | 63995242 | 6098 | 146.352 | 6.098 | 5.2 | 5.2 | 3B+1S | 0 | 1036 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42701828 | 1388 | 227.6156 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 133 | 64000451 | 5209 | 125.016 | 5.209 | 4.9 | 4.9 | 3B+1S | 0 | 1037 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 42703004 | 1176 | 225.7631 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 121 | 129 | 64005928 | 5477 | 131.448 | 5.477 | 4.5 | 4.5 | 3B+1S | 0 | 1036 | 1117 | 1185 | 1136 | N/A | N/A | N/A | N/A | 42704232 | 1228 | 224.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 108 | 126 | 64011272 | 5344 | 128.256 | 5.344 | 3.7 | 3.7 | 2B+1S | 0 | 1067 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42705316 | 1084 | 202.8443 | 0% | 100% | 0% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 16 | 11.2676 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 107 | 123 | 64016466 | 5194 | 124.656 | 5.194 | 3 | 3 | 2B+1S | 0 | 1108 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 42706292 | 976 | 187.9091 | 0% | 100% | 0% | 100% | 100% | 0% | 9917114 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 100 | 117 | 64021546 | 5080 | 121.92 | 5.08 | 2.2 | 2.2 | 2B+1S | 0 | 1108 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 42707228 | 936 | 184.252 | 0% | 100% | 0% | 100% | 100% | 0% | 9917114 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 105 | 64025730 | 4184 | 100.416 | 4.184 | 3.4 | 3.4 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42707964 | 736 | 175.9082 | 0% | 0% | 0% | 100% | 100% | 40% | 9918415 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 106 | 64029945 | 4215 | 101.16 | 4.215 | 4.9 | 4.9 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42708700 | 736 | 174.6145 | 0% | 0% | 0% | 100% | 100% | 40% | 9919725 | 1310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124093 | 124.093 | 124.093 | [12 empty] | 25568 | 25568 | 206.039 | [6 empty] | 7200 | 7200 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:03 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 24 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## DEC 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22024 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64029945 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42708700 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9919725 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 97 | 64034123 | 4178 | 100.272 | 4.178 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42709420 | 720 | 172.3313 | 0% | 0% | 0% | 100% | 100% | 40% | 9920904 | 1179 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 110 | 64038250 | 4127 | 99.048 | 4.127 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 42710140 | 720 | 174.4609 | 0% | 0% | 0% | 100% | 100% | 45% | 9922034 | 1130 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 93 | 64042165 | 3915 | 93.96 | 3.915 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 42710832 | 692 | 176.7561 | 0% | 0% | 0% | 100% | 100% | 45% | 9923339 | 1305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 96 | 64046052 | 3887 | 93.288 | 3.887 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 42711504 | 672 | 172.884 | 0% | 0% | 0% | 100% | 100% | 45% | 9924042 | 703 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 64050117 | 4065 | 97.56 | 4.065 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 42712192 | 688 | 169.2497 | 0% | 0% | 0% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 26 | 18.3099 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 105 | 105 | 64054436 | 4319 | 103.656 | 4.319 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 897 | N/A | N/A | N/A | N/A | 42712872 | 680 | 157.4439 | 0% | 0% | 0% | 100% | 100% | 0% | 9924042 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 126 | 126 | 64059255 | 4819 | 115.656 | 4.819 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42713740 | 868 | 180.1204 | 0% | 0% | 0% | 100% | 100% | 0% | 9924042 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 136 | 64064852 | 5597 | 134.328 | 5.597 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42714924 | 1184 | 211.5419 | 0% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 140 | 64070641 | 5789 | 138.936 | 5.789 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42716188 | 1264 | 218.3451 | 0% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 140 | 64076520 | 5879 | 141.096 | 5.879 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42717468 | 1280 | 217.7241 | 0% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 | 1.25
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 64082374 | 5854 | 140.496 | 5.854 | 8.9 | 8.9 | 3B+1S | 1037 | 0 | 1158 | 1185 | 1158 | N/A | N/A | N/A | N/A | 42718756 | 1288 | 220.0205 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 64088327 | 5953 | 142.872 | 5.953 | 8.5 | 8.5 | 3B+1S | 1026 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42720068 | 1312 | 220.3931 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 136 | 64094122 | 5795 | 139.08 | 5.795 | 8.1 | 8.1 | 3B+1S | 1048 | 0 | 1097 | 1185 | 1098 | N/A | N/A | N/A | N/A | 42721320 | 1252 | 216.0483 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 13 | 9.1549 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 136 | 64099786 | 5664 | 135.936 | 5.664 | 7.8 | 7.8 | 3B+1S | 1048 | 0 | 1097 | 1185 | 1098 | N/A | N/A | N/A | N/A | 42722563 | 1243 | 219.4562 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 16 | 11.2676 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 125 | 126 | 64105304 | 5518 | 132.432 | 5.518 | 7.3 | 7.3 | 3B+1S | 995 | 0 | 996 | 1185 | 1098 | N/A | N/A | N/A | N/A | 42723668 | 1105 | 200.2537 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 17 | 11.9718 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 120 | 126 | 64110629 | 5325 | 127.8 | 5.325 | 7 | 7 | 3B+1S | 1015 | 0 | 1027 | 1185 | 1027 | N/A | N/A | N/A | N/A | 42724764 | 1096 | 205.8216 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 15 | 10.5634 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 118 | 129 | 64115966 | 5337 | 128.088 | 5.337 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 42725844 | 1080 | 202.3609 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 13 | 9.1549 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 111 | 127 | 64121305 | 5339 | 128.136 | 5.339 | 6 | 6 | 3B+1S | 1047 | 0 | 1027 | 1185 | 1026 | N/A | N/A | N/A | N/A | 42726940 | 1096 | 205.2819 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 111 | 123 | 64126509 | 5204 | 124.896 | 5.204 | 5.4 | 5.4 | 3B+1S | 1047 | 0 | 1026 | 1185 | 1026 | N/A | N/A | N/A | N/A | 42728020 | 1080 | 207.5327 | 100% | 0% | 100% | 100% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 97 | 115 | 64131408 | 4899 | 117.576 | 4.899 | 4.6 | 4.6 | 2B+1S | 1118 | 0 | 1068 | 0 | 1067 | N/A | N/A | N/A | N/A | 42728900 | 880 | 179.6285 | 100% | 0% | 100% | 0% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 117 | 64136471 | 5063 | 121.512 | 5.063 | 3.9 | 3.9 | 2B+1S | 1016 | 0 | 1157 | 0 | 1158 | N/A | N/A | N/A | N/A | 42729852 | 952 | 188.0308 | 100% | 0% | 100% | 0% | 100% | 0% | 9924042 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 117 | 64141209 | 4738 | 113.712 | 4.738 | 3.6 | 3.6 | 2B+1S | 1006 | 0 | 1098 | 0 | 1097 | N/A | N/A | N/A | N/A | 42730724 | 872 | 184.0439 | 100% | 0% | 100% | 0% | 100% | 0% | 9924042 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 99 | 64145785 | 4576 | 109.824 | 4.576 | 5.3 | 5.3 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 38% | 9925336 | 1294 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 95 | 64149261 | 3476 | 83.424 | 3.476 | 6.6 | 6.6 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 38% | 9926716 | 1380 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 119316 | 119.316 | 119.316 | [12 empty] | 22024 | 22024 | 184.5855 | [6 empty] | 6991 | 6991 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 1:00 AM (45%)
XCV1- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 10:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 25 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
POWER INTERRUPTION @ 10:00 PM
ALL BOOSTER STOPPED @ 10 :00 PM
GENERATOR 2 STARTED @ 10:05 PM
BP1 - STARTED @ 10:07 PM
BP2 - STARTED @ 10:09 PM
XCV2 -OPENED @ 10:01 PM (38%)

## DEC 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 9768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64149261 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42730724 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9926716 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 89 | 64153243 | 3982 | 95.568 | 3.982 | 8.2 | 8.2 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 45% | 9928257 | 1541 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 96 | 64157050 | 3807 | 91.368 | 3.807 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 45% | 9929482 | 1225 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 93 | 64161062 | 4012 | 96.288 | 4.012 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 28 | 19.7183 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 101 | 64165268 | 4206 | 100.944 | 4.206 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 98 | 64169380 | 4112 | 98.688 | 4.112 | 9.5 | 9.5 | 2B | 0 | 0 | 847 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 24 | 16.9014 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 120 | 64173944 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 0% | 9929482 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 142 | 64179419 | 5475 | 131.4 | 5.475 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 143 | 64185349 | 5930 | 142.32 | 5.93 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 64191513 | 6164 | 147.936 | 6.164 | 9 | 9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 154 | 64197817 | 6304 | 151.296 | 6.304 | 8.3 | 8.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 | 1.24
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 153 | 64204053 | 6236 | 149.664 | 6.236 | 7.5 | 7.5 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 64210429 | 6376 | 153.024 | 6.376 | 6.7 | 6.7 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 153 | 64216609 | 6180 | 148.32 | 6.18 | 6 | 6 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 147 | 64222489 | 5880 | 141.12 | 5.88 | 5.3 | 5.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42730724 | 0 | 0 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 64227576 | 5087 | 122.088 | 5.087 | 4.8 | 4.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42731816 | 1092 | 214.6648 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 64233391 | 5815 | 139.56 | 5.815 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42733148 | 1332 | 229.0628 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 64239118 | 5727 | 137.448 | 5.727 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42734476 | 1328 | 231.8841 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 133 | 64244863 | 5745 | 137.88 | 5.745 | 4.2 | 4.2 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42735804 | 1328 | 231.1575 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 131 | 64250459 | 5596 | 134.304 | 5.596 | 4.2 | 4.2 | 3B+1S | 0 | 984 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42737116 | 1312 | 234.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 127 | 64255832 | 5373 | 128.952 | 5.373 | 3.6 | 3.6 | 2B+1S | 0 | 1047 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 42738192 | 1076 | 200.2606 | 0% | 100% | 100% | 0% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 122 | 64261285 | 5453 | 130.872 | 5.453 | 3.1 | 3.1 | 2B+1S | 0 | 1018 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42739260 | 1068 | 195.8555 | 0% | 100% | 100% | 0% | 100% | 0% | 9929482 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 123 | 64266556 | 5271 | 126.504 | 5.271 | 2.9 | 2.9 | 2B+1S | 0 | 1016 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 42740300 | 1040 | 197.306 | 0% | 100% | 100% | 0% | 100% | 0% | 9929482 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 120 | 102 | 64270805 | 4249 | 101.976 | 4.249 | 3.8 | 3.8 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 42740300 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 35% | 9930420 | 938 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 111 | 64274996 | 4191 | 100.584 | 4.191 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 42740492 | 192 | 45.8125 | 0% | 0% | 0% | 100% | 100% | 35% | 9931544 | 1124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125735 | 125.735 | 125.735 | [12 empty] | 9768 | 9768 | 77.6872 | [6 empty] | 4828 | 4828 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 1:53 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 26 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
ALL BOOSTER STOPED OPERATION @ 2:00 PM
MERALCO OPERATION STARTED @2:06PM
BP2- STARTED @ 2:07PM
BP3 - STARTED @ 2:08PM
BP1-STARTED @ 2:10PM
SP2 STARTED @ 2:11PM
GESET2 STOPPED OPERATION @ 2:11 PM
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)
ALL BOOSTER STOPED OPERATION @ 10:00 PM
GESET2 STARTED OPERATION @ 10:05 PM
BP2- STARTED @ 10:07PM
BP3 - STARTED @ 10:09PM
HIGH VOLTAGE @ 11:43PM
MERALCO ATS ENERGIZED @ 11:48PM
BP2- STARTED @ 11:50PM
BP3 - STARTED @ 11:52PM
GESET2 STOPPED OPERATION @ 11:53 PM

## DEC 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25320 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64274996 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42740492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9931544 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 97 | 64278733 | 3737 | 89.688 | 3.737 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 987 | N/A | N/A | N/A | N/A | 42741156 | 664 | 177.6826 | 0% | 0% | 0% | 100% | 100% | 45% | 9932751 | 1207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 96 | 64282873 | 4140 | 99.36 | 4.14 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 986 | N/A | N/A | N/A | N/A | 42741892 | 736 | 177.7778 | 0% | 0% | 0% | 100% | 100% | 45% | 9934204 | 1453 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 91 | 64287001 | 4128 | 99.072 | 4.128 | 9.3 | 9.3 | 2B | 0 | 0 | 0 | 1185 | 966 | N/A | N/A | N/A | N/A | 42742620 | 728 | 176.3566 | 0% | 0% | 0% | 100% | 100% | 45% | 9935597 | 1393 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 98 | 64290684 | 3683 | 88.392 | 3.683 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 887 | N/A | N/A | N/A | N/A | 42743236 | 616 | 167.255 | 0% | 0% | 0% | 100% | 100% | 45% | 9935864 | 267 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 22 | 15.493 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 98 | 64294864 | 4180 | 100.32 | 4.18 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 867 | N/A | N/A | N/A | N/A | 42743888 | 652 | 155.9809 | 0% | 0% | 0% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 116 | 64299307 | 4443 | 106.632 | 4.443 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 42744573 | 685 | 154.1751 | 0% | 0% | 0% | 100% | 100% | 0% | 9935864 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 138 | 64304556 | 5249 | 125.976 | 5.249 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42745596 | 1023 | 194.8943 | 0% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 142 | 64310444 | 5888 | 141.312 | 5.888 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42746852 | 1256 | 213.3152 | 0% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 64316517 | 6073 | 145.752 | 6.073 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42748212 | 1360 | 223.942 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 64322576 | 6059 | 145.416 | 6.059 | 8.9 | 8.9 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42749556 | 1344 | 221.8188 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 64328644 | 6068 | 145.632 | 6.068 | 8.5 | 8.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42750908 | 1352 | 222.8082 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 64334694 | 6050 | 145.2 | 6.05 | 8.1 | 8.1 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42752268 | 1360 | 224.7934 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 64340609 | 5915 | 141.96 | 5.915 | 7.8 | 7.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42753604 | 1336 | 225.8664 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 64346464 | 5855 | 140.52 | 5.855 | 7.4 | 7.4 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42754940 | 1336 | 228.181 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 64352282 | 5818 | 139.632 | 5.818 | 6.9 | 6.9 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42756264 | 1324 | 227.5696 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 64358101 | 5819 | 139.656 | 5.819 | 6.6 | 6.6 | 3B+1S | 1025 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42757588 | 1324 | 227.5305 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 64363771 | 5670 | 136.08 | 5.67 | 6.2 | 6.2 | 3B+1S | 1026 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42758880 | 1292 | 227.866 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 126 | 141 | 64369360 | 5589 | 134.136 | 5.589 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1127 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42760132 | 1252 | 224.0115 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 127 | 64374773 | 5413 | 129.912 | 5.413 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1117 | 1185 | 1127 | N/A | N/A | N/A | N/A | 42761340 | 1208 | 223.1665 | 100% | 0% | 100% | 100% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 124 | 64379910 | 5137 | 123.288 | 5.137 | 5 | 5 | 2B+1S | 1057 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 42762324 | 984 | 191.5515 | 100% | 0% | 100% | 0% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 109 | 121 | 64385035 | 5125 | 123 | 5.125 | 4.4 | 4.4 | 2B+1S | 1057 | 0 | 1138 | 0 | 1138 | N/A | N/A | N/A | N/A | 42763256 | 932 | 181.8537 | 100% | 0% | 100% | 0% | 100% | 0% | 9935864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 106 | 118 | 64390226 | 5191 | 124.584 | 5.191 | 3.7 | 3.7 | 2B+1S | 1017 | 0 | 1139 | 0 | 1138 | N/A | N/A | N/A | N/A | 42764256 | 1000 | 192.6411 | 100% | 0% | 100% | 0% | 100% | 0% | 9935864 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 100 | 64394873 | 4647 | 111.528 | 4.647 | 4.4 | 4.4 | 2B | 0 | 0 | 1098 | 0 | 1098 | N/A | N/A | N/A | N/A | 42765112 | 856 | 184.2049 | 0% | 0% | 100% | 0% | 100% | 35% | 9936711 | 847 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 97 | 64398946 | 4073 | 97.752 | 4.073 | 5.3 | 5.3 | 2B | 0 | 0 | 1048 | 0 | 1058 | N/A | N/A | N/A | N/A | 42765812 | 700 | 171.8635 | 0% | 0% | 100% | 0% | 100% | 35% | 9937573 | 862 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123950 | 123.95 | 123.95 | [12 empty] | 25320 | 25320 | 204.2759 | [6 empty] | 6029 | 6029 | 1.1667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 19 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## DEC 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64398946 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42765812 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9937573 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 92 | 64402522 | 3576 | 85.824 | 3.576 | 6.4 | 6.4 | 2B | 0 | 0 | 1047 | 0 | 1057 | N/A | N/A | N/A | N/A | 42766412 | 600 | 167.7852 | 0% | 0% | 100% | 0% | 100% | 45% | 9938505 | 932 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 90 | 64407121 | 4599 | 110.376 | 4.599 | 7.9 | 7.9 | 2B | 0 | 0 | 1038 | 0 | 1047 | N/A | N/A | N/A | N/A | 42767180 | 768 | 166.9928 | 0% | 0% | 100% | 0% | 100% | 45% | 9939950 | 1445 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 92 | 64410521 | 3400 | 81.6 | 3.4 | 9.3 | 9.3 | 2B | 0 | 0 | 1017 | 0 | 1027 | N/A | N/A | N/A | N/A | 42767724 | 544 | 160 | 0% | 0% | 100% | 0% | 100% | 45% | 9941317 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 95 | 64414573 | 4052 | 97.248 | 4.052 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 42768348 | 624 | 153.998 | 0% | 0% | 100% | 0% | 100% | 45% | 9941878 | 561 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 100 | 64418307 | 3734 | 89.616 | 3.734 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 0 | 998 | N/A | N/A | N/A | N/A | 42768880 | 532 | 142.4746 | 0% | 0% | 100% | 0% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 122 | 64422890 | 4583 | 109.992 | 4.583 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 0 | 1148 | N/A | N/A | N/A | N/A | 42769584 | 704 | 153.6112 | 0% | 0% | 100% | 0% | 100% | 0% | 9941878 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 140 | 64427617 | 4727 | 113.448 | 4.727 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42770332 | 748 | 158.2399 | 0% | 0% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 139 | 64433491 | 5874 | 140.976 | 5.874 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42771604 | 1272 | 216.5475 | 0% | 0% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 64439607 | 6116 | 146.784 | 6.116 | 9.4 | 9.4 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42772980 | 1376 | 224.9836 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 64445740 | 6133 | 147.192 | 6.133 | 8.8 | 8.8 | 3B+1S | 0 | 1049 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42774348 | 1368 | 223.0556 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 | 1.19
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 149 | 64451968 | 6228 | 149.472 | 6.228 | 8 | 8 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42775756 | 1408 | 226.0758 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 64458083 | 6115 | 146.76 | 6.115 | 7.2 | 7.2 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42777160 | 1404 | 229.5993 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 145 | 64464146 | 6063 | 145.512 | 6.063 | 6.5 | 6.5 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42778564 | 1404 | 231.5685 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 145 | 64470190 | 6044 | 145.056 | 6.044 | 5.7 | 5.7 | 3B+1S | 0 | 1098 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42779948 | 1384 | 228.9874 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 126 | 143 | 64475995 | 5805 | 139.32 | 5.805 | 5 | 5 | 3B+1S | 0 | 1097 | 1147 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42781256 | 1308 | 225.323 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 133 | 64481753 | 5758 | 138.192 | 5.758 | 4.4 | 4.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42782560 | 1304 | 226.4675 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 64487512 | 5759 | 138.216 | 5.759 | 3.9 | 3.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42783864 | 1304 | 226.4282 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 136 | 64493208 | 5696 | 136.704 | 5.696 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1147 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42785156 | 1292 | 226.8258 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 64498804 | 5596 | 134.304 | 5.596 | 3.4 | 3.4 | 3B+1S | 0 | 1005 | 1147 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42786440 | 1284 | 229.4496 | 0% | 100% | 100% | 100% | 100% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 64504128 | 5324 | 127.776 | 5.324 | 2.8 | 2.8 | 2B+1S | 0 | 1058 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42787508 | 1068 | 200.6011 | 0% | 100% | 100% | 100% | 0% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 127 | 64509355 | 5227 | 125.448 | 5.227 | 2.3 | 2.3 | 2B+1S | 0 | 1066 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42788556 | 1048 | 200.4974 | 0% | 100% | 100% | 100% | 0% | 0% | 9941878 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 118 | 64514281 | 4926 | 118.224 | 4.926 | 1.8 | 1.8 | 2B+1S | 0 | 1047 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42789540 | 984 | 199.7564 | 0% | 100% | 100% | 100% | 0% | 0% | 9941878 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 99 | 64518677 | 4396 | 105.504 | 4.396 | 2.9 | 2.9 | 2B | 0 | 0 | 1006 | 1185 | 0 | N/A | N/A | N/A | N/A | 42790316 | 776 | 176.5241 | 0% | 0% | 100% | 100% | 0% | 38% | 9943070 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 97 | 64522784 | 4107 | 98.568 | 4.107 | 4.3 | 4.3 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 42791044 | 728 | 177.2583 | 0% | 0% | 100% | 100% | 0% | 38% | 9944292 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123838 | 123.838 | 123.838 | [12 empty] | 25232 | 25232 | 203.7501 | [6 empty] | 6719 | 6719 | 1.1533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
ALL BOOSTER STOPED OPERATION @ 6:01 AM
GESET1 STARTED OPERATION @ 6:06 AM
BP2- STARTED @ 6:07AM
BP1- STARTED @ 6:07AM
BP3 - STARTED @ 6:09AM
MERALCO ATS ENERGIZED @ 6:12AM
BP2- STARTED @ 6:13AM
BP1- STARTED @ 6:14AM
BP3 - STARTED @ 6:16AM
GESET1 STOPPED OPERATION @ 6:17 AM
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 28 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (38%)

## DEC 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26168 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64522784 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42791044 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9944292 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 94 | 64526699 | 3915 | 93.96 | 3.915 | 6 | 6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42791734 | 690 | 176.2452 | 0% | 0% | 100% | 100% | 0% | 45% | 9945712 | 1420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 93 | 64530625 | 3926 | 94.224 | 3.926 | 7.4 | 7.4 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42792428 | 694 | 176.7702 | 0% | 0% | 100% | 100% | 0% | 45% | 9947137 | 1425 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 64534542 | 3917 | 94.008 | 3.917 | 8.8 | 8.8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42793128 | 700 | 178.7082 | 0% | 0% | 100% | 100% | 0% | 45% | 9948576 | 1439 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 103 | 98 | 64538632 | 4090 | 98.16 | 4.09 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42793818 | 690 | 168.7042 | 0% | 0% | 100% | 100% | 0% | 45% | 9949201 | 625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 99 | 64542728 | 4096 | 98.304 | 4.096 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 42794512 | 694 | 169.4336 | 0% | 0% | 100% | 100% | 0% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 121 | 117 | 64547360 | 4632 | 111.168 | 4.632 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 42795276 | 764 | 164.9396 | 0% | 0% | 100% | 100% | 0% | 0% | 9949201 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 140 | 64552987 | 5627 | 135.048 | 5.627 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42796444 | 1168 | 207.5706 | 0% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 139 | 64558753 | 5766 | 138.384 | 5.766 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42797700 | 1256 | 217.8287 | 0% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 64564841 | 6088 | 146.112 | 6.088 | 8.9 | 8.9 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42799076 | 1376 | 226.0184 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 64571020 | 6179 | 148.296 | 6.179 | 8.2 | 8.2 | 3B+1S | 1077 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42800472 | 1396 | 225.9265 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 64577192 | 6172 | 148.128 | 6.172 | 7.5 | 7.5 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42801864 | 1392 | 225.5347 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 64583367 | 6175 | 148.2 | 6.175 | 6.8 | 6.8 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42803252 | 1388 | 224.7773 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 142 | 64589401 | 6034 | 144.816 | 6.034 | 6.1 | 6.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42804636 | 1384 | 229.3669 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 64595324 | 5923 | 142.152 | 5.923 | 5.6 | 5.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42805988 | 1352 | 228.2627 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 64601105 | 5781 | 138.744 | 5.781 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42807308 | 1320 | 228.3342 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 64606873 | 5768 | 138.432 | 5.768 | 5 | 5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42808628 | 1320 | 228.8488 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 64612651 | 5778 | 138.672 | 5.778 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42809968 | 1340 | 231.9142 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 64618291 | 5640 | 135.36 | 5.64 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 1147 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42811240 | 1272 | 225.5319 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 64623914 | 5623 | 134.952 | 5.623 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 1147 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42812508 | 1268 | 225.5024 | 100% | 0% | 100% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 127 | 64629250 | 5336 | 128.064 | 5.336 | 3.5 | 3.5 | 2B+1S | 1058 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42813580 | 1072 | 200.8996 | 100% | 0% | 0% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 123 | 64634471 | 5221 | 125.304 | 5.221 | 3 | 3 | 2B+1S | 1057 | 0 | 0 | 1185 | 1139 | N/A | N/A | N/A | N/A | 42814580 | 1000 | 191.5342 | 100% | 0% | 0% | 100% | 100% | 0% | 9949201 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 112 | 64639979 | 5508 | 132.192 | 5.508 | 2.5 | 2.5 | 2B+1S | 1035 | 0 | 0 | 1185 | 1138 | N/A | N/A | N/A | N/A | 42815668 | 1088 | 197.5309 | 100% | 0% | 0% | 100% | 100% | 0% | 9949201 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 98 | 64644321 | 4342 | 104.208 | 4.342 | 3.2 | 3.2 | 2B | 0 | 0 | 0 | 1185 | 1016 | N/A | N/A | N/A | N/A | 42816472 | 804 | 185.1681 | 0% | 0% | 0% | 100% | 100% | 35% | 9950039 | 838 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 122 | 97 | 64648484 | 4163 | 99.912 | 4.163 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 42817212 | 740 | 177.7564 | 0% | 0% | 0% | 100% | 100% | 35% | 9951021 | 982 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125700 | 125.7 | 125.7 | [12 empty] | 26168 | 26168 | 208.1782 | [6 empty] | 6729 | 6729 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 29 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## DEC 30)
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26300 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64648484 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42817212 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9951021 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 96 | 64652713 | 4229 | 101.496 | 4.229 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 42817972 | 760 | 179.7115 | 0% | 0% | 0% | 100% | 100% | 40% | 9952245 | 1224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 93 | 64656374 | 3661 | 87.864 | 3.661 | 6.8 | 6.8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42818628 | 656 | 179.186 | 0% | 0% | 0% | 100% | 100% | 40% | 9953342 | 1097 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 93 | 64660465 | 4091 | 98.184 | 4.091 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 42819360 | 732 | 178.9294 | 0% | 0% | 0% | 100% | 100% | 40% | 9954648 | 1306 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 90 | 64664143 | 3678 | 88.272 | 3.678 | 9.2 | 9.2 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 42820012 | 652 | 177.2703 | 0% | 0% | 0% | 100% | 100% | 40% | 9955683 | 1035 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 98 | 64668242 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 897 | N/A | N/A | N/A | N/A | 42820700 | 688 | 167.8458 | 0% | 0% | 0% | 100% | 100% | 40% | 9955993 | 310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 115 | 114 | 64672737 | 4495 | 107.88 | 4.495 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42821412 | 712 | 158.3982 | 0% | 0% | 0% | 100% | 100% | 0% | 9955993 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 134 | 64678054 | 5317 | 127.608 | 5.317 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42822500 | 1088 | 204.6267 | 0% | 0% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 141 | 64683897 | 5843 | 140.232 | 5.843 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42823772 | 1272 | 217.6964 | 0% | 0% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 64690046 | 6149 | 147.576 | 6.149 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42825152 | 1380 | 224.4267 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 64696269 | 6223 | 149.352 | 6.223 | 8.4 | 8.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42826548 | 1396 | 224.3291 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 64702427 | 6158 | 147.792 | 6.158 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42827940 | 1392 | 226.0474 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 64708594 | 6167 | 148.008 | 6.167 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42829328 | 1388 | 225.0689 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 147 | 64714664 | 6070 | 145.68 | 6.07 | 6.6 | 6.6 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42830700 | 1372 | 226.0297 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 64720664 | 6000 | 144 | 6 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42832064 | 1364 | 227.3333 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 138 | 64726604 | 5940 | 142.56 | 5.94 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42833428 | 1364 | 229.6296 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 64732448 | 5844 | 140.256 | 5.844 | 5.2 | 5.2 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42834776 | 1348 | 230.6639 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 64738259 | 5811 | 139.464 | 5.811 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42836124 | 1348 | 231.9738 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 139 | 64743975 | 5716 | 137.184 | 5.716 | 4.4 | 4.4 | 3B+1S | 0 | 1067 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 42837388 | 1264 | 221.1337 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 130 | 64749643 | 5668 | 136.032 | 5.668 | 3.7 | 3.7 | 3B+1S | 0 | 1066 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 42838644 | 1256 | 221.5949 | 0% | 100% | 100% | 100% | 100% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 64754906 | 5263 | 126.312 | 5.263 | 3.1 | 3.1 | 2B+1S | 0 | 1068 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42839708 | 1064 | 202.1661 | 0% | 100% | 100% | 100% | 0% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 64760252 | 5346 | 128.304 | 5.346 | 2.4 | 2.4 | 2B+1S | 0 | 1099 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 42840772 | 1064 | 199.0273 | 0% | 100% | 100% | 100% | 0% | 0% | 9955993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 117 | 64766073 | 5821 | 139.704 | 5.821 | 1.7 | 1.7 | 2B+1S | 0 | 1026 | 1167 | 1185 | 0 | N/A | N/A | N/A | N/A | 42841948 | 1176 | 202.0271 | 0% | 100% | 100% | 100% | 0% | 0% | 9955993 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 101 | 64770133 | 4060 | 97.44 | 4.06 | 2.5 | 2.5 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 42842712 | 764 | 188.1773 | 0% | 0% | 100% | 100% | 0% | 35% | 9956910 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 88 | 64774536 | 4403 | 105.672 | 4.403 | 3.7 | 3.7 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 42843512 | 800 | 181.6943 | 0% | 0% | 100% | 100% | 0% | 35% | 9958072 | 1162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126052 | 126.052 | 126.052 | [12 empty] | 26300 | 26300 | 208.6441 | [6 empty] | 7051 | 7051 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 30 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:00 PM (35%)

## DEC 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2015-12-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26116 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64774536 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42843512 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9958072 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 92 | 64778713 | 4177 | 100.248 | 4.177 | 5.4 | 5.4 | 2B | 0 | 0 | 986 | 1185 | 0 | N/A | N/A | N/A | N/A | 42844268 | 756 | 180.9911 | 0% | 0% | 100% | 100% | 0% | 46% | 9959595 | 1523 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 95 | 64782492 | 3779 | 90.696 | 3.779 | 6.9 | 6.9 | 2B | 0 | 0 | 986 | 1185 | 0 | N/A | N/A | N/A | N/A | 42844956 | 688 | 182.0587 | 0% | 0% | 100% | 100% | 0% | 46% | 9961006 | 1411 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 92 | 64786326 | 3834 | 92.016 | 3.834 | 8.5 | 8.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42845644 | 688 | 179.4471 | 0% | 0% | 100% | 100% | 0% | 46% | 9962509 | 1503 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 98 | 64790304 | 3978 | 95.472 | 3.978 | 9.5 | 9.5 | 2B | 0 | 0 | 906 | 1185 | 0 | N/A | N/A | N/A | N/A | 42846348 | 704 | 176.9734 | 0% | 0% | 100% | 100% | 0% | 46% | 9963662 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 100 | 64794242 | 3938 | 94.512 | 3.938 | 9.5 | 9.5 | 2B | 0 | 0 | 876 | 1185 | 0 | N/A | N/A | N/A | N/A | 42846988 | 640 | 162.519 | 0% | 0% | 100% | 100% | 0% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 115 | 64798769 | 4527 | 108.648 | 4.527 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 42847716 | 728 | 160.8129 | 0% | 0% | 100% | 100% | 0% | 0% | 9963662 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 137 | 64804190 | 5421 | 130.104 | 5.421 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1097 | N/A | N/A | N/A | N/A | 42848788 | 1072 | 197.7495 | 0% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 141 | 64810081 | 5891 | 141.384 | 5.891 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42850072 | 1284 | 217.9596 | 0% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 64816191 | 6110 | 146.64 | 6.11 | 9.2 | 9.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42851444 | 1372 | 224.5499 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 64822399 | 6208 | 148.992 | 6.208 | 8.7 | 8.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42852844 | 1400 | 225.5155 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 | 1.2
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 64828588 | 6189 | 148.536 | 6.189 | 8.2 | 8.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42854236 | 1392 | 224.9152 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 64834652 | 6064 | 145.536 | 6.064 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42855546 | 1310 | 216.029 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 64840641 | 5989 | 143.736 | 5.989 | 7.4 | 7.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42856948 | 1402 | 234.0958 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 64846603 | 5962 | 143.088 | 5.962 | 7.1 | 7.1 | 3B+1S | 1007 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42858332 | 1384 | 232.1369 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 64852194 | 5591 | 134.184 | 5.591 | 6.8 | 6.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42859620 | 1288 | 230.3702 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 64858093 | 5899 | 141.576 | 5.899 | 6.6 | 6.6 | 3B+1S | 995 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42860988 | 1368 | 231.9037 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 64863733 | 5640 | 135.36 | 5.64 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42862300 | 1312 | 232.6241 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 64869652 | 5919 | 142.056 | 5.919 | 6 | 6 | 3B+1S | 996 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42863684 | 1384 | 233.8233 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 64875053 | 5401 | 129.624 | 5.401 | 5.7 | 5.7 | 3B+1S | 995 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42864924 | 1240 | 229.5871 | 100% | 0% | 100% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 64880765 | 5712 | 137.088 | 5.712 | 5.1 | 5.1 | 2B+1S | 1027 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42866060 | 1136 | 198.8796 | 100% | 0% | 0% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 122 | 64885846 | 5081 | 121.944 | 5.081 | 4.7 | 4.7 | 2B+1S | 1006 | 0 | 0 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42867052 | 992 | 195.2372 | 100% | 0% | 0% | 100% | 100% | 0% | 9963662 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 121 | 64890894 | 5048 | 121.152 | 5.048 | 4.5 | 4.5 | 2B+1S | 965 | 0 | 0 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42868032 | 980 | 194.1363 | 100% | 0% | 0% | 100% | 100% | 0% | 9963662 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 106 | 64895657 | 4763 | 114.312 | 4.763 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 42868892 | 860 | 180.5585 | 0% | 0% | 0% | 100% | 100% | 35% | 9964464 | 802 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 120 | 99 | 64899896 | 4239 | 101.736 | 4.239 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 988 | N/A | N/A | N/A | N/A | 42869628 | 736 | 173.6259 | 0% | 0% | 0% | 100% | 100% | 35% | 9965225 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125360 | 125.36 | 125.36 | [12 empty] | 26116 | 26116 | 208.328 | [6 empty] | 7153 | 7153 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (46%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:27 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (DEC 31 , 2015) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO LOW WATER LEVEL
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:00 PM (35%)