## JAN 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24036 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 64899896 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42869628 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9965225 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 106 | 64904326 | 4430 | 106.32 | 4.43 | 6.9 | 6.9 | 2B | 0 | 0 | 0 | 1185 | 1037 | N/A | N/A | N/A | N/A | 42870388 | 760 | 171.5576 | 0% | 0% | 0% | 100% | 100% | 0% | 9966014 | 789 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 100 | 64908776 | 4450 | 106.8 | 4.45 | 7.6 | 7.6 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42871172 | 784 | 176.1798 | 0% | 0% | 0% | 100% | 100% | 0% | 9966685 | 671 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 98 | 64912936 | 4160 | 99.84 | 4.16 | 8.5 | 8.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 42871908 | 736 | 176.9231 | 0% | 0% | 0% | 100% | 100% | 0% | 9967588 | 903 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 92 | 64916825 | 3889 | 93.336 | 3.889 | 9.4 | 9.4 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42872588 | 680 | 174.8521 | 0% | 0% | 0% | 100% | 100% | 0% | 9968483 | 895 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 98 | 97 | 64920664 | 3839 | 92.136 | 3.839 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 847 | N/A | N/A | N/A | N/A | 42873224 | 636 | 165.6681 | 0% | 0% | 0% | 100% | 100% | 0% | 9968610 | 127 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 26 | 18.3099 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 102 | 107 | 64924763 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 877 | N/A | N/A | N/A | N/A | 42873860 | 636 | 155.1598 | 0% | 0% | 0% | 100% | 100% | 0% | 9968610 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 19 | 13.3803 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 120 | 115 | 64929513 | 4750 | 114 | 4.75 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 42874700 | 840 | 176.8421 | 0% | 0% | 0% | 100% | 100% | 0% | 9968610 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 126 | 64934826 | 5313 | 127.512 | 5.313 | 9.5 | 9.5 | 3B | 0 | 0 | 986 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42875756 | 1056 | 198.7578 | 0% | 0% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 135 | 64940018 | 5192 | 124.608 | 5.192 | 9.5 | 9.5 | 3B | 0 | 0 | 1128 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42876860 | 1104 | 212.6348 | 0% | 0% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 64945985 | 5967 | 143.208 | 5.967 | 9.4 | 9.4 | 3B+1S | 0 | 1017 | 1167 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42878188 | 1328 | 222.5574 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 | 1.21
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 64951746 | 5761 | 138.264 | 5.761 | 9 | 9 | 3B+1S | 0 | 1038 | 1167 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42879460 | 1272 | 220.795 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 64957962 | 6216 | 149.184 | 6.216 | 8.6 | 8.6 | 3B+1S | 0 | 1037 | 1167 | 1185 | 1178 | N/A | N/A | N/A | N/A | 42880836 | 1376 | 221.3642 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 138 | 64963798 | 5836 | 140.064 | 5.836 | 8.2 | 8.2 | 3B+1S | 0 | 1006 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42882124 | 1288 | 220.6991 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 64969657 | 5859 | 140.616 | 5.859 | 7.9 | 7.9 | 3B+1S | 0 | 995 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 42883420 | 1296 | 221.1982 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 64975083 | 5426 | 130.224 | 5.426 | 7.8 | 7.8 | 3B+1S | 0 | 965 | 1137 | 1185 | 1136 | N/A | N/A | N/A | N/A | 42884628 | 1208 | 222.6318 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 64980625 | 5542 | 133.008 | 5.542 | 7.8 | 7.8 | 3B+1S | 0 | 985 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 42885844 | 1216 | 219.4154 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 64986298 | 5673 | 136.152 | 5.673 | 7.7 | 7.7 | 3B+1S | 0 | 984 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 42887100 | 1256 | 221.3996 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 131 | 64991746 | 5448 | 130.752 | 5.448 | 7.6 | 7.6 | 3B+1S | 0 | 964 | 1117 | 1185 | 1127 | N/A | N/A | N/A | N/A | 42888284 | 1184 | 217.3275 | 0% | 100% | 100% | 100% | 100% | 0% | 9968610 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 12 | 8.4507 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 118 | 126 | 64997094 | 5348 | 128.352 | 5.348 | 7.1 | 7.1 | 2B+1S | 0 | 1006 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 42889324 | 1040 | 194.4652 | 0% | 100% | 100% | 100% | 0% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 123 | 65002182 | 5088 | 122.112 | 5.088 | 6.7 | 6.7 | 2B+1S | 0 | 1006 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 42890300 | 976 | 191.8239 | 0% | 100% | 100% | 100% | 0% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 125 | 65007365 | 5183 | 124.392 | 5.183 | 6.4 | 6.4 | 2B+1S | 0 | 985 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 42891300 | 1000 | 192.9385 | 0% | 100% | 100% | 100% | 0% | 0% | 9968610 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 18 | 12.6761 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 116 | 65012401 | 5036 | 120.864 | 5.036 | 6.2 | 6.2 | 2B+1S | 0 | 986 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 42892252 | 952 | 189.0389 | 0% | 100% | 100% | 100% | 0% | 0% | 9968610 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 122 | 98 | 65016645 | 4244 | 101.856 | 4.244 | 6.9 | 6.9 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42892992 | 740 | 174.3638 | 0% | 0% | 100% | 100% | 0% | 30% | 9969361 | 751 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 119 | 92 | 65020630 | 3985 | 95.64 | 3.985 | 7.8 | 7.8 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 42893664 | 672 | 168.6324 | 0% | 0% | 100% | 100% | 0% | 30% | 9970277 | 916 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 120734 | 120.734 | 120.734 | [12 empty] | 24036 | 24036 | 199.0823 | [6 empty] | 5052 | 5052 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 7:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 9:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 1 , 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 6:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:00 PM (30%)

## JAN 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65020630 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42893664 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9970277 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 89 | 65024460 | 3830 | 91.92 | 3.83 | 9.1 | 9.1 | 2B | 0 | 0 | 875 | 1185 | 0 | N/A | N/A | N/A | N/A | 42894312 | 648 | 169.1906 | 0% | 0% | 100% | 100% | 0% | 0% | 9971513 | 1236 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 92 | 65028466 | 4006 | 96.144 | 4.006 | 9.5 | 9.5 | 2B | 0 | 0 | 877 | 1185 | 0 | N/A | N/A | N/A | N/A | 42894972 | 660 | 164.7529 | 0% | 0% | 100% | 100% | 0% | 0% | 9972008 | 495 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 87 | 65032209 | 3743 | 89.832 | 3.743 | 9.5 | 9.5 | 2B | 0 | 0 | 796 | 1185 | 0 | N/A | N/A | N/A | N/A | 42895572 | 600 | 160.2992 | 0% | 0% | 100% | 100% | 0% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 93 | 65036034 | 3825 | 91.8 | 3.825 | 9.5 | 9.5 | 2B | 0 | 0 | 796 | 1185 | 0 | N/A | N/A | N/A | N/A | 42896188 | 616 | 161.0458 | 0% | 0% | 100% | 100% | 0% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 27 | 19.0141 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 99 | 97 | 65040004 | 3970 | 95.28 | 3.97 | 9.5 | 9.5 | 2B | 0 | 0 | 796 | 1185 | 0 | N/A | N/A | N/A | N/A | 42896804 | 616 | 155.1637 | 0% | 0% | 100% | 100% | 0% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 23 | 16.1972 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 110 | 106 | 65044444 | 4440 | 106.56 | 4.44 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42897500 | 696 | 156.7568 | 0% | 0% | 100% | 100% | 0% | 0% | 9972008 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 137 | 65049596 | 5152 | 123.648 | 5.152 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1086 | N/A | N/A | N/A | N/A | 42898516 | 1016 | 197.205 | 0% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 142 | 65055583 | 5987 | 143.688 | 5.987 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42899776 | 1260 | 210.456 | 0% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 65061415 | 5832 | 139.968 | 5.832 | 9.3 | 9.3 | 3B+1S | 0 | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42901068 | 1292 | 221.5364 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 151 | 65067884 | 6469 | 155.256 | 6.469 | 8.4 | 8.4 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42902524 | 1456 | 225.0734 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 | 1.27
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 156 | 65074423 | 6539 | 156.936 | 6.539 | 7.4 | 7.4 | 3B+1S | 0 | 1150 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42904004 | 1480 | 226.3343 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 152 | 65080496 | 6073 | 145.752 | 6.073 | 6.5 | 6.5 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42905380 | 1376 | 226.5767 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 146 | 65086813 | 6317 | 151.608 | 6.317 | 5.7 | 5.7 | 3B+1S | 0 | 1097 | 1177 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42906824 | 1444 | 228.5895 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 142 | 65092803 | 5990 | 143.76 | 5.99 | 5 | 5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42908184 | 1360 | 227.0451 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 65098800 | 5997 | 143.928 | 5.997 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42909556 | 1372 | 228.7811 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 65104636 | 5836 | 140.064 | 5.836 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42910884 | 1328 | 227.5531 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 65110344 | 5708 | 136.992 | 5.708 | 4 | 4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42912208 | 1324 | 231.9552 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 65116094 | 5750 | 138 | 5.75 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42913532 | 1324 | 230.2609 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 137 | 65121755 | 5661 | 135.864 | 5.661 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 42914844 | 1312 | 231.7612 | 100% | 0% | 100% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 128 | 65127163 | 5408 | 129.792 | 5.408 | 3.2 | 3.2 | 2B+1S | 0 | 1047 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42915916 | 1072 | 198.2249 | 100% | 0% | 0% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 131 | 65132488 | 5325 | 127.8 | 5.325 | 2.7 | 2.7 | 2B+1S | 0 | 1046 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42916956 | 1040 | 195.3052 | 100% | 0% | 0% | 100% | 100% | 0% | 9972008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 120 | 65137659 | 5171 | 124.104 | 5.171 | 2.3 | 2.3 | 2B+1S | 0 | 1045 | 0 | 1185 | 1108 | N/A | N/A | N/A | N/A | 42917956 | 1000 | 193.3862 | 100% | 0% | 0% | 100% | 100% | 0% | 9972008 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 106 | 65142126 | 4467 | 107.208 | 4.467 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 42918764 | 808 | 180.882 | 0% | 0% | 0% | 100% | 100% | 40% | 9972991 | 983 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 98 | 65146435 | 4309 | 103.416 | 4.309 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1006 | N/A | N/A | N/A | N/A | 42919524 | 760 | 176.375 | 0% | 0% | 0% | 100% | 100% | 40% | 9974144 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125805 | 125.805 | 125.805 | [12 empty] | 25860 | 25860 | 205.5562 | [6 empty] | 3867 | 3867 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (35%)
XCV1- CLOSED @ 1:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 2 , 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26244 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65146435 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42919524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9974144 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 98 | 65150590 | 4155 | 99.72 | 4.155 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 42920260 | 736 | 177.136 | 0% | 0% | 0% | 100% | 100% | 0% | 9975503 | 1359 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 93 | 65154466 | 3876 | 93.024 | 3.876 | 7.1 | 7.1 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42920948 | 688 | 177.5026 | 0% | 0% | 0% | 100% | 100% | 0% | 9976751 | 1248 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 65158374 | 3908 | 93.792 | 3.908 | 8.5 | 8.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 42921632 | 684 | 175.0256 | 0% | 0% | 0% | 100% | 100% | 0% | 9978043 | 1292 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 90 | 65162145 | 3771 | 90.504 | 3.771 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 42922300 | 668 | 177.1413 | 0% | 0% | 0% | 100% | 100% | 0% | 9979111 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 103 | 65166231 | 4086 | 98.064 | 4.086 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 846 | N/A | N/A | N/A | N/A | 42922980 | 680 | 166.4219 | 0% | 0% | 0% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 23 | 16.1972 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 113 | 1056 | 65170658 | 4427 | 106.248 | 4.427 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 42923636 | 656 | 148.1816 | 0% | 0% | 0% | 100% | 100% | 0% | 9979111 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 136 | 65175992 | 5334 | 128.016 | 5.334 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42924716 | 1080 | 202.4747 | 0% | 0% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 146 | 65181733 | 5741 | 137.784 | 5.741 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42925920 | 1204 | 209.7196 | 0% | 0% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 154 | 65187996 | 6263 | 150.312 | 6.263 | 9.4 | 9.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42927308 | 1388 | 221.619 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 149 | 65194337 | 6341 | 152.184 | 6.341 | 8.6 | 8.6 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42928724 | 1416 | 223.3086 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 | 0.96
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 154 | 65200795 | 6458 | 154.992 | 6.458 | 7.7 | 7.7 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42930196 | 1472 | 227.9343 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 152 | 65206783 | 5988 | 143.712 | 5.988 | 6.8 | 6.8 | 3B+1S | 0 | 1147 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42931556 | 1360 | 227.1209 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 65212865 | 6082 | 145.968 | 6.082 | 6 | 6 | 3B+1S | 0 | 1098 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42932892 | 1336 | 219.6646 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 147 | 65218867 | 6002 | 144.048 | 6.002 | 5.3 | 5.3 | 3B+1S | 0 | 1097 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 42934252 | 1360 | 226.5911 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 65224805 | 5938 | 142.512 | 5.938 | 4.8 | 4.8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42935612 | 1360 | 229.0333 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 65230528 | 5723 | 137.352 | 5.723 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1158 | 1187 | N/A | N/A | N/A | N/A | 42936944 | 1332 | 232.7451 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 65236243 | 5715 | 137.16 | 5.715 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42938264 | 1320 | 230.9711 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 65241978 | 5735 | 137.64 | 5.735 | 4 | 4 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42939592 | 1328 | 231.5606 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 137 | 65247602 | 5624 | 134.976 | 5.624 | 4 | 4 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42940908 | 1316 | 233.9972 | 0% | 100% | 100% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 65253083 | 5481 | 131.544 | 5.481 | 3.4 | 3.4 | 2B+1S | 0 | 1077 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42942032 | 1124 | 205.0721 | 0% | 100% | 0% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 128 | 65258618 | 5535 | 132.84 | 5.535 | 2.8 | 2.8 | 2B+1S | 0 | 1077 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42943116 | 1084 | 195.8446 | 0% | 100% | 0% | 100% | 100% | 0% | 9979111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 121 | 65263696 | 5078 | 121.872 | 5.078 | 2.4 | 2.4 | 2B+1S | 0 | 1045 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42944132 | 1016 | 200.0788 | 0% | 100% | 0% | 100% | 100% | 0% | 9979111 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 108 | 65268282 | 4586 | 110.064 | 4.586 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1147 | N/A | N/A | N/A | N/A | 42945020 | 888 | 193.6328 | 0% | 0% | 0% | 100% | 100% | 40% | 9980149 | 1038 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 95 | 65272446 | 4164 | 99.936 | 4.164 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 987 | N/A | N/A | N/A | N/A | 42945768 | 748 | 179.635 | 0% | 0% | 0% | 100% | 100% | 40% | 9981491 | 1342 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126011 | 126.011 | 126.011 | [12 empty] | 26244 | 26244 | 208.2675 | [6 empty] | 7347 | 7347 | 1.115 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 2 , 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26748 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65272446 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42945768 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9981491 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 94 | 65276369 | 3923 | 94.152 | 3.923 | 6.5 | 6.5 | 2B | 0 | 0 | 0 | 1185 | 966 | N/A | N/A | N/A | N/A | 42946464 | 696 | 177.4152 | 0% | 0% | 0% | 100% | 100% | 45% | 9983037 | 1546 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 93 | 65280293 | 3924 | 94.176 | 3.924 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 42947160 | 696 | 177.37 | 0% | 0% | 0% | 100% | 100% | 45% | 9984584 | 1547 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 100 | 95 | 65284136 | 3843 | 92.232 | 3.843 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42947828 | 668 | 173.8225 | 0% | 0% | 0% | 100% | 100% | 45% | 9985995 | 1411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 98 | 65288255 | 4119 | 98.856 | 4.119 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42948508 | 680 | 165.0886 | 0% | 0% | 0% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 100 | 65292517 | 4262 | 102.288 | 4.262 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42949176 | 668 | 156.7339 | 0% | 0% | 0% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 113 | 111 | 65296885 | 4368 | 104.832 | 4.368 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 42949886 | 710 | 162.5458 | 0% | 0% | 0% | 100% | 100% | 0% | 9985995 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 152 | 65303246 | 6361 | 152.664 | 6.361 | 9.3 | 9.3 | 3B | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42951248 | 1362 | 214.1173 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 65309155 | 5909 | 141.816 | 5.909 | 8.7 | 8.7 | 3B | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42952604 | 1356 | 229.4805 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 65315526 | 6371 | 152.904 | 6.371 | 8 | 8 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42954004 | 1400 | 219.7457 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 65321665 | 6139 | 147.336 | 6.139 | 7.3 | 7.3 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42955376 | 1372 | 223.4892 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 | 1.41
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 65327728 | 6063 | 145.512 | 6.063 | 6.7 | 6.7 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42956732 | 1356 | 223.6517 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 65333912 | 6184 | 148.416 | 6.184 | 6.1 | 6.1 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42958108 | 1376 | 222.5097 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 147 | 65340024 | 6112 | 146.688 | 6.112 | 5.6 | 5.6 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42959494 | 1386 | 226.767 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 65346090 | 6066 | 145.584 | 6.066 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42960860 | 1366 | 225.1896 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 146 | 65352007 | 5917 | 142.008 | 5.917 | 4.7 | 4.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42962212 | 1352 | 228.4942 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 65357846 | 5839 | 140.136 | 5.839 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42963552 | 1340 | 229.4914 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 65363596 | 5750 | 138 | 5.75 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42964884 | 1332 | 231.6522 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 65369293 | 5697 | 136.728 | 5.697 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42966204 | 1320 | 231.7009 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 131 | 65374953 | 5660 | 135.84 | 5.66 | 3.7 | 3.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 42967532 | 1328 | 234.629 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 | 131 | 65380539 | 5586 | 134.064 | 5.586 | 3.5 | 3.5 | 3B+1S | 1005 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 42968820 | 1288 | 230.5764 | 100% | 0% | 100% | 100% | 100% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 65385928 | 5389 | 129.336 | 5.389 | 2.9 | 2.9 | 2B+1S | 1077 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42969900 | 1080 | 200.4082 | 100% | 0% | 100% | 100% | 0% | 0% | 9985995 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 121 | 65391207 | 5279 | 126.696 | 5.279 | 2.3 | 2.3 | 2B+1S | 1077 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42970960 | 1060 | 200.7956 | 100% | 0% | 100% | 100% | 0% | 0% | 9985995 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 102 | 65395571 | 4364 | 104.736 | 4.364 | 3.2 | 3.2 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 42971748 | 788 | 180.5683 | 0% | 0% | 100% | 100% | 0% | 38% | 9986945 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 99 | 65399800 | 4229 | 101.496 | 4.229 | 4.4 | 4.4 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 42972516 | 768 | 181.6032 | 0% | 0% | 100% | 100% | 0% | 38% | 9988152 | 1207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127354 | 127.354 | 127.354 | [12 empty] | 26748 | 26748 | 210.0287 | [6 empty] | 6661 | 6661 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 4 , 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (38%)

## JAN 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27152 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65399800 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42972516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9988152 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 93 | 65403670 | 3870 | 92.88 | 3.87 | 6 | 6 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 42973196 | 680 | 175.7106 | 0% | 0% | 100% | 100% | 0% | 0% | 9989552 | 1400 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 65407546 | 3876 | 93.024 | 3.876 | 7.5 | 7.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 42973885 | 689 | 177.7606 | 0% | 0% | 100% | 100% | 0% | 0% | 9990960 | 1408 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 94 | 65411430 | 3884 | 93.216 | 3.884 | 8.9 | 8.9 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 42974584 | 699 | 179.9691 | 0% | 0% | 100% | 100% | 0% | 0% | 9992370 | 1410 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 103 | 65415690 | 4260 | 102.24 | 4.26 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 42975284 | 700 | 164.3192 | 0% | 0% | 100% | 100% | 0% | 0% | 9992851 | 481 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 23 | 16.1972 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 111 | 65419957 | 4267 | 102.408 | 4.267 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 42976000 | 716 | 167.7994 | 0% | 0% | 100% | 100% | 0% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 126 | 65424985 | 5028 | 120.672 | 5.028 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42976900 | 900 | 178.9976 | 0% | 0% | 100% | 100% | 0% | 0% | 9992851 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 144 | 65431293 | 6308 | 151.392 | 6.308 | 9.4 | 9.4 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42978260 | 1360 | 215.5992 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 154 | 65437246 | 5953 | 142.872 | 5.953 | 9 | 9 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42979580 | 1320 | 221.7369 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 150 | 65443394 | 6148 | 147.552 | 6.148 | 8.1 | 8.1 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42980988 | 1408 | 229.0176 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 146 | 65450230 | 6836 | 164.064 | 6.836 | 7.1 | 7.1 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42982395 | 1407 | 205.8221 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 147 | 65455886 | 5656 | 135.744 | 5.656 | 6.2 | 6.2 | 3B+1S | 0 | 1148 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42983810 | 1415 | 250.1768 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 151 | 65462381 | 6495 | 155.88 | 6.495 | 5.4 | 5.4 | 3B+1S | 0 | 1149 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42985340 | 1530 | 235.5658 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 65468364 | 5983 | 143.592 | 5.983 | 4.6 | 4.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42986724 | 1384 | 231.3221 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 142 | 65474302 | 5938 | 142.512 | 5.938 | 4.2 | 4.2 | 3B+1S | 0 | 1020 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42988100 | 1376 | 231.7279 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 140 | 65480096 | 5794 | 139.056 | 5.794 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42989436 | 1336 | 230.5834 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 65485903 | 5807 | 139.368 | 5.807 | 3.8 | 3.8 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42990784 | 1348 | 232.1336 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 65491613 | 5710 | 137.04 | 5.71 | 3.6 | 3.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 42992108 | 1324 | 231.8739 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 137 | 65497412 | 5799 | 139.176 | 5.799 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42993440 | 1332 | 229.6948 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 65503185 | 5773 | 138.552 | 5.773 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 42994776 | 1336 | 231.4221 | 0% | 100% | 100% | 100% | 100% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 128 | 65508706 | 5521 | 132.504 | 5.521 | 2.7 | 2.7 | 2B+1S | 0 | 1066 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42995908 | 1132 | 205.0353 | 0% | 100% | 100% | 100% | 0% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 65513988 | 5282 | 126.768 | 5.282 | 2 | 2 | 2B+1S | 0 | 1067 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 42996956 | 1048 | 198.4097 | 0% | 100% | 100% | 100% | 0% | 0% | 9992851 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 119 | 65519187 | 5199 | 124.776 | 5.199 | 1.6 | 1.6 | 2B+1S | 0 | 1046 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 42997988 | 1032 | 198.4997 | 0% | 100% | 100% | 100% | 0% | 0% | 9992851 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 105 | 65523735 | 4548 | 109.152 | 4.548 | 2.5 | 2.5 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 42998852 | 864 | 189.9736 | 0% | 0% | 100% | 100% | 0% | 35% | 9993812 | 961 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 102 | 65528136 | 4401 | 105.624 | 4.401 | 3.7 | 3.7 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 42999668 | 816 | 185.4124 | 0% | 0% | 100% | 100% | 0% | 35% | 9995003 | 1191 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128336 | 128.336 | 128.336 | [12 empty] | 27152 | 27152 | 211.5696 | [6 empty] | 6851 | 6851 | 1.1633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:38 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 5 , 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## JAN 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65528136 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 42999668 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 9995003 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 96 | 65532181 | 4045 | 97.08 | 4.045 | 5.4 | 5.4 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 43000420 | 752 | 185.9085 | 0% | 0% | 100% | 100% | 0% | 0% | 9996290 | 1287 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 65536126 | 3945 | 94.68 | 3.945 | 6.7 | 6.7 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43001132 | 712 | 180.4816 | 0% | 0% | 100% | 100% | 0% | 0% | 9997696 | 1406 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 88 | 65539839 | 3713 | 89.112 | 3.713 | 8.1 | 8.1 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43001792 | 660 | 177.7538 | 0% | 0% | 100% | 100% | 0% | 0% | 9999059 | 1363 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 92 | 65543603 | 3764 | 90.336 | 3.764 | 9.3 | 9.3 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43002452 | 660 | 175.3454 | 0% | 0% | 100% | 100% | 0% | 0% | 10000239 | 1180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 106 | 65547707 | 4104 | 98.496 | 4.104 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43003128 | 676 | 164.7173 | 0% | 0% | 100% | 100% | 0% | 0% | 10000746 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 65553342 | 5635 | 135.24 | 5.635 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43004132 | 1004 | 178.1721 | 0% | 0% | 100% | 100% | 0% | 0% | 10000746 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 148 | 65558712 | 5370 | 128.88 | 5.37 | 9.5 | 9.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43005300 | 1168 | 217.5047 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 65564706 | 5994 | 143.856 | 5.994 | 9.2 | 9.2 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43006652 | 1352 | 225.5589 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 151 | 65571133 | 6427 | 154.248 | 6.427 | 8.3 | 8.3 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43008112 | 1460 | 227.1666 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 148 | 65577243 | 6110 | 146.64 | 6.11 | 7.6 | 7.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43009484 | 1372 | 224.5499 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 | 1.06
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 65583584 | 6341 | 152.184 | 6.341 | 6.9 | 6.9 | 3B+1S | 1078 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43010924 | 1440 | 227.0935 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 139 | 65589527 | 5943 | 142.632 | 5.943 | 6.4 | 6.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43012268 | 1344 | 226.1484 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 138 | 65595256 | 5729 | 137.496 | 5.729 | 6 | 6 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43013588 | 1320 | 230.4067 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 65601105 | 5849 | 140.376 | 5.849 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43014932 | 1344 | 229.7829 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 140 | 65606886 | 5781 | 138.744 | 5.781 | 5.6 | 5.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43016276 | 1344 | 232.4857 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 151 | 65612650 | 5764 | 138.336 | 5.764 | 5.4 | 5.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43017608 | 1332 | 231.0895 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 65618437 | 5787 | 138.888 | 5.787 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43018952 | 1344 | 232.2447 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 65624102 | 5665 | 135.96 | 5.665 | 5 | 5 | 3B+1S | 1006 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43020256 | 1304 | 230.1853 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 65629713 | 5611 | 134.664 | 5.611 | 4.8 | 4.8 | 3B+1S | 1007 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 43021528 | 1272 | 226.6976 | 100% | 0% | 100% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 133 | 65635179 | 5466 | 131.184 | 5.466 | 4.1 | 4.1 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43022628 | 1100 | 201.2441 | 100% | 0% | 0% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 65640598 | 5419 | 130.056 | 5.419 | 3.3 | 3.3 | 2B+1S | 1047 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43023708 | 1080 | 199.2988 | 100% | 0% | 0% | 100% | 100% | 0% | 10000746 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 120 | 65645770 | 5172 | 124.128 | 5.172 | 2.7 | 2.7 | 2B+1S | 1098 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 43024732 | 1024 | 197.9892 | 100% | 0% | 0% | 100% | 100% | 0% | 10000746 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 106 | 65650156 | 4386 | 105.264 | 4.386 | 3.4 | 3.4 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43025532 | 800 | 182.3985 | 0% | 0% | 0% | 100% | 100% | 40% | 10001637 | 891 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 99 | 65654384 | 4228 | 101.472 | 4.228 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43026308 | 776 | 183.5383 | 0% | 0% | 0% | 100% | 100% | 40% | 10002782 | 1145 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126248 | 126.248 | 126.248 | [12 empty] | 26640 | 26640 | 211.0132 | [6 empty] | 7779 | 7779 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:48 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26360 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65654384 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43026308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10002782 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 93 | 65658354 | 3970 | 95.28 | 3.97 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 43027028 | 720 | 181.3602 | 0% | 0% | 0% | 100% | 100% | 0% | 10004101 | 1319 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 92 | 65662230 | 3876 | 93.024 | 3.876 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43027728 | 700 | 180.5986 | 0% | 0% | 0% | 100% | 100% | 0% | 10005441 | 1340 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 107 | 65666022 | 3792 | 91.008 | 3.792 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 43028404 | 676 | 178.27 | 0% | 0% | 0% | 100% | 100% | 0% | 10006727 | 1286 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 94 | 65669910 | 3888 | 93.312 | 3.888 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 43029088 | 684 | 175.9259 | 0% | 0% | 0% | 100% | 100% | 0% | 10007337 | 610 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 102 | 65674153 | 4243 | 101.832 | 4.243 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43029776 | 688 | 162.1494 | 0% | 0% | 0% | 100% | 100% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 65678891 | 4738 | 113.712 | 4.738 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43030564 | 788 | 166.3149 | 0% | 0% | 0% | 100% | 100% | 0% | 10007337 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 65684813 | 5922 | 142.128 | 5.922 | 9.3 | 9.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43031884 | 1320 | 222.8977 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 65690912 | 6099 | 146.376 | 6.099 | 8.8 | 8.8 | 3B+1S | 0 | 1040 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43033268 | 1384 | 226.9224 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 146 | 65697075 | 6163 | 147.912 | 6.163 | 8.1 | 8.1 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43034664 | 1396 | 226.5131 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 65703365 | 6290 | 150.96 | 6.29 | 7.4 | 7.4 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43036084 | 1420 | 225.7552 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 | 1.08
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 65709412 | 6047 | 145.128 | 6.047 | 6.7 | 6.7 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43037452 | 1368 | 226.2279 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 65715455 | 6043 | 145.032 | 6.043 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43038812 | 1360 | 225.0538 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 136 | 65721574 | 6119 | 146.856 | 6.119 | 5.9 | 5.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43040192 | 1380 | 225.527 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 138 | 65727351 | 5777 | 138.648 | 5.777 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43041516 | 1324 | 229.1847 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 65733127 | 5776 | 138.624 | 5.776 | 5.4 | 5.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43042852 | 1336 | 231.3019 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 65738780 | 5653 | 135.672 | 5.653 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43044124 | 1272 | 225.0133 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 65744505 | 5725 | 137.4 | 5.725 | 5 | 5 | 3B+1S | 0 | 1014 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43045416 | 1292 | 225.6769 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 141 | 65750178 | 5673 | 136.152 | 5.673 | 4.8 | 4.8 | 3B+1S | 0 | 1006 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 43046668 | 1252 | 220.6945 | 0% | 100% | 100% | 100% | 100% | 0% | 10007337 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 65755748 | 5570 | 133.68 | 5.57 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 43047908 | 1240 | 222.6212 | 0% | 100% | 100% | 100% | 0% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 138 | 65761234 | 5486 | 131.664 | 5.486 | 3.6 | 3.6 | 2B+1S | 0 | 1099 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43049004 | 1096 | 199.7813 | 0% | 100% | 100% | 100% | 0% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 127 | 65766673 | 5439 | 130.536 | 5.439 | 2.9 | 2.9 | 2B+1S | 0 | 1097 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43050100 | 1096 | 201.5076 | 0% | 100% | 100% | 100% | 0% | 0% | 10007337 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 133 | 65771705 | 5032 | 120.768 | 5.032 | 2.4 | 2.4 | 2B+1S | 0 | 1056 | 1167 | 1185 | 0 | N/A | N/A | N/A | N/A | 43051104 | 1004 | 199.5231 | 0% | 100% | 100% | 100% | 0% | 0% | 10007337 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 104 | 65776254 | 4549 | 109.176 | 4.549 | 3.4 | 3.4 | 2B | 0 | 0 | 1046 | 1185 | 0 | N/A | N/A | N/A | N/A | 43051948 | 844 | 185.5353 | 0% | 0% | 100% | 100% | 0% | 40% | 10008379 | 1042 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 95 | 65780296 | 4042 | 97.008 | 4.042 | 4.9 | 4.9 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 43052668 | 720 | 178.1296 | 0% | 0% | 100% | 100% | 0% | 40% | 10009746 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125912 | 125.912 | 125.912 | [12 empty] | 26360 | 26360 | 209.3526 | [6 empty] | 6964 | 6964 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:34 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:24 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26360 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65780296 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43052668 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10009746 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 90 | 65784222 | 3926 | 94.224 | 3.926 | 6.5 | 6.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 43053372 | 704 | 179.3174 | 0% | 0% | 100% | 100% | 0% | 45% | 10011246 | 1500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 96 | 65788096 | 3874 | 92.976 | 3.874 | 7.9 | 7.9 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43054064 | 692 | 178.6267 | 0% | 0% | 100% | 100% | 0% | 45% | 10012785 | 1539 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 89 | 65791792 | 3696 | 88.704 | 3.696 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43054716 | 652 | 176.4069 | 0% | 0% | 100% | 100% | 0% | 45% | 10014303 | 1518 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 88 | 65795628 | 3836 | 92.064 | 3.836 | 9.5 | 9.5 | 2B | 0 | 0 | 845 | 1185 | 0 | N/A | N/A | N/A | N/A | 43055356 | 640 | 166.8405 | 0% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 110 | 65799738 | 4110 | 98.64 | 4.11 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43056044 | 688 | 167.3966 | 0% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 115 | 109 | 65803950 | 4212 | 101.088 | 4.212 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43056736 | 692 | 164.2925 | 0% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 65810305 | 6355 | 152.52 | 6.355 | 9.4 | 9.4 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43058020 | 1284 | 202.0456 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 65816525 | 6220 | 149.28 | 6.22 | 8.8 | 8.8 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43059412 | 1392 | 223.7942 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 65822865 | 6340 | 152.16 | 6.34 | 8 | 8 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43060828 | 1416 | 223.3438 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 65828974 | 6109 | 146.616 | 6.109 | 7.3 | 7.3 | 3B+1S | 1079 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43062204 | 1376 | 225.2414 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 | 1.36
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 65835217 | 6243 | 149.832 | 6.243 | 6.6 | 6.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43063604 | 1400 | 224.2512 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 65841376 | 6159 | 147.816 | 6.159 | 6 | 6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43064992 | 1388 | 225.3613 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 65847355 | 5979 | 143.496 | 5.979 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43066352 | 1360 | 227.4628 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 65853240 | 5885 | 141.24 | 5.885 | 5 | 5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43067692 | 1340 | 227.6975 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 65859161 | 5921 | 142.104 | 5.921 | 4.6 | 4.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43069052 | 1360 | 229.6909 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 65864937 | 5776 | 138.624 | 5.776 | 4.5 | 4.5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43070376 | 1324 | 229.2244 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 136 | 65870743 | 5806 | 139.344 | 5.806 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43071708 | 1332 | 229.4178 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 65876431 | 5688 | 136.512 | 5.688 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43072984 | 1276 | 224.3319 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 65882078 | 5647 | 135.528 | 5.647 | 3.8 | 3.8 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43074236 | 1252 | 221.7106 | 100% | 0% | 100% | 100% | 100% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 65887562 | 5484 | 131.616 | 5.484 | 3.1 | 3.1 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43075360 | 1124 | 204.9599 | 100% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 131 | 65892870 | 5308 | 127.392 | 5.308 | 2.4 | 2.4 | 2B+1S | 1097 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43076392 | 1032 | 194.4235 | 100% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 126 | 65898118 | 5248 | 125.952 | 5.248 | 1.8 | 1.8 | 2B+1S | 1097 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43077460 | 1068 | 203.5061 | 100% | 0% | 100% | 100% | 0% | 0% | 10014303 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 103 | 65902580 | 4462 | 107.088 | 4.462 | 2.6 | 2.6 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 43078276 | 816 | 182.8776 | 0% | 0% | 100% | 100% | 0% | 40% | 10015335 | 1032 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 94 | 65906787 | 4207 | 100.968 | 4.207 | 3.9 | 3.9 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43079028 | 752 | 178.7497 | 0% | 0% | 100% | 100% | 0% | 40% | 10016566 | 1231 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126491 | 126.491 | 126.491 | [12 empty] | 26360 | 26360 | 208.3943 | [6 empty] | 6820 | 6820 | 1.2017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26484 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 65906787 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43079028 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10016566 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 92 | 65910775 | 3988 | 95.712 | 3.988 | 5.5 | 5.5 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 43079748 | 720 | 180.5416 | 0% | 0% | 100% | 100% | 0% | 45% | 10017957 | 1391 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 65914639 | 3864 | 92.736 | 3.864 | 7 | 7 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 43080436 | 688 | 178.0538 | 0% | 0% | 100% | 100% | 0% | 45% | 10019427 | 1470 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 90 | 65918386 | 3747 | 89.928 | 3.747 | 8.7 | 8.7 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43081092 | 656 | 175.0734 | 0% | 0% | 100% | 100% | 0% | 45% | 10020632 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 89 | 65922153 | 3767 | 90.408 | 3.767 | 9.5 | 9.5 | 2B | 0 | 0 | 846 | 1185 | 0 | N/A | N/A | N/A | N/A | 43081748 | 656 | 174.1439 | 0% | 0% | 100% | 100% | 0% | 45% | 10021721 | 1089 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 102 | 102 | 65926132 | 3979 | 95.496 | 3.979 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 43082396 | 648 | 162.855 | 0% | 0% | 100% | 100% | 0% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 118 | 115 | 65930842 | 4710 | 113.04 | 4.71 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43083180 | 784 | 166.4544 | 0% | 0% | 100% | 100% | 0% | 0% | 10021721 | 0 | 1.37 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 140 | 65936365 | 5523 | 132.552 | 5.523 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43084308 | 1128 | 204.2368 | 0% | 0% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 65942613 | 6248 | 149.952 | 6.248 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43085688 | 1380 | 220.8707 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 151 | 65948984 | 6371 | 152.904 | 6.371 | 8.4 | 8.4 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43087116 | 1428 | 224.1406 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 65955316 | 6332 | 151.968 | 6.332 | 7.6 | 7.6 | 3B+1S | 0 | 1078 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43088516 | 1400 | 221.0992 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 | 1.38
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 65961357 | 6041 | 144.984 | 6.041 | 6.9 | 6.9 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43089858 | 1342 | 222.1487 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 65967484 | 6127 | 147.048 | 6.127 | 6.2 | 6.2 | 3B+1S | 0 | 1077 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43091228 | 1370 | 223.6005 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 144 | 65973658 | 6174 | 148.176 | 6.174 | 5.6 | 5.6 | 3B+1S | 0 | 1067 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43092612 | 1384 | 224.1659 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 65979649 | 5991 | 143.784 | 5.991 | 5 | 5 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43093941 | 1329 | 221.8327 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 143 | 65985580 | 5931 | 142.344 | 5.931 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43095332 | 1391 | 234.5304 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 65991383 | 5803 | 139.272 | 5.803 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43096664 | 1332 | 229.5364 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 65997181 | 5798 | 139.152 | 5.798 | 4 | 4 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43098012 | 1348 | 232.494 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 66002995 | 5814 | 139.536 | 5.814 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43099356 | 1344 | 231.1662 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 131 | 66008665 | 5670 | 136.08 | 5.67 | 3.4 | 3.4 | 3B+1S | 0 | 1000 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43100672 | 1316 | 232.0988 | 0% | 100% | 100% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 66014135 | 5470 | 131.28 | 5.47 | 2.8 | 2.8 | 2B+1S | 0 | 1078 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43101772 | 1100 | 201.0969 | 0% | 100% | 0% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 122 | 66019475 | 5340 | 128.16 | 5.34 | 2.2 | 2.2 | 2B+1S | 0 | 1057 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43102820 | 1048 | 196.2547 | 0% | 100% | 0% | 100% | 100% | 0% | 10021721 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 125 | 66024753 | 5278 | 126.672 | 5.278 | 1.8 | 1.8 | 2B+1S | 0 | 1055 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43103868 | 1048 | 198.5601 | 0% | 100% | 0% | 100% | 100% | 0% | 10021721 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 108 | 66029288 | 4535 | 108.84 | 4.535 | 2.8 | 2.8 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 43104708 | 840 | 185.226 | 0% | 0% | 0% | 100% | 100% | 40% | 10022762 | 1041 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 104 | 66033615 | 4327 | 103.848 | 4.327 | 4.1 | 4.1 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43105512 | 804 | 185.81 | 0% | 0% | 0% | 100% | 100% | 40% | 10024017 | 1255 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126828 | 126.828 | 126.828 | [12 empty] | 26484 | 26484 | 208.8182 | [6 empty] | 7451 | 7451 | 1.215 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:41 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26212 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66033615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43105512 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10024017 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 96 | 66037636 | 4021 | 96.504 | 4.021 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43106244 | 732 | 182.0443 | 0% | 0% | 0% | 100% | 100% | 45% | 10025391 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 92 | 66041570 | 3934 | 94.416 | 3.934 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43106956 | 712 | 180.9863 | 0% | 0% | 0% | 100% | 100% | 45% | 10026845 | 1454 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 87 | 66045413 | 3843 | 92.232 | 3.843 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43107644 | 688 | 179.0268 | 0% | 0% | 0% | 100% | 100% | 45% | 10028285 | 1440 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 91 | 66049205 | 3792 | 91.008 | 3.792 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43108304 | 660 | 174.0506 | 0% | 0% | 0% | 100% | 100% | 45% | 10029100 | 815 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 102 | 66053270 | 4065 | 97.56 | 4.065 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43108964 | 660 | 162.3616 | 0% | 0% | 0% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 21 | 14.7887 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 116 | 108 | 66058011 | 4741 | 113.784 | 4.741 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43109732 | 768 | 161.9911 | 0% | 0% | 0% | 100% | 100% | 0% | 10029100 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 66063476 | 5465 | 131.16 | 5.465 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43110828 | 1096 | 200.5489 | 0% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 124 | 140 | 66069430 | 5954 | 142.896 | 5.954 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43112072 | 1244 | 208.9352 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 151 | 66074762 | 5332 | 127.968 | 5.332 | 8.9 | 8.9 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43113292 | 1220 | 228.8072 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 66080786 | 6024 | 144.576 | 6.024 | 8.2 | 8.2 | 3B+1S | 1058 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43114660 | 1368 | 227.0916 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 | 1.38
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 66087072 | 6286 | 150.864 | 6.286 | 7.6 | 7.6 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43116080 | 1420 | 225.8988 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 66093425 | 6353 | 152.472 | 6.353 | 6.9 | 6.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43117524 | 1444 | 227.2942 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 139 | 66099250 | 5825 | 139.8 | 5.825 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43118844 | 1320 | 226.6094 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 140 | 66105199 | 5949 | 142.776 | 5.949 | 5.8 | 5.8 | 3B+1S | 1098 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43120216 | 1372 | 230.627 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 66111082 | 5883 | 141.192 | 5.883 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43121568 | 1352 | 229.8147 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 66116945 | 5863 | 140.712 | 5.863 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43122916 | 1348 | 229.9164 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 66122696 | 5751 | 138.024 | 5.751 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43124248 | 1332 | 231.6119 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 141 | 66128505 | 5809 | 139.416 | 5.809 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43125580 | 1332 | 229.2994 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 66134250 | 5745 | 137.88 | 5.745 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1116 | N/A | N/A | N/A | N/A | 43126908 | 1328 | 231.1575 | 100% | 0% | 100% | 100% | 100% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 140 | 66139771 | 5521 | 132.504 | 5.521 | 3.6 | 3.6 | 2B+1S | 1099 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43128012 | 1104 | 199.9638 | 100% | 0% | 100% | 100% | 0% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 130 | 66145167 | 5396 | 129.504 | 5.396 | 2.8 | 2.8 | 2B+1S | 1077 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43129084 | 1072 | 198.6657 | 100% | 0% | 100% | 100% | 0% | 0% | 10029100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 124 | 66150412 | 5245 | 125.88 | 5.245 | 2.3 | 2.3 | 2B+1S | 1077 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43130140 | 1056 | 201.3346 | 100% | 0% | 100% | 100% | 0% | 0% | 10029100 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 105 | 66154865 | 4453 | 106.872 | 4.453 | 3 | 3 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43130976 | 836 | 187.7386 | 0% | 0% | 100% | 100% | 0% | 40% | 10030045 | 945 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 98 | 66159002 | 4137 | 99.288 | 4.137 | 4.5 | 4.5 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 43131724 | 748 | 180.8073 | 0% | 0% | 100% | 100% | 0% | 40% | 10031329 | 1284 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125387 | 125.387 | 125.387 | [12 empty] | 26212 | 26212 | 209.0488 | [6 empty] | 7312 | 7312 | 1.2283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MERALCO POWER FLUCTUATION @ 7:50AM
ALL PUMP STOPPED DUE TO POWER FLUCTUATION @ 7:50AM
BP2 POWER RESUME @ 7:52AM
BP3 POWER RESUME @ 7:54AM
BP1 POWER RESUME @ 7:56AM
SP1 POWER RESUME @ 7:58AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26472 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66159002 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43131724 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10031329 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 96 | 66162962 | 3960 | 95.04 | 3.96 | 6 | 6 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 43132436 | 712 | 179.798 | 0% | 0% | 100% | 100% | 0% | 45% | 10032752 | 1423 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 89 | 66166830 | 3868 | 92.832 | 3.868 | 7.4 | 7.4 | 2B | 0 | 0 | 945 | 1185 | 0 | N/A | N/A | N/A | N/A | 43133140 | 704 | 182.0062 | 0% | 0% | 100% | 100% | 0% | 45% | 10034066 | 1314 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 66170600 | 3770 | 90.48 | 3.77 | 8.7 | 8.7 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43133824 | 684 | 181.4324 | 0% | 0% | 100% | 100% | 0% | 45% | 10035372 | 1306 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 95 | 66174459 | 3859 | 92.616 | 3.859 | 9.5 | 9.5 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43134500 | 676 | 175.1749 | 0% | 0% | 100% | 100% | 0% | 45% | 10035948 | 576 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 106 | 66178638 | 4179 | 100.296 | 4.179 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43135196 | 696 | 166.547 | 0% | 0% | 100% | 100% | 0% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 126 | 66183737 | 5099 | 122.376 | 5.099 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43136100 | 904 | 177.2897 | 0% | 0% | 100% | 100% | 0% | 0% | 10035948 | 0 | 1.37 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 141 | 66189254 | 5517 | 132.408 | 5.517 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43137268 | 1168 | 211.7093 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 66195346 | 6092 | 146.208 | 6.092 | 8.7 | 8.7 | 3B+1S | 0 | 1058 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43138628 | 1360 | 223.2436 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 144 | 66201535 | 6189 | 148.536 | 6.189 | 8 | 8 | 3B+1S | 0 | 1057 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43139996 | 1368 | 221.0373 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 66208196 | 6661 | 159.864 | 6.661 | 7.2 | 7.2 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43141492 | 1496 | 224.5909 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 | 1.36
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 66213918 | 5722 | 137.328 | 5.722 | 6.7 | 6.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43142776 | 1284 | 224.3971 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 66220023 | 6105 | 146.52 | 6.105 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43144148 | 1372 | 224.7338 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 145 | 66226174 | 6151 | 147.624 | 6.151 | 5.6 | 5.6 | 3B+1S | 0 | 1037 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43145548 | 1400 | 227.6053 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 140 | 66232002 | 5828 | 139.872 | 5.828 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43146876 | 1328 | 227.8655 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 140 | 66237834 | 5832 | 139.968 | 5.832 | 5.1 | 5.1 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43148220 | 1344 | 230.4527 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 66243571 | 5737 | 137.688 | 5.737 | 5 | 5 | 3B+1S | 0 | 1005 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43149540 | 1320 | 230.0854 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 66249319 | 5748 | 137.952 | 5.748 | 4.8 | 4.8 | 3B+1S | 0 | 1007 | 1168 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43150840 | 1300 | 226.1656 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 66255049 | 5730 | 137.52 | 5.73 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43152112 | 1272 | 221.9895 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 66260646 | 5597 | 134.328 | 5.597 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43153364 | 1252 | 223.6913 | 0% | 100% | 100% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 132 | 66266115 | 5469 | 131.256 | 5.469 | 3.5 | 3.5 | 2B+1S | 0 | 1098 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43154476 | 1112 | 203.3278 | 0% | 100% | 0% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 130 | 66271563 | 5448 | 130.752 | 5.448 | 2.7 | 2.7 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43155576 | 1100 | 201.909 | 0% | 100% | 0% | 100% | 100% | 0% | 10035948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 123 | 66276793 | 5230 | 125.52 | 5.23 | 2.1 | 2.1 | 2B+1S | 0 | 1050 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43156640 | 1064 | 203.4417 | 0% | 100% | 0% | 100% | 100% | 0% | 10035948 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 102 | 66281174 | 4381 | 105.144 | 4.381 | 3 | 3 | 2B | 0 | 0 | 0 | 1185 | 1046 | N/A | N/A | N/A | N/A | 43157436 | 796 | 181.6937 | 0% | 0% | 0% | 100% | 100% | 38% | 10036922 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 99 | 66285384 | 4210 | 101.04 | 4.21 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43158196 | 760 | 180.5226 | 0% | 0% | 0% | 100% | 100% | 38% | 10038160 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126382 | 126.382 | 126.382 | [12 empty] | 26472 | 26472 | 209.4602 | [6 empty] | 6831 | 6831 | 1.2733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (38%)

## JAN 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16 |  |  |  | S
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26560 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66285384 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43158196 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10038160 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 93 | 66289314 | 3930 | 94.32 | 3.93 | 6 | 6 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 43158892 | 696 | 177.0992 | 0% | 0% | 0% | 100% | 100% | 47% | 10039610 | 1450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 92 | 66293242 | 3928 | 94.272 | 3.928 | 7.7 | 7.7 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 43159592 | 700 | 178.2077 | 0% | 0% | 0% | 100% | 100% | 47% | 10041065 | 1455 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 66297189 | 3947 | 94.728 | 3.947 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 43160300 | 708 | 179.3767 | 0% | 0% | 0% | 100% | 100% | 47% | 10042534 | 1469 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 105 | 66301309 | 4120 | 98.88 | 4.12 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43161000 | 700 | 169.9029 | 0% | 0% | 0% | 100% | 100% | 47% | 10042977 | 443 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 109 | 66305447 | 4138 | 99.312 | 4.138 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43161708 | 708 | 171.0971 | 0% | 0% | 0% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 145 | 66310508 | 5061 | 121.464 | 5.061 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43162628 | 920 | 181.7823 | 0% | 0% | 0% | 100% | 100% | 0% | 10042977 | 0 | 1.46 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 66316742 | 6234 | 149.616 | 6.234 | 9.3 | 9.3 | 3B+1S | 1026 |  | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43163976 | 1348 | 216.2336 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 66322665 | 5923 | 142.152 | 5.923 | 8.7 | 8.7 | 3B+1S | 1037 |  | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43165292 | 1316 | 222.1847 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 66328846 | 6181 | 148.344 | 6.181 | 8.1 | 8.1 | 3B+1S | 1037 |  | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43166676 | 1384 | 223.912 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 66334898 | 6052 | 145.248 | 6.052 | 7.5 | 7.5 | 3B+1S | 1036 |  | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43168028 | 1352 | 223.3972 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 | 1.47
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 66340932 | 6034 | 144.816 | 6.034 | 6.9 | 6.9 | 3B+1S | 1046 |  | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43169388 | 1360 | 225.3895 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 66347059 | 6127 | 147.048 | 6.127 | 6.2 | 6.2 | 3B+1S | 1046 |  | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43170772 | 1384 | 225.8854 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 66353187 | 6128 | 147.072 | 6.128 | 6 | 6 | 3B+1S | 1005 |  | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43172084 | 1312 | 214.0992 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 141 | 66358922 | 5735 | 137.64 | 5.735 | 5.8 | 5.8 | 3B+1S | 1005 |  | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43173440 | 1356 | 236.4429 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 | 1.45 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 140 | 66364771 | 5849 | 140.376 | 5.849 | 5.5 | 5.5 | 3B+1S | 1005 |  | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43174756 | 1316 | 224.9957 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 66370558 | 5787 | 138.888 | 5.787 | 5.3 | 5.3 | 3B+1S | 1005 |  | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43176064 | 1308 | 226.0238 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 66376405 | 5847 | 140.328 | 5.847 | 5.1 | 5.1 | 3B+1S | 1005 |  | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43177388 | 1324 | 226.4409 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 66382207 | 5802 | 139.248 | 5.802 | 4.9 | 4.9 | 3B+1S | 1006 |  | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43178700 | 1312 | 226.1289 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 66388013 | 5806 | 139.344 | 5.806 | 4.6 | 4.6 | 3B+1S | 1005 |  | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43180012 | 1312 | 225.9731 | 100% | 0% | 100% | 100% | 100% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 66393396 | 5383 | 129.192 | 5.383 | 3.8 | 3.8 | 2B+1S | 1098 |  | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43181100 | 1088 | 202.1178 | 100% | 0% | 100% | 100% | 0% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 129 | 66398807 | 5411 | 129.864 | 5.411 | 3 | 3 | 2B+1S | 1097 |  | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43182192 | 1092 | 201.8111 | 100% | 0% | 100% | 100% | 0% | 0% | 10042977 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 125 | 66403977 | 5170 | 124.08 | 5.17 | 2.5 | 2.5 | 2B+1S | 1016 |  | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 43183212 | 1020 | 197.2921 | 100% | 0% | 100% | 100% | 0% | 0% | 10042977 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 101 | 66408456 | 4479 | 107.496 | 4.479 | 3.2 | 3.2 | 2B | 0 |  | 1047 | 1185 |  | N/A | N/A | N/A | N/A | 43184020 | 808 | 180.3974 | 0% | 0% | 100% | 100% | 0% | 40% | 10043878 | 901 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 97 | 66412631 | 4175 | 100.2 | 4.175 | 4.5 | 4.5 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 43184756 | 736 | 176.2874 | 0% | 0% | 0% | 100% | 100% | 40% | 10045014 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127247 | 127.247 | 127.247 | [12 empty] | 26560 | 26560 | 208.7279 | [6 empty] | 6854 | 6854 | 1.3333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:22 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66412631 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43184756 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10045014 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 88 | 66416599 | 3968 | 95.232 | 3.968 | 6 | 6 | 2B | 0 | 0 | 1017 | 0 | 997 | N/A | N/A | N/A | N/A | 43185416 | 660 | 166.3306 | 0% | 0% | 100% | 0% | 100% | 45% | 10046383 | 1369 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 85 | 66420232 | 3633 | 87.192 | 3.633 | 7.4 | 7.4 | 2B | 0 | 0 | 1017 | 0 | 997 | N/A | N/A | N/A | N/A | 43185964 | 548 | 150.8395 | 0% | 0% | 100% | 0% | 100% | 45% | 10047801 | 1418 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 90 | 66423974 | 3742 | 89.808 | 3.742 | 8.9 | 8.9 | 2B | 0 | 0 | 1017 | 0 | 997 | N/A | N/A | N/A | N/A | 43186528 | 564 | 150.7215 | 0% | 0% | 100% | 0% | 100% | 45% | 10049184 | 1383 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 93 | 66427790 | 3816 | 91.584 | 3.816 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 0 | 948 | N/A | N/A | N/A | N/A | 43187060 | 532 | 139.413 | 0% | 0% | 100% | 0% | 100% | 45% | 10049629 | 445 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 105 | 66431909 | 4119 | 98.856 | 4.119 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1047 | N/A | N/A | N/A | N/A | 43187620 | 560 | 135.9553 | 0% | 0% | 100% | 0% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 113 | 112 | 66436613 | 4704 | 112.896 | 4.704 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 0 | 1048 | N/A | N/A | N/A | N/A | 43188284 | 664 | 141.1565 | 0% | 0% | 100% | 0% | 100% | 0% | 10049629 | 0 | 1.32 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 146 | 66442473 | 5860 | 140.64 | 5.86 | 9.2 | 9.2 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43189556 | 1272 | 217.0648 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 66448735 | 6262 | 150.288 | 6.262 | 8.6 | 8.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43190972 | 1416 | 226.1258 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 66455167 | 6432 | 154.368 | 6.432 | 7.9 | 7.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43192360 | 1388 | 215.796 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 66461208 | 6041 | 144.984 | 6.041 | 7.3 | 7.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43193740 | 1380 | 228.439 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 | 1.35
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 151 | 66467613 | 6405 | 153.72 | 6.405 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43195154 | 1414 | 220.765 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 66473475 | 5862 | 140.688 | 5.862 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43196464 | 1310 | 223.4732 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 66479389 | 5914 | 141.936 | 5.914 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43197796 | 1332 | 225.2283 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 66485279 | 5890 | 141.36 | 5.89 | 5.3 | 5.3 | 3B+1S | 0 | 1036 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43199136 | 1340 | 227.5042 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 66491039 | 5760 | 138.24 | 5.76 | 5 | 5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43200452 | 1316 | 228.4722 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 66496773 | 5734 | 137.616 | 5.734 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43201772 | 1320 | 230.2058 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 66502540 | 5767 | 138.408 | 5.767 | 4.7 | 4.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43203072 | 1300 | 225.4205 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 141 | 66508305 | 5765 | 138.36 | 5.765 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43204380 | 1308 | 226.8864 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 66513947 | 5642 | 135.408 | 5.642 | 4.1 | 4.1 | 3B+1S | 0 | 1016 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43205648 | 1268 | 224.743 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 139 | 66519409 | 5462 | 131.088 | 5.462 | 3.3 | 3.3 | 2B+1S | 0 | 1097 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43206748 | 1100 | 201.3914 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 125 | 66524793 | 5384 | 129.216 | 5.384 | 2.6 | 2.6 | 2B+1S | 0 | 1077 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43207824 | 1076 | 199.8514 | 0% | 100% | 100% | 100% | 100% | 0% | 10049629 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 125 | 66530048 | 5255 | 126.12 | 5.255 | 2 | 2 | 2B+1S | 0 | 1026 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43208868 | 1044 | 198.6679 | 0% | 100% | 0% | 100% | 100% | 0% | 10049629 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 104 | 66534483 | 4435 | 106.44 | 4.435 | 2.9 | 2.9 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 43209700 | 832 | 187.5986 | 0% | 0% | 0% | 100% | 100% | 40% | 10050589 | 960 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 98 | 66538694 | 4211 | 101.064 | 4.211 | 4.3 | 4.3 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43210452 | 752 | 178.5799 | 0% | 0% | 0% | 100% | 100% | 40% | 10051840 | 1251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126063 | 126.063 | 126.063 | [12 empty] | 25696 | 25696 | 203.8346 | [6 empty] | 6826 | 6826 | 1.2517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (47%)
XCV2- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
MAINTENANCE TEAM ARRIVE @9:10PM FOR QUARTERLY PREVENTIVE MAINTENANCE, REGREASING PUMP/ MOTOR BEARING @ COUPLING OF ALL UNITS AND VACUME CLEANING OF VFD FILTER.
BP1- STOP @ 11:28PM FOR QUARTERLY PREVENTIVE MAINTENANCE
BP3- START @ 11:25PM FOR QUARTERLY PREVENTIVE MAINTENANCE
BP1- START @ 12:30AM FOR QUARTERLY PREVENTIVE MAINTENANCE
BP2- STOP @ 12:31AM FOR QUARTERLY PREVENTIVE MAINTENANCE | [9 empty] | BP1- STOP @ 11:28 FOR QUARTERLY PREVENTIVE MAINTENANCE
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26576 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66538694 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43210452 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10051840 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 89 | 66542709 | 4015 | 96.36 | 4.015 | 5.7 | 5.7 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43211176 | 724 | 180.3238 | 0% | 0% | 0% | 100% | 100% | 45% | 10053164 | 1324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 89 | 66546633 | 3924 | 94.176 | 3.924 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43211876 | 700 | 178.3894 | 0% | 0% | 0% | 100% | 100% | 45% | 10054539 | 1375 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 88 | 66550420 | 3787 | 90.888 | 3.787 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43212556 | 680 | 179.5617 | 0% | 0% | 0% | 100% | 100% | 45% | 10055861 | 1322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 98 | 66554265 | 3845 | 92.28 | 3.845 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43213236 | 680 | 176.8531 | 0% | 0% | 0% | 100% | 100% | 45% | 10056674 | 813 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 105 | 66558369 | 4104 | 98.496 | 4.104 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43213900 | 664 | 161.7934 | 0% | 0% | 0% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 127 | 66563426 | 5057 | 121.368 | 5.057 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43214788 | 888 | 175.5982 | 0% | 0% | 0% | 100% | 100% | 0% | 10056674 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 130 | 66569405 | 5979 | 143.496 | 5.979 | 9 | 9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43216132 | 1344 | 224.7868 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 151 | 66575614 | 6209 | 149.016 | 6.209 | 8.4 | 8.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43217524 | 1392 | 224.1907 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 152 | 66581770 | 6156 | 147.744 | 6.156 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43218900 | 1376 | 223.5218 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 66588013 | 6243 | 149.832 | 6.243 | 7.2 | 7.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43220244 | 1344 | 215.2811 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 | 1.27
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 66594090 | 6077 | 145.848 | 6.077 | 6.6 | 6.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43221644 | 1400 | 230.3768 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 66600203 | 6113 | 146.712 | 6.113 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43223020 | 1376 | 225.0941 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 66606106 | 5903 | 141.672 | 5.903 | 5.7 | 5.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43224364 | 1344 | 227.6808 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 139 | 66611892 | 5786 | 138.864 | 5.786 | 5.4 | 5.4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43225708 | 1344 | 232.2848 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 66617655 | 5763 | 138.312 | 5.763 | 5.1 | 5.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43227036 | 1328 | 230.4355 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 66623271 | 5616 | 134.784 | 5.616 | 4.8 | 4.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43228336 | 1300 | 231.4815 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 66629038 | 5767 | 138.408 | 5.767 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43229660 | 1324 | 229.5821 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 66634729 | 5691 | 136.584 | 5.691 | 4.2 | 4.2 | 3B+1S | 1006 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43230964 | 1304 | 229.1337 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 137 | 66640365 | 5636 | 135.264 | 5.636 | 3.9 | 3.9 | 3B+1S | 1005 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43232268 | 1304 | 231.3698 | 100% | 0% | 100% | 100% | 100% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 131 | 66645843 | 5478 | 131.472 | 5.478 | 3.1 | 3.1 | 2B+1S | 1118 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43233372 | 1104 | 201.5334 | 100% | 0% | 100% | 100% | 0% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 128 | 66651223 | 5380 | 129.12 | 5.38 | 2.3 | 2.3 | 2B+1S | 1117 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43234460 | 1088 | 202.2305 | 100% | 0% | 100% | 100% | 0% | 0% | 10056674 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 126 | 66656452 | 5229 | 125.496 | 5.229 | 1.6 | 1.6 | 2B+1S | 1116 | 0 | 1147 | 1185 | 0 | N/A | N/A | N/A | N/A | 43235500 | 1040 | 198.8908 | 100% | 0% | 100% | 100% | 0% | 0% | 10056674 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 103 | 66660786 | 4334 | 104.016 | 4.334 | 2.4 | 2.4 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43236280 | 780 | 179.9723 | 0% | 0% | 100% | 100% | 0% | 40% | 10057679 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 94 | 66664970 | 4184 | 100.416 | 4.184 | 3.7 | 3.7 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43237028 | 748 | 178.7763 | 0% | 0% | 100% | 100% | 0% | 40% | 10058916 | 1237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126276 | 126.276 | 126.276 | [12 empty] | 26576 | 26576 | 210.4596 | [6 empty] | 7076 | 7076 | 1.2233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26720 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66664970 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43237028 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10058916 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 94 | 66668880 | 3910 | 93.84 | 3.91 | 5.3 | 5.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 43237728 | 700 | 179.0281 | 0% | 0% | 100% | 100% | 0% | 45% | 10060358 | 1442 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 89 | 66672763 | 3883 | 93.192 | 3.883 | 6.8 | 6.8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43238420 | 692 | 178.2127 | 0% | 0% | 100% | 100% | 0% | 45% | 10061809 | 1451 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 90 | 66676618 | 3855 | 92.52 | 3.855 | 8.2 | 8.2 | 2B | 0 | 0 | 945 | 1185 | 0 | N/A | N/A | N/A | N/A | 43239100 | 680 | 176.3943 | 0% | 0% | 100% | 100% | 0% | 45% | 10063164 | 1355 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 91 | 66680438 | 3820 | 91.68 | 3.82 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 43239772 | 672 | 175.9162 | 0% | 0% | 100% | 100% | 0% | 45% | 10064232 | 1068 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 109 | 66684641 | 4203 | 100.872 | 4.203 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 43240452 | 680 | 161.7892 | 0% | 0% | 100% | 100% | 0% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 66689772 | 5131 | 123.144 | 5.131 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43241340 | 888 | 173.0657 | 0% | 0% | 100% | 100% | 0% | 0% | 10064232 | 0 | 1.36 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 143 | 66695713 | 5941 | 142.584 | 5.941 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43242636 | 1296 | 218.1451 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 66701820 | 6107 | 146.568 | 6.107 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43244000 | 1364 | 223.3503 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 123 | 66708026 | 6206 | 148.944 | 6.206 | 7.9 | 7.9 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43245380 | 1380 | 222.3655 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 152 | 66714208 | 6182 | 148.368 | 6.182 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43246764 | 1384 | 223.8758 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 | 1.33
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 66720376 | 6168 | 148.032 | 6.168 | 6.6 | 6.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43248156 | 1392 | 225.6809 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 66726573 | 6197 | 148.728 | 6.197 | 6 | 6 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43249556 | 1400 | 225.9158 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 139 | 66732957 | 6384 | 153.216 | 6.384 | 5.4 | 5.4 | 3B+1S | 0 | 1046 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43251000 | 1444 | 226.1905 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 66738375 | 5418 | 130.032 | 5.418 | 5 | 5 | 3B+1S | 0 | 1046 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43252248 | 1248 | 230.3433 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 136 | 66744259 | 5884 | 141.216 | 5.884 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43253620 | 1372 | 233.1747 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 66749923 | 5664 | 135.936 | 5.664 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43254912 | 1292 | 228.1073 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 66755668 | 5745 | 137.88 | 5.745 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43256244 | 1332 | 231.8538 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 66761459 | 5791 | 138.984 | 5.791 | 4.3 | 4.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43257576 | 1332 | 230.0121 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 131 | 66767167 | 5708 | 136.992 | 5.708 | 4 | 4 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43258900 | 1324 | 231.9552 | 0% | 100% | 100% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 66772652 | 5485 | 131.64 | 5.485 | 3.1 | 3.1 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43260004 | 1104 | 201.2762 | 0% | 100% | 0% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 126 | 66778077 | 5425 | 130.2 | 5.425 | 2.5 | 2.5 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43261100 | 1096 | 202.0276 | 0% | 100% | 0% | 100% | 100% | 0% | 10064232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 123 | 66783309 | 5232 | 125.568 | 5.232 | 2 | 2 | 2B+1S | 0 | 1046 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43262140 | 1040 | 198.7768 | 0% | 100% | 0% | 100% | 100% | 0% | 10064232 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 103 | 66787797 | 4488 | 107.712 | 4.488 | 2.7 | 2.7 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 43262972 | 832 | 185.3832 | 0% | 0% | 0% | 100% | 100% | 40% | 10065139 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 101 | 66792100 | 4303 | 103.272 | 4.303 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 43263748 | 776 | 180.3393 | 0% | 0% | 0% | 100% | 100% | 40% | 10066397 | 1258 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127130 | 127.13 | 127.13 | [12 empty] | 26720 | 26720 | 210.1786 | [6 empty] | 7481 | 7481 | 1.2633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:22 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26488 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66792100 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43263748 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10066397 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 97 | 66796145 | 4045 | 97.08 | 4.045 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43264476 | 728 | 179.9753 | 0% | 0% | 0% | 100% | 100% | 45% | 10067796 | 1399 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 97 | 66800203 | 4058 | 97.392 | 4.058 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43265204 | 728 | 179.3987 | 0% | 0% | 0% | 100% | 100% | 45% | 10069147 | 1351 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 89 | 66804087 | 3884 | 93.216 | 3.884 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43265884 | 680 | 175.0772 | 0% | 0% | 0% | 100% | 100% | 45% | 10070529 | 1382 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 95 | 66807850 | 3763 | 90.312 | 3.763 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43266540 | 656 | 174.329 | 0% | 0% | 0% | 100% | 100% | 45% | 10071345 | 816 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 101 | 66811922 | 4072 | 97.728 | 4.072 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 897 | N/A | N/A | N/A | N/A | 43267204 | 664 | 163.0648 | 0% | 0% | 0% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 124 | 66816903 | 4981 | 119.544 | 4.981 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43267972 | 768 | 154.1859 | 0% | 0% | 0% | 100% | 100% | 0% | 10071345 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 148 | 66821986 | 5083 | 121.992 | 5.083 | 9.4 | 9.4 | 3B+1S | 997 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43269048 | 1076 | 211.686 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 66828174 | 6188 | 148.512 | 6.188 | 9 | 9 | 3B+1S | 997 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43270408 | 1360 | 219.7802 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 66834338 | 6164 | 147.936 | 6.164 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43271772 | 1364 | 221.2849 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 66840627 | 6289 | 150.936 | 6.289 | 8.1 | 8.1 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43273160 | 1388 | 220.7028 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 | 1.08
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 66846765 | 6138 | 147.312 | 6.138 | 7.6 | 7.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43274520 | 1360 | 221.5705 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 66852926 | 6161 | 147.864 | 6.161 | 7.1 | 7.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43275892 | 1372 | 222.6911 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 66859043 | 6117 | 146.808 | 6.117 | 6.6 | 6.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43277276 | 1384 | 226.2547 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 145 | 66864892 | 5849 | 140.376 | 5.849 | 6.1 | 6.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43278621 | 1345 | 229.9538 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 66870811 | 5919 | 142.056 | 5.919 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43279976 | 1355 | 228.9238 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 66876677 | 5866 | 140.784 | 5.866 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43281320 | 1344 | 229.1169 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 66882490 | 5813 | 139.512 | 5.813 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43282660 | 1340 | 230.5178 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 66888296 | 5806 | 139.344 | 5.806 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43284000 | 1340 | 230.7957 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 66894041 | 5745 | 137.88 | 5.745 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43285332 | 1332 | 231.8538 | 100% | 0% | 100% | 100% | 100% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 132 | 66899509 | 5468 | 131.232 | 5.468 | 3.7 | 3.7 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43286436 | 1104 | 201.902 | 100% | 0% | 100% | 100% | 0% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 126 | 66904864 | 5355 | 128.52 | 5.355 | 2.9 | 2.9 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43287524 | 1088 | 203.1746 | 100% | 0% | 100% | 100% | 0% | 0% | 10071345 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 125 | 66910120 | 5256 | 126.144 | 5.256 | 2.3 | 2.3 | 2B+1S | 1046 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43288580 | 1056 | 200.9132 | 100% | 0% | 100% | 100% | 0% | 0% | 10071345 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 119 | 66914700 | 4580 | 109.92 | 4.58 | 3 | 3 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 43289432 | 852 | 186.0262 | 0% | 0% | 100% | 100% | 0% | 40% | 10072157 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 103 | 66919097 | 4397 | 105.528 | 4.397 | 4.1 | 4.1 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43290236 | 804 | 182.8519 | 0% | 0% | 100% | 100% | 0% | 40% | 10073167 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126997 | 126.997 | 126.997 | [12 empty] | 26488 | 26488 | 208.5719 | [6 empty] | 6770 | 6770 | 1.12 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:42 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26508 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 66919097 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43290236 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10073167 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 98 | 66923272 | 4175 | 100.2 | 4.175 | 5.4 | 5.4 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43290996 | 760 | 182.0359 | 0% | 0% | 100% | 100% | 0% | 45% | 10074368 | 1201 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 95 | 66927363 | 4091 | 98.184 | 4.091 | 6.7 | 6.7 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 43291724 | 728 | 177.9516 | 0% | 0% | 100% | 100% | 0% | 45% | 10075670 | 1302 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 66931334 | 3971 | 95.304 | 3.971 | 8.1 | 8.1 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43292424 | 700 | 176.278 | 0% | 0% | 100% | 100% | 0% | 45% | 10076943 | 1273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 92 | 66935307 | 3973 | 95.352 | 3.973 | 9.1 | 9.1 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43293100 | 676 | 170.1485 | 0% | 0% | 100% | 100% | 0% | 45% | 10077918 | 975 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 100 | 66939290 | 3983 | 95.592 | 3.983 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43293796 | 696 | 174.7427 | 0% | 0% | 100% | 100% | 0% | 45% | 10078145 | 227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 116 | 115 | 66944327 | 5037 | 120.888 | 5.037 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 43294572 | 776 | 154.06 | 0% | 0% | 100% | 100% | 0% | 0% | 10078145 | 0 | 1.37 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 134 | 66949206 | 4879 | 117.096 | 4.879 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43295588 | 1016 | 208.2394 | 0% | 0% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 66955534 | 6328 | 151.872 | 6.328 | 9.4 | 9.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43296924 | 1336 | 211.1252 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 150 | 66961546 | 6012 | 144.288 | 6.012 | 9 | 9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43298268 | 1344 | 223.5529 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 66967714 | 6168 | 148.032 | 6.168 | 8.4 | 8.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43299624 | 1356 | 219.8444 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 | 1.31
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 66973927 | 6213 | 149.112 | 6.213 | 7.9 | 7.9 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43300992 | 1368 | 220.1835 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 66980048 | 6121 | 146.904 | 6.121 | 7.4 | 7.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43302356 | 1364 | 222.8394 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 66986352 | 6304 | 151.296 | 6.304 | 6.9 | 6.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43303750 | 1394 | 221.1294 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 142 | 66992254 | 5902 | 141.648 | 5.902 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43305100 | 1350 | 228.736 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 142 | 66998164 | 5910 | 141.84 | 5.91 | 5.9 | 5.9 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43306456 | 1356 | 229.4416 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 67004094 | 5930 | 142.32 | 5.93 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43307820 | 1364 | 230.0169 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 67009948 | 5854 | 140.496 | 5.854 | 5 | 5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43309176 | 1356 | 231.6365 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 67015720 | 5772 | 138.528 | 5.772 | 4.7 | 4.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43310512 | 1336 | 231.4622 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 67021388 | 5668 | 136.032 | 5.668 | 4.5 | 4.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43311844 | 1332 | 235.0035 | 0% | 100% | 100% | 100% | 100% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 131 | 67026831 | 5443 | 130.632 | 5.443 | 3.7 | 3.7 | 2B+1S | 0 | 1098 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43312948 | 1104 | 202.8293 | 0% | 100% | 100% | 100% | 0% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 127 | 67032255 | 5424 | 130.176 | 5.424 | 2.9 | 2.9 | 2B+1S | 0 | 1128 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43314044 | 1096 | 202.0649 | 0% | 100% | 100% | 100% | 0% | 0% | 10078145 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 122 | 67037612 | 5357 | 128.568 | 5.357 | 2.2 | 2.2 | 2B+1S | 0 | 1046 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43315132 | 1088 | 203.0987 | 0% | 100% | 100% | 100% | 0% | 0% | 10078145 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 103 | 67042017 | 4405 | 105.72 | 4.405 | 3.1 | 3.1 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 43315964 | 832 | 188.8763 | 0% | 0% | 100% | 100% | 0% | 40% | 10079125 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 98 | 67046282 | 4265 | 102.36 | 4.265 | 4.5 | 4.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 43316744 | 780 | 182.8839 | 0% | 0% | 100% | 100% | 0% | 40% | 10080374 | 1249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127185 | 127.185 | 127.185 | [12 empty] | 26508 | 26508 | 208.4208 | [6 empty] | 7207 | 7207 | 1.235 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26620 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67046282 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43316744 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10080374 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 97 | 67050375 | 4093 | 98.232 | 4.093 | 6 | 6 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 43317484 | 740 | 180.7965 | 0% | 0% | 100% | 100% | 0% | 47% | 10081788 | 1414 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 92 | 67054319 | 3944 | 94.656 | 3.944 | 7.6 | 7.6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43318204 | 720 | 182.5558 | 0% | 0% | 100% | 100% | 0% | 47% | 10083303 | 1515 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 92 | 67058159 | 3840 | 92.16 | 3.84 | 8.9 | 8.9 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43318884 | 680 | 177.0833 | 0% | 0% | 100% | 100% | 0% | 47% | 10084767 | 1464 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 98 | 67062134 | 3975 | 95.4 | 3.975 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43319572 | 688 | 173.0818 | 0% | 0% | 100% | 100% | 0% | 47% | 10085262 | 495 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 105 | 67066203 | 4069 | 97.656 | 4.069 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43320236 | 664 | 163.1851 | 0% | 0% | 100% | 100% | 0% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 122 | 67071503 | 5300 | 127.2 | 5.3 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43321140 | 904 | 170.566 | 0% | 0% | 100% | 100% | 0% | 0% | 10085262 | 0 | 1.45 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 67077234 | 5731 | 137.544 | 5.731 | 9.4 | 9.4 | 3B+1S | 995 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43322412 | 1272 | 221.9508 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 67083202 | 5968 | 143.232 | 5.968 | 8.8 | 8.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43323756 | 1344 | 225.2011 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 67089603 | 6401 | 153.624 | 6.401 | 8.2 | 8.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43325180 | 1424 | 222.4652 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 67095747 | 6144 | 147.456 | 6.144 | 7.6 | 7.6 | 3B+1S | 1037 | 0 | 1179 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43326548 | 1368 | 222.6562 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 | 1.36
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 67101763 | 6016 | 144.384 | 6.016 | 7.1 | 7.1 | 3B+1S | 1037 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43327884 | 1336 | 222.0745 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 67107894 | 6131 | 147.144 | 6.131 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43329236 | 1352 | 220.5187 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 67113834 | 5940 | 142.56 | 5.94 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43330564 | 1328 | 223.569 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 67119793 | 5959 | 143.016 | 5.959 | 6 | 6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43331916 | 1352 | 226.8837 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 67125642 | 5849 | 140.376 | 5.849 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43333252 | 1336 | 228.4151 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 67131439 | 5797 | 139.128 | 5.797 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43334584 | 1332 | 229.774 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 139 | 67137248 | 5809 | 139.416 | 5.809 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43335916 | 1332 | 229.2994 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 67143014 | 5766 | 138.384 | 5.766 | 5 | 5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43337244 | 1328 | 230.3156 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 135 | 67148781 | 5767 | 138.408 | 5.767 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43338572 | 1328 | 230.2757 | 100% | 0% | 100% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 134 | 67154341 | 5560 | 133.44 | 5.56 | 3.9 | 3.9 | 2B+1S | 1129 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43339688 | 1116 | 200.7194 | 100% | 0% | 0% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 67159811 | 5470 | 131.28 | 5.47 | 3 | 3 | 2B+1S | 1097 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43340788 | 1100 | 201.0969 | 100% | 0% | 0% | 100% | 100% | 0% | 10085262 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 123 | 67165063 | 5252 | 126.048 | 5.252 | 2.4 | 2.4 | 2B+1S | 1046 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43341844 | 1056 | 201.0663 | 100% | 0% | 0% | 100% | 100% | 0% | 10085262 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 104 | 67169514 | 4451 | 106.824 | 4.451 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1068 | N/A | N/A | N/A | N/A | 43342660 | 816 | 183.3296 | 0% | 0% | 0% | 100% | 100% | 38% | 10086236 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 95 | 67173639 | 4125 | 99 | 4.125 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 43343364 | 704 | 170.6667 | 0% | 0% | 0% | 100% | 100% | 38% | 10087587 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127357 | 127.357 | 127.357 | [12 empty] | 26620 | 26620 | 209.0187 | [6 empty] | 7213 | 7213 | 1.26 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (38%)

## JAN 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67173639 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43343364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10087587 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 98 | 67177524 | 3885 | 93.24 | 3.885 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43344042 | 678 | 174.5174 | 0% | 0% | 0% | 100% | 100% | 46% | 10088947 | 1360 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 92 | 67181414 | 3890 | 93.36 | 3.89 | 8.2 | 8.2 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43344732 | 690 | 177.3779 | 0% | 0% | 0% | 100% | 100% | 46% | 10090312 | 1365 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 67185321 | 3907 | 93.768 | 3.907 | 9.1 | 9.1 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43345440 | 708 | 181.2132 | 0% | 0% | 0% | 100% | 100% | 46% | 10091690 | 1378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 99 | 67189521 | 4200 | 100.8 | 4.2 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43346140 | 700 | 166.6667 | 0% | 0% | 0% | 100% | 100% | 46% | 10092098 | 408 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 105 | 67193740 | 4219 | 101.256 | 4.219 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43346860 | 720 | 170.6566 | 0% | 0% | 0% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 67198713 | 4973 | 119.352 | 4.973 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43347748 | 888 | 178.5642 | 0% | 0% | 0% | 100% | 100% | 0% | 10092098 | 0 | 1.3 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 142 | 67204615 | 5902 | 141.648 | 5.902 | 9.3 | 9.3 | 3B+1S | 0 | 1048 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43349028 | 1280 | 216.8756 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 67210813 | 6198 | 148.752 | 6.198 | 8.7 | 8.7 | 3B+1S | 0 | 1048 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43350412 | 1384 | 223.2978 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 67217074 | 6261 | 150.264 | 6.261 | 8 | 8 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43351805 | 1393 | 222.4884 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 67223165 | 6091 | 146.184 | 6.091 | 7.4 | 7.4 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43353172 | 1367 | 224.4295 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 | 1.33
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 67229334 | 6169 | 148.056 | 6.169 | 6.9 | 6.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43354552 | 1380 | 223.6991 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 67235446 | 6112 | 146.688 | 6.112 | 6.5 | 6.5 | 3B+1S | 0 | 1036 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43355916 | 1364 | 223.1675 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 67241582 | 6136 | 147.264 | 6.136 | 6.1 | 6.1 | 3B+1S | 0 | 1027 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43357300 | 1384 | 225.5541 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 67247317 | 5735 | 137.64 | 5.735 | 5.7 | 5.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43358620 | 1320 | 230.1656 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 67253185 | 5868 | 140.832 | 5.868 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43359968 | 1348 | 229.7205 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 67258894 | 5709 | 137.016 | 5.709 | 5.2 | 5.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43361300 | 1332 | 233.3158 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 67264753 | 5859 | 140.616 | 5.859 | 5 | 5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43362644 | 1344 | 229.3907 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 67270497 | 5744 | 137.856 | 5.744 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43363976 | 1332 | 231.8942 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 67276251 | 5754 | 138.096 | 5.754 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43365308 | 1332 | 231.4911 | 0% | 100% | 100% | 100% | 100% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 130 | 67281776 | 5525 | 132.6 | 5.525 | 3.6 | 3.6 | 2B+1S | 0 | 1128 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43366436 | 1128 | 204.1629 | 0% | 100% | 100% | 100% | 0% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 110 | 129 | 67287163 | 5387 | 129.288 | 5.387 | 2.7 | 2.7 | 2B+1S | 0 | 1129 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43367532 | 1096 | 203.4528 | 0% | 100% | 100% | 100% | 0% | 0% | 10092098 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 125 | 67292484 | 5321 | 127.704 | 5.321 | 2 | 2 | 2B+1S | 0 | 1047 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43368604 | 1072 | 201.4659 | 0% | 100% | 100% | 100% | 0% | 0% | 10092098 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 103 | 67297010 | 4526 | 108.624 | 4.526 | 2.8 | 2.8 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 43369444 | 840 | 185.5943 | 0% | 0% | 100% | 100% | 0% | 40% | 10093009 | 911 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 102 | 67301440 | 4430 | 106.32 | 4.43 | 4.1 | 4.1 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43370244 | 800 | 180.5869 | 0% | 0% | 100% | 100% | 0% | 40% | 10094178 | 1169 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127801 | 127.801 | 127.801 | [12 empty] | 26880 | 26880 | 210.327 | [6 empty] | 6591 | 6591 | 1.2317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (46%)
XCV1- CLOSED @ 3:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67301440 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43370244 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10094178 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 95 | 67305444 | 4004 | 96.096 | 4.004 | 5.5 | 5.5 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43370960 | 716 | 178.8212 | 0% | 0% | 100% | 100% | 0% | 45% | 10095481 | 1303 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 92 | 67309472 | 4028 | 96.672 | 4.028 | 6.9 | 6.9 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43371676 | 716 | 177.7557 | 0% | 0% | 100% | 100% | 0% | 45% | 10096866 | 1385 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 93 | 67313380 | 3908 | 93.792 | 3.908 | 8.3 | 8.3 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43372364 | 688 | 176.0491 | 0% | 0% | 100% | 100% | 0% | 45% | 10098239 | 1373 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 96 | 67317277 | 3897 | 93.528 | 3.897 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43373052 | 688 | 176.5461 | 0% | 0% | 100% | 100% | 0% | 45% | 10099251 | 1012 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 107 | 67321649 | 4372 | 104.928 | 4.372 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43373756 | 704 | 161.0247 | 0% | 0% | 100% | 100% | 0% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 114 | 67326608 | 4959 | 119.016 | 4.959 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43374644 | 888 | 179.0684 | 0% | 0% | 100% | 100% | 0% | 0% | 10099251 | 0 | 1.33 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 146 | 67332797 | 6189 | 148.536 | 6.189 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43375996 | 1352 | 218.4521 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 67338818 | 6021 | 144.504 | 6.021 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43377332 | 1336 | 221.8901 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 67344902 | 6084 | 146.016 | 6.084 | 7.8 | 7.8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43378672 | 1340 | 220.2498 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 67351356 | 6454 | 154.896 | 6.454 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43380070 | 1398 | 216.6099 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 | 1.28
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 67357897 | 6541 | 156.984 | 6.541 | 6.7 | 6.7 | 3B+1S | 1037 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43381498 | 1428 | 218.3152 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 67363524 | 5627 | 135.048 | 5.627 | 6.3 | 6.3 | 3B+1S | 1036 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43382804 | 1306 | 232.0953 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 67369617 | 6093 | 146.232 | 6.093 | 6 | 6 | 3B+1S | 996 | 0 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43384148 | 1344 | 220.581 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 67375561 | 5944 | 142.656 | 5.944 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43385524 | 1376 | 231.4939 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 67381398 | 5837 | 140.088 | 5.837 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43386860 | 1336 | 228.8847 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 67387124 | 5726 | 137.424 | 5.726 | 5.3 | 5.3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43388180 | 1320 | 230.5274 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 67392923 | 5799 | 139.176 | 5.799 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43389512 | 1332 | 229.6948 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 67398727 | 5804 | 139.296 | 5.804 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43390828 | 1316 | 226.7402 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 67404431 | 5704 | 136.896 | 5.704 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43392116 | 1288 | 225.8065 | 100% | 0% | 100% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 67409945 | 5514 | 132.336 | 5.514 | 3.7 | 3.7 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43393228 | 1112 | 201.6685 | 100% | 0% | 0% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 67415364 | 5419 | 130.056 | 5.419 | 3 | 3 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43394308 | 1080 | 199.2988 | 100% | 0% | 0% | 100% | 100% | 0% | 10099251 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 123 | 67420648 | 5284 | 126.816 | 5.284 | 2.3 | 2.3 | 2B+1S | 995 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43395372 | 1064 | 201.3626 | 100% | 0% | 0% | 100% | 100% | 0% | 10099251 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 104 | 67424993 | 4345 | 104.28 | 4.345 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43396168 | 796 | 183.1991 | 0% | 0% | 0% | 100% | 100% | 40% | 10100224 | 973 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 97 | 67429257 | 4264 | 102.336 | 4.264 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43396940 | 772 | 181.0507 | 0% | 0% | 0% | 100% | 100% | 40% | 10101476 | 1252 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127817 | 127.817 | 127.817 | [12 empty] | 26696 | 26696 | 208.8611 | [6 empty] | 7298 | 7298 | 1.2217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (46%)
XCV2- CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27000 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67429257 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43396940 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10101476 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 95 | 67433374 | 4117 | 98.808 | 4.117 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 43397676 | 736 | 178.7709 | 0% | 0% | 0% | 100% | 100% | 45% | 10102779 | 1303 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 96 | 67437410 | 4036 | 96.864 | 4.036 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43398400 | 724 | 179.3855 | 0% | 0% | 0% | 100% | 100% | 45% | 10104118 | 1339 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 67441303 | 3893 | 93.432 | 3.893 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43399084 | 684 | 175.7 | 0% | 0% | 0% | 100% | 100% | 45% | 10105449 | 1331 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 94 | 67445211 | 3908 | 93.792 | 3.908 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43399768 | 684 | 175.0256 | 0% | 0% | 0% | 100% | 100% | 45% | 10106090 | 641 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 108 | 67449371 | 4160 | 99.84 | 4.16 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43400452 | 684 | 164.4231 | 0% | 0% | 0% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 129 | 67454397 | 5026 | 120.624 | 5.026 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43401336 | 884 | 175.8854 | 0% | 0% | 0% | 100% | 100% | 0% | 10106090 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 148 | 67460319 | 5922 | 142.128 | 5.922 | 9.2 | 9.2 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43402660 | 1324 | 223.5731 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 157 | 67466528 | 6209 | 149.016 | 6.209 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43404060 | 1400 | 225.4791 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 150 | 67472720 | 6192 | 148.608 | 6.192 | 7.9 | 7.9 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43405452 | 1392 | 224.8062 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 67478936 | 6216 | 149.184 | 6.216 | 7.2 | 7.2 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43406852 | 1400 | 225.2252 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 | 1.27
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 67485206 | 6270 | 150.48 | 6.27 | 6.8 | 6.8 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43408264 | 1412 | 225.1994 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 67491288 | 6082 | 145.968 | 6.082 | 5.9 | 5.9 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43409652 | 1388 | 228.2144 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 139 | 67497264 | 5976 | 143.424 | 5.976 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43411012 | 1360 | 227.577 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 67503136 | 5872 | 140.928 | 5.872 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43412368 | 1356 | 230.9264 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 67508935 | 5799 | 139.176 | 5.799 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43413708 | 1340 | 231.0743 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 67514656 | 5721 | 137.304 | 5.721 | 5 | 5 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43415044 | 1336 | 233.5256 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 67520405 | 5749 | 137.976 | 5.749 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43416371 | 1327 | 230.8228 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 67526154 | 5749 | 137.976 | 5.749 | 4.6 | 4.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43417700 | 1329 | 231.1706 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 67531906 | 5752 | 138.048 | 5.752 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43419028 | 1328 | 230.8762 | 0% | 100% | 100% | 100% | 100% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 132 | 67537499 | 5593 | 134.232 | 5.593 | 3.4 | 3.4 | 2B+1S | 0 | 1148 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43420160 | 1132 | 202.3959 | 0% | 100% | 100% | 100% | 0% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 133 | 67542931 | 5432 | 130.368 | 5.432 | 2.6 | 2.6 | 2B+1S | 0 | 1117 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43421264 | 1104 | 203.2401 | 0% | 100% | 100% | 100% | 0% | 0% | 10106090 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 125 | 67548289 | 5358 | 128.592 | 5.358 | 1.9 | 1.9 | 2B+1S | 0 | 1076 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43422336 | 1072 | 200.0747 | 0% | 100% | 100% | 100% | 0% | 0% | 10106090 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 103 | 67552764 | 4475 | 107.4 | 4.475 | 2.7 | 2.7 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 43423156 | 820 | 183.2402 | 0% | 0% | 100% | 100% | 0% | 40% | 10107024 | 934 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 101 | 67557072 | 4308 | 103.392 | 4.308 | 3.9 | 3.9 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43423940 | 784 | 181.987 | 0% | 0% | 100% | 100% | 0% | 40% | 10108209 | 1185 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127815 | 127.815 | 127.815 | [12 empty] | 27000 | 27000 | 211.2428 | [6 empty] | 6733 | 6733 | 1.2017 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (46%)
XCV1- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:23 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26944 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67557072 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43423940 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10108209 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 110 | 67561085 | 4013 | 96.312 | 4.013 | 5.4 | 5.4 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43424672 | 732 | 182.4072 | 0% | 0% | 100% | 100% | 0% | 47% | 10109536 | 1327 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 93 | 67565000 | 3915 | 93.96 | 3.915 | 6.8 | 6.8 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43425396 | 724 | 184.9298 | 0% | 0% | 100% | 100% | 0% | 47% | 10110905 | 1369 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 67568809 | 3809 | 91.416 | 3.809 | 8.2 | 8.2 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43426076 | 680 | 178.5245 | 0% | 0% | 100% | 100% | 0% | 47% | 10112277 | 1372 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 95 | 67572691 | 3882 | 93.168 | 3.882 | 9.3 | 9.3 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43426764 | 688 | 177.2282 | 0% | 0% | 100% | 100% | 0% | 47% | 10113307 | 1030 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 108 | 67577010 | 4319 | 103.656 | 4.319 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 1185 | 0 | N/A | N/A | N/A | N/A | 43427476 | 712 | 164.853 | 0% | 0% | 100% | 100% | 0% | 47% | 10113541 | 234 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 67582052 | 5042 | 121.008 | 5.042 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43428372 | 896 | 177.7073 | 0% | 0% | 100% | 100% | 0% | 0% | 10113541 | 0 | 1.34 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 139 | 67588107 | 6055 | 145.32 | 6.055 | 9.3 | 9.3 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43429728 | 1356 | 223.9472 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 67594304 | 6197 | 148.728 | 6.197 | 8.7 | 8.7 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43431124 | 1396 | 225.2703 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 67600536 | 6232 | 149.568 | 6.232 | 8 | 8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43432516 | 1392 | 223.3633 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 67606716 | 6180 | 148.32 | 6.18 | 7.3 | 7.3 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43433908 | 1392 | 225.2427 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 | 1.32
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 67612955 | 6239 | 149.736 | 6.239 | 6.9 | 6.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43435300 | 1392 | 223.1127 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 147 | 67618995 | 6040 | 144.96 | 6.04 | 6.5 | 6.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43436676 | 1376 | 227.8146 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 137 | 67624885 | 5890 | 141.36 | 5.89 | 6.1 | 6.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43438028 | 1352 | 229.5416 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 135 | 67630647 | 5762 | 138.288 | 5.762 | 5.9 | 5.9 | 3B+1S | 0 | 1010 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43439364 | 1336 | 231.8639 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 67636392 | 5745 | 137.88 | 5.745 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43440696 | 1332 | 231.8538 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 67642091 | 5699 | 136.776 | 5.699 | 5.5 | 5.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43442024 | 1328 | 233.0233 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 67647882 | 5791 | 138.984 | 5.791 | 5.3 | 5.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43443356 | 1332 | 230.0121 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 67653699 | 5817 | 139.608 | 5.817 | 5 | 5 | 3B+1S | 0 | 1005 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43444676 | 1320 | 226.9211 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 67659364 | 5665 | 135.96 | 5.665 | 4.7 | 4.7 | 3B+1S | 0 | 1006 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43445968 | 1292 | 228.0671 | 0% | 100% | 100% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 129 | 67664850 | 5486 | 131.664 | 5.486 | 3.8 | 3.8 | 2B+1S | 0 | 1099 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43447076 | 1108 | 201.9686 | 0% | 100% | 0% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 67670356 | 5506 | 132.144 | 5.506 | 3.1 | 3.1 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43448172 | 1096 | 199.0556 | 0% | 100% | 0% | 100% | 100% | 0% | 10113541 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 126 | 67675694 | 5338 | 128.112 | 5.338 | 2.6 | 2.6 | 2B+1S | 0 | 1047 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43449244 | 1072 | 200.8243 | 0% | 100% | 0% | 100% | 100% | 0% | 10113541 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 107 | 67680225 | 4531 | 108.744 | 4.531 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1078 | N/A | N/A | N/A | N/A | 43450084 | 840 | 185.3895 | 0% | 0% | 0% | 100% | 100% | 40% | 10114433 | 892 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 101 | 67684529 | 4304 | 103.296 | 4.304 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43450884 | 800 | 185.8736 | 0% | 0% | 0% | 100% | 100% | 40% | 10115577 | 1144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127457 | 127.457 | 127.457 | [12 empty] | 26944 | 26944 | 211.3968 | [6 empty] | 7368 | 7368 | 1.25 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (47%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JAN 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26604 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67684529 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43450884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10115577 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 97 | 67688593 | 4064 | 97.536 | 4.064 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43451640 | 756 | 186.0236 | 0% | 0% | 0% | 100% | 100% | 46% | 10116817 | 1240 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 67692643 | 4050 | 97.2 | 4.05 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43452356 | 716 | 176.7901 | 0% | 0% | 0% | 100% | 100% | 46% | 10118019 | 1202 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 67696456 | 3813 | 91.512 | 3.813 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 43453044 | 688 | 180.4354 | 0% | 0% | 0% | 100% | 100% | 46% | 10119298 | 1279 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 93 | 67700244 | 3788 | 90.912 | 3.788 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43453724 | 680 | 179.5143 | 0% | 0% | 0% | 100% | 100% | 46% | 10120244 | 946 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 67704260 | 4016 | 96.384 | 4.016 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 43454400 | 676 | 168.3267 | 0% | 0% | 0% | 100% | 100% |  | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 118 | 67709107 | 4847 | 116.328 | 4.847 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43455204 | 804 | 165.8758 | 0% | 0% | 0% | 100% | 100% | 0% | 10120244 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 139 | 67714513 | 5406 | 129.744 | 5.406 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43456332 | 1128 | 208.657 | 0% | 0% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 67720777 | 6264 | 150.336 | 6.264 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43457722 | 1390 | 221.9029 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 67726903 | 6126 | 147.024 | 6.126 | 8.6 | 8.6 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43459084 | 1362 | 222.331 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 67733312 | 6409 | 153.816 | 6.409 | 8 | 8 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43460479 | 1395 | 217.6627 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 | 1.19
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 67739487 | 6175 | 148.2 | 6.175 | 7.5 | 7.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43461876 | 1397 | 226.2348 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 67745663 | 6176 | 148.224 | 6.176 | 7 | 7 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43463248 | 1372 | 222.1503 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 148 | 67751754 | 6091 | 146.184 | 6.091 | 6.5 | 6.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43464612 | 1364 | 223.937 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 146 | 67757714 | 5960 | 143.04 | 5.96 | 6 | 6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43465956 | 1344 | 225.5034 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 67763628 | 5914 | 141.936 | 5.914 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43467300 | 1344 | 227.2574 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 67769512 | 5884 | 141.216 | 5.884 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43468636 | 1336 | 227.0564 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 67775348 | 5836 | 140.064 | 5.836 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43469972 | 1336 | 228.9239 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 140 | 67781162 | 5814 | 139.536 | 5.814 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43471308 | 1336 | 229.7902 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 132 | 67786907 | 5745 | 137.88 | 5.745 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43472628 | 1320 | 229.765 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 67792546 | 5639 | 135.336 | 5.639 | 3.4 | 3.4 | 2B+1S | 0 | 1098 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43473764 | 1136 | 201.4542 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 67797833 | 5287 | 126.888 | 5.287 | 2.7 | 2.7 | 2B+1S | 0 | 1068 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43474812 | 1048 | 198.2221 | 0% | 100% | 100% | 100% | 100% | 0% | 10120244 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 123 | 67803165 | 5332 | 127.968 | 5.332 | 2.2 | 2.2 | 2B+1S | 0 | 1035 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43475860 | 1048 | 196.5491 | 0% | 100% | 100% | 100% | 0% | 0% | 10120244 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 108 | 67807702 | 4537 | 108.888 | 4.537 | 2.9 | 2.9 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 43476692 | 832 | 183.3811 | 0% | 0% | 100% | 100% | 0% | 40% | 10121072 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 100 | 67812071 | 4369 | 104.856 | 4.369 | 3.9 | 3.9 | 2B | 0 | 0 | 1016 | 1185 | 0 | N/A | N/A | N/A | N/A | 43477488 | 796 | 182.1927 | 0% | 0% | 100% | 100% | 0% | 40% | 10122082 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127542 | 127.542 | 127.542 | [12 empty] | 26604 | 26604 | 208.5901 | [6 empty] | 6505 | 6505 | 1.1833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (46%)
XCV1- CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## JAN 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24772 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67812071 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43477488 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10122082 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 100 | 67816218 | 4147 | 99.528 | 4.147 | 5.3 | 5.3 | 2B | 0 | 0 | 998 | 1185 | 0 | N/A | N/A | N/A | N/A | 43478228 | 740 | 178.4422 | 0% | 0% | 100% | 100% | 0% | 47% | 10123369 | 1287 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 91 | 67820284 | 4066 | 97.584 | 4.066 | 6.7 | 6.7 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43478952 | 724 | 178.062 | 0% | 0% | 100% | 100% | 0% | 47% | 10124704 | 1335 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 92 | 67824162 | 3878 | 93.072 | 3.878 | 8.2 | 8.2 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43479632 | 680 | 175.3481 | 0% | 0% | 100% | 100% | 0% | 47% | 10126118 | 1414 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 111 | 93 | 67827900 | 3738 | 89.712 | 3.738 | 9.5 | 9.5 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43480292 | 660 | 176.565 | 0% | 0% | 100% | 100% | 0% | 47% | 10127288 | 1170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 87 | 83 | 67831273 | 3373 | 80.952 | 3.373 | 10.4 | 10.4 | 1B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A | 43480780 | 488 | 144.6783 | 0% | 0% | 0% | 100% | 0% |  | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 25 | 17.6056 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 88 | 88 | 67834912 | 3639 | 87.336 | 3.639 | 10 | 10 | 1B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A | 43481252 | 472 | 129.706 | 0% | 0% | 0% | 100% | 0% | 0% | 10127288 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 20 | 14.0845 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 84 | 82 | 67838509 | 3597 | 86.328 | 3.597 | 10 | 10 | 1B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A | 43481732 | 480 | 133.4445 | 0% | 0% | 0% | 100% | 0% | 0% | 10127288 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 67844267 | 5758 | 138.192 | 5.758 | 10 | 10 | 3B+1S | 996 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43482916 | 1184 | 205.627 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 141 | 67850226 | 5959 | 143.016 | 5.959 | 9.8 | 9.8 | 3B+1S | 996 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43484220 | 1304 | 218.8287 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 67856133 | 5907 | 141.768 | 5.907 | 9.4 | 9.4 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43485524 | 1304 | 220.755 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 | 1.08
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 67862321 | 6188 | 148.512 | 6.188 | 8.9 | 8.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43486900 | 1376 | 222.3659 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 142 | 67868355 | 6034 | 144.816 | 6.034 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43488244 | 1344 | 222.7378 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 67874393 | 6038 | 144.912 | 6.038 | 8.1 | 8.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43489604 | 1360 | 225.2401 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 144 | 67880506 | 6113 | 146.712 | 6.113 | 7.7 | 7.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43491004 | 1400 | 229.0201 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 143 | 67886171 | 5665 | 135.96 | 5.665 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43492324 | 1320 | 233.0097 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 67891947 | 5776 | 138.624 | 5.776 | 6.8 | 6.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43493660 | 1336 | 231.3019 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 67897742 | 5795 | 139.08 | 5.795 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43495012 | 1352 | 233.3046 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 67903373 | 5631 | 135.144 | 5.631 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1168 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43496300 | 1288 | 228.7338 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 67909061 | 5688 | 136.512 | 5.688 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43497596 | 1296 | 227.8481 | 100% | 0% | 100% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 118 | 67914421 | 5360 | 128.64 | 5.36 | 5.3 | 5.3 | 2B+1S | 1016 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43498680 | 1084 | 202.2388 | 100% | 0% | 0% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 125 | 67919690 | 5269 | 126.456 | 5.269 | 4.9 | 4.9 | 2B+1S | 1016 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43499724 | 1044 | 198.1401 | 100% | 0% | 0% | 100% | 100% | 0% | 10127288 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 121 | 67924852 | 5162 | 123.888 | 5.162 | 4.5 | 4.5 | 2B+1S | 996 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 43500728 | 1004 | 194.4983 | 100% | 0% | 0% | 100% | 100% | 0% | 10127288 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 105 | 67929307 | 4455 | 106.92 | 4.455 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43501524 | 796 | 178.6756 | 0% | 0% | 0% | 100% | 100% | 35% | 10128914 | 1626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 101 | 67933545 | 4238 | 101.712 | 4.238 | 6.4 | 6.4 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43502260 | 736 | 173.6668 | 0% | 0% | 0% | 100% | 100% | 35% | 10129945 | 1031 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 121474 | 121.474 | 121.474 | [12 empty] | 24772 | 24772 | 203.9284 | [6 empty] | 7863 | 7863 | 1.0717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (47%)
BP2 STILL OPERATIONAL AS OF 4:00AM
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (10.4M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
4:00 AM - SP2 WAS TRIP AND ALL MOV UN- ABLE TO OPERATE DUE TO NO ELECTRICAL POWER SUPPLY.
AFFECTED THE POWER SUPPLY AT ALL VFD AND ALL MOV DUE TO TRIP THE MAIN BREAKER OF THE POWER SUPPLY OF SP2 MOV
DISCHARGE PRESSURE 48 PSI DUE ALL MOV UNABLE TO OPERATE AND ALL VFD NO POWER SUPPLY AS OF 6:00AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 7:16 AM TO 12:01 PM AS PER SCHEDULE
POWER SUPPLY OF ALL MOV AND ALL VFD @7:10AM
BP3 STARTED @ 7:12AM
BP1 STARTED @ 7:14AM
SP1 STARTED @ 7:16AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (35%)

## JAN 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26068 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 67933545 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43502260 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10129945 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 93 | 67937646 | 4101 | 98.424 | 4.101 | 7.7 | 7.7 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43502964 | 704 | 171.6654 | 0% | 0% | 0% | 100% | 100% | 40% | 10131309 | 1364 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 92 | 67941475 | 3829 | 91.896 | 3.829 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43503628 | 664 | 173.4134 | 0% | 0% | 0% | 100% | 100% | 40% | 10132398 | 1089 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 93 | 67945410 | 3935 | 94.44 | 3.935 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 846 | N/A | N/A | N/A | N/A | 43504292 | 664 | 168.7421 | 0% | 0% | 0% | 100% | 100% | 40% | 10132930 | 532 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 97 | 67949294 | 3884 | 93.216 | 3.884 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43504924 | 632 | 162.7188 | 0% | 0% | 0% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 104 | 67953461 | 4167 | 100.008 | 4.167 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43505604 | 680 | 163.1869 | 0% | 0% | 0% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 144 | 67958324 | 4863 | 116.712 | 4.863 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43506380 | 776 | 159.5723 | 0% | 0% | 0% | 100% | 100% | 0% | 10132930 | 0 | 1.39 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 139 | 67964394 | 6070 | 145.68 | 6.07 | 9.4 | 9.4 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43507700 | 1320 | 217.4629 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 152 | 67970365 | 5971 | 143.304 | 5.971 | 8.9 | 8.9 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43509020 | 1320 | 221.0685 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 67976486 | 6121 | 146.904 | 6.121 | 8.4 | 8.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43510388 | 1368 | 223.4929 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 67982799 | 6313 | 151.512 | 6.313 | 7.9 | 7.9 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43511780 | 1392 | 220.4974 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 | 1.11
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 67988867 | 6068 | 145.632 | 6.068 | 7.4 | 7.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43513140 | 1360 | 224.1266 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 148 | 67995042 | 6175 | 148.2 | 6.175 | 7.1 | 7.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43514516 | 1376 | 222.834 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 145 | 68001005 | 5963 | 143.112 | 5.963 | 6.9 | 6.9 | 3B+1S | 995 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43515844 | 1328 | 222.7067 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 138 | 68006816 | 5811 | 139.464 | 5.811 | 6.6 | 6.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43517160 | 1316 | 226.467 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 139 | 68012568 | 5752 | 138.048 | 5.752 | 6.4 | 6.4 | 3B+1S | 1006 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43518484 | 1324 | 230.1808 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 68018260 | 5692 | 136.608 | 5.692 | 6.2 | 6.2 | 3B+1S | 1008 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43519780 | 1296 | 227.688 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 68024064 | 5804 | 139.296 | 5.804 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43521100 | 1320 | 227.4294 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 68029745 | 5681 | 136.344 | 5.681 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43522376 | 1276 | 224.6083 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 68035382 | 5637 | 135.288 | 5.637 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43523632 | 1256 | 222.8136 | 100% | 0% | 100% | 100% | 100% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 132 | 68040856 | 5474 | 131.376 | 5.474 | 4.7 | 4.7 | 2B+1S | 1078 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43524724 | 1092 | 199.4885 | 100% | 0% | 100% | 100% | 0% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 68046195 | 5339 | 128.136 | 5.339 | 3.9 | 3.9 | 2B+1S | 1078 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43525792 | 1068 | 200.0375 | 100% | 0% | 100% | 100% | 0% | 0% | 10132930 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 128 | 68051321 | 5126 | 123.024 | 5.126 | 3.4 | 3.4 | 2B+1S | 1015 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43526804 | 1012 | 197.4249 | 100% | 0% | 100% | 100% | 0% | 0% | 10132930 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 103 | 68055772 | 4451 | 106.824 | 4.451 | 4.3 | 4.3 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 43527600 | 796 | 178.8362 | 0% | 0% | 100% | 100% | 0% | 35% | 10133779 | 849 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 129 | 95 | 68059955 | 4183 | 100.392 | 4.183 | 5.5 | 5.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 43528328 | 728 | 174.0378 | 0% | 0% | 100% | 100% | 0% | 35% | 10134895 | 1116 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126410 | 126.41 | 126.41 | [12 empty] | 26068 | 26068 | 206.2179 | [6 empty] | 4950 | 4950 | 1.13 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 2:25 AM,WATER ELEVATION (10.4M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (35%)

## JAN 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26228 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68059955 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43528328 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10134895 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 96 | 68063840 | 3885 | 93.24 | 3.885 | 6.8 | 6.8 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 43528999 | 671 | 172.7156 | 0% | 0% | 100% | 100% | 0% | 40% | 10136113 | 1218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 98 | 68067732 | 3892 | 93.408 | 3.892 | 7.9 | 7.9 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 43529679 | 680 | 174.7174 | 0% | 0% | 100% | 100% | 0% | 40% | 10137328 | 1215 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 92 | 68071631 | 3899 | 93.576 | 3.899 | 9.3 | 9.3 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 43530368 | 689 | 176.712 | 0% | 0% | 100% | 100% | 0% | 40% | 10138567 | 1239 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 97 | 68075756 | 4125 | 99 | 4.125 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 43531033 | 665 | 161.2121 | 0% | 0% | 100% | 100% | 0% | 40% | 10138703 | 136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 108 | 68079894 | 4138 | 99.312 | 4.138 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 43531708 | 675 | 163.1223 | 0% | 0% | 100% | 100% | 0% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 68085153 | 5259 | 126.216 | 5.259 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43532660 | 952 | 181.023 | 0% | 0% | 100% | 100% | 0% | 0% | 10138703 | 0 | 1.33 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 144 | 68091137 | 5984 | 143.616 | 5.984 | 9.3 | 9.3 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43533960 | 1300 | 217.246 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 68097104 | 5967 | 143.208 | 5.967 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43535292 | 1332 | 223.2278 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 68103156 | 6052 | 145.248 | 6.052 | 8.3 | 8.3 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43536640 | 1348 | 222.7363 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 68109383 | 6227 | 149.448 | 6.227 | 7.8 | 7.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43538024 | 1384 | 222.2579 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 | 1.36
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 68115784 | 6401 | 153.624 | 6.401 | 7.3 | 7.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43539426 | 1402 | 219.0283 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 146 | 68121932 | 6148 | 147.552 | 6.148 | 6.9 | 6.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43540772 | 1346 | 218.933 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 137 | 68128024 | 6092 | 146.208 | 6.092 | 6.7 | 6.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43542156 | 1384 | 227.1832 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 68134056 | 6032 | 144.768 | 6.032 | 6.4 | 6.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43543556 | 1400 | 232.0955 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 68139532 | 5476 | 131.424 | 5.476 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43544780 | 1224 | 223.5208 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 68145180 | 5648 | 135.552 | 5.648 | 6 | 6 | 3B+1S | 1005 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43546036 | 1256 | 222.3796 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 68150788 | 5608 | 134.592 | 5.608 | 5.7 | 5.7 | 3B+1S | 1007 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43547292 | 1256 | 223.9658 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 68156428 | 5640 | 135.36 | 5.64 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 43548556 | 1264 | 224.1135 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 130 | 68162025 | 5597 | 134.328 | 5.597 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43549804 | 1248 | 222.9766 | 100% | 0% | 100% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 127 | 68167416 | 5391 | 129.384 | 5.391 | 4.6 | 4.6 | 2B+1S | 1077 | 0 |  | 1185 | 1188 | N/A | N/A | N/A | N/A | 43550900 | 1096 | 203.3018 | 100% | 0% | 0% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 132 | 68172802 | 5386 | 129.264 | 5.386 | 3.8 | 3.8 | 2B+1S | 1045 | 0 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 43551972 | 1072 | 199.0345 | 100% | 0% | 0% | 100% | 100% | 0% | 10138703 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 122 | 68178035 | 5233 | 125.592 | 5.233 | 3.3 | 3.3 | 2B+1S | 995 | 0 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 43553004 | 1032 | 197.21 | 100% | 0% | 0% | 100% | 100% | 0% | 10138703 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 102 | 68182466 | 4431 | 106.344 | 4.431 | 4.2 | 4.2 | 2B | 0 | 0 |  | 1185 | 1047 | N/A | N/A | N/A | N/A | 43553788 | 784 | 176.9352 | 0% | 0% | 0% | 100% | 100% | 35% | 10139524 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 93 | 68186808 | 4342 | 104.208 | 4.342 | 5.4 | 5.4 | 2B | 0 | 0 |  | 1185 | 946 | N/A | N/A | N/A | N/A | 43554556 | 768 | 176.877 | 0% | 0% | 0% | 100% | 100% | 35% | 10140623 | 1099 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126853 | 126.853 | 126.853 | [12 empty] | 26228 | 26228 | 206.759 | [6 empty] | 5728 | 5728 | 1.2517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (35%)

## JAN 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26158 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68186808 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43554556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10140623 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 92 | 68190680 | 3872 | 92.928 | 3.872 | 6.7 | 6.7 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43555236 | 680 | 175.6198 | 0% | 0% | 0% | 100% | 100% | 40% | 10141877 | 1254 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 91 | 68194581 | 3901 | 93.624 | 3.901 | 7.9 | 7.9 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43555916 | 680 | 174.3143 | 0% | 0% | 0% | 100% | 100% | 40% | 10143146 | 1269 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 91 | 68198440 | 3859 | 92.616 | 3.859 | 9.3 | 9.3 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43556572 | 656 | 169.9922 | 0% | 0% | 0% | 100% | 100% | 40% | 10144400 | 1254 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 97 | 68202387 | 3947 | 94.728 | 3.947 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43557232 | 660 | 167.2156 | 0% | 0% | 0% | 100% | 100% | 40% | 10144709 | 309 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 103 | 68206573 | 4186 | 100.464 | 4.186 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43557900 | 668 | 159.5796 | 0% | 0% | 0% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 124 | 68211793 | 5220 | 125.28 | 5.22 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43558796 | 896 | 171.6475 | 0% | 0% | 0% | 100% | 100% | 0% | 10144709 | 0 | 1.25 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 146 | 68217414 | 5621 | 134.904 | 5.621 | 9.4 | 9.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43560036 | 1240 | 220.6013 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 68223742 | 6328 | 151.872 | 6.328 | 8.8 | 8.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43561434 | 1398 | 220.9229 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 149 | 68230396 | 6654 | 159.696 | 6.654 | 8.2 | 8.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43562820 | 1386 | 208.2958 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 68236132 | 5736 | 137.664 | 5.736 | 7.7 | 7.7 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43564202 | 1382 | 240.9344 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 | 1.36
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 68242319 | 6187 | 148.488 | 6.187 | 7.2 | 7.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43565564 | 1362 | 220.139 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 145 | 68248334 | 6015 | 144.36 | 6.015 | 6.8 | 6.8 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43566940 | 1376 | 228.7614 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 138 | 68254302 | 5968 | 143.232 | 5.968 | 6.5 | 6.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43568288 | 1348 | 225.8713 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 68260097 | 5795 | 139.08 | 5.795 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43569620 | 1332 | 229.8533 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 133 | 68265784 | 5687 | 136.488 | 5.687 | 6 | 6 | 3B+1S | 1005 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43570916 | 1296 | 227.8882 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 68271495 | 5711 | 137.064 | 5.711 | 5.8 | 5.8 | 3B+1S | 1006 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43572188 | 1272 | 222.7281 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 68277184 | 5689 | 136.536 | 5.689 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43573460 | 1272 | 223.5894 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 68282863 | 5679 | 136.296 | 5.679 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43574720 | 1260 | 221.87 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 134 | 68288498 | 5635 | 135.24 | 5.635 | 5 | 5 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43575980 | 1260 | 223.6025 | 100% | 0% | 100% | 100% | 100% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 68293902 | 5404 | 129.696 | 5.404 | 4.2 | 4.2 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43577068 | 1088 | 201.3323 | 100% | 0% | 100% | 100% | 0% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 127 | 68299246 | 5344 | 128.256 | 5.344 | 3.5 | 3.5 | 2B+1S | 1047 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43578132 | 1064 | 199.1018 | 100% | 0% | 100% | 100% | 0% | 0% | 10144709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 121 | 68304432 | 5186 | 124.464 | 5.186 | 3 | 3 | 2B+1S | 1026 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 43579156 | 1024 | 197.4547 | 100% | 0% | 100% | 100% | 0% | 0% | 10144709 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 103 | 68308798 | 4366 | 104.784 | 4.366 | 3.7 | 3.7 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 43579940 | 784 | 179.5694 | 0% | 0% | 100% | 100% | 0% | 35% | 10145464 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 98 | 68313035 | 4237 | 101.688 | 4.237 | 5 | 5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43580714 | 774 | 182.6764 | 0% | 0% | 100% | 100% | 0% | 35% | 10146531 | 1067 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126227 | 126.227 | 126.227 | [12 empty] | 26158 | 26158 | 207.2298 | [6 empty] | 5908 | 5908 | 1.225 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:26 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (35%)

## JAN 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26482 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68313035 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43580714 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10146531 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 94 | 68317091 | 4056 | 97.344 | 4.056 | 5.9 | 5.9 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 43581404 | 690 | 170.1183 | 0% | 0% | 100% | 100% | 0% | 40% | 10147501 | 970 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 68321011 | 3920 | 94.08 | 3.92 | 7.1 | 7.1 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43582092 | 688 | 175.5102 | 0% | 0% | 100% | 100% | 0% | 40% | 10148736 | 1235 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 68324806 | 3795 | 91.08 | 3.795 | 8.4 | 8.4 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 43582756 | 664 | 174.9671 | 0% | 0% | 100% | 100% | 0% | 40% | 10149997 | 1261 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 96 | 68328585 | 3779 | 90.696 | 3.779 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43583412 | 656 | 173.5909 | 0% | 0% | 100% | 100% | 0% | 40% | 10150854 | 857 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 103 | 68332772 | 4187 | 100.488 | 4.187 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43584088 | 676 | 161.4521 | 0% | 0% | 100% | 100% | 0% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 68337750 | 4978 | 119.472 | 4.978 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43584924 | 836 | 167.9389 | 0% | 0% | 100% | 100% | 0% | 0% | 10150854 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 144 | 68343571 | 5821 | 139.704 | 5.821 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43586196 | 1272 | 218.5192 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 68349728 | 6157 | 147.768 | 6.157 | 8.9 | 8.9 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43587564 | 1368 | 222.1861 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 68355901 | 6173 | 148.152 | 6.173 | 8.4 | 8.4 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43588940 | 1376 | 222.9062 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 68362177 | 6276 | 150.624 | 6.276 | 7.9 | 7.9 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43590328 | 1388 | 221.16 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 | 1.31
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 146 | 68368345 | 6168 | 148.032 | 6.168 | 7.4 | 7.4 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43591692 | 1364 | 221.1414 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Normal operation schedule
59:00 | 12:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 148 | 68374507 | 6162 | 147.888 | 6.162 | 7 | 7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43593060 | 1368 | 222.0058 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 134 | 68380556 | 6049 | 145.176 | 6.049 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43594420 | 1360 | 224.8306 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 68386438 | 5882 | 141.168 | 5.882 | 6.4 | 6.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43595772 | 1352 | 229.8538 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 138 | 68392134 | 5696 | 136.704 | 5.696 | 6.1 | 6.1 | 3B+1S | 1005 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43597088 | 1316 | 231.0393 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 68397838 | 5704 | 136.896 | 5.704 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43598396 | 1308 | 229.3128 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 68403531 | 5693 | 136.632 | 5.693 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43599692 | 1296 | 227.648 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 68409300 | 5769 | 138.456 | 5.769 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43601012 | 1320 | 228.8092 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 68414963 | 5663 | 135.912 | 5.663 | 5 | 5 | 3B+1S | 1006 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43602316 | 1304 | 230.2666 | 100% | 0% | 100% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 111 | 131 | 68420410 | 5447 | 130.728 | 5.447 | 4.1 | 4.1 | 2B+1S | 1129 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43603420 | 1104 | 202.6804 | 100% | 0% | 0% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 130 | 68425897 | 5487 | 131.688 | 5.487 | 3.2 | 3.2 | 2B+1S | 1129 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43604536 | 1116 | 203.3898 | 100% | 0% | 0% | 100% | 100% | 0% | 10150854 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 121 | 68431240 | 5343 | 128.232 | 5.343 | 2.6 | 2.6 | 2B+1S | 994 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43605592 | 1056 | 197.6418 | 100% | 0% | 0% | 100% | 100% | 0% | 10150854 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 106 | 68435697 | 4457 | 106.968 | 4.457 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1067 | N/A | N/A | N/A | N/A | 43606400 | 808 | 181.2879 | 0% | 0% | 0% | 100% | 100% | 40% | 10151830 | 976 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 104 | 68440063 | 4366 | 104.784 | 4.366 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43607196 | 796 | 182.3179 | 0% | 0% | 0% | 100% | 100% | 40% | 10153079 | 1249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127028 | 127.028 | 127.028 | [12 empty] | 26482 | 26482 | 208.4737 | 0% | 0% | 0% | 0% | 0% |  | 6548 | 6548 | 1.22 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:20 AM (40%)
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (40%)

## JAN 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26516 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68440063 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43607196 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10153079 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 104 | 68444176 | 4113 | 98.712 | 4.113 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 43607932 | 736 | 178.9448 | 0% | 0% | 0% | 100% | 100% | 45% | 10154388 | 1309 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 92 | 68448111 | 3935 | 94.44 | 3.935 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43608636 | 704 | 178.9072 | 0% | 0% | 0% | 100% | 100% | 45% | 10155791 | 1403 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 68451993 | 3882 | 93.168 | 3.882 | 9.2 | 9.2 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43609324 | 688 | 177.2282 | 0% | 0% | 0% | 100% | 100% | 45% | 10157158 | 1367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 90 | 68455904 | 3911 | 93.864 | 3.911 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 846 | N/A | N/A | N/A | N/A | 43609972 | 648 | 165.6865 | 0% | 0% | 0% | 100% | 100% | 45% | 10157433 | 275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 109 | 68460095 | 4191 | 100.584 | 4.191 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43610648 | 676 | 161.298 | 0% | 0% | 0% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 123 | 68465058 | 4963 | 119.112 | 4.963 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43611484 | 836 | 168.4465 | 0% | 0% | 0% | 100% | 100% | 0% | 10157433 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 146 | 68470952 | 5894 | 141.456 | 5.894 | 9.4 | 9.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43612756 | 1272 | 215.8127 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 68477063 | 6111 | 146.664 | 6.111 | 8.8 | 8.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43614108 | 1352 | 221.2404 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 68483326 | 6263 | 150.312 | 6.263 | 8.2 | 8.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43615500 | 1392 | 222.2577 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 68489602 | 6276 | 150.624 | 6.276 | 7.7 | 7.7 | 3B+1S | 1037 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43616884 | 1384 | 220.5226 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 | 1.27
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 68495918 | 6316 | 151.584 | 6.316 | 7.2 | 7.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43618282 | 1398 | 221.3426 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 68501871 | 5953 | 142.872 | 5.953 | 6.8 | 6.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43619620 | 1338 | 224.7606 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 134 | 68507906 | 6035 | 144.84 | 6.035 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43620996 | 1376 | 228.0033 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 136 | 68513702 | 5796 | 139.104 | 5.796 | 6 | 6 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43622348 | 1352 | 233.2643 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 68519402 | 5700 | 136.8 | 5.7 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43623660 | 1312 | 230.1754 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 68525280 | 5878 | 141.072 | 5.878 | 5.5 | 5.5 | 3B+1S | 1020 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43625036 | 1376 | 234.0932 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 68530848 | 5568 | 133.632 | 5.568 | 5.2 | 5.2 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43626332 | 1296 | 232.7586 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 68536619 | 5771 | 138.504 | 5.771 | 4.9 | 4.9 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43627668 | 1336 | 231.5023 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 135 | 68542248 | 5629 | 135.096 | 5.629 | 4.7 | 4.7 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43628968 | 1300 | 230.9469 | 100% | 0% | 100% | 100% | 100% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 68547610 | 5362 | 128.688 | 5.362 | 3.8 | 3.8 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43630060 | 1092 | 203.6554 | 100% | 0% | 100% | 100% | 0% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 127 | 68552961 | 5351 | 128.424 | 5.351 | 3.1 | 3.1 | 2B+1S | 1077 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 43631132 | 1072 | 200.3364 | 100% | 0% | 100% | 100% | 0% | 0% | 10157433 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 68558232 | 5271 | 126.504 | 5.271 | 2.5 | 2.5 | 2B+1S | 1016 | 0 | 1169 | 1185 | 0 | N/A | N/A | N/A | N/A | 43632164 | 1032 | 195.7883 | 100% | 0% | 100% | 100% | 0% | 0% | 10157433 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 106 | 68562572 | 4340 | 104.16 | 4.34 | 3.4 | 3.4 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43632948 | 784 | 180.6452 | 0% | 0% | 100% | 100% | 0% | 40% | 10158380 | 947 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 100 | 68566840 | 4268 | 102.432 | 4.268 | 4.6 | 4.6 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 43633712 | 764 | 179.0066 | 0% | 0% | 100% | 100% | 0% | 40% | 10159458 | 1078 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126777 | 126.777 | 126.777 | [12 empty] | 26516 | 26516 | 209.1547 | 0% | 0% | 0% | 0% | 0% |  | 6379 | 6379 | 1.1933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:26 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)

## JAN 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26596 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68566840 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43633712 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10159458 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 96 | 68570944 | 4104 | 98.496 | 4.104 | 6 | 6 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43634452 | 740 | 180.3119 | 0% | 0% | 100% | 100% | 0% | 45% | 10160736 | 1278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 92 | 68574929 | 3985 | 95.64 | 3.985 | 7.3 | 7.3 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43635168 | 716 | 179.6738 | 0% | 0% | 100% | 100% | 0% | 45% | 10162044 | 1308 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 91 | 68578760 | 3831 | 91.944 | 3.831 | 8.6 | 8.6 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43635844 | 676 | 176.4552 | 0% | 0% | 100% | 100% | 0% | 45% | 10163357 | 1313 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 95 | 68582619 | 3859 | 92.616 | 3.859 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43636512 | 668 | 173.1018 | 0% | 0% | 100% | 100% | 0% | 45% | 10164104 | 747 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 68586735 | 4116 | 98.784 | 4.116 | 9.5 | 9.5 | 2B | 0 | 0 | 897 | 1185 | 0 | N/A | N/A | N/A | N/A | 43637176 | 664 | 161.3217 | 0% | 0% | 100% | 100% | 0% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 123 | 68591542 | 4807 | 115.368 | 4.807 | 9.5 | 9.5 | 2B | 0 | 0 | 1129 | 1185 | 0 | N/A | N/A | N/A | N/A | 43637932 | 756 | 157.2706 | 0% | 0% | 100% | 100% | 0% | 0% | 10164104 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 147 | 68597213 | 5671 | 136.104 | 5.671 | 9.5 | 9.5 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43639124 | 1192 | 210.1922 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 68603386 | 6173 | 148.152 | 6.173 | 9.1 | 9.1 | 3B+1S | 996 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43640492 | 1368 | 221.6102 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 68609447 | 6061 | 145.464 | 6.061 | 8.7 | 8.7 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43641828 | 1336 | 220.4257 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 68615885 | 6438 | 154.512 | 6.438 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43643232 | 1404 | 218.0801 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 | 1.09
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 68621953 | 6068 | 145.632 | 6.068 | 7.7 | 7.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43644592 | 1360 | 224.1266 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 146 | 68628307 | 6354 | 152.496 | 6.354 | 7.2 | 7.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43645986 | 1394 | 219.3894 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 68634512 | 6205 | 148.92 | 6.205 | 6.8 | 6.8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43647382 | 1396 | 224.9799 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 68640269 | 5757 | 138.168 | 5.757 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43648714 | 1332 | 231.3705 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 142 | 68646210 | 5941 | 142.584 | 5.941 | 6 | 6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43650054 | 1340 | 225.5513 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 68652063 | 5853 | 140.472 | 5.853 | 5.7 | 5.7 | 3B+1S | 1011 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43651412 | 1358 | 232.0178 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 68657858 | 5795 | 139.08 | 5.795 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43652740 | 1328 | 229.1631 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 68663652 | 5794 | 139.056 | 5.794 | 4.9 | 4.9 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43654076 | 1336 | 230.5834 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 132 | 68669429 | 5777 | 138.648 | 5.777 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43655404 | 1328 | 229.8771 | 100% | 0% | 100% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 133 | 68674926 | 5497 | 131.928 | 5.497 | 3.7 | 3.7 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43656508 | 1104 | 200.8368 | 100% | 0% | 0% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 68680235 | 5309 | 127.416 | 5.309 | 3 | 3 | 2B+1S | 1087 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43657572 | 1064 | 200.4144 | 100% | 0% | 0% | 100% | 100% | 0% | 10164104 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 129 | 68685656 | 5421 | 130.104 | 5.421 | 2.3 | 2.3 | 2B+1S | 1087 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43658652 | 1080 | 199.2252 | 100% | 0% | 0% | 100% | 100% | 0% | 10164104 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 110 | 68690270 | 4614 | 110.736 | 4.614 | 3 | 3 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 43659492 | 840 | 182.0546 | 0% | 0% | 0% | 100% | 100% | 40% | 10164943 | 839 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 105 | 68694749 | 4479 | 107.496 | 4.479 | 4 | 4 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43660308 | 816 | 182.1835 | 0% | 0% | 0% | 100% | 100% | 40% | 10165839 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127909 | 127.909 | 127.909 | [12 empty] | 26596 | 26596 | 207.9291 | 0% | 0% | 0% | 0% | 0% |  | 6381 | 6381 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (40%)

## JAN 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-01-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26024 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68694749 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43660308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10165839 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 101 | 68698995 | 4246 | 101.904 | 4.246 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 996 | N/A | N/A | N/A | N/A | 43661068 | 760 | 178.992 | 0% | 0% | 0% | 100% | 100% | 45% | 10167129 | 1290 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 92 | 68702989 | 3994 | 95.856 | 3.994 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43661776 | 708 | 177.2659 | 0% | 0% | 0% | 100% | 100% | 45% | 10168585 | 1456 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 91 | 68706933 | 3944 | 94.656 | 3.944 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 43662464 | 688 | 174.4422 | 0% | 0% | 0% | 100% | 100% | 45% | 10170021 | 1436 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 95 | 68710814 | 3881 | 93.144 | 3.881 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43663132 | 668 | 172.1206 | 0% | 0% | 0% | 100% | 100% | 45% | 10170989 | 968 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 100 | 68714947 | 4133 | 99.192 | 4.133 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43663800 | 668 | 161.6259 | 0% | 0% | 0% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 23 | 16.1972 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 119 | 68719674 | 4727 | 113.448 | 4.727 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 43664528 | 728 | 154.0089 | 0% | 0% | 0% | 100% | 100% | 0% | 10170989 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 127 | 68725082 | 5408 | 129.792 | 5.408 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43665532 | 1004 | 185.6509 | 0% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 148 | 68730936 | 5854 | 140.496 | 5.854 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43666756 | 1224 | 209.0878 | 0% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 68737084 | 6148 | 147.552 | 6.148 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43668100 | 1344 | 218.6077 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 68743382 | 6298 | 151.152 | 6.298 | 8.6 | 8.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43669492 | 1392 | 221.0225 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 | 1.34
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 152 | 68749557 | 6175 | 148.2 | 6.175 | 8.1 | 8.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43670848 | 1356 | 219.5951 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 68755713 | 6156 | 147.744 | 6.156 | 7.7 | 7.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43672220 | 1372 | 222.872 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 68761824 | 6111 | 146.664 | 6.111 | 7.3 | 7.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43673596 | 1376 | 225.1677 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 68767575 | 5751 | 138.024 | 5.751 | 6.8 | 6.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43674908 | 1312 | 228.1342 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 144 | 68773714 | 6139 | 147.336 | 6.139 | 6.5 | 6.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43676302 | 1394 | 227.0728 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 6 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 139 | 68779436 | 5722 | 137.328 | 5.722 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43677612 | 1310 | 228.9409 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 68785286 | 5850 | 140.4 | 5.85 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43678964 | 1352 | 231.1111 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 139 | 68790988 | 5702 | 136.848 | 5.702 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43680260 | 1296 | 227.2887 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 | 0.74 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 68796793 | 5805 | 139.32 | 5.805 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1177 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43681576 | 1316 | 226.7011 | 100% | 0% | 100% | 100% | 100% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 133 | 68802334 | 5541 | 132.984 | 5.541 | 4.7 | 4.7 | 2B+1S | 1117 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43682704 | 1128 | 203.5734 | 100% | 0% | 100% | 100% | 0% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 134 | 68807658 | 5324 | 127.776 | 5.324 | 3.7 | 3.7 | 2B+1S | 1066 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43683760 | 1056 | 198.3471 | 100% | 0% | 100% | 100% | 0% | 0% | 10170989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 134 | 68813026 | 5368 | 128.832 | 5.368 | 3.2 | 3.2 | 2B+1S | 995 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43684812 | 1052 | 195.9762 | 100% | 0% | 100% | 100% | 0% | 0% | 10170989 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 103 | 68817447 | 4421 | 106.104 | 4.421 | 4.1 | 4.1 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43685596 | 784 | 177.3354 | 0% | 0% | 100% | 100% | 0% | 40% | 10171870 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 104 | 68821673 | 4226 | 101.424 | 4.226 | 5.3 | 5.3 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 43686332 | 736 | 174.16 | 0% | 0% | 100% | 100% | 0% | 40% | 10173010 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126924 | 126.924 | 126.924 | [12 empty] | 26024 | 26024 | 205.0361 | 0% | 0% | 0% | 0% | 0% |  | 7171 | 7171 | 1.1533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:41 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JAN 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)