## FEB 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26680 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68821673 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43686332 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10173010 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 94 | 68825692 | 4019 | 96.456 | 4.019 | 6.6 | 6.6 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 43687044 | 712 | 177.1585 | 0% | 0% | 100% | 100% | 0% | 45% | 10174311 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 92 | 68829570 | 3878 | 93.072 | 3.878 | 8 | 8 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 43687724 | 680 | 175.3481 | 0% | 0% | 100% | 100% | 0% | 45% | 10175666 | 1355 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 90 | 68833296 | 3726 | 89.424 | 3.726 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 43688372 | 648 | 173.913 | 0% | 0% | 100% | 100% | 0% | 45% | 10177028 | 1362 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 95 | 68837360 | 4064 | 97.536 | 4.064 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43689032 | 660 | 162.4016 | 0% | 0% | 100% | 100% | 0% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 103 | 68841444 | 4084 | 98.016 | 4.084 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43689692 | 660 | 161.6063 | 0% | 0% | 100% | 100% | 0% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 119 | 68846418 | 4974 | 119.376 | 4.974 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43690492 | 800 | 160.8363 | 0% | 0% | 100% | 100% | 0% | 0% | 10177028 | 0 | 1.24 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 149 | 68852336 | 5918 | 142.032 | 5.918 | 9.4 | 9.4 | 3B+1S | 1020 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43691768 | 1276 | 215.6134 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 152 | 68858431 | 6095 | 146.28 | 6.095 | 8.9 | 8.9 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43693124 | 1356 | 222.4774 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 68864625 | 6194 | 148.656 | 6.194 | 8.4 | 8.4 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43694492 | 1368 | 220.8589 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 122 | 68870833 | 6208 | 148.992 | 6.208 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43695880 | 1388 | 223.5825 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 | 1.21
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 68876988 | 6155 | 147.72 | 6.155 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43697244 | 1364 | 221.6084 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 68883153 | 6165 | 147.96 | 6.165 | 6.7 | 6.7 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43698616 | 1372 | 222.5466 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 144 | 68889147 | 5994 | 143.856 | 5.994 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43699976 | 1360 | 226.8936 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 139 | 68895223 | 6076 | 145.824 | 6.076 | 5.7 | 5.7 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43701372 | 1396 | 229.7564 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 68900824 | 5601 | 134.424 | 5.601 | 5.5 | 5.5 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43702652 | 1280 | 228.5306 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 68906621 | 5797 | 139.128 | 5.797 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43703984 | 1332 | 229.774 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 143 | 68912426 | 5805 | 139.32 | 5.805 | 5 | 5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43705316 | 1332 | 229.4574 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 140 | 68918293 | 5867 | 140.808 | 5.867 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43706644 | 1328 | 226.3508 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 68924216 | 5923 | 142.152 | 5.923 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43707980 | 1336 | 225.5614 | 100% | 0% | 100% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 140 | 68930056 | 5840 | 140.16 | 5.84 | 3.5 | 3.5 | 2B+1S | 1149 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43709180 | 1200 | 205.4795 | 100% | 0% | 0% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 138 | 68935778 | 5722 | 137.328 | 5.722 | 2.6 | 2.6 | 2B+1S | 1149 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43710308 | 1128 | 197.1339 | 100% | 0% | 0% | 100% | 100% | 0% | 10177028 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 129 | 68941250 | 5472 | 131.328 | 5.472 | 1.8 | 1.8 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43711396 | 1088 | 198.8304 | 100% | 0% | 0% | 100% | 100% | 0% | 10177028 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 107 | 68945908 | 4658 | 111.792 | 4.658 | 2.8 | 2.8 | 2B | 0 | 0 | 0 | 1185 | 1068 | N/A | N/A | N/A | N/A | 43712228 | 832 | 178.6174 | 0% | 0% | 0% | 100% | 100% | 40% | 10178114 | 1086 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 105 | 68950324 | 4416 | 105.984 | 4.416 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 1036 | N/A | N/A | N/A | N/A | 43713012 | 784 | 177.5362 | 0% | 0% | 0% | 100% | 100% | 40% | 10179304 | 1190 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128651 | 128.651 | 128.651 | [12 empty] | 26680 | 26680 | 207.3828 | 0% | 0% | 0% | 0% | 0% |  | 6294 | 6294 | 1.2067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (40%)

## FEB 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 68950324 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43713012 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10179304 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 96 | 68954413 | 4089 | 98.136 | 4.089 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 43713712 | 700 | 171.191 | 0% | 0% | 0% | 100% | 100% | 47% | 10180604 | 1300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 68958508 | 4095 | 98.28 | 4.095 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 43714410 | 698 | 170.4518 | 0% | 0% | 0% | 100% | 100% | 47% | 10181914 | 1310 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 99 | 68962623 | 4115 | 98.76 | 4.115 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43715156 | 746 | 181.288 | 0% | 0% | 0% | 100% | 100% | 47% | 10183224 | 1310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 121 | 98 | 68966676 | 4053 | 97.272 | 4.053 | 9.4 | 9.4 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43715856 | 700 | 172.7116 | 0% | 0% | 0% | 100% | 100% | 47% | 10184277 | 1053 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 128 | 68970887 | 4211 | 101.064 | 4.211 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43716564 | 708 | 168.1311 | 0% | 0% | 0% | 100% | 100% | 47% | 10184342 | 65 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 126 | 68976203 | 5316 | 127.584 | 5.316 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43717500 | 936 | 176.0722 | 0% | 0% | 0% | 100% | 100% | 0% | 10184342 |  | 1.34 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 144 | 68982225 | 6022 | 144.528 | 6.022 | 9.2 | 9.2 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43718824 | 1324 | 219.8605 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 68988394 | 6169 | 148.056 | 6.169 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43720200 | 1376 | 223.0507 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 144 | 68994596 | 6202 | 148.848 | 6.202 | 7.9 | 7.9 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43721580 | 1380 | 222.5089 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 69000860 | 6264 | 150.336 | 6.264 | 7.2 | 7.2 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43722960 | 1380 | 220.3065 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 | 1.3
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 69007113 | 6253 | 150.072 | 6.253 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43724340 | 1380 | 220.6941 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 152 | 69013285 | 6172 | 148.128 | 6.172 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43725708 | 1368 | 221.6461 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 69019246 | 5961 | 143.064 | 5.961 | 5.8 | 5.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43727068 | 1360 | 228.1496 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 69025086 | 5840 | 140.16 | 5.84 | 5.4 | 5.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43728408 | 1340 | 229.4521 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 69031077 | 5991 | 143.784 | 5.991 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43729746 | 1338 | 223.335 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 69036477 | 5400 | 129.6 | 5.4 | 5 | 5 | 3B+1S | 1004 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43731068 | 1322 | 244.8148 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 69042234 | 5757 | 138.168 | 5.757 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43732404 | 1336 | 232.0653 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 135 | 69047806 | 5572 | 133.728 | 5.572 | 4.7 | 4.7 | 3B+1S | 984 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43733700 | 1296 | 232.5915 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 | 0.62 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 69053467 | 5661 | 135.864 | 5.661 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43735004 | 1304 | 230.348 | 100% | 0% | 100% | 100% | 100% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 132 | 69059061 | 5594 | 134.256 | 5.594 | 3.8 | 3.8 | 2B+1S | 1078 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43736132 | 1128 | 201.6446 | 100% | 0% | 100% | 100% | 0% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 122 | 69064172 | 5111 | 122.664 | 5.111 | 3.2 | 3.2 | 2B+1S | 1036 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43737140 | 1008 | 197.2217 | 100% | 0% | 100% | 100% | 0% | 0% | 10184342 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 128 | 69069573 | 5401 | 129.624 | 5.401 | 2.7 | 2.7 | 2B+1S | 1036 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43738204 | 1064 | 197.0006 | 100% | 0% | 100% | 100% | 0% | 0% | 10184342 | 0 | 0.61 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 110 | 69074220 | 4647 | 111.528 | 4.647 | 3.6 | 3.6 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 43739072 | 868 | 186.7872 | 0% | 0% | 100% | 100% | 0% | 40% | 10185302 | 960 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 107 | 69078644 | 4424 | 106.176 | 4.424 | 4.9 | 4.9 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 43739872 | 800 | 180.8318 | 0% | 0% | 100% | 100% | 0% | 40% | 10186411 | 1109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128320 | 128.32 | 128.32 | [12 empty] | 26860 | 26860 | 209.3204 | 0% | 0% | 0% | 0% | 0% |  | 7107 | 7107 | 0.99167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 4:06 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)

## FEB 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26644 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69078644 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43739872 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10186411 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 103 | 69082828 | 4184 | 100.416 | 4.184 | 6.1 | 6.1 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43740608 | 736 | 175.9082 | 0% | 0% | 100% | 100% | 0% | 45% | 10187570 | 1159 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 100 | 69086818 | 3990 | 95.76 | 3.99 | 7.3 | 7.3 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43741308 | 700 | 175.4386 | 0% | 0% | 100% | 100% | 0% | 45% | 10188690 | 1120 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 69090802 | 3984 | 95.616 | 3.984 | 8.5 | 8.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43741996 | 688 | 172.6908 | 0% | 0% | 100% | 100% | 0% | 45% | 10189906 | 1216 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 95 | 69094690 | 3888 | 93.312 | 3.888 | 9.5 | 9.5 | 2B | 0 | 0 | 945 | 1185 | 0 | N/A | N/A | N/A | N/A | 43742676 | 680 | 174.8971 | 0% | 0% | 100% | 100% | 0% | 45% | 10190733 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 108 | 69098904 | 4214 | 101.136 | 4.214 | 9.5 | 9.5 | 2B | 0 | 0 | 978 | 1185 | 0 | N/A | N/A | N/A | N/A | 43743372 | 696 | 165.1637 | 0% | 0% | 100% | 100% | 0% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 69103895 | 4991 | 119.784 | 4.991 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43744196 | 824 | 165.0972 | 0% | 0% | 100% | 100% | 0% | 0% | 10190733 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 150 | 69109898 | 6003 | 144.072 | 6.003 | 9.1 | 9.1 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43745500 | 1304 | 217.2247 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 69116197 | 6299 | 151.176 | 6.299 | 8.5 | 8.5 | 3B+1S | 1068 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43746896 | 1396 | 221.6225 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 69122391 | 6194 | 148.656 | 6.194 | 7.8 | 7.8 | 3B+1S | 1068 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43748268 | 1372 | 221.5047 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 69128624 | 6233 | 149.592 | 6.233 | 7.1 | 7.1 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43749660 | 1392 | 223.3275 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 | 1.23
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 69134860 | 6236 | 149.664 | 6.236 | 6.5 | 6.5 | 3B+1S | 1067 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43751052 | 1392 | 223.22 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 69141017 | 6157 | 147.768 | 6.157 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43752432 | 1380 | 224.1351 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 137 | 69146985 | 5968 | 143.232 | 5.968 | 5.6 | 5.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43753780 | 1348 | 225.8713 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 69152913 | 5928 | 142.272 | 5.928 | 5.2 | 5.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43755140 | 1360 | 229.4197 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 69158624 | 5711 | 137.064 | 5.711 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43756460 | 1320 | 231.1329 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 69164328 | 5704 | 136.896 | 5.704 | 5 | 5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43757776 | 1316 | 230.7153 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 69170116 | 5788 | 138.912 | 5.788 | 4.9 | 4.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43759112 | 1336 | 230.8224 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 69175826 | 5710 | 137.04 | 5.71 | 4.7 | 4.7 | 3B+1S | 995 | 0 | 1157 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43760428 | 1316 | 230.4729 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 139 | 69181573 | 5747 | 137.928 | 5.747 | 4.6 | 4.6 | 3B+1S | 995 | 0 | 1147 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43761740 | 1312 | 228.293 | 100% | 0% | 100% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 132 | 69187044 | 5471 | 131.304 | 5.471 | 3.9 | 3.9 | 2B+1S | 1078 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43762844 | 1104 | 201.7913 | 100% | 0% | 0% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 130 | 69192436 | 5392 | 129.408 | 5.392 | 3.2 | 3.2 | 2B+1S | 1048 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43763916 | 1072 | 198.8131 | 100% | 0% | 0% | 100% | 100% | 0% | 10190733 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 132 | 69197650 | 5214 | 125.136 | 5.214 | 2.9 | 2.9 | 2B+1S | 995 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43764956 | 1040 | 199.463 | 100% | 0% | 0% | 100% | 100% | 0% | 10190733 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 105 | 69202130 | 4480 | 107.52 | 4.48 | 3.9 | 3.9 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43765788 | 832 | 185.7143 | 0% | 0% | 0% | 100% | 100% | 45% | 10191762 | 1029 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 139 | 129 | 69206226 | 4096 | 98.304 | 4.096 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 43766516 | 728 | 177.7344 | 0% | 0% | 0% | 100% | 100% | 45% | 10193258 | 1496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127582 | 127.582 | 127.582 | [12 empty] | 26644 | 26644 | 208.8382 | 0% | 0% | 0% | 0% | 0% |  | 6847 | 6847 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
B1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (45%)

## FEB 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69206226 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43766516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10193258 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 94 | 69210167 | 3941 | 94.584 | 3.941 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43767216 | 700 | 177.6199 | 0% | 0% | 0% | 100% | 100% | 47% | 10194598 | 1340 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 69214055 | 3888 | 93.312 | 3.888 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43767904 | 688 | 176.9547 | 0% | 0% | 0% | 100% | 100% | 47% | 10195997 | 1399 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 99 | 98 | 69217959 | 3904 | 93.696 | 3.904 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43768592 | 688 | 176.2295 | 0% | 0% | 0% | 100% | 100% | 47% | 10197070 | 1073 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 107 | 100 | 69222047 | 4088 | 98.112 | 4.088 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43769284 | 692 | 169.2759 | 0% | 0% | 0% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 108 | 69226407 | 4360 | 104.64 | 4.36 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43769996 | 712 | 163.3028 | 0% | 0% | 0% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 69231502 | 5095 | 122.28 | 5.095 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43770900 | 904 | 177.4289 | 0% | 0% | 0% | 100% | 100% | 0% | 10197070 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 146 | 69237420 | 5918 | 142.032 | 5.918 | 9.3 | 9.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43772224 | 1324 | 223.7242 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 69243565 | 6145 | 147.48 | 6.145 | 8.7 | 8.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43773604 | 1380 | 224.5728 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 145 | 69249745 | 6180 | 148.32 | 6.18 | 8.1 | 8.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43774979 | 1375 | 222.4919 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 69255933 | 6188 | 148.512 | 6.188 | 7.6 | 7.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43776364 | 1385 | 223.8203 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 | 1.25
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 69262133 | 6200 | 148.8 | 6.2 | 7.1 | 7.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43777744 | 1380 | 222.5806 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 69268255 | 6122 | 146.928 | 6.122 | 6.7 | 6.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43779116 | 1372 | 224.1098 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 69274202 | 5947 | 142.728 | 5.947 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43780464 | 1348 | 226.6689 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 137 | 69280183 | 5981 | 143.544 | 5.981 | 6 | 6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43781828 | 1364 | 228.0555 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 69286126 | 5943 | 142.632 | 5.943 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43783196 | 1368 | 230.1868 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 69291712 | 5586 | 134.064 | 5.586 | 5.7 | 5.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43784484 | 1288 | 230.5764 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 69297418 | 5706 | 136.944 | 5.706 | 5.6 | 5.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43785804 | 1320 | 231.3354 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 69303070 | 5652 | 135.648 | 5.652 | 5.5 | 5.5 | 3B+1S | 985 | 0 | 1186 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43787100 | 1296 | 229.2994 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 69308966 | 5896 | 141.504 | 5.896 | 5.4 | 5.4 | 3B+1S | 984 | 0 | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43788436 | 1336 | 226.5943 | 100% | 0% | 100% | 100% | 100% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 124 | 69314295 | 5329 | 127.896 | 5.329 | 4.8 | 4.8 | 2B+1S | 1078 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43789532 | 1096 | 205.6671 | 100% | 0% | 100% | 100% | 0% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 69319567 | 5272 | 126.528 | 5.272 | 4.1 | 4.1 | 2B+1S | 1077 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43790564 | 1032 | 195.7511 | 100% | 0% | 100% | 100% | 0% | 0% | 10197070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 133 | 69325092 | 5525 | 132.6 | 5.525 | 3.4 | 3.4 | 2B+1S | 1078 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 43791652 | 1088 | 196.9231 | 100% | 0% | 100% | 100% | 0% | 0% | 10197070 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 111 | 69329750 | 4658 | 111.792 | 4.658 | 4.3 | 4.3 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 43792516 | 864 | 185.4873 | 0% | 0% | 100% | 100% | 0% | 45% | 10198039 | 969 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 101 | 69334079 | 4329 | 103.896 | 4.329 | 5.7 | 5.7 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 43793284 | 768 | 177.4082 | 0% | 0% | 100% | 100% | 0% | 45% | 10199389 | 1350 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127853 | 127.853 | 127.853 | [12 empty] | 26768 | 26768 | 209.3654 | 0% | 0% | 0% | 0% | 0% |  | 6131 | 6131 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:22 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (45%)

## FEB 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26608 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69334079 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43793284 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10199389 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 101 | 69338248 | 4169 | 100.056 | 4.169 | 7.1 | 7.1 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 43794000 | 716 | 171.7438 | 0% | 0% | 100% | 100% | 0% | 47% | 10200763 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 99 | 69342174 | 3926 | 94.224 | 3.926 | 8.5 | 8.5 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 43794672 | 672 | 171.1666 | 0% | 0% | 100% | 100% | 0% | 47% | 10202098 | 1335 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 92 | 69345926 | 3752 | 90.048 | 3.752 | 9.5 | 9.5 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 43795344 | 672 | 179.1045 | 0% | 0% | 100% | 100% | 0% | 47% | 10203333 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 97 | 69350047 | 4121 | 98.904 | 4.121 | 9.5 | 9.5 | 2B | 0 | 0 | 974 | 1185 | 0 | N/A | N/A | N/A | N/A | 43796020 | 676 | 164.0379 | 0% | 0% | 100% | 100% | 0% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 105 | 69354245 | 4198 | 100.752 | 4.198 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43796716 | 696 | 165.7932 | 0% | 0% | 100% | 100% | 0% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 121 | 69359407 | 5162 | 123.888 | 5.162 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43797612 | 896 | 173.5761 | 0% | 0% | 100% | 100% | 0% | 0% | 10203333 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 141 | 69365161 | 5754 | 138.096 | 5.754 | 9.4 | 9.4 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43798880 | 1268 | 220.3684 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 69371306 | 6145 | 147.48 | 6.145 | 9.3 | 9.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43800244 | 1364 | 221.9691 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 69377492 | 6186 | 148.464 | 6.186 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43801620 | 1376 | 222.4378 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 151 | 69383730 | 6238 | 149.712 | 6.238 | 8.1 | 8.1 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43803004 | 1384 | 221.866 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 | 1.32
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 69389944 | 6214 | 149.136 | 6.214 | 7.4 | 7.4 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43804396 | 1392 | 224.0103 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 69396072 | 6128 | 147.072 | 6.128 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43805768 | 1372 | 223.8903 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 69402075 | 6003 | 144.072 | 6.003 | 6.4 | 6.4 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43807132 | 1364 | 227.2197 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 69407963 | 5888 | 141.312 | 5.888 | 6 | 6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43808488 | 1356 | 230.2989 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 69413597 | 5634 | 135.216 | 5.634 | 5.7 | 5.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43809780 | 1292 | 229.322 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 69419436 | 5839 | 140.136 | 5.839 | 5.5 | 5.5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43811124 | 1344 | 230.1764 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 69425147 | 5711 | 137.064 | 5.711 | 5.3 | 5.3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43812432 | 1308 | 229.0317 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 69430925 | 5778 | 138.672 | 5.778 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43813756 | 1324 | 229.145 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 69436733 | 5808 | 139.392 | 5.808 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43815092 | 1336 | 230.0275 | 100% | 0% | 100% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 131 | 69442246 | 5513 | 132.312 | 5.513 | 4.1 | 4.1 | 2B+1S | 1108 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43816212 | 1120 | 203.1562 | 100% | 0% | 0% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 69447642 | 5396 | 129.504 | 5.396 | 3.3 | 3.3 | 2B+1S | 1088 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43817292 | 1080 | 200.1483 | 100% | 0% | 0% | 100% | 100% | 0% | 10203333 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 127 | 69453021 | 5379 | 129.096 | 5.379 | 2.8 | 2.8 | 2B+1S | 1016 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43818356 | 1064 | 197.8063 | 100% | 0% | 0% | 100% | 100% | 0% | 10203333 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 102 | 69457384 | 4363 | 104.712 | 4.363 | 3.9 | 3.9 | 2B | 0 | 0 | 1047 | 0 | 1097 | N/A | N/A | N/A | N/A | 43819148 | 792 | 181.5265 | 0% | 0% | 100% | 0% | 100% | 45% | 10204477 | 1144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 141 | 98 | 69461568 | 4184 | 100.416 | 4.184 | 5.5 | 5.5 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 43819892 | 744 | 177.8203 | 0% | 0% | 100% | 100% | 0% | 45% | 10205920 | 1443 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127489 | 127.489 | 127.489 | [12 empty] | 26608 | 26608 | 208.7082 | 0% | 0% | 0% | 0% | 0% |  | 6531 | 6531 | 1.2067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (47%)
XCV2- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (45%)
BP1-STARTED @ 10:20PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP2-STOPPED @ 10:25PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP2-STARTED @ 11:01PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP3-STOPPED @ 11:05PM DUE TO MONTHLY PREVENTIVE MAINTENANCE

## FEB 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69461568 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43819892 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10205920 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 92 | 69465558 | 3990 | 95.76 | 3.99 | 6.6 | 6.6 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43820588 | 696 | 174.4361 | 0% | 0% | 100% | 100% | 0% | 47% | 10207180 | 1260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 69469422 | 3864 | 92.736 | 3.864 | 8.1 | 8.1 | 2B | 0 | 0 | 950 | 1185 | 0 | N/A | N/A | N/A | N/A | 43821276 | 688 | 178.0538 | 0% | 0% | 100% | 100% | 0% | 47% | 10208453 | 1273 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 69473244 | 3822 | 91.728 | 3.822 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43821948 | 672 | 175.8242 | 0% | 0% | 100% | 100% | 0% | 47% | 10209692 | 1239 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 104 | 69477316 | 4072 | 97.728 | 4.072 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43822636 | 688 | 168.9587 | 0% | 0% | 100% | 100% | 0% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 102 | 69481751 | 4435 | 106.44 | 4.435 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43823384 | 748 | 168.6584 | 0% | 0% | 100% | 100% | 0% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 115 | 69486380 | 4629 | 111.096 | 4.629 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 43824148 | 764 | 165.0464 | 0% | 0% | 100% | 100% | 0% | 0% | 10209692 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 135 | 69491856 | 5476 | 131.424 | 5.476 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43825288 | 1140 | 208.1812 | 0% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 144 | 69497853 | 5997 | 143.928 | 5.997 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43826556 | 1268 | 211.4391 | 0% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 147 | 142 | 69503716 | 5863 | 140.712 | 5.863 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43827820 | 1264 | 215.5893 | 0% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 69509947 | 6231 | 149.544 | 6.231 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43829188 | 1368 | 219.5474 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 | 1.27
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 69516171 | 6224 | 149.376 | 6.224 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43830560 | 1372 | 220.437 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 148 | 69522313 | 6142 | 147.408 | 6.142 | 8.3 | 8.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43831924 | 1364 | 222.0775 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 69528380 | 6067 | 145.608 | 6.067 | 7.9 | 7.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43833284 | 1360 | 224.1635 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 145 | 69534376 | 5996 | 143.904 | 5.996 | 7.4 | 7.4 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43834656 | 1372 | 228.8192 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 69540250 | 5874 | 140.976 | 5.874 | 6.9 | 6.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43836004 | 1348 | 229.4859 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 174 | 137 | 69545903 | 5653 | 135.672 | 5.653 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43837308 | 1304 | 230.674 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 69551531 | 5628 | 135.072 | 5.628 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43838584 | 1276 | 226.7235 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 124 | 134 | 69557195 | 5664 | 135.936 | 5.664 | 5.9 | 5.9 | 3B+1S | 1017 | 0 | 1137 | 1185 | 1147 | N/A | N/A | N/A | N/A | 43839868 | 1284 | 226.6949 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 124 | 134 | 69562761 | 5566 | 133.584 | 5.566 | 5.6 | 5.6 | 3B+1S | 1018 | 0 | 1107 | 1185 | 1127 | N/A | N/A | N/A | N/A | 43841084 | 1216 | 218.4693 | 100% | 0% | 100% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 69568055 | 5294 | 127.056 | 5.294 | 5.1 | 5.1 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43842163 | 1079 | 203.8156 | 100% | 0% | 0% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 122 | 69573348 | 5293 | 127.032 | 5.293 | 4.6 | 4.6 | 2B+1S | 1037 | 0 | 0 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43843172 | 1009 | 190.6291 | 100% | 0% | 0% | 100% | 100% | 0% | 10209692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 14 | 9.8592 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 109 | 117 | 69578472 | 5124 | 122.976 | 5.124 | 4.1 | 4.1 | 2B+1S | 995 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 43844156 | 984 | 192.0375 | 100% | 0% | 0% | 100% | 100% | 0% | 10209692 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 105 | 69582778 | 4306 | 103.344 | 4.306 | 5.1 | 5.1 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43844963 | 807 | 187.4129 | 0% | 0% | 0% | 100% | 100% | 40% | 10210722 | 1030 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 123 | 101 | 69586950 | 4172 | 100.128 | 4.172 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 43845660 | 697 | 167.0662 | 0% | 0% | 0% | 100% | 100% | 40% | 10211891 | 1169 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125382 | 125.382 | 125.382 | [12 empty] | 25768 | 25768 | 205.5159 | 0% | 0% | 0% | 0% | 0% |  | 5971 | 5971 | 1.1817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 9:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)

## FEB 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69586950 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43845660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10211891 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 114 | 69590923 | 3973 | 95.352 | 3.973 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 43846368 | 708 | 178.2029 | 0% | 0% | 0% | 100% | 100% | 43% | 10212995 | 1104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 92 | 69594837 | 3914 | 93.936 | 3.914 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43847060 | 692 | 176.8012 | 0% | 0% | 0% | 100% | 100% | 43% | 10214253 | 1258 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 94 | 69598713 | 3876 | 93.024 | 3.876 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43847728 | 668 | 172.3426 | 0% | 0% | 0% | 100% | 100% | 43% | 10214907 | 654 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 96 | 69602643 | 3930 | 94.32 | 3.93 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 43848388 | 660 | 167.9389 | 0% | 0% | 0% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 101 | 69606706 | 4063 | 97.512 | 4.063 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 897 | N/A | N/A | N/A | N/A | 43849052 | 664 | 163.426 | 0% | 0% | 0% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 23 | 16.1972 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 116 | 112 | 69611377 | 4671 | 112.104 | 4.671 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43849804 | 752 | 160.9934 | 0% | 0% | 0% | 100% | 100% | 0% | 10214907 | 0 | 1.01 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 134 | 69616591 | 5214 | 125.136 | 5.214 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43850780 | 976 | 187.1883 | 0% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 142 | 69622439 | 5848 | 140.352 | 5.848 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43851980 | 1200 | 205.1984 | 0% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 144 | 69628525 | 6086 | 146.064 | 6.086 | 9.4 | 9.4 | 3B+1S | 995 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43853284 | 1304 | 214.2622 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 69634767 | 6242 | 149.808 | 6.242 | 8.9 | 8.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43854660 | 1376 | 220.4422 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 | 1.16
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 69641063 | 6296 | 151.104 | 6.296 | 8.3 | 8.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43856052 | 1392 | 221.0928 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 69647316 | 6253 | 150.072 | 6.253 | 7.7 | 7.7 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43857444 | 1392 | 222.6131 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 69653402 | 6086 | 146.064 | 6.086 | 7.3 | 7.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43858800 | 1356 | 222.8064 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 69659322 | 5920 | 142.08 | 5.92 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43860148 | 1348 | 227.7027 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 69665255 | 5933 | 142.392 | 5.933 | 6.4 | 6.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43861500 | 1352 | 227.878 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 69671090 | 5835 | 140.04 | 5.835 | 6.1 | 6.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43862836 | 1336 | 228.9632 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 69676859 | 5769 | 138.456 | 5.769 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43864160 | 1324 | 229.5025 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 134 | 69682521 | 5662 | 135.888 | 5.662 | 5.6 | 5.6 | 3B+1S | 1007 | 0 | 1148 | 1185 | 1127 | N/A | N/A | N/A | N/A | 43865408 | 1248 | 220.4168 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 137 | 69688144 | 5623 | 134.952 | 5.623 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1117 | N/A | N/A | N/A | N/A | 43866640 | 1232 | 219.1001 | 100% | 0% | 100% | 100% | 100% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 124 | 69693527 | 5383 | 129.192 | 5.383 | 4.8 | 4.8 | 2B+1S | 1025 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43867692 | 1052 | 195.4301 | 100% | 0% | 100% | 100% | 0% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 125 | 69698830 | 5303 | 127.272 | 5.303 | 4.3 | 4.3 | 2B+1S | 1016 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43868724 | 1032 | 194.6068 | 100% | 0% | 100% | 100% | 0% | 0% | 10214907 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 122 | 69703872 | 5042 | 121.008 | 5.042 | 4.1 | 4.1 | 2B+1S | 945 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 43869700 | 976 | 193.574 | 100% | 0% | 100% | 100% | 0% | 0% | 10214907 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 105 | 69708341 | 4469 | 107.256 | 4.469 | 5.2 | 5.2 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 43870508 | 808 | 180.8011 | 0% | 0% | 100% | 100% | 0% | 40% | 10215877 | 970 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 104 | 69712650 | 4309 | 103.416 | 4.309 | 6.3 | 6.3 | 2B | 0 | 0 | 998 | 1185 | 0 | N/A | N/A | N/A | N/A | 43871260 | 752 | 174.5184 | 0% | 0% | 100% | 100% | 0% | 40% | 10217064 | 1187 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125700 | 125.7 | 125.7 | [12 empty] | 25600 | 25600 | 203.6595 | 0% | 0% | 0% | 0% | 0% |  | 5173 | 5173 | 1.0717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (43%)
XCV2- CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:33 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (40%)

## FEB 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26264 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69712650 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43871260 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10217064 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 96 | 69716648 | 3998 | 95.952 | 3.998 | 7.5 | 7.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43871948 | 688 | 172.086 | 0% | 0% | 100% | 100% | 0% | 43% | 10218245 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 95 | 69720556 | 3908 | 93.792 | 3.908 | 8.7 | 8.7 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43872624 | 676 | 172.9785 | 0% | 0% | 100% | 100% | 0% | 43% | 10219370 | 1125 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 103 | 96 | 69724256 | 3700 | 88.8 | 3.7 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43873312 | 688 | 185.9459 | 0% | 0% | 100% | 100% | 0% | 43% | 10220344 | 974 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 98 | 69728534 | 4278 | 102.672 | 4.278 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 1185 | 0 | N/A | N/A | N/A | N/A | 43873980 | 668 | 156.1477 | 0% | 0% | 100% | 100% | 0% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 99 | 69732631 | 4097 | 98.328 | 4.097 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 1185 | 0 | N/A | N/A | N/A | N/A | 43874652 | 672 | 164.0225 | 0% | 0% | 100% | 100% | 0% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 111 | 69737270 | 4639 | 111.336 | 4.639 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43875388 | 736 | 158.6549 | 0% | 0% | 100% | 100% | 0% | 0% | 10220344 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 138 | 69742681 | 5411 | 129.864 | 5.411 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1096 | N/A | N/A | N/A | N/A | 43876444 | 1056 | 195.158 | 0% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 142 | 69748634 | 5953 | 142.872 | 5.953 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43877700 | 1256 | 210.9861 | 0% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 150 | 69754814 | 6180 | 148.32 | 6.18 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43879060 | 1360 | 220.0647 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 69761107 | 6293 | 151.032 | 6.293 | 8.9 | 8.9 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43880452 | 1392 | 221.1982 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 | 1.05
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 153 | 69767451 | 6344 | 152.256 | 6.344 | 8.1 | 8.1 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 43881868 | 1416 | 223.203 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 69773730 | 6279 | 150.696 | 6.279 | 7.4 | 7.4 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43883268 | 1400 | 222.9654 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 147 | 69779888 | 6158 | 147.792 | 6.158 | 6.9 | 6.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43884652 | 1384 | 224.7483 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 69785812 | 5924 | 142.176 | 5.924 | 6.4 | 6.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43885996 | 1344 | 226.8737 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 154 | 69791826 | 6014 | 144.336 | 6.014 | 5.9 | 5.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43887356 | 1360 | 226.139 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 69797776 | 5950 | 142.8 | 5.95 | 5.5 | 5.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43888708 | 1352 | 227.2269 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 69803642 | 5866 | 140.784 | 5.866 | 5.1 | 5.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43890040 | 1332 | 227.0713 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 137 | 69809486 | 5844 | 140.256 | 5.844 | 4.7 | 4.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43891380 | 1340 | 229.295 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 69815236 | 5750 | 138 | 5.75 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43892708 | 1328 | 230.9565 | 100% | 0% | 100% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 135 | 69820872 | 5636 | 135.264 | 5.636 | 3.5 | 3.5 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43893844 | 1136 | 201.5614 | 100% | 0% | 0% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 132 | 69826364 | 5492 | 131.808 | 5.492 | 2.7 | 2.7 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43894924 | 1080 | 196.6497 | 100% | 0% | 0% | 100% | 100% | 0% | 10220344 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 130 | 69831796 | 5432 | 130.368 | 5.432 | 2.2 | 2.2 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43896008 | 1084 | 199.5582 | 100% | 0% | 0% | 100% | 100% | 0% | 10220344 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 105 | 69836158 | 4362 | 104.688 | 4.362 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 43896772 | 764 | 175.149 | 0% | 0% | 0% | 100% | 100% | 37% | 10221377 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 101 | 69840467 | 4309 | 103.416 | 4.309 | 4.5 | 4.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43897524 | 752 | 174.5184 | 0% | 0% | 0% | 100% | 100% | 37% | 10222598 | 1221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127817 | 127.817 | 127.817 | [13 empty] | 26264 | 205.4813 | 0% | 0% | 0% | 0% | 0% |  | 5534 | 5534 | 1.0683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (43%)
XCV1- CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (37%)

## FEB 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26884 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69840467 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43897524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10222598 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 98 | 69844534 | 4067 | 97.608 | 4.067 | 6 | 6 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43898214 | 690 | 169.6582 | 0% | 0% | 0% | 100% | 100% | 43% | 10223908 | 1310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 96 | 69848584 | 4050 | 97.2 | 4.05 | 7.4 | 7.4 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43898903 | 689 | 170.1235 | 0% | 0% | 0% | 100% | 100% | 43% | 10225223 | 1315 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 96 | 69852683 | 4099 | 98.376 | 4.099 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 43899616 | 713 | 173.9449 | 0% | 0% | 0% | 100% | 100% | 43% | 10226554 | 1331 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 97 | 69856781 | 4098 | 98.352 | 4.098 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 43900294 | 678 | 165.4466 | 0% | 0% | 0% | 100% | 100% | 43% | 10227324 | 770 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 103 | 69860880 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 43900980 | 686 | 167.3579 | 0% | 0% | 0% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 127 | 69866119 | 5239 | 125.736 | 5.239 | 9.5 | 9.5 | 2B | 0 | 0 |  | 1185 | 1188 | N/A | N/A | N/A | N/A | 43901916 | 936 | 178.66 | 0% | 0% | 0% | 100% | 100% | 0% | 10227324 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 144 | 69871996 | 5877 | 141.048 | 5.877 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43903212 | 1296 | 220.5207 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 153 | 69878193 | 6197 | 148.728 | 6.197 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43904588 | 1376 | 222.0429 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 69884456 | 6263 | 150.312 | 6.263 | 8.2 | 8.2 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43905980 | 1392 | 222.2577 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 69890686 | 6230 | 149.52 | 6.23 | 7.5 | 7.5 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43907372 | 1392 | 223.435 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 | 1.22
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 69896969 | 6283 | 150.792 | 6.283 | 6.9 | 6.9 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43908780 | 1408 | 224.0968 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 69903072 | 6103 | 146.472 | 6.103 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43910144 | 1364 | 223.4966 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 144 | 69909035 | 5963 | 143.112 | 5.963 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 43911468 | 1324 | 222.0359 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 141 | 69915174 | 6139 | 147.336 | 6.139 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43912856 | 1388 | 226.0955 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 142 | 69920708 | 5534 | 132.816 | 5.534 | 5.7 | 5.7 | 3B+1S | 1004 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43914124 | 1268 | 229.129 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 69926432 | 5724 | 137.376 | 5.724 | 5.4 | 5.4 | 3B+1S | 1004 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43915436 | 1312 | 229.2103 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 69932430 | 5998 | 143.952 | 5.998 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43916804 | 1368 | 228.076 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 136 | 69938367 | 5937 | 142.488 | 5.937 | 4.9 | 4.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43918156 | 1352 | 227.7244 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 69944168 | 5801 | 139.224 | 5.801 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43919484 | 1328 | 228.926 | 100% | 0% | 100% | 100% | 100% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 130 | 69949625 | 5457 | 130.968 | 5.457 | 3.8 | 3.8 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43920580 | 1096 | 200.843 | 100% | 0% | 100% | 100% | 0% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 131 | 69955112 | 5487 | 131.688 | 5.487 | 3.1 | 3.1 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43921660 | 1080 | 196.8289 | 100% | 0% | 100% | 100% | 0% | 0% | 10227324 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 126 | 69960592 | 5480 | 131.52 | 5.48 | 2.6 | 2.6 | 2B+1S | 995 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 43922736 | 1076 | 196.3504 | 100% | 0% | 100% | 100% | 0% | 0% | 10227324 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 109 | 69965212 | 4620 | 110.88 | 4.62 | 3.5 | 3.5 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 43923612 | 876 | 189.6104 | 0% | 0% | 100% | 100% | 0% | 45% | 10228364 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 139 | 105 | 69969609 | 4397 | 105.528 | 4.397 | 5.2 | 5.2 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43924408 | 796 | 181.0325 | 0% | 0% | 100% | 100% | 0% | 45% | 10229794 | 1430 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129142 | 129.142 | 129.142 | [13 empty] | 26884 | 208.1739 | 0% | 0% | 0% | 0% | 0% |  | 7196 | 7196 | 1.135 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (43%)
XCV2 - CLOSED @ 3:54 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26428 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 69969609 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43924408 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10229794 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 95 | 69973598 | 3989 | 95.736 | 3.989 | 6.6 | 6.6 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43925108 | 700 | 175.4826 | 0% | 0% | 100% | 100% | 0% | 47% | 10231113 | 1319 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 69977564 | 3966 | 95.184 | 3.966 | 8 | 8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 43925788 | 680 | 171.4574 | 0% | 0% | 100% | 100% | 0% | 47% | 10232484 | 1371 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 96 | 69981469 | 3905 | 93.72 | 3.905 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 43926460 | 672 | 172.0871 | 0% | 0% | 100% | 100% | 0% | 47% | 10233820 | 1336 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 95 | 69985461 | 3992 | 95.808 | 3.992 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 1185 | 0 | N/A | N/A | N/A | N/A | 43927132 | 672 | 168.3367 | 0% | 0% | 100% | 100% | 0% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 115 | 106 | 69989564 | 4103 | 98.472 | 4.103 | 9.5 | 9.5 | 2B | 0 | 0 | 998 | 1185 | 0 | N/A | N/A | N/A | N/A | 43927808 | 676 | 164.7575 | 0% | 0% | 100% | 100% | 0% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 125 | 69994636 | 5072 | 121.728 | 5.072 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43928680 | 872 | 171.9243 | 0% | 0% | 100% | 100% | 0% | 0% | 10233820 | 0 | 1.06 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 70000466 | 5830 | 139.92 | 5.83 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43929956 | 1276 | 218.8679 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 70006619 | 6153 | 147.672 | 6.153 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43931324 | 1368 | 222.3306 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 152 | 70012834 | 6215 | 149.16 | 6.215 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43932704 | 1380 | 222.0434 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 70019094 | 6260 | 150.24 | 6.26 | 7.5 | 7.5 | 3B+1S | 1068 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43934088 | 1384 | 221.0863 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 | 1.1
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 70025347 | 6253 | 150.072 | 6.253 | 6.9 | 6.9 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43935484 | 1396 | 223.2528 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 70031535 | 6188 | 148.512 | 6.188 | 6.3 | 6.3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43936868 | 1384 | 223.6587 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 137 | 70037515 | 5980 | 143.52 | 5.98 | 6.1 | 6.1 | 3B+1S | 1006 | 0 | 1158 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43938188 | 1320 | 220.7358 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 131 | 70043146 | 5631 | 135.144 | 5.631 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1158 | 1185 | 1158 | N/A | N/A | N/A | N/A | 43939452 | 1264 | 224.4717 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 70048772 | 5626 | 135.024 | 5.626 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43940724 | 1272 | 226.0931 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 70054428 | 5656 | 135.744 | 5.656 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 43942012 | 1288 | 227.7228 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 70060201 | 5773 | 138.552 | 5.773 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1167 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43943228 | 1216 | 210.6357 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 70066014 | 5813 | 139.512 | 5.813 | 5 | 5 | 3B+1S | 1015 | 0 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 43944622 | 1394 | 239.8073 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 70071813 | 5799 | 139.176 | 5.799 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1178 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43945964 | 1342 | 231.4192 | 100% | 0% | 100% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 130 | 70077296 | 5483 | 131.592 | 5.483 | 3.8 | 3.8 | 2B+1S | 1098 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43947060 | 1096 | 199.8906 | 100% | 0% | 0% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 133 | 70082712 | 5416 | 129.984 | 5.416 | 3.1 | 3.1 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43948140 | 1080 | 199.4092 | 100% | 0% | 0% | 100% | 100% | 0% | 10233820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 126 | 70088189 | 5477 | 131.448 | 5.477 | 2.5 | 2.5 | 2B+1S | 1067 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43949240 | 1100 | 200.8399 | 100% | 0% | 0% | 100% | 100% | 0% | 10233820 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 110 | 70092698 | 4509 | 108.216 | 4.509 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 43950060 | 820 | 181.8585 | 0% | 0% | 0% | 100% | 100% | 45% | 10234800 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 99 | 70097016 | 4318 | 103.632 | 4.318 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43950836 | 776 | 179.7128 | 0% | 0% | 0% | 100% | 100% | 45% | 10236081 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127407 | 127.407 | 127.407 | [13 empty] | 26428 | 207.4297 | 0% | 0% | 0% | 0% | 0% |  | 6287 | 6287 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## FEB 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70097016 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43950836 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10236081 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 95 | 70101059 | 4043 | 97.032 | 4.043 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 43951556 | 720 | 178.0856 | 0% | 0% | 0% | 100% | 100% | 47% | 10237066 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 92 | 70104950 | 3891 | 93.384 | 3.891 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43952244 | 688 | 176.8183 | 0% | 0% | 0% | 100% | 100% | 47% | 10238156 | 1090 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 91 | 70108807 | 3857 | 92.568 | 3.857 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 43952932 | 688 | 178.377 | 0% | 0% | 0% | 100% | 100% | 47% | 10239221 | 1065 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 90 | 70112640 | 3833 | 91.992 | 3.833 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 43953612 | 680 | 177.4067 | 0% | 0% | 0% | 100% | 100% | 47% | 10239659 | 438 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 108 | 70116745 | 4105 | 98.52 | 4.105 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 43954332 | 720 | 175.3959 | 0% | 0% | 0% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 120 | 70121550 | 4805 | 115.32 | 4.805 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43955164 | 832 | 173.153 | 0% | 0% | 0% | 100% | 100% | 0% | 10239659 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 143 | 70127399 | 5849 | 140.376 | 5.849 | 8.8 | 8.8 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43956500 | 1336 | 228.4151 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 150 | 70133543 | 6144 | 147.456 | 6.144 | 7.9 | 7.9 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43957884 | 1384 | 225.2604 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 70139628 | 6085 | 146.04 | 6.085 | 7 | 7 | 3B+1S | 1086 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43959256 | 1372 | 225.4725 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 70145744 | 6116 | 146.784 | 6.116 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43960624 | 1368 | 223.6756 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 | 1.02
58:00 | 11:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 124 | 143 | 70151821 | 6077 | 145.848 | 6.077 | 5.5 | 5.5 | 3B+1S | 1189 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43962036 | 1412 | 232.3515 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 146 | 70157825 | 6004 | 144.096 | 6.004 | 4.6 | 4.6 | 3B+1S | 1117 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43963448 | 1412 | 235.1765 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 121 | 133 | 70163652 | 5827 | 139.848 | 5.827 | 3.6 | 3.6 | 3B+1S | 1128 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 43964836 | 1388 | 238.2015 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 121 | 134 | 70169254 | 5602 | 134.448 | 5.602 | 2.8 | 2.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 43966188 | 1352 | 241.3424 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 74 | 52.1127 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 125 | 132 | 70174586 | 5332 | 127.968 | 5.332 | 2.4 | 2.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43967476 | 1288 | 241.5604 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 | 136 | 70180050 | 5464 | 131.136 | 5.464 | 2.2 | 2.2 | 3B+1S | 995 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43968804 | 1328 | 243.0454 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 138 | 134 | 70185604 | 5554 | 133.296 | 5.554 | 2.1 | 2.1 | 3B+1S | 964 | 0 | 1188 | 1185 | 1178 | N/A | N/A | N/A | N/A | 43970080 | 1276 | 229.7443 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 70191236 | 5632 | 135.168 | 5.632 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43971380 | 1300 | 230.8239 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 135 | 70197084 | 5848 | 140.352 | 5.848 | 1.9 | 1.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43972732 | 1352 | 231.1902 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 70202757 | 5673 | 136.152 | 5.673 | 1.8 | 1.8 | 3B+1S | 995 | 0 | 1187 | 1185 | 1157 | N/A | N/A | N/A | N/A | 43974048 | 1316 | 231.976 | 100% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 129 | 129 | 70208345 | 5588 | 134.112 | 5.588 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1097 | N/A | N/A | N/A | N/A | 43975280 | 1232 | 220.4724 | 0% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 120 | 70213619 | 5274 | 126.576 | 5.274 | 1.5 | 1.5 | 3B | 0 | 0 | 1188 | 1185 | 995 | N/A | N/A | N/A | N/A | 43976436 | 1156 | 219.1885 | 0% | 0% | 100% | 100% | 100% | 0% | 10239659 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 106 | 70218124 | 4505 | 108.12 | 4.505 | 3.1 | 3.1 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 43977276 | 840 | 186.4595 | 0% | 0% | 100% | 100% | 0% | 45% | 10240795 | 1136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 103 | 70222505 | 4381 | 105.144 | 4.381 | 4.7 | 4.7 | 2B | 0 | 0 | 1046 | 1185 | 0 | N/A | N/A | N/A | N/A | 43978068 | 792 | 180.7806 | 0% | 0% | 100% | 100% | 0% | 45% | 10242189 | 1394 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125489 | 125.489 | 125.489 | [13 empty] | 27232 | 217.0071 | 0% | 0% | 0% | 0% | 0% |  | 6108 | 6108 | 1.0533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (47%)
XCV2 - CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 8:00 PM DUE TO EXCESS CAPACITY
BP3 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26916 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70222505 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 43978068 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10242189 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 97 | 70226633 | 4128 | 99.072 | 4.128 | 5.9 | 5.9 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 43978812 | 744 | 180.2326 | 0% | 0% | 100% | 100% | 0% | 47% | 10243414 | 1225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 94 | 70230585 | 3952 | 94.848 | 3.952 | 7.3 | 7.3 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 43979508 | 696 | 176.1134 | 0% | 0% | 100% | 100% | 0% | 47% | 10244762 | 1348 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 70234483 | 3898 | 93.552 | 3.898 | 8.7 | 8.7 | 2B | 0 | 0 | 950 | 1185 | 0 | N/A | N/A | N/A | N/A | 43980196 | 688 | 176.5008 | 0% | 0% | 100% | 100% | 0% | 47% | 10246054 | 1292 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 97 | 70238417 | 3934 | 94.416 | 3.934 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 43980884 | 688 | 174.8856 | 0% | 0% | 100% | 100% | 0% | 47% | 10246774 | 720 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 104 | 70242634 | 4217 | 101.208 | 4.217 | 9.5 | 9.5 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 43981584 | 700 | 165.9948 | 0% | 0% | 100% | 100% | 0% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 121 | 70247716 | 5082 | 121.968 | 5.082 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 43982484 | 900 | 177.0956 | 0% | 0% | 100% | 100% | 0% | 0% | 10246774 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 70253579 | 5863 | 140.712 | 5.863 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43983788 | 1304 | 222.4117 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 70259766 | 6187 | 148.488 | 6.187 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43985164 | 1376 | 222.4018 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 70265996 | 6230 | 149.52 | 6.23 | 7.9 | 7.9 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43986540 | 1376 | 220.8668 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 70272305 | 6309 | 151.416 | 6.309 | 7.3 | 7.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43987932 | 1392 | 220.6372 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 | 1.11
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 70278498 | 6193 | 148.632 | 6.193 | 6.7 | 6.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43989320 | 1388 | 224.124 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 147 | 70284656 | 6158 | 147.792 | 6.158 | 6.1 | 6.1 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43990692 | 1372 | 222.7996 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 136 | 70290656 | 6000 | 144 | 6 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43992028 | 1336 | 222.6667 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 140 | 70296673 | 6017 | 144.408 | 6.017 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43993408 | 1380 | 229.3502 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 138 | 70302287 | 5614 | 134.736 | 5.614 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43994684 | 1276 | 227.2889 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 70308224 | 5937 | 142.488 | 5.937 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43996036 | 1352 | 227.7244 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 70313823 | 5599 | 134.376 | 5.599 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43997324 | 1288 | 230.0411 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 143 | 70319783 | 5960 | 143.04 | 5.96 | 4.8 | 4.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43998660 | 1336 | 224.1611 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 141 | 70325903 | 6120 | 146.88 | 6.12 | 4.6 | 4.6 | 3B+1S | 994 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44000040 | 1380 | 225.4902 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 70331516 | 5613 | 134.712 | 5.613 | 4.4 | 4.4 | 3B+1S | 997 | 0 | 1077 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44001276 | 1236 | 220.2031 | 100% | 0% | 100% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 133 | 70337038 | 5522 | 132.528 | 5.522 | 3.7 | 3.7 | 3B | 1087 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44002372 | 1096 | 198.4788 | 100% | 0% | 0% | 100% | 100% | 0% | 10246774 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 122 | 70342452 | 5414 | 129.936 | 5.414 | 3.1 | 3.1 | 3B | 1046 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44003436 | 1064 | 196.5275 | 100% | 0% | 0% | 100% | 100% | 0% | 10246774 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 107 | 70346983 | 4531 | 108.744 | 4.531 | 4 | 4 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44004252 | 816 | 180.0927 | 0% | 0% | 0% | 100% | 100% | 45% | 10247743 | 969 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 101 | 70351181 | 4198 | 100.752 | 4.198 | 5.4 | 5.4 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44004984 | 732 | 174.3687 | 0% | 0% | 0% | 100% | 100% | 45% | 10249010 | 1267 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128676 | 128.676 | 128.676 | [13 empty] | 26916 | 209.1765 | 0% | 0% | 0% | 0% | 0% |  | 6821 | 6821 | 1.0617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1 - CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## FEB 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26800 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70351181 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44004984 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10249010 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 96 | 70355230 | 4049 | 97.176 | 4.049 | 6.5 | 6.5 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 44005696 | 712 | 175.8459 | 0% | 0% | 0% | 100% | 100% | 47% | 10250061 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 97 | 70359221 | 3991 | 95.784 | 3.991 | 7.6 | 7.6 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44006364 | 668 | 167.3766 | 0% | 0% | 0% | 100% | 100% | 47% | 10251113 | 1052 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 95 | 70363175 | 3954 | 94.896 | 3.954 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44007068 | 704 | 178.0475 | 0% | 0% | 0% | 100% | 100% | 47% | 10252156 | 1043 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 98 | 70367221 | 4046 | 97.104 | 4.046 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44007752 | 684 | 169.0559 | 0% | 0% | 0% | 100% | 100% | 47% | 10253108 | 952 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 103 | 70371398 | 4177 | 100.248 | 4.177 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44008448 | 696 | 166.6268 | 0% | 0% | 0% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 125 | 70376212 | 4814 | 115.536 | 4.814 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44009252 | 804 | 167.0129 | 0% | 0% | 0% | 100% | 100% | 0% | 10253108 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 142 | 70381928 | 5716 | 137.184 | 5.716 | 9.4 | 9.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44010460 | 1208 | 211.3366 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 148 | 70388080 | 6152 | 147.648 | 6.152 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44011820 | 1360 | 221.0663 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 70394407 | 6327 | 151.848 | 6.327 | 8.6 | 8.6 | 3B+1S | 1088 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44013204 | 1384 | 218.7451 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 70400822 | 6415 | 153.96 | 6.415 | 7.8 | 7.8 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44014612 | 1408 | 219.4856 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 | 1.13
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 70407177 | 6355 | 152.52 | 6.355 | 7.1 | 7.1 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44016024 | 1412 | 222.1873 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 152 | 70413577 | 6400 | 153.6 | 6.4 | 6.5 | 6.5 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44017441 | 1417 | 221.4062 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 146 | 70419695 | 6118 | 146.832 | 6.118 | 5.9 | 5.9 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44018808 | 1367 | 223.439 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 144 | 70425683 | 5988 | 143.712 | 5.988 | 5.2 | 5.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44020176 | 1368 | 228.4569 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 147 | 70431666 | 5983 | 143.592 | 5.983 | 4.8 | 4.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44021532 | 1356 | 226.6422 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 70437512 | 5846 | 140.304 | 5.846 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44022868 | 1336 | 228.5323 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 70443270 | 5758 | 138.192 | 5.758 | 4.1 | 4.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44024188 | 1320 | 229.2463 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 130 | 70448986 | 5716 | 137.184 | 5.716 | 3.7 | 3.7 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44025508 | 1320 | 230.9307 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 70454666 | 5680 | 136.32 | 5.68 | 3.6 | 3.6 | 3B+1S | 1000 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44026820 | 1312 | 230.9859 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 133 | 70460288 | 5622 | 134.928 | 5.622 | 3.4 | 3.4 | 3B+1S | 1000 | 0 | 1187 | 1185 | 1077 | N/A | N/A | N/A | N/A | 44028076 | 1256 | 223.408 | 100% | 0% | 100% | 100% | 100% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 127 | 70465704 | 5416 | 129.984 | 5.416 | 2.9 | 2.9 | 2B+1S | 1056 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44029140 | 1064 | 196.4549 | 100% | 0% | 100% | 100% | 0% | 0% | 10253108 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 128 | 70471041 | 5337 | 128.088 | 5.337 | 2.4 | 2.4 | 2B+1S | 1045 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44030180 | 1040 | 194.866 | 100% | 0% | 100% | 100% | 0% | 0% | 10253108 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 109 | 70475576 | 4535 | 108.84 | 4.535 | 3.3 | 3.3 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 44031020 | 840 | 185.226 | 0% | 0% | 100% | 100% | 0% | 45% | 10254089 | 981 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 100 | 70479826 | 4250 | 102 | 4.25 | 4.6 | 4.6 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 44031784 | 764 | 179.7647 | 0% | 0% | 100% | 100% | 0% | 45% | 10255272 | 1183 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128645 | 128.645 | 128.645 | [13 empty] | 26800 | 208.3252 | 0% | 0% | 0% | 0% | 0% |  | 6262 | 6262 | 1.09 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (47%)
XCV2 - CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25636 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70479826 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44031784 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10255272 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 126 | 106 | 70483706 | 3880 | 93.12 | 3.88 | 6 | 6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44032484 | 700 | 180.4124 | 0% | 0% | 100% | 100% | 0% | 47% | 10256493 | 1221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 96 | 70487562 | 3856 | 92.544 | 3.856 | 7.3 | 7.3 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44033184 | 700 | 181.5353 | 0% | 0% | 100% | 100% | 0% | 47% | 10257778 | 1285 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 94 | 70491314 | 3752 | 90.048 | 3.752 | 8.6 | 8.6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44033856 | 672 | 179.1045 | 0% | 0% | 100% | 100% | 0% | 47% | 10259115 | 1337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 108 | 92 | 70495039 | 3725 | 89.4 | 3.725 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44034528 | 672 | 180.4027 | 0% | 0% | 100% | 100% | 0% | 47% | 10259967 | 852 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 95 | 70498987 | 3948 | 94.752 | 3.948 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44035212 | 684 | 173.2523 | 0% | 0% | 100% | 100% | 0% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 115 | 104 | 70503551 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44035964 | 752 | 164.7677 | 0% | 0% | 100% | 100% | 0% | 0% | 10259967 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 136 | 70508833 | 5282 | 126.768 | 5.282 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44037004 | 1040 | 196.8951 | 0% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 142 | 70514748 | 5915 | 141.96 | 5.915 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44038240 | 1236 | 208.9603 | 0% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 70520877 | 6129 | 147.096 | 6.129 | 9.3 | 9.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44039572 | 1332 | 217.3275 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 70527076 | 6199 | 148.776 | 6.199 | 8.8 | 8.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44040944 | 1372 | 221.326 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 | 1.23
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 70533323 | 6247 | 149.928 | 6.247 | 8.3 | 8.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44042332 | 1388 | 222.1866 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 70539543 | 6220 | 149.28 | 6.22 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44043708 | 1376 | 221.2219 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 70545604 | 6061 | 145.464 | 6.061 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44045060 | 1352 | 223.0655 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 70551388 | 5784 | 138.816 | 5.784 | 6.9 | 6.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44046388 | 1328 | 229.5989 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 70557186 | 5798 | 139.152 | 5.798 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44047724 | 1336 | 230.4243 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 70562777 | 5591 | 134.184 | 5.591 | 6.4 | 6.4 | 3B+1S | 995 | 0 | 1177 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44049012 | 1288 | 230.3702 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 70568554 | 5777 | 138.648 | 5.777 | 6.2 | 6.2 | 3B+1S | 994 | 0 | 1178 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44050344 | 1332 | 230.5695 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 70574111 | 5557 | 133.368 | 5.557 | 6 | 6 | 3B+1S | 995 | 0 | 1127 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44051588 | 1244 | 223.8618 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 70579712 | 5601 | 134.424 | 5.601 | 5.8 | 5.8 | 3B+1S | 986 | 0 | 1077 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44052836 | 1248 | 222.8174 | 100% | 0% | 100% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 125 | 70584961 | 5249 | 125.976 | 5.249 | 5.3 | 5.3 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44053892 | 1056 | 201.1812 | 100% | 0% | 0% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 123 | 70590054 | 5093 | 122.232 | 5.093 | 5 | 5 | 2B+1S | 1005 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44054900 | 1008 | 197.9187 | 100% | 0% | 0% | 100% | 100% | 0% | 10259967 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 112 | 70595171 | 5117 | 122.808 | 5.117 | 4.8 | 4.8 | 2B+1S | 944 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44055916 | 1016 | 198.5538 | 100% | 0% | 0% | 100% | 100% | 0% | 10259967 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 99 | 70599463 | 4292 | 103.008 | 4.292 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44056708 | 792 | 184.5294 | 0% | 0% | 0% | 100% | 100% | 40% | 10260814 | 847 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 95 | 70603554 | 4091 | 98.184 | 4.091 | 6.7 | 6.7 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44057420 | 712 | 174.0406 | 0% | 0% | 0% | 100% | 100% | 40% | 10261944 | 1130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123728 | 123.728 | 123.728 | [13 empty] | 25636 | 207.1964 | 0% | 0% | 0% | 0% | 0% |  | 6672 | 6672 | 1.0767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1 - CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## FEB 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25988 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70603554 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44057420 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10261944 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 121 | 95 | 70607452 | 3898 | 93.552 | 3.898 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44058104 | 684 | 175.4746 | 0% | 0% | 0% | 100% | 100% | 43% | 10262967 | 1023 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 94 | 70611289 | 3837 | 92.088 | 3.837 | 8.9 | 8.9 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44058792 | 688 | 179.3068 | 0% | 0% | 0% | 100% | 100% | 43% | 10264043 | 1076 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 87 | 90 | 70614975 | 3686 | 88.464 | 3.686 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 796 | N/A | N/A | N/A | N/A | 44059436 | 644 | 174.7151 | 0% | 0% | 0% | 100% | 100% | 43% | 10264576 | 533 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 20 | 14.0845 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 93 | 90 | 70618680 | 3705 | 88.92 | 3.705 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 816 | N/A | N/A | N/A | N/A | 44060052 | 616 | 166.2618 | 0% | 0% | 0% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 107 | 70622779 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44060692 | 640 | 156.1356 | 0% | 0% | 0% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 128 | 70627908 | 5129 | 123.096 | 5.129 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44061580 | 888 | 173.1332 | 0% | 0% | 0% | 100% | 100% | 0% | 10264576 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 143 | 70633720 | 5812 | 139.488 | 5.812 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44062884 | 1304 | 224.3634 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 70639829 | 6109 | 146.616 | 6.109 | 9 | 9 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44064248 | 1364 | 223.2771 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 70645946 | 6117 | 146.808 | 6.117 | 8.5 | 8.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44065624 | 1376 | 224.9469 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 151 | 70652231 | 6285 | 150.84 | 6.285 | 7.9 | 7.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44067012 | 1388 | 220.8433 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 | 1.09
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 70658410 | 6179 | 148.296 | 6.179 | 7.4 | 7.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44068396 | 1384 | 223.9845 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 147 | 70664527 | 6117 | 146.808 | 6.117 | 6.9 | 6.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44069764 | 1368 | 223.639 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 70670472 | 5945 | 142.68 | 5.945 | 6.6 | 6.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44071116 | 1352 | 227.418 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 70676256 | 5784 | 138.816 | 5.784 | 6.3 | 6.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44072440 | 1324 | 228.9073 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 70681875 | 5619 | 134.856 | 5.619 | 6.1 | 6.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1127 | N/A | N/A | N/A | N/A | 44073716 | 1276 | 227.0867 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 70687468 | 5593 | 134.232 | 5.593 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1127 | N/A | N/A | N/A | N/A | 44074980 | 1264 | 225.9968 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 70693136 | 5668 | 136.032 | 5.668 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1128 | N/A | N/A | N/A | N/A | 44076252 | 1272 | 224.4178 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 70698842 | 5706 | 136.944 | 5.706 | 5.5 | 5.5 | 3B+1S | 996 | 0 | 1187 | 1185 | 1106 | N/A | N/A | N/A | N/A | 44077532 | 1280 | 224.3253 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 70704376 | 5534 | 132.816 | 5.534 | 5.3 | 5.3 | 3B+1S | 996 | 0 | 1188 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44078764 | 1232 | 222.6238 | 100% | 0% | 100% | 100% | 100% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 132 | 70709724 | 5348 | 128.352 | 5.348 | 4.7 | 4.7 | 3B+1S | 1077 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44079820 | 1056 | 197.457 | 100% | 0% | 100% | 100% | 0% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 121 | 70715256 | 5532 | 132.768 | 5.532 | 3.9 | 3.9 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44080908 | 1088 | 196.6739 | 100% | 0% | 100% | 100% | 0% | 0% | 10264576 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 120 | 70720370 | 5114 | 122.736 | 5.114 | 3.4 | 3.4 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44081924 | 1016 | 198.6703 | 100% | 0% | 100% | 100% | 0% | 0% | 10264576 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 127 | 97 | 70724597 | 4227 | 101.448 | 4.227 | 4.3 | 4.3 | 2B | 0 | 0 | 1026 | 1185 | 0 | N/A | N/A | N/A | N/A | 44082684 | 760 | 179.7965 | 0% | 0% | 100% | 100% | 0% | 35% | 10265402 | 826 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 126 | 94 | 70728665 | 4068 | 97.632 | 4.068 | 5.5 | 5.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44083408 | 724 | 177.9744 | 0% | 0% | 100% | 100% | 0% | 35% | 10266515 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125111 | 125.111 | 125.111 | [13 empty] | 25988 | 207.7195 | 0% | 0% | 0% | 0% | 0% |  | 4571 | 4571 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (43%)
XCV2 - CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (35%)

## FEB 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26280 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70728665 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44083408 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10266515 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 95 | 70732480 | 3815 | 91.56 | 3.815 | 6.7 | 6.7 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44084078 | 670 | 175.6225 | 0% | 0% | 100% | 100% | 0% | 44% | 10267840 | 1325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 93 | 70736298 | 3818 | 91.632 | 3.818 | 8.2 | 8.2 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44084757 | 679 | 177.8418 | 0% | 0% | 100% | 100% | 0% | 44% | 10269168 | 1328 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 98 | 95 | 70740136 | 3838 | 92.112 | 3.838 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44085460 | 703 | 183.1683 | 0% | 0% | 100% | 100% | 0% | 44% | 10270519 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 98 | 70744106 | 3970 | 95.28 | 3.97 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44086130 | 670 | 168.7657 | 0% | 0% | 100% | 100% | 0% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 101 | 70748092 | 3986 | 95.664 | 3.986 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44086808 | 678 | 170.0953 | 0% | 0% | 100% | 100% | 0% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 70753348 | 5256 | 126.144 | 5.256 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44087748 | 940 | 178.8432 | 0% | 0% | 100% | 100% | 0% | 0% | 10270519 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 70759222 | 5874 | 140.976 | 5.874 | 9.4 | 9.4 | 3B+1S | 1048 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44089036 | 1288 | 219.2714 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 70765415 | 6193 | 148.632 | 6.193 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44090412 | 1376 | 222.1863 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 70771469 | 6054 | 145.296 | 6.054 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44091772 | 1360 | 224.6449 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 70777842 | 6373 | 152.952 | 6.373 | 7.5 | 7.5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44093172 | 1400 | 219.6768 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 | 1.13
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 70784050 | 6208 | 148.992 | 6.208 | 7 | 7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44094548 | 1376 | 221.6495 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 70790148 | 6098 | 146.352 | 6.098 | 6.6 | 6.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44095916 | 1368 | 224.3358 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 142 | 70796177 | 6029 | 144.696 | 6.029 | 6.4 | 6.4 | 3B+1S | 995 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 44097260 | 1344 | 222.9225 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 70801805 | 5628 | 135.072 | 5.628 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44098536 | 1276 | 226.7235 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 134 | 70807727 | 5922 | 142.128 | 5.922 | 6 | 6 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44099892 | 1356 | 228.9767 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 135 | 70812996 | 5269 | 126.456 | 5.269 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44101116 | 1224 | 232.3021 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 70818692 | 5696 | 136.704 | 5.696 | 5.7 | 5.7 | 3B+1S | 1015 | 0 | 1157 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44102420 | 1304 | 228.9326 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 70824227 | 5535 | 132.84 | 5.535 | 5.4 | 5.4 | 3B+1S | 1006 | 0 | 1137 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44103676 | 1256 | 226.9196 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 135 | 70829916 | 5689 | 136.536 | 5.689 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1128 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44104964 | 1288 | 226.4018 | 100% | 0% | 100% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 70835294 | 5378 | 129.072 | 5.378 | 4.6 | 4.6 | 2B+1S | 1078 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44106048 | 1084 | 201.5619 | 100% | 0% | 0% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 125 | 70840705 | 5411 | 129.864 | 5.411 | 3.8 | 3.8 | 2B+1S | 1058 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44107116 | 1068 | 197.3757 | 100% | 0% | 0% | 100% | 100% | 0% | 10270519 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 120 | 70845885 | 5180 | 124.32 | 5.18 | 3.5 | 3.5 | 2B+1S | 945 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 44108148 | 1032 | 199.2278 | 100% | 0% | 0% | 100% | 100% | 0% | 10270519 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 98 | 70850199 | 4314 | 103.536 | 4.314 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 44108972 | 824 | 191.006 | 0% | 0% | 0% | 100% | 100% | 43% | 10271597 | 1078 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 95 | 70854230 | 4031 | 96.744 | 4.031 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 966 | N/A | N/A | N/A | N/A | 44109688 | 716 | 177.6234 | 0% | 0% | 0% | 100% | 100% | 43% | 10272989 | 1392 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125565 | 125.565 | 125.565 | [13 empty] | 26280 | 209.294 | 0% | 0% | 0% | 0% | 0% |  | 6474 | 6474 | 1.1083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (44%)
XCV1 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (43%)

## FEB 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26092 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70854230 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44109688 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10272989 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 92 | 70858051 | 3821 | 91.704 | 3.821 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44110380 | 692 | 181.1044 | 0% | 0% | 0% | 100% | 100% | 45% | 10274171 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 90 | 70861741 | 3690 | 88.56 | 3.69 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44111060 | 680 | 184.2818 | 0% | 0% | 0% | 100% | 100% | 45% | 10275443 | 1272 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 89 | 70865260 | 3519 | 84.456 | 3.519 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44111716 | 656 | 186.4166 | 0% | 0% | 0% | 100% | 100% | 45% | 10276653 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 91 | 70869092 | 3832 | 91.968 | 3.832 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44112372 | 656 | 171.19 | 0% | 0% | 0% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 105 | 70873184 | 4092 | 98.208 | 4.092 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44113040 | 668 | 163.2454 | 0% | 0% | 0% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 126 | 70878208 | 5024 | 120.576 | 5.024 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44113932 | 892 | 177.5478 | 0% | 0% | 0% | 100% | 100% | 0% | 10276653 | 0 | 1.06 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 70884033 | 5825 | 139.8 | 5.825 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44115232 | 1300 | 223.176 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 70890242 | 6209 | 149.016 | 6.209 | 9 | 9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44116608 | 1376 | 221.6138 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 70896514 | 6272 | 150.528 | 6.272 | 8.4 | 8.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44117996 | 1388 | 221.301 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 70902767 | 6253 | 150.072 | 6.253 | 7.7 | 7.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44119380 | 1384 | 221.3338 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 | 1.19
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 70908970 | 6203 | 148.872 | 6.203 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44120756 | 1376 | 221.8281 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 70915112 | 6142 | 147.408 | 6.142 | 6.7 | 6.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44122120 | 1364 | 222.0775 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 138 | 70921041 | 5929 | 142.296 | 5.929 | 6.4 | 6.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44123452 | 1332 | 224.6585 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 70926964 | 5923 | 142.152 | 5.923 | 6.1 | 6.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44124824 | 1372 | 231.6394 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 135 | 70932428 | 5464 | 131.136 | 5.464 | 5.9 | 5.9 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1137 | N/A | N/A | N/A | N/A | 44126064 | 1240 | 226.94 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 70938054 | 5626 | 135.024 | 5.626 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1168 | 1185 | 1137 | N/A | N/A | N/A | N/A | 44127340 | 1276 | 226.8041 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 70943496 | 5442 | 130.608 | 5.442 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1158 | N/A | N/A | N/A | N/A | 44128572 | 1232 | 226.3874 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 70949297 | 5801 | 139.224 | 5.801 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1168 | 1185 | 1137 | N/A | N/A | N/A | N/A | 44129869 | 1297 | 223.5821 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 135 | 70954768 | 5471 | 131.304 | 5.471 | 5 | 5 | 3B+1S | 1005 | 0 | 1157 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44131076 | 1207 | 220.6178 | 100% | 0% | 100% | 100% | 100% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 123 | 70960153 | 5385 | 129.24 | 5.385 | 4.5 | 4.5 | 2B+1S | 1048 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44132160 | 1084 | 201.2999 | 100% | 0% | 100% | 100% | 0% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 128 | 70965634 | 5481 | 131.544 | 5.481 | 3.8 | 3.8 | 2B+1S | 1046 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44133248 | 1088 | 198.5039 | 100% | 0% | 100% | 100% | 0% | 0% | 10276653 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 114 | 70970727 | 5093 | 122.232 | 5.093 | 3.4 | 3.4 | 2B+1S | 995 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 44134268 | 1020 | 200.2749 | 100% | 0% | 100% | 100% | 0% | 0% | 10276653 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 102 | 70975022 | 4295 | 103.08 | 4.295 | 4.6 | 4.6 | 2B | 0 | 0 | 1016 | 1185 | 0 | N/A | N/A | N/A | N/A | 44135056 | 788 | 183.4692 | 0% | 0% | 100% | 100% | 0% | 43% | 10277828 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 96 | 70979041 | 4019 | 96.456 | 4.019 | 6 | 6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44135780 | 724 | 180.1443 | 0% | 0% | 100% | 100% | 0% | 43% | 10279222 | 1394 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124811 | 124.811 | 124.811 | [13 empty] | 26092 | 209.0521 | 0% | 0% | 0% | 0% | 0% |  | 6233 | 6233 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (43%)

## FEB 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26268 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 70979041 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44135780 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10279222 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 70982801 | 3760 | 90.24 | 3.76 | 7.5 | 7.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44136452 | 672 | 178.7234 | 0% | 0% | 100% | 100% | 0% | 45% | 10280592 | 1370 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 86 | 70986474 | 3673 | 88.152 | 3.673 | 8.8 | 8.8 | 2B | 0 | 0 | 917 | 1185 | 0 | N/A | N/A | N/A | N/A | 44137116 | 664 | 180.7787 | 0% | 0% | 100% | 100% | 0% | 45% | 10281862 | 1270 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 91 | 91 | 70990174 | 3700 | 88.8 | 3.7 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 44137776 | 660 | 178.3784 | 0% | 0% | 100% | 100% | 0% | 45% | 10282492 | 630 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 93 | 70993957 | 3783 | 90.792 | 3.783 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 44138432 | 656 | 173.4073 | 0% | 0% | 100% | 100% | 0% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 103 | 70998083 | 4126 | 99.024 | 4.126 | 9.5 | 9.5 | 2B | 0 | 0 | 896 | 1185 | 0 | N/A | N/A | N/A | N/A | 44139076 | 644 | 156.0834 | 0% | 0% | 100% | 100% | 0% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 121 | 71003075 | 4992 | 119.808 | 4.992 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44139987 | 911 | 182.492 | 0% | 0% | 100% | 100% | 0% | 0% | 10282492 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 71009033 | 5958 | 142.992 | 5.958 | 9.2 | 9.2 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44141316 | 1329 | 223.0614 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 156 | 71015215 | 6182 | 148.368 | 6.182 | 8.6 | 8.6 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44142692 | 1376 | 222.5817 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 71021355 | 6140 | 147.36 | 6.14 | 8 | 8 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44144068 | 1376 | 224.1042 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 71027562 | 6207 | 148.968 | 6.207 | 7.5 | 7.5 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44145436 | 1368 | 220.3963 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 71033647 | 6085 | 146.04 | 6.085 | 7.1 | 7.1 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44146788 | 1352 | 222.1857 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 71039755 | 6108 | 146.592 | 6.108 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44148148 | 1360 | 222.6588 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 71045520 | 5765 | 138.36 | 5.765 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44149428 | 1280 | 222.0295 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 134 | 71051236 | 5716 | 137.184 | 5.716 | 6.1 | 6.1 | 3B+1S | 1015 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 44150698 | 1270 | 222.1833 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 135 | 71056714 | 5478 | 131.472 | 5.478 | 5.8 | 5.8 | 3B+1S | 1015 | 0 | 1147 | 1185 | 1157 | N/A | N/A | N/A | N/A | 44151932 | 1234 | 225.2647 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 71062605 | 5891 | 141.384 | 5.891 | 5.6 | 5.6 | 3B+1S | 1004 | 0 | 1147 | 1185 | 1168 | N/A | N/A | N/A | N/A | 44153232 | 1300 | 220.6756 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 71068313 | 5708 | 136.992 | 5.708 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1157 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44154500 | 1268 | 222.1444 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 71074090 | 5777 | 138.648 | 5.777 | 5 | 5 | 3B+1S | 1006 | 0 | 1157 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44155804 | 1304 | 225.7227 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 71079856 | 5766 | 138.384 | 5.766 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1147 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44157092 | 1288 | 223.3784 | 100% | 0% | 100% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 134 | 71085438 | 5582 | 133.968 | 5.582 | 4.1 | 4.1 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44158200 | 1108 | 198.4952 | 100% | 0% | 0% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 131 | 71090934 | 5496 | 131.904 | 5.496 | 3.2 | 3.2 | 2B+1S | 1098 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44159284 | 1084 | 197.2344 | 100% | 0% | 0% | 100% | 100% | 0% | 10282492 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 129 | 71096554 | 5620 | 134.88 | 5.62 | 2.5 | 2.5 | 2B+1S | 1046 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44160400 | 1116 | 198.5765 | 100% | 0% | 0% | 100% | 100% | 0% | 10282492 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 105 | 71101162 | 4608 | 110.592 | 4.608 | 3.4 | 3.4 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44161252 | 852 | 184.8958 | 0% | 0% | 0% | 100% | 100% | 43% | 10283472 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 104 | 71105610 | 4448 | 106.752 | 4.448 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44162048 | 796 | 178.9568 | 0% | 0% | 0% | 100% | 100% | 43% | 10284668 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126569 | 126.569 | 126.569 | [13 empty] | 26268 | 207.539 | 0% | 0% | 0% | 0% | 0% |  | 5446 | 5446 | 1.1867 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 - CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:17 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (43%)

## FEB 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26596 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71105610 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44162048 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10284668 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 108 | 71109763 | 4153 | 99.672 | 4.153 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44162796 | 748 | 180.1108 | 0% | 0% | 0% | 100% | 100% | 45% | 10285821 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 96 | 71113744 | 3981 | 95.544 | 3.981 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44163492 | 696 | 174.8304 | 0% | 0% | 0% | 100% | 100% | 45% | 10287136 | 1315 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 94 | 71117640 | 3896 | 93.504 | 3.896 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44164168 | 676 | 173.5113 | 0% | 0% | 0% | 100% | 100% | 45% | 10288357 | 1221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 109 | 94 | 71121555 | 3915 | 93.96 | 3.915 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44164856 | 688 | 175.7344 | 0% | 0% | 0% | 100% | 100% | 45% | 10289162 | 805 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 105 | 71125759 | 4204 | 100.896 | 4.204 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44165564 | 708 | 168.411 | 0% | 0% | 0% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 71130715 | 4956 | 118.944 | 4.956 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44166436 | 872 | 175.9483 | 0% | 0% | 0% | 100% | 100% | 0% | 10289162 | 0 | 1.29 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 71136611 | 5896 | 141.504 | 5.896 | 9.2 | 9.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44167756 | 1320 | 223.8806 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 71142729 | 6118 | 146.832 | 6.118 | 8.6 | 8.6 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44169124 | 1368 | 223.6025 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 71148859 | 6130 | 147.12 | 6.13 | 8.2 | 8.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44170496 | 1372 | 223.8173 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 71155072 | 6213 | 149.112 | 6.213 | 7.6 | 7.6 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44171884 | 1388 | 223.4025 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 71161293 | 6221 | 149.304 | 6.221 | 6.9 | 6.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44173256 | 1372 | 220.5433 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 71167329 | 6036 | 144.864 | 6.036 | 6.6 | 6.6 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44174624 | 1368 | 226.6402 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 71173346 | 6017 | 144.408 | 6.017 | 6 | 6 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44176004 | 1380 | 229.3502 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 71179419 | 6073 | 145.752 | 6.073 | 5.4 | 5.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44177399 | 1395 | 229.7053 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 71184996 | 5577 | 133.848 | 5.577 | 5 | 5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44178692 | 1293 | 231.8451 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 71190807 | 5811 | 139.464 | 5.811 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44180036 | 1344 | 231.2855 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 71196628 | 5821 | 139.704 | 5.821 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44181380 | 1344 | 230.8882 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 133 | 71202184 | 5556 | 133.344 | 5.556 | 4.4 | 4.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1117 | N/A | N/A | N/A | N/A | 44182656 | 1276 | 229.6616 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 | 1.4 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 131 | 71207647 | 5463 | 131.112 | 5.463 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1107 | N/A | N/A | N/A | N/A | 44183888 | 1232 | 225.5171 | 100% | 0% | 100% | 100% | 100% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 129 | 71213257 | 5610 | 134.64 | 5.61 | 3.4 | 3.4 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44185036 | 1148 | 204.6346 | 100% | 0% | 100% | 100% | 0% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 122 | 71218414 | 5157 | 123.768 | 5.157 | 2.9 | 2.9 | 2B+1S | 1046 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44186052 | 1016 | 197.0138 | 100% | 0% | 100% | 100% | 0% | 0% | 10289162 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 120 | 71223545 | 5131 | 123.144 | 5.131 | 2.6 | 2.6 | 2B+1S | 945 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44187076 | 1024 | 199.5712 | 100% | 0% | 100% | 100% | 0% | 0% | 10289162 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 103 | 71227947 | 4402 | 105.648 | 4.402 | 3.8 | 3.8 | 2B | 0 | 0 | 1046 | 1185 | 0 | N/A | N/A | N/A | N/A | 44187900 | 824 | 187.1876 | 0% | 0% | 100% | 100% | 0% | 45% | 10290409 | 1247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 98 | 71232083 | 4136 | 99.264 | 4.136 | 5.4 | 5.4 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 44188644 | 744 | 179.8839 | 0% | 0% | 100% | 100% | 0% | 45% | 10291836 | 1427 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126473 | 126.473 | 126.473 | [13 empty] | 26596 | 210.2899 | 0% | 0% | 0% | 0% | 0% |  | 7168 | 7168 | 1.2283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (45%)
XCV2 - CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26496 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71232083 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44188644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10291836 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 96 | 71235978 | 3895 | 93.48 | 3.895 | 6.8 | 6.8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44189348 | 704 | 180.7445 | 0% | 0% | 100% | 100% | 0% | 47% | 10293134 | 1298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 92 | 71239714 | 3736 | 89.664 | 3.736 | 8.2 | 8.2 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44190020 | 672 | 179.8715 | 0% | 0% | 100% | 100% | 0% | 47% | 10294405 | 1271 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 114 | 89 | 71243403 | 3689 | 88.536 | 3.689 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44190700 | 680 | 184.3318 | 0% | 0% | 100% | 100% | 0% | 47% | 10295694 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 97 | 71247216 | 3813 | 91.512 | 3.813 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44191380 | 680 | 178.3373 | 0% | 0% | 100% | 100% | 0% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 101 | 71251334 | 4118 | 98.832 | 4.118 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44192076 | 696 | 169.0141 | 0% | 0% | 100% | 100% | 0% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 120 | 116 | 71256025 | 4691 | 112.584 | 4.691 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 44192852 | 776 | 165.4232 | 0% | 0% | 100% | 100% | 0% | 0% | 10295694 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 142 | 71261720 | 5695 | 136.68 | 5.695 | 9.4 | 9.4 | 3B+1S | 975 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44194068 | 1216 | 213.5206 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 71267881 | 6161 | 147.864 | 6.161 | 9.2 | 9.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44195412 | 1344 | 218.1464 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 71274082 | 6201 | 148.824 | 6.201 | 8.6 | 8.6 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44196796 | 1384 | 223.1898 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 71280419 | 6337 | 152.088 | 6.337 | 7.9 | 7.9 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44198196 | 1400 | 220.9247 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 71286750 | 6331 | 151.944 | 6.331 | 7.3 | 7.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44199596 | 1400 | 221.1341 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 71292995 | 6245 | 149.88 | 6.245 | 6.6 | 6.6 | 3B+1S | 1066 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44200980 | 1384 | 221.6173 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 131 | 71299195 | 6200 | 148.8 | 6.2 | 6 | 6 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44202349 | 1369 | 220.8065 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 145 | 71305086 | 5891 | 141.384 | 5.891 | 5.5 | 5.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44203716 | 1367 | 232.0489 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 71310956 | 5870 | 140.88 | 5.87 | 5.2 | 5.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44205044 | 1328 | 226.2351 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 71316736 | 5780 | 138.72 | 5.78 | 4.9 | 4.9 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44206372 | 1328 | 229.7578 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 71322496 | 5760 | 138.24 | 5.76 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44207692 | 1320 | 229.1667 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 71328205 | 5709 | 137.016 | 5.709 | 4.4 | 4.4 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44209000 | 1308 | 229.1119 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 140 | 71333918 | 5713 | 137.112 | 5.713 | 4.1 | 4.1 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44210312 | 1312 | 229.6517 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 131 | 71339437 | 5519 | 132.456 | 5.519 | 3.8 | 3.8 | 3B+1S | 1001 | 0 | 1157 | 1185 | 1107 | N/A | N/A | N/A | N/A | 44211524 | 1212 | 219.605 | 100% | 0% | 100% | 100% | 100% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 124 | 71344768 | 5331 | 127.944 | 5.331 | 3.2 | 3.2 | 2B+1S | 1066 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44212580 | 1056 | 198.0867 | 100% | 0% | 100% | 100% | 0% | 0% | 10295694 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 120 | 71349939 | 5171 | 124.104 | 5.171 | 2.9 | 2.9 | 2B+1S | 995 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44213603 | 1023 | 197.8341 | 100% | 0% | 100% | 100% | 0% | 0% | 10295694 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 99 | 71354240 | 4301 | 103.224 | 4.301 | 4.1 | 4.1 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44214396 | 793 | 184.3757 | 0% | 0% | 100% | 100% | 0% | 45% | 10296838 | 1144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 95 | 71358374 | 4134 | 99.216 | 4.134 | 5.6 | 5.6 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 44215140 | 744 | 179.971 | 0% | 0% | 100% | 100% | 0% | 45% | 10298225 | 1387 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126291 | 126.291 | 126.291 | [13 empty] | 26496 | 209.8012 | 0% | 0% | 0% | 0% | 0% |  | 6389 | 6389 | 1.1817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25672 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71358374 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44215140 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10298225 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 92 | 71362260 | 3886 | 93.264 | 3.886 | 7.1 | 7.1 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44215836 | 696 | 179.1045 | 0% | 0% | 100% | 100% | 0% | 47% | 10299628 | 1403 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 90 | 71366010 | 3750 | 90 | 3.75 | 8.4 | 8.4 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44216512 | 676 | 180.2667 | 0% | 0% | 100% | 100% | 0% | 47% | 10300901 | 1273 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 93 | 71369702 | 3692 | 88.608 | 3.692 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44217176 | 664 | 179.8483 | 0% | 0% | 100% | 100% | 0% | 47% | 10302050 | 1149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 94 | 71373621 | 3919 | 94.056 | 3.919 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44217868 | 692 | 176.5757 | 0% | 0% | 100% | 100% | 0% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 100 | 71377682 | 4061 | 97.464 | 4.061 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44218560 | 692 | 170.4014 | 0% | 0% | 100% | 100% | 0% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 22 | 15.493 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 114 | 108 | 71382230 | 4548 | 109.152 | 4.548 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 44219284 | 724 | 159.1909 | 0% | 0% | 100% | 100% | 0% | 0% | 10302050 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 138 | 71387560 | 5330 | 127.92 | 5.33 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44220340 | 1056 | 198.1238 | 0% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 143 | 71393430 | 5870 | 140.88 | 5.87 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44221572 | 1232 | 209.8807 | 0% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 147 | 71399525 | 6095 | 146.28 | 6.095 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44222892 | 1320 | 216.571 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 71405722 | 6197 | 148.728 | 6.197 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44224268 | 1376 | 222.0429 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 | 1.06 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 71411993 | 6271 | 150.504 | 6.271 | 8.5 | 8.5 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44225664 | 1396 | 222.612 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 150 | 71418244 | 6251 | 150.024 | 6.251 | 7.9 | 7.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44227060 | 1396 | 223.3243 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 71424401 | 6157 | 147.768 | 6.157 | 7.4 | 7.4 | 3B+1S | 1037 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44228428 | 1368 | 222.1861 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 137 | 71430326 | 5925 | 142.2 | 5.925 | 6.8 | 6.8 | 3B+1S | 1037 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44229764 | 1336 | 225.4852 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 139 | 71435977 | 5651 | 135.624 | 5.651 | 6.4 | 6.4 | 3B+1S | 1037 | 0 | 1167 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44231052 | 1288 | 227.9243 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 133 | 71441798 | 5821 | 139.704 | 5.821 | 6 | 6 | 3B+1S | 1026 | 0 | 1157 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44232384 | 1332 | 228.8267 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 71447325 | 5527 | 132.648 | 5.527 | 5.6 | 5.6 | 3B+1S | 1026 | 0 | 1157 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44233660 | 1276 | 230.8667 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 134 | 71453145 | 5820 | 139.68 | 5.82 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1106 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44234956 | 1296 | 222.6804 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 130 | 71458526 | 5381 | 129.144 | 5.381 | 4.9 | 4.9 | 3B+1S | 1017 | 0 | 1046 | 1185 | 1178 | N/A | N/A | N/A | N/A | 44236168 | 1212 | 225.2369 | 100% | 0% | 100% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 126 | 71464033 | 5507 | 132.168 | 5.507 | 4.5 | 4.5 | 3B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44237276 | 1108 | 201.1985 | 100% | 0% | 0% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 126 | 71469240 | 5207 | 124.968 | 5.207 | 3.8 | 3.8 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44238300 | 1024 | 196.6583 | 100% | 0% | 0% | 100% | 100% | 0% | 10302050 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 115 | 71474371 | 5131 | 123.144 | 5.131 | 3.5 | 3.5 | 2B+1S | 995 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44239300 | 1000 | 194.8938 | 100% | 0% | 0% | 100% | 100% | 0% | 10302050 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 100 | 71478659 | 4288 | 102.912 | 4.288 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44240100 | 800 | 186.5672 | 0% | 0% | 0% | 100% | 100% | 43% | 10303225 | 1175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 96 | 71482664 | 4005 | 96.12 | 4.005 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44240812 | 712 | 177.7778 | 0% | 0% | 0% | 100% | 100% | 43% | 10304690 | 1465 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124290 | 124.29 | 124.29 | [13 empty] | 25672 | 206.5492 | 0% | 0% | 0% | 0% | 0% |  | 6465 | 6465 | 1.0817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (47%)
XCV2 - CLOSED @ 2:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (43%)

## FEB 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26552 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71482664 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44240812 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10304690 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 92 | 71486609 | 3945 | 94.68 | 3.945 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44241532 | 720 | 182.5095 | 0% | 0% | 0% | 100% | 100% | 45% | 10306221 | 1531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 90 | 71490397 | 3788 | 90.912 | 3.788 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44242204 | 672 | 177.4023 | 0% | 0% | 0% | 100% | 100% | 45% | 10307546 | 1325 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 93 | 71494192 | 3795 | 91.08 | 3.795 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44242876 | 672 | 177.0751 | 0% | 0% | 0% | 100% | 100% | 45% | 10308277 | 731 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 96 | 71498122 | 3930 | 94.32 | 3.93 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44243564 | 688 | 175.0636 | 0% | 0% | 0% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 105 | 71502354 | 4232 | 101.568 | 4.232 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44244240 | 676 | 159.7353 | 0% | 0% | 0% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 126 | 71507506 | 5152 | 123.648 | 5.152 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44245164 | 924 | 179.3478 | 0% | 0% | 0% | 100% | 100% | 0% | 10308277 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 144 | 71513365 | 5859 | 140.616 | 5.859 | 9.4 | 9.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44246460 | 1296 | 221.1982 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 71519480 | 6115 | 146.76 | 6.115 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44247828 | 1368 | 223.7122 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 71525661 | 6181 | 148.344 | 6.181 | 8.7 | 8.7 | 3B+1S | 1037 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44249200 | 1372 | 221.9706 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 71531860 | 6199 | 148.776 | 6.199 | 8.1 | 8.1 | 3B+1S | 1057 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44250588 | 1388 | 223.9071 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 | 1.04 | Normal operation schedule
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 71538072 | 6212 | 149.088 | 6.212 | 7.6 | 7.6 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44251972 | 1384 | 222.7946 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 71544196 | 6124 | 146.976 | 6.124 | 7 | 7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44253352 | 1380 | 225.3429 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 143 | 71550152 | 5956 | 142.944 | 5.956 | 6.8 | 6.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44254700 | 1348 | 226.3264 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 136 | 71555997 | 5845 | 140.28 | 5.845 | 6.5 | 6.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44256036 | 1336 | 228.5714 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 133 | 71561714 | 5717 | 137.208 | 5.717 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44257356 | 1320 | 230.8903 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 71567556 | 5842 | 140.208 | 5.842 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44258704 | 1348 | 230.7429 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 71573335 | 5779 | 138.696 | 5.779 | 5.6 | 5.6 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44260024 | 1320 | 228.4132 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 141 | 71578970 | 5635 | 135.24 | 5.635 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44261316 | 1292 | 229.2813 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 71584786 | 5816 | 139.584 | 5.816 | 5 | 5 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44262644 | 1328 | 228.3356 | 100% | 0% | 100% | 100% | 100% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 130 | 71590215 | 5429 | 130.296 | 5.429 | 4.5 | 4.5 | 3B+1S | 1078 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44263732 | 1088 | 200.4052 | 100% | 0% | 100% | 100% | 0% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 122 | 71595813 | 5598 | 134.352 | 5.598 | 3.6 | 3.6 | 2B+1S | 1077 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44264823 | 1091 | 194.891 | 100% | 0% | 100% | 100% | 0% | 0% | 10308277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 125 | 71600986 | 5173 | 124.152 | 5.173 | 3.1 | 3.1 | 2B+1S | 1016 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44265864 | 1041 | 201.2372 | 100% | 0% | 100% | 100% | 0% | 0% | 10308277 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 124 | 93 | 71605425 | 4439 | 106.536 | 4.439 | 3.9 | 3.9 | 2B | 0 | 0 | 995 | 1185 | 0 | N/A | N/A | N/A | N/A | 44266656 | 792 | 178.4186 | 0% | 0% | 100% | 100% | 0% | 35% | 10309160 | 883 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 97 | 71609379 | 3954 | 94.896 | 3.954 | 5.4 | 5.4 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44267364 | 708 | 179.0592 | 0% | 0% | 100% | 100% | 0% | 35% | 10310511 | 1351 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126715 | 126.715 | 126.715 | [13 empty] | 26552 | 209.5411 | 0% | 0% | 0% | 0% | 0% |  | 5821 | 5821 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 - CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (35%)

## FEB 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26792 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71609379 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44267364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10310511 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 93 | 71613154 | 3775 | 90.6 | 3.775 | 6.8 | 6.8 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44268039 | 675 | 178.8079 | 0% | 0% | 100% | 100% | 0% | 46% | 10311826 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 71616914 | 3760 | 90.24 | 3.76 | 8.1 | 8.1 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44268719 | 680 | 180.8511 | 0% | 0% | 100% | 100% | 0% | 46% | 10313156 | 1330 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 95 | 71620685 | 3771 | 90.504 | 3.771 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44269416 | 697 | 184.8316 | 0% | 0% | 100% | 100% | 0% | 46% | 10314484 | 1328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 98 | 71624738 | 4053 | 97.272 | 4.053 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44270092 | 676 | 166.79 | 0% | 0% | 100% | 100% | 0% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 103 | 71628805 | 4067 | 97.608 | 4.067 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44270780 | 688 | 169.1665 | 0% | 0% | 100% | 100% | 0% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 123 | 71633980 | 5175 | 124.2 | 5.175 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44271716 | 936 | 180.8696 | 0% | 0% | 100% | 100% |  | 0% | 10314484 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 150 | 71639822 | 5842 | 140.208 | 5.842 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44273020 | 1304 | 223.2112 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 71645940 | 6118 | 146.832 | 6.118 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44274400 | 1380 | 225.5639 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 71652123 | 6183 | 148.392 | 6.183 | 8.2 | 8.2 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44275780 | 1380 | 223.1926 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 71658348 | 6225 | 149.4 | 6.225 | 7.4 | 7.4 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44277184 | 1404 | 225.5422 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 71664517 | 6169 | 148.056 | 6.169 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44278564 | 1380 | 223.6991 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 127 | 71670545 | 6028 | 144.672 | 6.028 | 6.5 | 6.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44279924 | 1360 | 225.6138 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 143 | 143 | 71676660 | 6115 | 146.76 | 6.115 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44281284 | 1360 | 222.4039 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 141 | 71682567 | 5907 | 141.768 | 5.907 | 6 | 6 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44282612 | 1328 | 224.818 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 71688465 | 5898 | 141.552 | 5.898 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44283940 | 1328 | 225.1611 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 139 | 71694276 | 5811 | 139.464 | 5.811 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1147 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44285244 | 1304 | 224.402 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 144 | 71700142 | 5866 | 140.784 | 5.866 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44286548 | 1304 | 222.298 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 142 | 71706283 | 6141 | 147.384 | 6.141 | 5 | 5 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44287932 | 1384 | 225.3705 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 71712079 | 5796 | 139.104 | 5.796 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1137 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44289212 | 1280 | 220.842 | 100% | 0% | 100% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 134 | 71717726 | 5647 | 135.528 | 5.647 | 4 | 4 | 2B+1S | 1097 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44290324 | 1112 | 196.9187 | 100% | 0% | 0% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 148 | 71723304 | 5578 | 133.872 | 5.578 | 3.2 | 3.2 | 2B+1S | 1099 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44291420 | 1096 | 196.4862 | 100% | 0% | 0% | 100% | 100% | 0% | 10314484 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 128 | 71728856 | 5552 | 133.248 | 5.552 | 2.6 | 2.6 | 2B+1S | 1056 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44292516 | 1096 | 197.4063 | 100% | 0% | 0% | 100% | 100% | 0% | 10314484 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 142 | 109 | 71733406 | 4550 | 109.2 | 4.55 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44293368 | 852 | 187.2527 | 0% | 0% | 0% | 100% | 100% | 45% | 10315509 | 1025 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 128 | 102 | 71737766 | 4360 | 104.64 | 4.36 | 5.1 | 5.1 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44294156 | 788 | 180.7339 | 0% | 0% | 0% | 100% | 100% | 45% | 10316883 | 1374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128387 | 128.387 | 128.387 | [13 empty] | 26792 | 208.6816 | 0% | 0% | 0% | 0% | 0% |  | 6372 | 6372 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (46%)
XCV2 - CLOSED @ 2:54 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## FEB 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26376 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71737766 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44294156 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10316883 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 71741805 | 4039 | 96.936 | 4.039 | 6.4 | 6.4 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44294876 | 720 | 178.2619 | 0% | 0% | 0% | 100% | 100% | 47% | 10318185 | 1302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 90 | 71745635 | 3830 | 91.92 | 3.83 | 7.9 | 7.9 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 44295556 | 680 | 177.5457 | 0% | 0% | 0% | 100% | 100% | 47% | 10319646 | 1461 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 94 | 71749397 | 3762 | 90.288 | 3.762 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44296236 | 680 | 180.7549 | 0% | 0% | 0% | 100% | 100% | 47% | 10321128 | 1482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 21 | 14.7887 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 96 | 71753322 | 3925 | 94.2 | 3.925 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44296900 | 664 | 169.172 | 0% | 0% | 0% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 100 | 71757556 | 4234 | 101.616 | 4.234 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44297580 | 680 | 160.6046 | 0% | 0% | 0% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 120 | 71762398 | 4842 | 116.208 | 4.842 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1187 | 1185 | N/A | N/A | N/A | N/A | 44298356 | 776 | 160.2644 | 0% | 0% | 0% | 100% | 100% | 0% | 10321128 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 142 | 71768223 | 5825 | 139.8 | 5.825 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44299656 | 1300 | 223.176 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 71774340 | 6117 | 146.808 | 6.117 | 8.7 | 8.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44301020 | 1364 | 222.9851 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 71780452 | 6112 | 146.688 | 6.112 | 8.2 | 8.2 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44302380 | 1360 | 222.5131 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 71786602 | 6150 | 147.6 | 6.15 | 7.5 | 7.5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44303760 | 1380 | 224.3902 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 71792727 | 6125 | 147 | 6.125 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44305120 | 1360 | 222.0408 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 71798696 | 5969 | 143.256 | 5.969 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44306458 | 1338 | 224.1582 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 71804576 | 5880 | 141.12 | 5.88 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44307804 | 1346 | 228.9116 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 71810864 | 6288 | 150.912 | 6.288 | 5.9 | 5.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44309175 | 1371 | 218.0344 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 71816167 | 5303 | 127.272 | 5.303 | 5.7 | 5.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44310460 | 1285 | 242.3157 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 71821807 | 5640 | 135.36 | 5.64 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44311740 | 1280 | 226.9504 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 71827638 | 5831 | 139.944 | 5.831 | 5.1 | 5.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44313052 | 1312 | 225.0043 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 71833374 | 5736 | 137.664 | 5.736 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44314344 | 1292 | 225.2441 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 140 | 71839228 | 5854 | 140.496 | 5.854 | 4.5 | 4.5 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1137 | N/A | N/A | N/A | N/A | 44315652 | 1308 | 223.437 | 100% | 0% | 100% | 100% | 100% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 71844816 | 5588 | 134.112 | 5.588 | 3.6 | 3.6 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44316780 | 1128 | 201.8611 | 100% | 0% | 100% | 100% | 0% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 108 | 71851068 | 6252 | 150.048 | 6.252 | 2.8 | 2.8 | 2B+1S | 1088 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44318024 | 1244 | 198.9763 | 100% | 0% | 100% | 100% | 0% | 0% | 10321128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 121 | 71855621 | 4553 | 109.272 | 4.553 | 2.5 | 2.5 | 2B+1S | 1015 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44318924 | 900 | 197.6719 | 100% | 0% | 100% | 100% | 0% | 0% | 10321128 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 140 | 104 | 71860099 | 4478 | 107.472 | 4.478 | 3.5 | 3.5 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 44319760 | 836 | 186.6905 | 0% | 0% | 100% | 100% | 0% | 45% | 10322256 | 1128 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 141 | 102 | 71864408 | 4309 | 103.416 | 4.309 | 5.2 | 5.2 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 44320532 | 772 | 179.1599 | 0% | 0% | 100% | 100% | 0% | 45% | 10323736 | 1480 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126642 | 126.642 | 126.642 | [13 empty] | 26376 | 208.2721 | 0% | 0% | 0% | 0% | 0% |  | 6853 | 6853 | 1.0167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (47%)
XCV1 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## FEB 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26268 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71864408 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44320532 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10323736 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 137 | 95 | 71868551 | 4143 | 99.432 | 4.143 | 6.6 | 6.6 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 44321280 | 748 | 180.5455 | 0% | 0% | 100% | 100% | 0% | 47% | 10325142 | 1406 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 94 | 71872501 | 3950 | 94.8 | 3.95 | 8.3 | 8.3 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44321980 | 700 | 177.2152 | 0% | 0% | 100% | 100% | 0% | 47% | 10326745 | 1603 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 96 | 71876313 | 3812 | 91.488 | 3.812 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 44322660 | 680 | 178.3841 | 0% | 0% | 100% | 100% | 0% | 47% | 10328031 | 1286 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 97 | 71880357 | 4044 | 97.056 | 4.044 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 44323380 | 720 | 178.0415 | 0% | 0% | 100% | 100% | 0% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 103 | 71884415 | 4058 | 97.392 | 4.058 | 9.5 | 9.5 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 44324040 | 660 | 162.6417 | 0% | 0% | 100% | 100% | 0% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 114 | 71889129 | 4714 | 113.136 | 4.714 | 9.5 | 9.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44324812 | 772 | 163.7675 | 0% | 0% | 100% | 100% | 0% | 0% | 10328031 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 136 | 71894685 | 5556 | 133.344 | 5.556 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44325996 | 1184 | 213.103 | 0% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 143 | 71900559 | 5874 | 140.976 | 5.874 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44327276 | 1280 | 217.9094 | 0% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 71906707 | 6148 | 147.552 | 6.148 | 9.2 | 9.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44328644 | 1368 | 222.5114 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 71912866 | 6159 | 147.816 | 6.159 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44330020 | 1376 | 223.4129 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 | 1.2 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 71919033 | 6167 | 148.008 | 6.167 | 8.2 | 8.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44331400 | 1380 | 223.7717 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 71925196 | 6163 | 147.912 | 6.163 | 7.7 | 7.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44332780 | 1380 | 223.9169 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 143 | 71931273 | 6077 | 145.848 | 6.077 | 7.3 | 7.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44334148 | 1368 | 225.1111 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 71937148 | 5875 | 141 | 5.875 | 6.8 | 6.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44335496 | 1348 | 229.4468 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 71943067 | 5919 | 142.056 | 5.919 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44336848 | 1352 | 228.417 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 71948946 | 5879 | 141.096 | 5.879 | 6.2 | 6.2 | 3B+1S | 1015 | 0 | 1177 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44338188 | 1340 | 227.9299 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 71954736 | 5790 | 138.96 | 5.79 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 1177 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44339524 | 1336 | 230.7427 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 134 | 71960428 | 5692 | 136.608 | 5.692 | 5.5 | 5.5 | 3B+1S | 1015 | 0 | 1157 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44340812 | 1288 | 226.2825 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 135 | 71966263 | 5835 | 140.04 | 5.835 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44342128 | 1316 | 225.5356 | 100% | 0% | 100% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 126 | 71971636 | 5373 | 128.952 | 5.373 | 4.5 | 4.5 | 2B+1S | 1059 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44343216 | 1088 | 202.494 | 100% | 0% | 0% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 128 | 71976986 | 5350 | 128.4 | 5.35 | 3.8 | 3.8 | 2B+1S | 1036 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44344284 | 1068 | 199.6262 | 100% | 0% | 0% | 100% | 100% | 0% | 10328031 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 115 | 71982166 | 5180 | 124.32 | 5.18 | 3.5 | 3.5 | 2B+1S | 944 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44345300 | 1016 | 196.139 | 100% | 0% | 0% | 100% | 100% | 0% | 10328031 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 95 | 71986426 | 4260 | 102.24 | 4.26 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44346092 | 792 | 185.9155 | 0% | 0% | 0% | 100% | 100% | 42% | 10329094 | 1063 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 93 | 71990443 | 4017 | 96.408 | 4.017 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 966 | N/A | N/A | N/A | N/A | 44346800 | 708 | 176.2509 | 0% | 0% | 0% | 100% | 100% | 42% | 10330446 | 1352 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126035 | 126.035 | 126.035 | [13 empty] | 26268 | 208.4183 | 0% | 0% | 0% | 0% | 0% |  | 6710 | 6710 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (47%)
XCV2 - CLOSED @ 2:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (42%)

## FEB 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25652 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 71990443 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44346800 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10330446 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 122 | 90 | 71994281 | 3838 | 92.112 | 3.838 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44347488 | 688 | 179.26 | 0% | 0% | 0% | 100% | 100% | 45% | 10331777 | 1331 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 90 | 71998086 | 3805 | 91.32 | 3.805 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44348172 | 684 | 179.7635 | 0% | 0% | 0% | 100% | 100% | 45% | 10333044 | 1267 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 95 | 91 | 72001951 | 3865 | 92.76 | 3.865 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44348868 | 696 | 180.0776 | 0% | 0% | 0% | 100% | 100% | 45% | 10333748 | 704 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 93 | 72005951 | 4000 | 96 | 4 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44349540 | 672 | 168 | 0% | 0% | 0% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 120 | 72010141 | 4190 | 100.56 | 4.19 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44350236 | 696 | 166.1098 | 0% | 0% | 0% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 125 | 72015287 | 5146 | 123.504 | 5.146 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44351136 | 900 | 174.8931 | 0% | 0% | 0% | 100% | 100% | 0% | 10333748 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 141 | 72020874 | 5587 | 134.088 | 5.587 | 9.5 | 9.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44352364 | 1228 | 219.796 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 72026975 | 6101 | 146.424 | 6.101 | 9 | 9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44353716 | 1352 | 221.603 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 72032896 | 5921 | 142.104 | 5.921 | 8.6 | 8.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44355032 | 1316 | 222.2598 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 144 | 72039224 | 6328 | 151.872 | 6.328 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44356428 | 1396 | 220.6068 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 | 1.22 | Normal operation schedule
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 143 | 72045346 | 6122 | 146.928 | 6.122 | 7.9 | 7.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44357784 | 1356 | 221.4962 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 140 | 72051212 | 5866 | 140.784 | 5.866 | 7.6 | 7.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44359100 | 1316 | 224.3437 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 12 | 8.4507 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 142 | 72057184 | 5972 | 143.328 | 5.972 | 7.4 | 7.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44360416 | 1316 | 220.3617 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 137 | 72062838 | 5654 | 135.696 | 5.654 | 7.1 | 7.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1116 | N/A | N/A | N/A | N/A | 44361668 | 1252 | 221.4362 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 130 | 72068371 | 5533 | 132.792 | 5.533 | 6.9 | 6.9 | 3B+1S | 1005 | 0 | 1178 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44362908 | 1240 | 224.1099 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 129 | 72073784 | 5413 | 129.912 | 5.413 | 6.6 | 6.6 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44364108 | 1200 | 221.6885 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 134 | 72079506 | 5722 | 137.328 | 5.722 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1167 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44365372 | 1264 | 220.9018 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 131 | 72084907 | 5401 | 129.624 | 5.401 | 6 | 6 | 3B+1S | 995 | 0 | 1168 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44366576 | 1204 | 222.9217 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 72090454 | 5547 | 133.128 | 5.547 | 5.7 | 5.7 | 3B+1S | 996 | 0 | 1168 | 1185 | 1046 | N/A | N/A | N/A | N/A | 44367768 | 1192 | 214.8909 | 100% | 0% | 100% | 100% | 100% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 131 | 72095921 | 5467 | 131.208 | 5.467 | 5.2 | 5.2 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44368828 | 1060 | 193.8906 | 100% | 0% | 100% | 100% | 0% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 127 | 72101325 | 5404 | 129.696 | 5.404 | 4.6 | 4.6 | 2B+1S | 1046 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44369884 | 1056 | 195.4108 | 100% | 0% | 100% | 100% | 0% | 0% | 10333748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 122 | 72106583 | 5258 | 126.192 | 5.258 | 4.3 | 4.3 | 2B+1S | 944 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44370900 | 1016 | 193.2294 | 100% | 0% | 100% | 100% | 0% | 0% | 10333748 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 103 | 72110974 | 4391 | 105.384 | 4.391 | 5.1 | 5.1 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44371688 | 788 | 179.458 | 0% | 0% | 100% | 100% | 0% | 40% | 10334663 | 915 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 98 | 72115258 | 4284 | 102.816 | 4.284 | 6.3 | 6.3 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 44372452 | 764 | 178.338 | 0% | 0% | 100% | 100% | 0% | 40% | 10335781 | 1118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124815 | 124.815 | 124.815 | [13 empty] | 25652 | 205.5202 | 0% | 0% | 0% | 0% | 0% |  | 5335 | 5335 | 1.1533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 - CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:32 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## FEB 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26452 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72115258 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44372452 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10335781 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 92 | 72119228 | 3970 | 95.28 | 3.97 | 7.5 | 7.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44373152 | 700 | 176.3224 | 0% | 0% | 100% | 100% | 0% | 42% | 10336866 | 1085 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 89 | 72123122 | 3894 | 93.456 | 3.894 | 8.6 | 8.6 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44373828 | 676 | 173.6004 | 0% | 0% | 100% | 100% | 0% | 42% | 10338003 | 1137 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 99 | 95 | 72126795 | 3673 | 88.152 | 3.673 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44374496 | 668 | 181.8677 | 0% | 0% | 100% | 100% | 0% | 42% | 10338998 | 995 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 94 | 90 | 72130932 | 4137 | 99.288 | 4.137 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44375196 | 700 | 169.2047 | 0% | 0% | 100% | 100% | 0% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 100 | 72134942 | 4010 | 96.24 | 4.01 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 44375876 | 680 | 169.5761 | 0% | 0% | 100% | 100% | 0% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 18 | 12.6761 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 139 | 72139657 | 4715 | 113.16 | 4.715 | 9.5 | 9.5 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 44376672 | 796 | 168.8229 | 0% | 0% | 100% | 100% | 0% | 0% | 10338998 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 144 | 72145392 | 5735 | 137.64 | 5.735 | 9.5 | 9.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44377908 | 1236 | 215.5187 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 148 | 72151562 | 6170 | 148.08 | 6.17 | 9.3 | 9.3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44379260 | 1352 | 219.1248 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 152 | 72157777 | 6215 | 149.16 | 6.215 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44380640 | 1380 | 222.0434 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 154 | 72164047 | 6270 | 150.48 | 6.27 | 8.2 | 8.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44382021 | 1381 | 220.2552 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 72170303 | 6256 | 150.144 | 6.256 | 7.6 | 7.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44383392 | 1371 | 219.1496 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 72176524 | 6221 | 149.304 | 6.221 | 7.1 | 7.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44384754 | 1362 | 218.9359 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 149 | 72182613 | 6089 | 146.136 | 6.089 | 6.7 | 6.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44386124 | 1370 | 224.9959 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 72188654 | 6041 | 144.984 | 6.041 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44387508 | 1384 | 229.1011 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 72194547 | 5893 | 141.432 | 5.893 | 5.7 | 5.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44388852 | 1344 | 228.0672 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 72200392 | 5845 | 140.28 | 5.845 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44390196 | 1344 | 229.9401 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 72206144 | 5752 | 138.048 | 5.752 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44391516 | 1320 | 229.4854 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 72211845 | 5701 | 136.824 | 5.701 | 4.8 | 4.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44392832 | 1316 | 230.8367 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 72217432 | 5587 | 134.088 | 5.587 | 4.7 | 4.7 | 3B+1S | 944 | 0 | 1147 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44394144 | 1312 | 234.8309 | 100% | 0% | 100% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 133 | 72222956 | 5524 | 132.576 | 5.524 | 4.1 | 4.1 | 2B+1S | 1067 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44395208 | 1064 | 192.614 | 100% | 0% | 0% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 126 | 72228419 | 5463 | 131.112 | 5.463 | 3.4 | 3.4 | 2B+1S | 1046 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44396268 | 1060 | 194.0326 | 100% | 0% | 0% | 100% | 100% | 0% | 10338998 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 125 | 72233705 | 5286 | 126.864 | 5.286 | 3.1 | 3.1 | 2B+1S | 995 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44397300 | 1032 | 195.2327 | 100% | 0% | 0% | 100% | 100% | 0% | 10338998 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 104 | 72238265 | 4560 | 109.44 | 4.56 | 4 | 4 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44398140 | 840 | 184.2105 | 0% | 0% | 0% | 100% | 100% | 42% | 10339999 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 130 | 102 | 72242532 | 4267 | 102.408 | 4.267 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1046 | N/A | N/A | N/A | N/A | 44398904 | 764 | 179.0485 | 0% | 0% | 0% | 100% | 100% | 42% | 10341152 | 1153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127274 | 127.274 | 127.274 | [13 empty] | 26452 | 207.8351 | 0% | 0% | 0% | 0% | 0% |  | 5371 | 5371 | 1.065 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2 - INCREASE OPENING @ 12:00 AM (42%)
XCV2 - CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:50 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (42%)

## FEB 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS/ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26052 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72242532 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44398904 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10341152 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 98 | 72246641 | 4109 | 98.616 | 4.109 | 6.5 | 6.5 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 44399636 | 732 | 178.1455 | 0% | 0% | 0% | 100% | 100% | 45% | 10342324 | 1172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 97 | 72250757 | 4116 | 98.784 | 4.116 | 7.7 | 7.7 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 44400356 | 720 | 174.9271 | 0% | 0% | 0% | 100% | 100% | 45% | 10343461 | 1137 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 96 | 72254645 | 3888 | 93.312 | 3.888 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44401044 | 688 | 176.9547 | 0% | 0% | 0% | 100% | 100% | 45% | 10344525 | 1064 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 101 | 97 | 72258590 | 3945 | 94.68 | 3.945 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 960 | N/A | N/A | N/A | N/A | 44401732 | 688 | 174.398 | 0% | 0% | 0% | 100% | 100% | 45% | 10345093 | 568 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL A. RAMOS/ANDRO MIRAFLOR
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 95 | 72262625 | 4035 | 96.84 | 4.035 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44402424 | 692 | 171.4994 | 0% | 0% | 0% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 116 | 109 | 72267201 | 4576 | 109.824 | 4.576 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1026 | N/A | N/A | N/A | N/A | 44403180 | 756 | 165.2098 | 0% | 0% | 0% | 100% | 100% | 0% | 10345093 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 140 | 72272534 | 5333 | 127.992 | 5.333 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1138 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44404272 | 1092 | 204.7628 | 0% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 140 | 72278467 | 5933 | 142.392 | 5.933 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44405508 | 1236 | 208.3263 | 0% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 144 | 72284839 | 6372 | 152.928 | 6.372 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44406896 | 1388 | 217.828 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 72290892 | 6053 | 145.272 | 6.053 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44408236 | 1340 | 221.3778 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 144 | 72297034 | 6142 | 147.408 | 6.142 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44409588 | 1352 | 220.1237 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 72303264 | 6230 | 149.52 | 6.23 | 7.7 | 7.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44410972 | 1384 | 222.1509 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 142 | 72309276 | 6012 | 144.288 | 6.012 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44412324 | 1352 | 224.8836 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 72315136 | 5860 | 140.64 | 5.86 | 7 | 7 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44413644 | 1320 | 225.256 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 72321111 | 5975 | 143.4 | 5.975 | 6.6 | 6.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44414996 | 1352 | 226.2762 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 72326983 | 5872 | 140.928 | 5.872 | 6.2 | 6.2 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44416320 | 1324 | 225.4768 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 72332758 | 5775 | 138.6 | 5.775 | 5.9 | 5.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44417644 | 1324 | 229.2641 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 72338648 | 5890 | 141.36 | 5.89 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44418972 | 1328 | 225.4669 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 72344360 | 5712 | 137.088 | 5.712 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44420260 | 1288 | 225.4902 | 100% | 0% | 100% | 100% | 100% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 126 | 72349826 | 5466 | 131.184 | 5.466 | 4.6 | 4.6 | 2B+1S | 1048 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44421328 | 1068 | 195.3897 | 100% | 0% | 100% | 100% | 0% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 72355227 | 5401 | 129.624 | 5.401 | 3.9 | 3.9 | 2B+1S | 1049 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44422372 | 1044 | 193.2975 | 100% | 0% | 100% | 100% | 0% | 0% | 10345093 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 125 | 72360499 | 5272 | 126.528 | 5.272 | 3.4 | 3.4 | 2B+1S | 996 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44423408 | 1036 | 196.5099 | 100% | 0% | 100% | 100% | 0% | 0% | 10345093 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 105 | 72364928 | 4429 | 106.296 | 4.429 | 4.4 | 4.4 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44424224 | 816 | 184.2402 | 0% | 0% | 100% | 100% | 0% | 40% | 10346071 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 100 | 72369061 | 4133 | 99.192 | 4.133 | 5.8 | 5.8 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 44424956 | 732 | 177.1111 | 0% | 0% | 100% | 100% | 0% | 40% | 10347367 | 1296 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126529 | 126.529 | 126.529 | [13 empty] | 26052 | 205.8975 | 0% | 0% | 0% | 0% | 0% |  | 6215 | 6215 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 - CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (FEB 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## FEB 29 (hidden)
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm
WATER NETWORK | [12 empty] | 2pm - 10pm
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-02-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | -44424956 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72369061 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44424956 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10347367 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 100% | 0% | 45% |  | -10347367 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 100% | 0% | 45% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 100% | 0% | 45% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 1185 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 |  | 0 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule | Error - General | E
54:00 | 7:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule
58:00 | 11:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule
59:00 | 12:00 |  | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 |  | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 |  | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 3B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 |  | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B+1S | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 |  | 0 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 |  |  |  | - | #VALUE! | #VALUE! |  | 0 | 2B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A |  | - | #VALUE! | 0% | 0% | 0% | 0% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 0 | #VALUE! | #VALUE! | [13 empty] | 0 | #VALUE! | 0% | 0% | 0% | 0% | 0% |  | -10347367 | -10347367 | #DIV/0! |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1 - INCREASE OPENING @ 12:00 AM (45%)
XCV1 - CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE