## MAR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26260 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72494009 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44450936 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10353179 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 87 | 72497680 | 3671 | 88.104 | 3.671 | 6.9 | 6.9 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44451601 | 665 | 181.1496 | 0% | 0% | 0% | 100% | 100% | 40% | 10354164 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 85 | 72501356 | 3676 | 88.224 | 3.676 | 8 | 8 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44452271 | 670 | 182.2633 | 0% | 0% | 0% | 100% | 100% | 40% | 10355154 | 990 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | ANDRO MIRAFLOR
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 113 | 96 | 72505074 | 3718 | 89.232 | 3.718 | 8.9 | 8.9 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44452972 | 701 | 188.5422 | 0% | 0% | 0% | 100% | 100% | 40% | 10356165 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 102 | 99 | 72509052 | 3978 | 95.472 | 3.978 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44453652 | 680 | 170.9402 | 0% | 0% | 0% | 100% | 100% | 40% | 10356695 | 530 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 103 | 72513047 | 3995 | 95.88 | 3.995 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44454348 | 696 | 174.2178 | 0% | 0% | 0% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 123 | 72518124 | 5077 | 121.848 | 5.077 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44455284 | 936 | 184.3608 | 0% | 0% | 0% | 100% | 100% | 0% | 10356695 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 72524039 | 5915 | 141.96 | 5.915 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44456612 | 1328 | 224.5139 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 72530198 | 6159 | 147.816 | 6.159 | 8.6 | 8.6 | 3B+1S | 1050 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44457996 | 1384 | 224.7118 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 72536395 | 6197 | 148.728 | 6.197 | 8 | 8 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44459380 | 1384 | 223.3339 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 72542545 | 6150 | 147.6 | 6.15 | 7.4 | 7.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44460756 | 1376 | 223.7398 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 | 1.26
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 72548730 | 6185 | 148.44 | 6.185 | 6.9 | 6.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44462132 | 1376 | 222.4737 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 147 | 72554840 | 6110 | 146.64 | 6.11 | 6.6 | 6.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44463500 | 1368 | 223.8953 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 141 | 72560781 | 5941 | 142.584 | 5.941 | 6.5 | 6.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44464840 | 1340 | 225.5513 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 133 | 72566520 | 5739 | 137.736 | 5.739 | 6.3 | 6.3 | 3B+1S | 986 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44466156 | 1316 | 229.3082 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 132 | 72572236 | 5716 | 137.184 | 5.716 | 6.2 | 6.2 | 3B+1S | 996 | 0 | 1178 | 1185 | 1177 | N/A | N/A | N/A | N/A | 44467470 | 1314 | 229.881 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 72577811 | 5575 | 133.8 | 5.575 | 6 | 6 | 3B+1S | 1016 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44468713 | 1243 | 222.9596 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 134 | 72583387 | 5576 | 133.824 | 5.576 | 5.8 | 5.8 | 3B+1S | 1015 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44469956 | 1243 | 222.9197 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 135 | 72589016 | 5629 | 135.096 | 5.629 | 5.4 | 5.4 | 3B+1S | 1015 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44471228 | 1272 | 225.9726 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 72594612 | 5596 | 134.304 | 5.596 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44472504 | 1276 | 228.02 | 100% | 0% | 100% | 100% | 100% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 130 | 72599960 | 5348 | 128.352 | 5.348 | 4.5 | 4.5 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44473580 | 1076 | 201.1967 | 100% | 0% | 100% | 100% | 0% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 124 | 72605373 | 5413 | 129.912 | 5.413 | 3.7 | 3.7 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44474636 | 1056 | 195.0859 | 100% | 0% | 100% | 100% | 0% | 0% | 10356695 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 122 | 72610506 | 5133 | 123.192 | 5.133 | 3.2 | 3.2 | 2B+1S | 1046 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44475652 | 1016 | 197.9349 | 100% | 0% | 100% | 100% | 0% | 0% | 10356695 | 0 | 1.4 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 121 | 100 | 72615012 | 4506 | 108.144 | 4.506 | 3.8 | 3.8 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44476472 | 820 | 181.9796 | 0% | 0% | 100% | 100% | 0% | 30% | 10357350 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 118 | 93 | 72619125 | 4113 | 98.712 | 4.113 | 4.8 | 4.8 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44477196 | 724 | 176.0272 | 0% | 0% | 100% | 100% | 0% | 30% | 10358169 | 819 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125116 | 125.116 | 125.116 | [12 empty] | 26260 | 26260 | 209.8852 | 0% | 0% | 0% | 0% | 0% |  | 4990 | 4990 | 1.1883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 3:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 01, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (30%)

## MAR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25968 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72619125 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44477196 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10358169 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 89 | 72622915 | 3790 | 90.96 | 3.79 | 5.9 | 5.9 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 44477876 | 680 | 179.4195 | 0% | 0% | 100% | 100% | 0% | 40% | 10359272 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 91 | 72626499 | 3584 | 86.016 | 3.584 | 7.1 | 7.1 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44478532 | 656 | 183.0357 | 0% | 0% | 100% | 100% | 0% | 40% | 10360376 | 1104 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 91 | 72630295 | 3796 | 91.104 | 3.796 | 8.2 | 8.2 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44479220 | 688 | 181.2434 | 0% | 0% | 100% | 100% | 0% | 40% | 10361489 | 1113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 126 | 92 | 72634203 | 3908 | 93.792 | 3.908 | 9.4 | 9.4 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44479908 | 688 | 176.0491 | 0% | 0% | 100% | 100% | 0% | 40% | 10362671 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 106 | 72638464 | 4261 | 102.264 | 4.261 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44480612 | 704 | 165.2194 | 0% | 0% | 100% | 100% | 0% | 40% | 10362826 | 155 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 72643623 | 5159 | 123.816 | 5.159 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44481528 | 916 | 177.5538 | 0% | 0% | 100% | 100% | 0% | 0% | 10362826 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 145 | 72649573 | 5950 | 142.8 | 5.95 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44482868 | 1340 | 225.2101 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 72655701 | 6128 | 147.072 | 6.128 | 8.5 | 8.5 | 3B+1S | 1048 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44484236 | 1368 | 223.2376 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 72661829 | 6128 | 147.072 | 6.128 | 7.7 | 7.7 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44485676 | 1440 | 234.9869 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 72668083 | 6254 | 150.096 | 6.254 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1187 | 1187 | 1187 | N/A | N/A | N/A | N/A | 44486980 | 1304 | 208.5066 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 | 1.28
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 156 | 72674221 | 6138 | 147.312 | 6.138 | 6.9 | 6.9 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44488348 | 1368 | 222.8739 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 72680210 | 5989 | 143.736 | 5.989 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44489700 | 1352 | 225.7472 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 137 | 72686049 | 5839 | 140.136 | 5.839 | 6.4 | 6.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44491032 | 1332 | 228.1213 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 131 | 72691668 | 5619 | 134.856 | 5.619 | 6.3 | 6.3 | 3B+1S | 994 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44492332 | 1300 | 231.3579 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 72697152 | 5484 | 131.616 | 5.484 | 6.2 | 6.2 | 3B+1S | 995 | 0 | 1147 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44493608 | 1276 | 232.6769 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 128 | 72702612 | 5460 | 131.04 | 5.46 | 6.1 | 6.1 | 3B+1S | 995 | 0 | 1147 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44494868 | 1260 | 230.7692 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 72708190 | 5578 | 133.872 | 5.578 | 6 | 6 | 3B+1S | 995 | 0 | 1147 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44496124 | 1256 | 225.1703 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 129 | 72713761 | 5571 | 133.704 | 5.571 | 5.7 | 5.7 | 3B+1S | 996 | 0 | 1097 | 1185 | 1148 | N/A | N/A | N/A | N/A | 44497340 | 1216 | 218.2732 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 130 | 72719280 | 5519 | 132.456 | 5.519 | 5.5 | 5.5 | 3B+1S | 995 | 0 | 1097 | 1185 | 1148 | N/A | N/A | N/A | N/A | 44498540 | 1200 | 217.4307 | 100% | 0% | 100% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 127 | 72724699 | 5419 | 130.056 | 5.419 | 4.9 | 4.9 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44499612 | 1072 | 197.8225 | 100% | 0% | 0% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 124 | 72730010 | 5311 | 127.464 | 5.311 | 4.3 | 4.3 | 2B+1S | 1046 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 44500660 | 1048 | 197.3263 | 100% | 0% | 0% | 100% | 100% | 0% | 10362826 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 123 | 72735033 | 5023 | 120.552 | 5.023 | 3.8 | 3.8 | 2B+1S | 1006 | 0 | 0 | 1185 | 1158 | N/A | N/A | N/A | N/A | 44501656 | 996 | 198.2879 | 100% | 0% | 0% | 100% | 100% | 0% | 10362826 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 125 | 102 | 72739443 | 4410 | 105.84 | 4.41 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1038 | N/A | N/A | N/A | N/A | 44502476 | 820 | 185.941 | 0% | 0% | 0% | 100% | 100% | 35% | 10363650 | 824 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 100 | 72743609 | 4166 | 99.984 | 4.166 | 5.6 | 5.6 | 2B | 0 | 0 | 1077 | 0 | 1067 | N/A | N/A | N/A | N/A | 44503164 | 688 | 165.1464 | 0% | 0% | 100% | 0% | 100% | 35% | 10364663 | 1013 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124484 | 124.484 | 124.484 | [12 empty] | 25968 | 25968 | 208.6051 | 0% | 0% | 0% | 0% | 0% |  | 6494 | 6494 | 1.27 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:07 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 02, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (35%)
BP1 - STARTED @ 11:00 PM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP2 - STOPPED @ 11:00 PM DUE TO TERMINATION FOR POWER SUPPLY OF NEW PANEL SOFT STARTER

## MAR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26352 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72743609 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44503164 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10364663 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 119 | 92 | 72747621 | 4012 | 96.288 | 4.012 | 6.8 | 6.8 | 2B | 0 | 0 | 1048 | 0 | 1047 | N/A | N/A | N/A | N/A | 44503844 | 680 | 169.4915 | 0% | 0% | 100% | 0% | 100% | 40% | 10365711 | 1048 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 118 | 89 | 72751393 | 3772 | 90.528 | 3.772 | 7.9 | 7.9 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44504496 | 652 | 172.8526 | 0% | 0% | 0% | 100% | 100% | 40% | 10366849 | 1138 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 88 | 72755044 | 3651 | 87.624 | 3.651 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44505168 | 672 | 184.0592 | 0% | 0% | 0% | 100% | 100% | 40% | 10367930 | 1081 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 91 | 72758667 | 3623 | 86.952 | 3.623 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44505812 | 644 | 177.7532 | 0% | 0% | 0% | 100% | 100% | 40% | 10368903 | 973 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 113 | 110 | 72763306 | 4639 | 111.336 | 4.639 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 958 | N/A | N/A | N/A | N/A | 44506664 | 852 | 183.6603 | 0% | 0% | 0% | 100% | 100% | 40% | 10368913 | 10 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 122 | 72767920 | 4614 | 110.736 | 4.614 | 9.5 | 9.5 | 2B | 1058 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44507364 | 700 | 151.7122 | 0% | 0% | 0% | 100% | 100% | 0% | 10368913 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 144 | 72773937 | 6017 | 144.408 | 6.017 | 9.2 | 9.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44508716 | 1352 | 224.6967 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 72780108 | 6171 | 148.104 | 6.171 | 9 | 9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44510100 | 1384 | 224.2748 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 72786172 | 6064 | 145.536 | 6.064 | 8.4 | 8.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44511460 | 1360 | 224.2744 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 72792326 | 6154 | 147.696 | 6.154 | 7.9 | 7.9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44512836 | 1376 | 223.5944 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 | 1.29
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 72798398 | 6072 | 145.728 | 6.072 | 7.5 | 7.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44514196 | 1360 | 223.9789 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 72804427 | 6029 | 144.696 | 6.029 | 7.1 | 7.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44515540 | 1344 | 222.9225 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 138 | 72810257 | 5830 | 139.92 | 5.83 | 6.9 | 6.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44516872 | 1332 | 228.4734 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 72815986 | 5729 | 137.496 | 5.729 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44518196 | 1324 | 231.1049 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 132 | 72821490 | 5504 | 132.096 | 5.504 | 6.4 | 6.4 | 3B+1S | 1005 | 0 | 1148 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44519452 | 1256 | 228.1977 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 72827152 | 5662 | 135.888 | 5.662 | 6.1 | 6.1 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44520716 | 1264 | 223.2427 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 72832980 | 5828 | 139.872 | 5.828 | 5.8 | 5.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44522052 | 1336 | 229.2382 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 144 | 72838863 | 5883 | 141.192 | 5.883 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44523396 | 1344 | 228.4549 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 147 | 72844682 | 5819 | 139.656 | 5.819 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44524732 | 1336 | 229.5927 | 100% | 0% | 100% | 100% | 100% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 129 | 72850234 | 5552 | 133.248 | 5.552 | 4.5 | 4.5 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44525844 | 1112 | 200.2882 | 100% | 0% | 100% | 100% | 0% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 125 | 72855587 | 5353 | 128.472 | 5.353 | 3.6 | 3.6 | 2B+1S | 1097 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44526924 | 1080 | 201.756 | 100% | 0% | 100% | 100% | 0% | 0% | 10368913 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 127 | 72860725 | 5138 | 123.312 | 5.138 | 2.9 | 2.9 | 2B+1S | 1036 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44527964 | 1040 | 202.4134 | 100% | 0% | 100% | 100% | 0% | 0% | 10368913 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 123 | 101 | 72865156 | 4431 | 106.344 | 4.431 | 3.6 | 3.6 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 44528800 | 836 | 188.6707 | 0% | 0% | 100% | 100% | 0% | 35% | 10369701 | 788 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 124 | 91 | 72869178 | 4022 | 96.528 | 4.022 | 4.8 | 4.8 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 44529516 | 716 | 178.0209 | 0% | 0% | 100% | 100% | 0% | 35% | 10370719 | 1018 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125569 | 125.569 | 125.569 | [12 empty] | 26352 | 26352 | 209.8607 | [6 empty] | 6056 | 6056 | 1.205 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (40%)
BP2 - STARTED @ 1:45 AM TO MEET 66 PSI TARGET DISCHARGE PRESSURE
BP1 - STOPPED @ 1:46 AM DUE TO HIGH DISCHARGE
XCV1- CLOSED @ 3:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (35%)

## MAR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26096 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72869178 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44529516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10370719 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 120 | 89 | 72872986 | 3808 | 91.392 | 3.808 | 6 | 6 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44530212 | 696 | 182.7731 | 0% | 0% | 100% | 100% | 0% | 40% | 10371883 | 1164 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 89 | 72876768 | 3782 | 90.768 | 3.782 | 7.3 | 7.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44530908 | 696 | 184.0296 | 0% | 0% | 100% | 100% | 0% | 40% | 10373073 | 1190 | 1.46 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 91 | 72880476 | 3708 | 88.992 | 3.708 | 8.5 | 8.5 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44531592 | 684 | 184.466 | 0% | 0% | 100% | 100% | 0% | 40% | 10374233 | 1160 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 87 | 72884047 | 3571 | 85.704 | 3.571 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44532224 | 632 | 176.9812 | 0% | 0% | 100% | 100% | 0% | 40% | 10375422 | 1189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 105 | 72888224 | 4177 | 100.248 | 4.177 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 44532924 | 700 | 167.5844 | 0% | 0% | 100% | 100% | 0% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 127 | 72893462 | 5238 | 125.712 | 5.238 | 9.5 | 9.5 | 2B | 0 | 0 | 1179 | 1185 | 0 | N/A | N/A | N/A | N/A | 44533856 | 932 | 177.9305 | 0% | 0% | 100% | 100% | 0% | 0% | 10375422 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 145 | 72899400 | 5938 | 142.512 | 5.938 | 9.4 | 9.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44535184 | 1328 | 223.6443 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 72905520 | 6120 | 146.88 | 6.12 | 8.9 | 8.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44536548 | 1364 | 222.8758 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 142 | 72911664 | 6144 | 147.456 | 6.144 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44537920 | 1372 | 223.3073 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 72917881 | 6217 | 149.208 | 6.217 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44539324 | 1404 | 225.8324 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 | 1.35
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 72924048 | 6167 | 148.008 | 6.167 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44540676 | 1352 | 219.2314 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 141 | 72930091 | 6043 | 145.032 | 6.043 | 6.9 | 6.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44542044 | 1368 | 226.3776 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 139 | 72935955 | 5864 | 140.736 | 5.864 | 6.7 | 6.7 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44543372 | 1328 | 226.4666 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 140 | 72941763 | 5808 | 139.392 | 5.808 | 6.5 | 6.5 | 3B+1S | 996 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44544680 | 1308 | 225.2066 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 134 | 72947433 | 5670 | 136.08 | 5.67 | 6.4 | 6.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1166 | N/A | N/A | N/A | N/A | 44545972 | 1292 | 227.866 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 130 | 72953015 | 5582 | 133.968 | 5.582 | 6.3 | 6.3 | 3B+1S | 994 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 44547244 | 1272 | 227.8753 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 72958641 | 5626 | 135.024 | 5.626 | 6.2 | 6.2 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 44548520 | 1276 | 226.8041 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 138 | 72964251 | 5610 | 134.64 | 5.61 | 5.8 | 5.8 | 3B+1S | 1006 | 0 | 1097 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44549740 | 1220 | 217.4688 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 132 | 72969809 | 5558 | 133.392 | 5.558 | 5.5 | 5.5 | 3B+1S | 1007 | 0 | 1097 | 1185 | 1148 | N/A | N/A | N/A | N/A | 44550940 | 1200 | 215.905 | 100% | 0% | 100% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 127 | 72975173 | 5364 | 128.736 | 5.364 | 5 | 5 | 2B+1S | 1026 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44552012 | 1072 | 199.8509 | 100% | 0% | 0% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 129 | 72980460 | 5287 | 126.888 | 5.287 | 4.5 | 4.5 | 2B+1S | 1027 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44553048 | 1036 | 195.9523 | 100% | 0% | 0% | 100% | 100% | 0% | 10375422 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 116 | 72985482 | 5022 | 120.528 | 5.022 | 4.1 | 4.1 | 2B+1S | 1014 | 0 | 0 | 1185 | 1128 | N/A | N/A | N/A | N/A | 44554044 | 996 | 198.3274 | 100% | 0% | 0% | 100% | 100% | 0% | 10375422 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 126 | 101 | 72989967 | 4485 | 107.64 | 4.485 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1088 | N/A | N/A | N/A | N/A | 44554880 | 836 | 186.3991 | 0% | 0% | 0% | 100% | 100% | 35% | 10376180 | 758 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 125 | 94 | 72994095 | 4128 | 99.072 | 4.128 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 986 | N/A | N/A | N/A | N/A | 44555612 | 732 | 177.3256 | 0% | 0% | 0% | 100% | 100% | 35% | 10377227 | 1047 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124917 | 124.917 | 124.917 | [12 empty] | 26096 | 26096 | 208.9067 | [6 empty] | 6508 | 6508 | 1.29 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (40%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (35%)

## MAR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26832 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 72994095 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44555612 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10377227 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 125 | 83 | 72997968 | 3873 | 92.952 | 3.873 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 44556308 | 696 | 179.7057 | 0% | 0% | 0% | 100% | 100% | 40% | 10378520 | 1293 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 119 | 87 | 73001613 | 3645 | 87.48 | 3.645 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 44556972 | 664 | 182.1674 | 0% | 0% | 0% | 100% | 100% | 40% | 10379757 | 1237 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 87 | 73005156 | 3543 | 85.032 | 3.543 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 44557620 | 648 | 182.8959 | 0% | 0% | 0% | 100% | 100% | 40% | 10380927 | 1170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 88 | 73008761 | 3605 | 86.52 | 3.605 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 927 | N/A | N/A | N/A | N/A | 44558264 | 644 | 178.6408 | 0% | 0% | 0% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 123 | 99 | 73012664 | 3903 | 93.672 | 3.903 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 44558918 | 654 | 167.5634 | 0% | 0% | 0% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 126 | 73017365 | 4701 | 112.824 | 4.701 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44559604 | 686 | 145.9264 | 0% | 0% | 0% | 100% | 100% | 0% | 10380927 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 144 | 73023304 | 5939 | 142.536 | 5.939 | 9.5 | 9.5 | 3B+1S | 996 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44560892 | 1288 | 216.8715 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 142 | 73029457 | 6153 | 147.672 | 6.153 | 9.2 | 9.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44562260 | 1368 | 222.3306 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 73035554 | 6097 | 146.328 | 6.097 | 8.6 | 8.6 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44563620 | 1360 | 223.0605 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 73041926 | 6372 | 152.928 | 6.372 | 7.9 | 7.9 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44565036 | 1416 | 222.2222 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 | 1.51
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 73048219 | 6293 | 151.032 | 6.293 | 7.2 | 7.2 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44566436 | 1400 | 222.4694 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 153 | 73054475 | 6256 | 150.144 | 6.256 | 6.6 | 6.6 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44567828 | 1392 | 222.5064 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 148 | 73060591 | 6116 | 146.784 | 6.116 | 6 | 6 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44569212 | 1384 | 226.2917 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 73066570 | 5979 | 143.496 | 5.979 | 5.4 | 5.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44570564 | 1352 | 226.1248 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 139 | 73072368 | 5798 | 139.152 | 5.798 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44571911 | 1347 | 232.3215 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 73078147 | 5779 | 138.696 | 5.779 | 4.9 | 4.9 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44573236 | 1325 | 229.2784 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 73083844 | 5697 | 136.728 | 5.697 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44574560 | 1324 | 232.403 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 73089588 | 5744 | 137.856 | 5.744 | 4.3 | 4.3 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44575884 | 1324 | 230.5014 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 73095526 | 5938 | 142.512 | 5.938 | 3.9 | 3.9 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44577228 | 1344 | 226.3388 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 73101249 | 5723 | 137.352 | 5.723 | 3.6 | 3.6 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44578516 | 1288 | 225.0568 | 100% | 0% | 100% | 100% | 100% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 133 | 73106724 | 5475 | 131.4 | 5.475 | 3 | 3 | 2B+1S | 1066 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44579612 | 1096 | 200.1826 | 100% | 0% | 100% | 100% | 0% | 0% | 10380927 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 127 | 73112293 | 5569 | 133.656 | 5.569 | 2.4 | 2.4 | 2B+1S | 1057 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44580708 | 1096 | 196.8037 | 100% | 0% | 100% | 100% | 0% | 0% | 10380927 | 0 | 1.36 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 112 | 73116973 | 4680 | 112.32 | 4.68 | 2.9 | 2.9 | 2B | 0 | 0 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 44581604 | 896 | 191.453 | 0% | 0% | 100% | 100% | 0% | 40% | 10381646 | 719 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 102 | 73121503 | 4530 | 108.72 | 4.53 | 4 | 4 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 44582444 | 840 | 185.4305 | 0% | 0% | 100% | 100% | 0% | 40% | 10382626 | 980 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127408 | 127.408 | 127.408 | [12 empty] | 26832 | 26832 | 210.599 | [6 empty] | 5399 | 5399 | 1.3 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (40%)
XCV1- CLOSED @ 2:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## MAR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26284 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73121503 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44582444 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10382626 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 128 | 99 | 73125616 | 4113 | 98.712 | 4.113 | 5.1 | 5.1 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 44583196 | 752 | 182.8349 | 0% | 0% | 0% | 100% | 100% | 46% | 10383631 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 95 | 73129633 | 4017 | 96.408 | 4.017 | 6.4 | 6.4 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 44583932 | 736 | 183.2213 | 0% | 0% | 0% | 100% | 100% | 46% | 10384850 | 1219 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 92 | 73133372 | 3739 | 89.736 | 3.739 | 7.7 | 7.7 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44584612 | 680 | 181.8668 | 0% | 0% | 0% | 100% | 100% | 46% | 10386139 | 1289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 133 | 88 | 73137148 | 3776 | 90.624 | 3.776 | 9..2 | 9..2 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 44585284 | 672 | 177.9661 | 0% | 0% | 0% | 100% | 100% | 46% | 10387691 | 1552 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 97 | 98 | 73141036 | 3888 | 93.312 | 3.888 | 9.5 | 9.5 | 2B | 0 | 0 | 876 | 1185 | 0 | N/A | N/A | N/A | N/A | 44585932 | 648 | 166.6667 | 0% | 0% | 0% | 100% | 100% | 46% | 10387885 | 194 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 118 | 73145667 | 4631 | 111.144 | 4.631 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 44586692 | 760 | 164.1114 | 0% | 0% | 0% | 100% | 100% | 0% | 10387885 | 0 | 1.38 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 136 | 73151208 | 5541 | 132.984 | 5.541 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44587852 | 1160 | 209.3485 | 0% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 143 | 73157286 | 6078 | 145.872 | 6.078 | 9.5 | 9.5 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44589164 | 1312 | 215.8605 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 147 | 73163494 | 6208 | 148.992 | 6.208 | 9.1 | 9.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44590532 | 1368 | 220.3608 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 154 | 73169852 | 6358 | 152.592 | 6.358 | 8.6 | 8.6 | 3B+1S | 1139 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44591940 | 1408 | 221.4533 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 | 1.1
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 73175904 | 6052 | 145.248 | 6.052 | 8 | 8 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44593276 | 1336 | 220.7535 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 73182426 | 6522 | 156.528 | 6.522 | 7.3 | 7.3 | 3B+1S | 1089 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44594732 | 1456 | 223.2444 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 73188076 | 5650 | 135.6 | 5.65 | 6.8 | 6.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44596008 | 1276 | 225.8407 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 145 | 73194160 | 6084 | 146.016 | 6.084 | 6.4 | 6.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44597384 | 1376 | 226.167 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 73199950 | 5790 | 138.96 | 5.79 | 6.1 | 6.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44598716 | 1332 | 230.0518 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 73205719 | 5769 | 138.456 | 5.769 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44600040 | 1324 | 229.5025 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 148 | 73211471 | 5752 | 138.048 | 5.752 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44601368 | 1328 | 230.8762 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 73217234 | 5763 | 138.312 | 5.763 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44602692 | 1324 | 229.7415 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 73222990 | 5756 | 138.144 | 5.756 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44604012 | 1320 | 229.3259 | 100% | 0% | 100% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 132 | 73228401 | 5411 | 129.864 | 5.411 | 4.4 | 4.4 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44605100 | 1088 | 201.0719 | 100% | 0% | 0% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 128 | 73233685 | 5284 | 126.816 | 5.284 | 3.8 | 3.8 | 2B+1S | 1016 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44606124 | 1024 | 193.7926 | 100% | 0% | 0% | 100% | 100% | 0% | 10387885 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 129 | 73238957 | 5272 | 126.528 | 5.272 | 3.5 | 3.5 | 2B+1S | 974 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44607164 | 1040 | 197.2686 | 100% | 0% | 0% | 100% | 100% | 0% | 10387885 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 106 | 73243254 | 4297 | 103.128 | 4.297 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44607964 | 800 | 186.1764 | 0% | 0% | 0% | 100% | 100% | 40% | 10388706 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 95 | 73247456 | 4202 | 100.848 | 4.202 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 987 | N/A | N/A | N/A | N/A | 44608728 | 764 | 181.8182 | 0% | 0% | 0% | 100% | 100% | 40% | 10389841 | 1135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125953 | 125.953 | 125.953 | [12 empty] | 26284 | 26284 | 208.681 | [6 empty] | 7215 | 7215 | 1.1867 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (46%)
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (40%)

## MAR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26356 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73247456 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44608728 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10389841 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 90 | 73251467 | 4011 | 96.264 | 4.011 | 7.1 | 7.1 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 44609444 | 716 | 178.5091 | 0% | 0% | 0% | 100% | 100% | 45% | 10391324 | 1483 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 88 | 73255746 | 4279 | 102.696 | 4.279 | 8.9 | 8.9 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44610204 | 760 | 177.6116 | 0% | 0% | 0% | 100% | 100% | 45% | 10392923 | 1599 | 0.73 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 95 | 73259096 | 3350 | 80.4 | 3.35 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 910 | N/A | N/A | N/A | N/A | 44610796 | 592 | 176.7164 | 0% | 0% | 0% | 100% | 100% | 45% | 10393639 | 716 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 90 | 73263734 | 4638 | 111.312 | 4.638 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 856 | N/A | N/A | N/A | N/A | 44611412 | 616 | 132.8159 | 0% | 0% | 0% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 104 | 73266756 | 3022 | 72.528 | 3.022 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 856 | N/A | N/A | N/A | N/A | 44612068 | 656 | 217.0748 | 0% | 0% | 0% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 124 | 73271884 | 5128 | 123.072 | 5.128 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44612984 | 916 | 178.6271 | 0% | 0% | 0% | 100% | 100% | 0% | 10393639 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 146 | 73277975 | 6091 | 146.184 | 6.091 | 9.1 | 9.1 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44614340 | 1356 | 222.6235 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 73284018 | 6043 | 145.032 | 6.043 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44615692 | 1352 | 223.7299 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 150 | 73290196 | 6178 | 148.272 | 6.178 | 7.9 | 7.9 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44617076 | 1384 | 224.0207 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 73296501 | 6305 | 151.32 | 6.305 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44618476 | 1400 | 222.046 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 | 1.21
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 73302600 | 6099 | 146.376 | 6.099 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44619828 | 1352 | 221.6757 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 73308759 | 6159 | 147.816 | 6.159 | 6.3 | 6.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44621200 | 1372 | 222.7634 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 139 | 73314660 | 5901 | 141.624 | 5.901 | 6 | 6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44622532 | 1332 | 225.7245 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 73320451 | 5791 | 138.984 | 5.791 | 5.8 | 5.8 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44623852 | 1320 | 227.9399 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 137 | 73326130 | 5679 | 136.296 | 5.679 | 5.7 | 5.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44625160 | 1308 | 230.3222 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 73331812 | 5682 | 136.368 | 5.682 | 5.6 | 5.6 | 3B+1S | 995 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44626488 | 1328 | 233.7205 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 73337584 | 5772 | 138.528 | 5.772 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44627808 | 1320 | 228.6902 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 73343313 | 5729 | 137.496 | 5.729 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1116 | N/A | N/A | N/A | N/A | 44629092 | 1284 | 224.1229 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 138 | 73349017 | 5704 | 136.896 | 5.704 | 4.9 | 4.9 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1117 | N/A | N/A | N/A | N/A | 44630364 | 1272 | 223.0014 | 100% | 0% | 100% | 100% | 100% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 122 | 73354453 | 5436 | 130.464 | 5.436 | 4.4 | 4.4 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44631440 | 1076 | 197.9397 | 100% | 0% | 100% | 100% | 0% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 73359829 | 5376 | 129.024 | 5.376 | 3.6 | 3.6 | 2B+1S | 1048 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44632500 | 1060 | 197.1726 | 100% | 0% | 100% | 100% | 0% | 0% | 10393639 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 122 | 73365018 | 5189 | 124.536 | 5.189 | 3.1 | 3.1 | 2B+1S | 1015 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44633532 | 1032 | 198.8823 | 100% | 0% | 100% | 100% | 0% | 0% | 10393639 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 102 | 73369404 | 4386 | 105.264 | 4.386 | 3.9 | 3.9 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 44634340 | 808 | 184.2225 | 0% | 0% | 100% | 100% | 0% | 43% | 10394521 | 882 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 93 | 73373565 | 4161 | 99.864 | 4.161 | 5.4 | 5.4 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44635084 | 744 | 178.8032 | 0% | 0% | 100% | 100% | 0% | 43% | 10395836 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126109 | 126.109 | 126.109 | [12 empty] | 26356 | 26356 | 208.9938 | [6 empty] | 5995 | 5995 | 1.05 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 2:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (43%)

## MAR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27048 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73373565 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44635084 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10395836 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 92 | 73377405 | 3840 | 92.16 | 3.84 | 7.3 | 7.3 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44635769 | 685 | 178.3854 | 0% | 0% | 100% | 100% | 0% | 47% | 10397151 | 1315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 90 | 73381250 | 3845 | 92.28 | 3.845 | 8.4 | 8.4 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44636441 | 672 | 174.7724 | 0% | 0% | 100% | 100% | 0% | 47% | 10398460 | 1309 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 99 | 88 | 73385140 | 3890 | 93.36 | 3.89 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44637164 | 723 | 185.8612 | 0% | 0% | 100% | 100% | 0% | 47% | 10399762 | 1302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 100 | 105 | 73389280 | 4140 | 99.36 | 4.14 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44637864 | 700 | 169.0821 | 0% | 0% | 100% | 100% | 0% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 111 | 73393434 | 4154 | 99.696 | 4.154 | 9.5 | 9.5 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44638580 | 716 | 172.364 | 0% | 0% | 100% | 100% | 0% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 129 | 73398672 | 5238 | 125.712 | 5.238 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44639532 | 952 | 181.7488 | 0% | 0% | 100% | 100% | 0% | 0% | 10399762 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 146 | 73404683 | 6011 | 144.264 | 6.011 | 9 | 9 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1185 | N/A | N/A | N/A | N/A | 44640884 | 1352 | 224.921 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 73410813 | 6130 | 147.12 | 6.13 | 8.3 | 8.3 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44642268 | 1384 | 225.7749 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 73417032 | 6219 | 149.256 | 6.219 | 7.6 | 7.6 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44643668 | 1400 | 225.1166 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 73423209 | 6177 | 148.248 | 6.177 | 7 | 7 | 3B+1S | 1067 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44645060 | 1392 | 225.3521 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 | 1.07
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 73429314 | 6105 | 146.52 | 6.105 | 6.4 | 6.4 | 3B+1S | 1067 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44646444 | 1384 | 226.6994 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 141 | 73435402 | 6088 | 146.112 | 6.088 | 5.8 | 5.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44647816 | 1372 | 225.3614 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 73441297 | 5895 | 141.48 | 5.895 | 5.5 | 5.5 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44649156 | 1340 | 227.3113 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 73447087 | 5790 | 138.96 | 5.79 | 5.2 | 5.2 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44650492 | 1336 | 230.7427 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 73452750 | 5663 | 135.912 | 5.663 | 5 | 5 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44651924 | 1432 | 252.8695 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 73458357 | 5607 | 134.568 | 5.607 | 4.9 | 4.9 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44653132 | 1208 | 215.445 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 73464077 | 5720 | 137.28 | 5.72 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44654460 | 1328 | 232.1678 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 73469860 | 5783 | 138.792 | 5.783 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1117 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44655748 | 1288 | 222.7218 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 132 | 73475606 | 5746 | 137.904 | 5.746 | 4.3 | 4.3 | 3B+1S | 1006 | 0 | 1116 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44657024 | 1276 | 222.0675 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 138 | 73481300 | 5694 | 136.656 | 5.694 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1116 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44658300 | 1276 | 224.0955 | 100% | 0% | 100% | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 129 | 73486727 | 5427 | 130.248 | 5.427 | 3.2 | 3.2 | 2B+1S | 1067 | 0 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 44659396 | 1096 | 201.9532 | 100% | 0% |  | 100% | 100% | 0% | 10399762 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 129 | 73492081 | 5354 | 128.496 | 5.354 | 2.6 | 2.6 | 2B+1S | 1066 | 0 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 44660460 | 1064 | 198.7299 | 100% | 0% |  | 100% | 100% | 0% | 10399762 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 107 | 73496750 | 4669 | 112.056 | 4.669 | 3.2 | 3.2 | 2B | 0 | 0 |  | 1185 | 1097 | N/A | N/A | N/A | N/A | 44661344 | 884 | 189.3339 | 0% | 0% |  | 100% | 100% | 40% | 10400516 | 754 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 100 | 73501085 | 4335 | 104.04 | 4.335 | 4.6 | 4.6 | 2B | 0 | 0 |  | 1185 | 1017 | N/A | N/A | N/A | N/A | 44662132 | 788 | 181.7762 | 0% | 0% |  | 100% | 100% | 40% | 10401642 | 1126 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127520 | 127.52 | 127.52 | [12 empty] | 27048 | 27048 | 212.1079 | [6 empty] | 5806 | 5806 | 1.0567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (47%)
XCV2- CLOSED @ 2:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (40%)

## MAR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27112 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73501085 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44662132 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10401642 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 143 | 99 | 73505323 | 4238 | 101.712 | 4.238 | 6.6 | 6.6 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44662860 | 728 | 171.7791 | 0% | 0% | 0% | 100% | 100% | 47% | 10403478 | 1836 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 93 | 73509317 | 3994 | 95.856 | 3.994 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 44663548 | 688 | 172.2584 | 0% | 0% | 0% | 100% | 100% | 47% | 10405193 | 1715 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 96 | 92 | 73513311 | 3994 | 95.856 | 3.994 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44664220 | 672 | 168.2524 | 0% | 0% | 0% | 100% | 100% | 47% | 10406428 | 1235 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 98 | 73517353 | 4042 | 97.008 | 4.042 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 896 | N/A | N/A | N/A | N/A | 44664880 | 660 | 163.2855 | 0% | 0% | 0% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 104 | 73521472 | 4119 | 98.856 | 4.119 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 44665540 | 660 | 160.2331 | 0% | 0% | 0% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 127 | 120 | 73526352 | 4880 | 117.12 | 4.88 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44666372 | 832 | 170.4918 | 0% | 0% | 0% | 100% | 100% | 0% | 10406428 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 144 | 73532325 | 5973 | 143.352 | 5.973 | 9.1 | 9.1 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44667700 | 1328 | 222.3338 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 73538479 | 6154 | 147.696 | 6.154 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44669068 | 1368 | 222.2944 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 155 | 73544735 | 6256 | 150.144 | 6.256 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44670468 | 1400 | 223.7852 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 73550967 | 6232 | 149.568 | 6.232 | 7.3 | 7.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44671860 | 1392 | 223.3633 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 | 1.13
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 73557125 | 6158 | 147.792 | 6.158 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44673236 | 1376 | 223.4492 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 73563157 | 6032 | 144.768 | 6.032 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44674596 | 1360 | 225.4642 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 132 | 73569109 | 5952 | 142.848 | 5.952 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44675980 | 1384 | 232.5269 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 137 | 73574841 | 5732 | 137.568 | 5.732 | 5.4 | 5.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44677304 | 1324 | 230.9839 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 73580666 | 5825 | 139.8 | 5.825 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44678644 | 1340 | 230.0429 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 73586590 | 5924 | 142.176 | 5.924 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44679988 | 1344 | 226.8737 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 139 | 73592482 | 5892 | 141.408 | 5.892 | 4.6 | 4.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44681324 | 1336 | 226.7481 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 146 | 73598341 | 5859 | 140.616 | 5.859 | 4.3 | 4.3 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44682668 | 1344 | 229.3907 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 139 | 73604187 | 5846 | 140.304 | 5.846 | 3.9 | 3.9 | 3B+1S | 996 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44684000 | 1332 | 227.8481 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 138 | 73610086 | 5899 | 141.576 | 5.899 | 3.7 | 3.7 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1148 | N/A | N/A | N/A | N/A | 44685336 | 1336 | 226.4791 | 100% | 0% | 100% | 100% | 100% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 135 | 73615681 | 5595 | 134.28 | 5.595 | 2.9 | 2.9 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44686452 | 1116 | 199.4638 | 100% | 0% | 100% | 100% | 0% | 0% | 10406428 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 126 | 73621256 | 5575 | 133.8 | 5.575 | 2.1 | 2.1 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44687564 | 1112 | 199.4619 | 100% | 0% | 100% | 100% | 0% | 0% | 10406428 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 112 | 73625998 | 4742 | 113.808 | 4.742 | 2.7 | 2.7 | 2B | 0 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 44688476 | 912 | 192.3239 | 0% | 0% | 100% | 100% | 0% | 40% | 10407094 | 666 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 108 | 73630621 | 4623 | 110.952 | 4.623 | 3.7 | 3.7 | 2B | 0 | 0 | 1128 | 1185 | 0 | N/A | N/A | N/A | N/A | 44689244 | 768 | 166.1259 | 0% | 0% | 100% | 100% | 0% | 40% | 10408127 | 1033 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129536 | 129.536 | 129.536 | [12 empty] | 27112 | 27112 | 209.3009 | [6 empty] | 6485 | 6485 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (47%)
XCV1- CLOSED @ 2:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## MAR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27016 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73630621 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44689244 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10408127 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 99 | 73634976 | 4355 | 104.52 | 4.355 | 5 | 5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 44690164 | 920 | 211.2514 | 0% | 0% | 100% | 100% | 0% | 45% | 10409208 | 1081 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 92 | 73638924 | 3948 | 94.752 | 3.948 | 6.3 | 6.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44690880 | 716 | 181.3576 | 0% | 0% | 100% | 100% | 0% | 45% | 10410457 | 1249 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 73642905 | 3981 | 95.544 | 3.981 | 7.6 | 7.6 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 44691588 | 708 | 177.8448 | 0% | 0% | 100% | 100% | 0% | 45% | 10411727 | 1270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 97 | 73647006 | 4101 | 98.424 | 4.101 | 9 | 9 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44692312 | 724 | 176.5423 | 0% | 0% | 100% | 100% | 0% | 45% | 10413139 | 1412 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 106 | 73651157 | 4151 | 99.624 | 4.151 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44693012 | 700 | 168.6341 | 0% | 0% | 100% | 100% | 0% | 45% | 10413498 | 359 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 122 | 73656219 | 5062 | 121.488 | 5.062 | 9.5 | 9.5 | 2B | 1048 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44693916 | 904 | 178.5855 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 145 | 73662219 | 6000 | 144 | 6 | 9 | 9 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44695260 | 1344 | 224 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 73668417 | 6198 | 148.752 | 6.198 | 8.4 | 8.4 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44696644 | 1384 | 223.2978 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 143 | 73674590 | 6173 | 148.152 | 6.173 | 7.8 | 7.8 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44698012 | 1368 | 221.6102 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 73680788 | 6198 | 148.752 | 6.198 | 7.3 | 7.3 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44699364 | 1352 | 218.1349 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 | 1.15
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 144 | 73686911 | 6123 | 146.952 | 6.123 | 6.9 | 6.9 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44700756 | 1392 | 227.3395 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 73692968 | 6057 | 145.368 | 6.057 | 6.5 | 6.5 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44702114 | 1358 | 224.2034 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 136 | 73698853 | 5885 | 141.24 | 5.885 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44703436 | 1322 | 224.6389 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 73704716 | 5863 | 140.712 | 5.863 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44704780 | 1344 | 229.2342 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 73710462 | 5746 | 137.904 | 5.746 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44706092 | 1312 | 228.3328 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 73716189 | 5727 | 137.448 | 5.727 | 5.6 | 5.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44707416 | 1324 | 231.1856 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 142 | 73721917 | 5728 | 137.472 | 5.728 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44708736 | 1320 | 230.4469 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 141 | 73727772 | 5855 | 140.52 | 5.855 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44710068 | 1332 | 227.4979 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 73733616 | 5844 | 140.256 | 5.844 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44711400 | 1332 | 227.9261 | 100% | 0% | 100% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 130 | 73739023 | 5407 | 129.768 | 5.407 | 4.3 | 4.3 | 2B+1S | 1048 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44712484 | 1084 | 200.4809 | 100% | 0% | 0% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 133 | 73744402 | 5379 | 129.096 | 5.379 | 3.6 | 3.6 | 2B+1S | 1046 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44713540 | 1056 | 196.319 | 100% | 0% | 0% | 100% | 100% | 0% | 10413498 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 122 | 73749886 | 5484 | 131.616 | 5.484 | 3 | 3 | 2B+1S | 1046 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44714620 | 1080 | 196.9365 | 100% | 0% | 0% | 100% | 100% | 0% | 10413498 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 111 | 73754326 | 4440 | 106.56 | 4.44 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1128 | N/A | N/A | N/A | N/A | 44715472 | 852 | 191.8919 | 0% | 0% | 0% | 100% | 100% | 40% | 10414152 | 654 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 106 | 73758687 | 4361 | 104.664 | 4.361 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 44716260 | 788 | 180.6925 | 0% | 0% | 0% | 100% | 100% | 40% | 10415308 | 1156 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128066 | 128.066 | 128.066 | [12 empty] | 27016 | 27016 | 210.9537 | [6 empty] | 7181 | 7181 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (40%)

## MAR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26936 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73758687 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44716260 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10415308 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 99 | 73762888 | 4201 | 100.824 | 4.201 | 6 | 6 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 44717040 | 780 | 185.6701 | 0% | 0% | 0% | 100% | 100% | 45% | 10416410 | 1102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 94 | 73766887 | 3999 | 95.976 | 3.999 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 44717756 | 716 | 179.0448 | 0% | 0% | 0% | 100% | 100% | 45% | 10417677 | 1267 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 94 | 73771035 | 4148 | 99.552 | 4.148 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 44718500 | 744 | 179.3635 | 0% | 0% | 0% | 100% | 100% | 45% | 10418961 | 1284 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 102 | 99 | 73774976 | 3941 | 94.584 | 3.941 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 946 | N/A | N/A | N/A | N/A | 44719188 | 688 | 174.575 | 0% | 0% | 0% | 100% | 100% | 45% | 10419722 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 106 | 73779218 | 4242 | 101.808 | 4.242 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 44719896 | 708 | 166.9024 | 0% | 0% | 0% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 124 | 73784622 | 5404 | 129.696 | 5.404 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44720868 | 972 | 179.8668 | 0% | 0% | 0% | 100% | 100% | 0% | 10419722 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 147 | 73790351 | 5729 | 137.496 | 5.729 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44722144 | 1276 | 222.7265 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 148 | 73796518 | 6167 | 148.008 | 6.167 | 8.3 | 8.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44723540 | 1396 | 226.3661 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 73802775 | 6257 | 150.168 | 6.257 | 7.6 | 7.6 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44724940 | 1400 | 223.7494 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 73808909 | 6134 | 147.216 | 6.134 | 7 | 7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44726328 | 1388 | 226.2798 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 | 1.16
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 73815075 | 6166 | 147.984 | 6.166 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44727716 | 1388 | 225.1054 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 73821123 | 6048 | 145.152 | 6.048 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44729076 | 1360 | 224.8677 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 142 | 73827107 | 5984 | 143.616 | 5.984 | 5.7 | 5.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44730432 | 1356 | 226.6043 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 73832920 | 5813 | 139.512 | 5.813 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44731764 | 1332 | 229.1416 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 73838610 | 5690 | 136.56 | 5.69 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44733084 | 1320 | 231.9859 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 73844220 | 5610 | 134.64 | 5.61 | 5 | 5 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44734396 | 1312 | 233.8681 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 73849987 | 5767 | 138.408 | 5.767 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44735744 | 1348 | 233.7437 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 73855715 | 5728 | 137.472 | 5.728 | 4.7 | 4.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44737064 | 1320 | 230.4469 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 137 | 73861464 | 5749 | 137.976 | 5.749 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44738388 | 1324 | 230.3009 | 100% | 0% | 100% | 100% | 100% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 127 | 73866882 | 5418 | 130.032 | 5.418 | 3.8 | 3.8 | 2B+1S | 1057 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44739460 | 1072 | 197.859 | 100% | 0% | 100% | 100% | 0% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 73872205 | 5323 | 127.752 | 5.323 | 3.2 | 3.2 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44740504 | 1044 | 196.13 | 100% | 0% | 100% | 100% | 0% | 0% | 10419722 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 124 | 73877405 | 5200 | 124.8 | 5.2 | 2.7 | 2.7 | 2B+1S | 1045 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44741524 | 1020 | 196.1538 | 100% | 0% | 100% | 100% | 0% | 0% | 10419722 | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 107 | 73882152 | 4747 | 113.928 | 4.747 | 3.4 | 3.4 | 2B | 0 | 0 | 1127 | 1185 | 0 | N/A | N/A | N/A | N/A | 44742440 | 916 | 192.964 | 0% | 0% | 100% | 100% | 0% | 40% | 10420489 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 95 | 73886305 | 4153 | 99.672 | 4.153 | 4.6 | 4.6 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 44743196 | 756 | 182.0371 | 0% | 0% | 100% | 100% | 0% | 40% | 10421510 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127618 | 127.618 | 127.618 | [12 empty] | 26936 | 26936 | 211.0674 | [6 empty] | 6202 | 6202 | 1.135 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## MAR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27536 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 73886305 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44743196 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10421510 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 95 | 73890468 | 4163 | 99.912 | 4.163 | 5.9 | 5.9 | 2B | 0 | 0 | 986 | 1185 | 0 | N/A | N/A | N/A | N/A | 44743948 | 752 | 180.639 | 0% | 0% | 100% | 100% | 0% | 45% | 10422811 | 1301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 93 | 73894256 | 3788 | 90.912 | 3.788 | 7.2 | 7.2 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44744628 | 680 | 179.5143 | 0% | 0% | 100% | 100% | 0% | 45% | 10424060 | 1249 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 89 | 73898053 | 3797 | 91.128 | 3.797 | 8.6 | 8.6 | 2B | 0 | 0 | 927 | 1185 | 0 | N/A | N/A | N/A | N/A | 44745304 | 676 | 178.0353 | 0% | 0% | 100% | 100% | 0% | 45% | 10425404 | 1344 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 92 | 73901794 | 3741 | 89.784 | 3.741 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 1185 | 0 | N/A | N/A | N/A | N/A | 44745964 | 660 | 176.4234 | 0% | 0% | 100% | 100% | 0% | 45% | 10426339 | 935 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 105 | 73905805 | 4011 | 96.264 | 4.011 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44746644 | 680 | 169.5338 | 0% | 0% | 100% | 100% | 0% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 124 | 73910665 | 4860 | 116.64 | 4.86 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44747500 | 856 | 176.1317 | 0% | 0% | 100% | 100% | 0% | 0% | 10426339 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 73916517 | 5852 | 140.448 | 5.852 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44748804 | 1304 | 222.8298 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 73922779 | 6262 | 150.288 | 6.262 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44750196 | 1392 | 222.2932 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 73928991 | 6212 | 149.088 | 6.212 | 8 | 8 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44751580 | 1384 | 222.7946 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 73935359 | 6368 | 152.832 | 6.368 | 7.3 | 7.3 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44752992 | 1412 | 221.7337 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 | 0.96
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 73941577 | 6218 | 149.232 | 6.218 | 6.6 | 6.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44754380 | 1388 | 223.2229 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 73947764 | 6187 | 148.488 | 6.187 | 5.9 | 5.9 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44755768 | 1388 | 224.3414 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 145 | 73954013 | 6249 | 149.976 | 6.249 | 5.3 | 5.3 | 3B+1S | 1096 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44757156 | 1388 | 222.1155 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 144 | 73960044 | 6031 | 144.744 | 6.031 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44758532 | 1376 | 228.1545 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 73965958 | 5914 | 141.936 | 5.914 | 4 | 4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44759854 | 1322 | 223.5374 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 73971964 | 6006 | 144.144 | 6.006 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44761224 | 1370 | 228.1052 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 73977789 | 5825 | 139.8 | 5.825 | 3.1 | 3.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44762548 | 1324 | 227.2961 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 141 | 73983617 | 5828 | 139.872 | 5.828 | 2.9 | 2.9 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44763876 | 1328 | 227.8655 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 142 | 73989604 | 5987 | 143.688 | 5.987 | 2.7 | 2.7 | 3B+1S | 1001 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44765212 | 1336 | 223.1502 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 140 | 131 | 73995418 | 5814 | 139.536 | 5.814 | 2.5 | 2.5 | 2B+1S | 1001 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44766540 | 1328 | 228.4142 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 141 | 74001202 | 5784 | 138.816 | 5.784 | 2.3 | 2.3 | 2B+1S | 1068 | 0 | 1187 | 1185 | 997 | N/A | N/A | N/A | N/A | 44767852 | 1312 | 226.8326 | 100% | 0% | 100% | 100% | 100% | 0% | 10426339 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 132 | 74006667 | 5465 | 131.16 | 5.465 | 1.7 | 1.7 | 2B+1S | 1097 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44768940 | 1088 | 199.0851 | 100% | 0% | 0% | 100% | 100% | 0% | 10426339 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 108 | 74011503 | 4836 | 116.064 | 4.836 | 2.4 | 2.4 | 2B | 0 | 0 | 0 | 1185 | 1138 | N/A | N/A | N/A | N/A | 44769876 | 936 | 193.5484 | 0% | 0% | 0% | 100% | 100% | 44% | 10427217 | 878 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 105 | 74016124 | 4621 | 110.904 | 4.621 | 3.6 | 3.6 | 2B | 0 | 0 | 0 | 1185 | 1078 | N/A | N/A | N/A | N/A | 44770732 | 856 | 185.2413 | 0% | 0% | 0% | 100% | 100% | 44% | 10428394 | 1177 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129819 | 129.819 | 129.819 | [12 empty] | 27536 | 27536 | 212.1107 | [6 empty] | 6884 | 6884 | 1.0617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 3:56 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 9:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (44%)

## MAR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26616 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74016124 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44770732 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10428394 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 97 | 74020286 | 4162 | 99.888 | 4.162 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 44771484 | 752 | 180.6824 | 0% | 0% | 0% | 100% | 100% | 50% | 10429602 | 1208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 98 | 74024556 | 4270 | 102.48 | 4.27 | 6.4 | 6.4 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 44772244 | 760 | 177.9859 | 0% | 0% | 0% | 100% | 100% | 50% | 10430971 | 1369 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 91 | 74028617 | 4061 | 97.464 | 4.061 | 7.9 | 7.9 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44772960 | 716 | 176.3113 | 0% | 0% | 0% | 100% | 100% | 50% | 10432330 | 1359 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 105 | 96 | 74032396 | 3779 | 90.696 | 3.779 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44773628 | 668 | 176.7663 | 0% | 0% | 0% | 100% | 100% | 50% | 10433098 | 768 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 99 | 74036435 | 4039 | 96.936 | 4.039 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 897 | N/A | N/A | N/A | N/A | 44774320 | 692 | 171.3295 | 0% | 0% | 0% | 100% | 100% | 50% | 10433855 | 757 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 118 | 74041125 | 4690 | 112.56 | 4.69 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 44775068 | 748 | 159.4883 | 0% | 0% | 0% | 100% | 100% | 0% | 10433855 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 132 | 74046948 | 5823 | 139.752 | 5.823 | 9.5 | 9.5 | 3B+1S | 945 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 44776308 | 1240 | 212.9487 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 151 | 74052886 | 5938 | 142.512 | 5.938 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44777604 | 1296 | 218.2553 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 151 | 74059229 | 6343 | 152.232 | 6.343 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44778996 | 1392 | 219.4545 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 74065427 | 6198 | 148.752 | 6.198 | 8.5 | 8.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44780356 | 1360 | 219.4256 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 | 1.06
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 74071582 | 6155 | 147.72 | 6.155 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44781724 | 1368 | 222.2583 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 74077754 | 6172 | 148.128 | 6.172 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44783096 | 1372 | 222.2942 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 144 | 74083789 | 6035 | 144.84 | 6.035 | 6.7 | 6.7 | 3B+1S | 1050 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44784476 | 1380 | 228.6661 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 145 | 74089726 | 5937 | 142.488 | 5.937 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44785804 | 1328 | 223.682 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 143 | 74095672 | 5946 | 142.704 | 5.946 | 5.7 | 5.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44787148 | 1344 | 226.0343 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 74101594 | 5922 | 142.128 | 5.922 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44788504 | 1356 | 228.9767 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 74107362 | 5768 | 138.432 | 5.768 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44789812 | 1308 | 226.7684 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 74113275 | 5913 | 141.912 | 5.913 | 4.7 | 4.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44791156 | 1344 | 227.2958 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 74119197 | 5922 | 142.128 | 5.922 | 4.5 | 4.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44792488 | 1332 | 224.924 | 100% | 0% | 100% | 100% | 100% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 120 | 130 | 74124705 | 5508 | 132.192 | 5.508 | 3.8 | 3.8 | 2B+1S | 1026 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44793564 | 1076 | 195.3522 | 100% | 0% | 100% | 100% | 0% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 129 | 74130164 | 5459 | 131.016 | 5.459 | 3.3 | 3.3 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44794608 | 1044 | 191.2438 | 100% | 0% | 100% | 100% | 0% | 0% | 10433855 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 121 | 74135768 | 5604 | 134.496 | 5.604 | 2.7 | 2.7 | 2B+1S | 1046 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44795700 | 1092 | 194.8608 | 100% | 0% | 100% | 100% | 0% | 0% | 10433855 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 105 | 74140419 | 4651 | 111.624 | 4.651 | 3.4 | 3.4 | 2B | 0 | 0 | 1108 | 1185 | 0 | N/A | N/A | N/A | N/A | 44796580 | 880 | 189.2066 | 0% | 0% | 100% | 100% | 0% | 46% | 10434739 | 884 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 103 | 74144673 | 4254 | 102.096 | 4.254 | 4.7 | 4.7 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 44797348 | 768 | 180.536 | 0% | 0% | 100% | 100% | 0% | 46% | 10435819 | 1080 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128549 | 128.549 | 128.549 | [12 empty] | 26616 | 26616 | 207.0495 | [6 empty] | 7425 | 7425 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (50%)
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (46%)

## MAR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26632 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74144673 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44797348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10435819 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 104 | 74148986 | 4313 | 103.512 | 4.313 | 6 | 6 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 44798124 | 776 | 179.9212 | 0% | 0% | 100% | 100% | 0% | 51% | 10437110 | 1291 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 117 | 74153072 | 4086 | 98.064 | 4.086 | 7.5 | 7.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 44798836 | 712 | 174.2535 | 0% | 0% | 100% | 100% | 0% | 51% | 10438492 | 1382 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 93 | 74157143 | 4071 | 97.704 | 4.071 | 9 | 9 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44799540 | 704 | 172.9305 | 0% | 0% | 100% | 100% | 0% | 51% | 10439903 | 1411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 93 | 74161008 | 3865 | 92.76 | 3.865 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 44800220 | 680 | 175.9379 | 0% | 0% | 100% | 100% | 0% | 51% | 10440565 | 662 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 116 | 74165338 | 4330 | 103.92 | 4.33 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 44800936 | 716 | 165.358 | 0% | 0% | 100% | 100% | 0% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 124 | 74170358 | 5020 | 120.48 | 5.02 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44801824 | 888 | 176.8924 | 0% | 0% | 100% | 100% | 0% | 0% | 10440565 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 144 | 74176446 | 6088 | 146.112 | 6.088 | 9.2 | 9.2 | 3B+1S | 1049 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44803164 | 1340 | 220.1051 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 74182679 | 6233 | 149.592 | 6.233 | 8.5 | 8.5 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44804548 | 1384 | 222.044 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 74188986 | 6307 | 151.368 | 6.307 | 7.7 | 9.1 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44805940 | 1392 | 220.7072 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 153 | 74195225 | 6239 | 149.736 | 6.239 | 7.1 | 7.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44807324 | 1384 | 221.8304 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 | 1.04
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 74201425 | 6200 | 148.8 | 6.2 | 6.6 | 6.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44808704 | 1380 | 222.5806 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 74207560 | 6135 | 147.24 | 6.135 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44810068 | 1364 | 222.3309 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 140 | 74213503 | 5943 | 142.632 | 5.943 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44811404 | 1336 | 224.8023 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 74219351 | 5848 | 140.352 | 5.848 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44812724 | 1320 | 225.7182 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 136 | 74225163 | 5812 | 139.488 | 5.812 | 5.3 | 5.3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44814060 | 1336 | 229.8692 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 74230831 | 5668 | 136.032 | 5.668 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44815332 | 1272 | 224.4178 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 74236690 | 5859 | 140.616 | 5.859 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1168 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44816668 | 1336 | 228.0253 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 135 | 74242523 | 5833 | 139.992 | 5.833 | 4.7 | 4.7 | 3B+1S | 1006 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44817980 | 1312 | 224.9271 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 74248318 | 5795 | 139.08 | 5.795 | 4.5 | 4.5 | 3B+1S | 996 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44819288 | 1308 | 225.7118 | 100% | 0% | 100% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 131 | 74253757 | 5439 | 130.536 | 5.439 | 3.8 | 3.8 | 2B+1S | 1048 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44820364 | 1076 | 197.8305 | 100% | 0% | 0% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 74259067 | 5310 | 127.44 | 5.31 | 3.3 | 3.3 | 2B+1S | 1027 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44821404 | 1040 | 195.8569 | 100% | 0% | 0% | 100% | 100% | 0% | 10440565 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 130 | 74264206 | 5139 | 123.336 | 5.139 | 2.8 | 2.8 | 2B+1S | 1027 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44822408 | 1004 | 195.3687 | 100% | 0% | 100% | 100% | 0% | 0% | 10440565 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 111 | 74268887 | 4681 | 112.344 | 4.681 | 3.5 | 3.5 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 44823244 | 836 | 178.5943 | 0% | 0% | 100% | 100% | 0% | 46% | 10441369 | 804 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 101 | 74273091 | 4204 | 100.896 | 4.204 | 5 | 5 | 2B | 0 | 0 | 1097 | 0 | 1097 | N/A | N/A | N/A | N/A | 44823980 | 736 | 175.0714 | 0% | 0% | 100% | 0% | 100% | 46% | 10442591 | 1222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128418 | 128.418 | 128.418 | [12 empty] | 26632 | 26632 | 207.3853 | [6 empty] | 6772 | 6772 | 1.0817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (51%)
XCV2- CLOSED @ 3:37 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @9:00 PM DUE TO PREVENTIVE MAINTENANCE
BP1 - STARTED @9:01 PM DUE TO PREVENTIVE MAINTENANCE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (46%)
BP2 - STOPPED @ 11:00 PM DUE TO PREVENTIVE MAINTENANCE
BP3 - STARTED @ 11:01 PM DUE TO PREVENTIVE MAINTENANCE

## MAR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26088 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74273091 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44823980 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10442591 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 94 | 74277085 | 3994 | 95.856 | 3.994 | 6.3 | 6.3 | 2B | 0 | 0 | 1078 | 0 | 1058 | N/A | N/A | N/A | N/A | 44824625 | 645 | 161.4922 | 0% | 0% | 100% | 0% | 100% | 55% | 10443886 | 1295 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 91 | 74281098 | 4013 | 96.312 | 4.013 | 7.8 | 7.8 | 2B | 0 | 0 | 1078 | 0 | 1058 | N/A | N/A | N/A | N/A | 44825275 | 650 | 161.9736 | 0% | 0% | 100% | 0% | 100% | 55% | 10445198 | 1312 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 125 | 93 | 74285130 | 4032 | 96.768 | 4.032 | 9 | 9 | 2B | 0 | 0 | 1078 | 0 | 1058 | N/A | N/A | N/A | N/A | 44825956 | 681 | 168.8988 | 0% | 0% | 100% | 0% | 100% | 55% | 10446527 | 1329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 95 | 74289030 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 0 | 997 | N/A | N/A | N/A | N/A | 44826496 | 540 | 138.4615 | 0% | 0% | 100% | 0% | 100% | 55% | 10446946 | 419 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 108 | 74292946 | 3916 | 93.984 | 3.916 | 9.5 | 9.5 | 2B | 0 | 0 | 1078 | 0 | 1048 | N/A | N/A | N/A | N/A | 44827052 | 556 | 141.9816 | 0% | 0% | 100% | 0% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 127 | 74298160 | 5214 | 125.136 | 5.214 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 44828008 | 956 | 183.3525 | 0% | 0% | 100% | 0% | 100% | 0% | 10446946 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 145 | 74304207 | 6047 | 145.128 | 6.047 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44829348 | 1340 | 221.5975 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 74310331 | 6124 | 146.976 | 6.124 | 8.5 | 8.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44830724 | 1376 | 224.6897 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 148 | 74316431 | 6100 | 146.4 | 6.1 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44832084 | 1360 | 222.9508 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 74323020 | 6589 | 158.136 | 6.589 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44833560 | 1476 | 224.0097 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 | 1.2
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 74329085 | 6065 | 145.56 | 6.065 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44834852 | 1292 | 213.0256 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 74335109 | 6024 | 144.576 | 6.024 | 6.3 | 6.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44836220 | 1368 | 227.0916 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 140 | 143 | 74340995 | 5886 | 141.264 | 5.886 | 6 | 6 | 3B+1S | 993 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44837572 | 1352 | 229.6976 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 119 | 74346751 | 5756 | 138.144 | 5.756 | 5.8 | 5.8 | 3B+1S | 994 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44838880 | 1308 | 227.2411 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 136 | 74352423 | 5672 | 136.128 | 5.672 | 5.7 | 5.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44840200 | 1320 | 232.7221 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 74358070 | 5647 | 135.528 | 5.647 | 5.6 | 5.6 | 3B+1S | 994 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44841512 | 1312 | 232.3358 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 147 | 74363803 | 5733 | 137.592 | 5.733 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44842836 | 1324 | 230.9437 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 135 | 74369447 | 5644 | 135.456 | 5.644 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44844100 | 1264 | 223.9546 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 74375005 | 5558 | 133.392 | 5.558 | 4.9 | 4.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1127 | N/A | N/A | N/A | N/A | 44845332 | 1232 | 221.6625 | 100% | 0% | 100% | 100% | 100% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 128 | 74380390 | 5385 | 129.24 | 5.385 | 4.4 | 4.4 | 2B+1S | 1037 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44846396 | 1064 | 197.5859 | 100% | 0% | 100% | 100% | 0% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 74385750 | 5360 | 128.64 | 5.36 | 3.7 | 3.7 | 2B+1S | 1057 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44847452 | 1056 | 197.0149 | 100% | 0% | 100% | 100% | 0% | 0% | 10446946 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 124 | 74391014 | 5264 | 126.336 | 5.264 | 3.2 | 3.2 | 2B+1S | 1025 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44848492 | 1040 | 197.5684 | 100% | 0% | 100% | 100% | 0% | 0% | 10446946 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 100 | 74395417 | 4403 | 105.672 | 4.403 | 4 | 4 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 44849324 | 832 | 188.9621 | 0% | 0% | 100% | 100% | 0% | 45% | 10447796 | 850 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 131 | 100 | 74399481 | 4064 | 97.536 | 4.064 | 5.2 | 5.2 | 2B | 0 | 0 | 986 | 1185 | 0 | N/A | N/A | N/A | N/A | 44850068 | 744 | 183.0709 | 0% | 0% | 100% | 100% | 0% | 45% | 10448975 | 1179 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126390 | 126.39 | 126.39 | [12 empty] | 26088 | 26088 | 206.4087 | [6 empty] | 6384 | 6384 | 1.1217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
XCV1- CLOSED @ 3:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## MAR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26656 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74399481 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44850068 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10448975 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 123 | 85 | 74403416 | 3935 | 94.44 | 3.935 | 6.6 | 6.6 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44850788 | 720 | 182.9733 | 0% | 0% | 100% | 100% | 0% | 51% | 10450280 | 1305 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 94 | 74407184 | 3768 | 90.432 | 3.768 | 8 | 8 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 44851476 | 688 | 182.5902 | 0% | 0% | 100% | 100% | 0% | 51% | 10451619 | 1339 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 121 | 88 | 74410857 | 3673 | 88.152 | 3.673 | 9.3 | 9.3 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44852136 | 660 | 179.6896 | 0% | 0% | 100% | 100% | 0% | 51% | 10452911 | 1292 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 97 | 94 | 74414935 | 4078 | 97.872 | 4.078 | 9.5 | 9.5 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44852844 | 708 | 173.6145 | 0% | 0% | 100% | 100% | 0% | 51% | 10453426 | 515 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 140 | 74419176 | 4241 | 101.784 | 4.241 | 9.5 | 9.5 | 2B | 0 | 0 | 927 | 1185 | 0 | N/A | N/A | N/A | N/A | 44853540 | 696 | 164.1122 | 0% | 0% | 100% | 100% | 0% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 126 | 123 | 74423904 | 4728 | 113.472 | 4.728 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44854372 | 832 | 175.9729 | 0% | 0% | 100% | 100% | 0% | 0% | 10453426 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 145 | 74429985 | 6081 | 145.944 | 6.081 | 9.3 | 9.3 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44855796 | 1424 | 234.172 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 74436148 | 6163 | 147.912 | 6.163 | 8.6 | 8.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44857116 | 1320 | 214.1814 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 151 | 74442374 | 6226 | 149.424 | 6.226 | 7.8 | 7.9 | 3B+1S | 1069 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44858508 | 1392 | 223.5785 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 150 | 74448655 | 6281 | 150.744 | 6.281 | 7.2 | 7.2 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44859900 | 1392 | 221.6208 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 | 1.02
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 74454803 | 6148 | 147.552 | 6.148 | 6.5 | 6.5 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44861292 | 1392 | 226.4151 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 74461026 | 6223 | 149.352 | 6.223 | 5.9 | 5.9 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44862692 | 1400 | 224.9719 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 143 | 139 | 74466980 | 5954 | 142.896 | 5.954 | 5.5 | 5.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44864036 | 1344 | 225.7306 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 74472808 | 5828 | 139.872 | 5.828 | 5.4 | 5.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44865356 | 1320 | 226.4928 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 134 | 74478501 | 5693 | 136.632 | 5.693 | 5.2 | 5.2 | 3B+1S | 994 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44866676 | 1320 | 231.8637 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 74484127 | 5626 | 135.024 | 5.626 | 5.1 | 5.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44867984 | 1308 | 232.492 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 74489883 | 5756 | 138.144 | 5.756 | 5 | 5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44869308 | 1324 | 230.0208 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 143 | 74495675 | 5792 | 139.008 | 5.792 | 4.9 | 4.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44870628 | 1320 | 227.9006 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 74501426 | 5751 | 138.024 | 5.751 | 4.7 | 4.7 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44871948 | 1320 | 229.5253 | 100% | 0% | 100% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 121 | 74506730 | 5304 | 127.296 | 5.304 | 4.2 | 4.2 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44873020 | 1072 | 202.1116 | 100% | 0% | 0% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 74512011 | 5281 | 126.744 | 5.281 | 3.6 | 3.6 | 2B+1S | 1036 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44874064 | 1044 | 197.6898 | 100% | 0% | 0% | 100% | 100% | 0% | 10453426 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 127 | 74517314 | 5303 | 127.272 | 5.303 | 3.1 | 3.1 | 2B+1S | 1037 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44875108 | 1044 | 196.8697 | 100% | 0% | 0% | 100% | 100% | 0% | 10453426 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 103 | 74521825 | 4511 | 108.264 | 4.511 | 3.7 | 3.7 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44875980 | 872 | 193.3053 | 0% | 0% | 0% | 100% | 100% | 45% | 10454191 | 765 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 99 | 74525974 | 4149 | 99.576 | 4.149 | 5.1 | 5.1 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 44876724 | 744 | 179.3203 | 0% | 0% | 0% | 100% | 100% | 45% | 10455479 | 1288 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126493 | 126.493 | 126.493 | [12 empty] | 26656 | 26656 | 210.731 | [6 empty] | 6504 | 6504 | 1.0683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (51%)
XCV2- CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## MAR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27008 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74525974 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44876724 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10455479 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 92 | 74530017 | 4043 | 97.032 | 4.043 | 6.7 | 6.7 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 44877448 | 724 | 179.0749 | 0% | 0% | 0% | 100% | 100% | 51% | 10457012 | 1533 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 90 | 74533784 | 3767 | 90.408 | 3.767 | 8.2 | 8.2 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44878132 | 684 | 181.5769 | 0% | 0% | 0% | 100% | 100% | 51% | 10458441 | 1429 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 122 | 92 | 74537408 | 3624 | 86.976 | 3.624 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 44878772 | 640 | 176.6004 | 0% | 0% | 0% | 100% | 100% | 51% | 10459779 | 1338 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 95 | 74541778 | 4370 | 104.88 | 4.37 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 44879452 | 680 | 155.6064 | 0% | 0% | 0% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 102 | 74546452 | 4674 | 112.176 | 4.674 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 44880252 | 800 | 171.1596 | 0% | 0% | 0% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 126 | 74551196 | 4744 | 113.856 | 4.744 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44880996 | 744 | 156.8297 | 0% | 0% | 0% | 100% | 100% | 0% | 10459779 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 156 | 74556401 | 5205 | 124.92 | 5.205 | 9.3 | 9.3 | 3B+1S | 1037 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44882268 | 1272 | 244.3804 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 149 | 74562538 | 6137 | 147.288 | 6.137 | 8.7 | 8.7 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44883628 | 1360 | 221.6066 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 74568729 | 6191 | 148.584 | 6.191 | 8.1 | 7.9 | 3B+1S | 1088 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44885014 | 1386 | 223.8734 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 74574938 | 6209 | 149.016 | 6.209 | 7.4 | 7.4 | 3B+1S | 1088 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44886414 | 1400 | 225.4791 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 | 1.05
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 74581133 | 6195 | 148.68 | 6.195 | 6.7 | 6.5 | 3B+1S | 1088 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44887814 | 1400 | 225.9887 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 74587263 | 6130 | 147.12 | 6.13 | 6.1 | 6.1 | 3B+1S | 1067 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44889144 | 1330 | 216.9657 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 136 | 74593191 | 5928 | 142.272 | 5.928 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44890540 | 1396 | 235.4926 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 148 | 74599088 | 5897 | 141.528 | 5.897 | 5.3 | 5.3 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44891892 | 1352 | 229.2691 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 74605136 | 6048 | 145.152 | 6.048 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44893268 | 1376 | 227.5132 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 146 | 74610952 | 5816 | 139.584 | 5.816 | 4.8 | 4.8 | 3B+1S | 995 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44894592 | 1324 | 227.6479 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 145 | 74616850 | 5898 | 141.552 | 5.898 | 4.6 | 4.6 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44895916 | 1324 | 224.4829 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 136 | 74622773 | 5923 | 142.152 | 5.923 | 4.4 | 4.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44897252 | 1336 | 225.5614 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 143 | 74628700 | 5927 | 142.248 | 5.927 | 4.2 | 4.2 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44898584 | 1332 | 224.7343 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 74634617 | 5917 | 142.008 | 5.917 | 3.9 | 3.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1096 | N/A | N/A | N/A | N/A | 44899906 | 1322 | 223.424 | 100% | 0% | 100% | 100% | 100% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 131 | 74640000 | 5383 | 129.192 | 5.383 | 3.5 | 3.5 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44901004 | 1098 | 203.9755 | 100% | 0% | 100% | 100% | 0% | 0% | 10459779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 129 | 74645305 | 5305 | 127.32 | 5.305 | 3 | 3 | 2B+1S | 1047 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 44902028 | 1024 | 193.0254 | 100% | 0% | 100% | 100% | 0% | 0% | 10459779 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 105 | 74650052 | 4747 | 113.928 | 4.747 | 3.6 | 3.6 | 2B | 0 | 0 | 1087 | 1185 | 0 | N/A | N/A | N/A | N/A | 44902928 | 900 | 189.5934 | 0% | 0% | 100% | 100% | 0% | 45% | 10460502 | 723 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 104 | 74654583 | 4531 | 108.744 | 4.531 | 4.9 | 4.9 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 44903732 | 804 | 177.4443 | 0% | 0% | 100% | 100% | 0% | 45% | 10461653 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128609 | 128.609 | 128.609 | [12 empty] | 27008 | 27008 | 210.0009 | [6 empty] | 6174 | 6174 | 1.1033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (51%)
XCV1- CLOSED @ 2:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## MAR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26872 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74654583 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44903732 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10461653 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 104 | 74658832 | 4249 | 101.976 | 4.249 | 6.3 | 6.3 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 44904484 | 752 | 176.9828 | 0% | 0% | 100% | 100% | 0% | 50% | 10462977 | 1324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 96 | 74663076 | 4244 | 101.856 | 4.244 | 7.7 | 7.7 | 2B | 0 | 0 | 956 | 1185 | 0 | N/A | N/A | N/A | N/A | 44905236 | 752 | 177.1913 | 0% | 0% | 100% | 100% | 0% | 50% | 10464386 | 1409 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 90 | 74666907 | 3831 | 91.944 | 3.831 | 9.1 | 9.1 | 2B | 0 | 0 | 926 | 1185 | 0 | N/A | N/A | N/A | N/A | 44905900 | 664 | 173.3229 | 0% | 0% | 100% | 100% | 0% | 50% | 10465713 | 1327 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 95 | 93 | 74670854 | 3947 | 94.728 | 3.947 | 9.5 | 9.5 | 2B | 0 | 0 | 886 | 1185 | 0 | N/A | N/A | N/A | N/A | 44906560 | 660 | 167.2156 | 0% | 0% | 100% | 100% | 0% | 50% | 10466109 | 396 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 110 | 74675480 | 4626 | 111.024 | 4.626 | 9.5 | 9.5 | 2B | 0 | 0 | 937 | 1185 | 0 | N/A | N/A | N/A | N/A | 44907320 | 760 | 164.2888 | 0% | 0% | 100% | 100% | 0% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 74679912 | 4432 | 106.368 | 4.432 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44908096 | 776 | 175.0903 | 0% | 0% | 100% | 100% | 0% | 0% | 10466109 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 148 | 74686021 | 6109 | 146.616 | 6.109 | 9.1 | 9.1 | 3B+1S | 1048 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44909460 | 1364 | 223.2771 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 74692146 | 6125 | 147 | 6.125 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44910828 | 1368 | 223.3469 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 143 | 74698357 | 6211 | 149.064 | 6.211 | 7.8 | 7.9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44912204 | 1376 | 221.5424 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 74704567 | 6210 | 149.04 | 6.21 | 7.2 | 7.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44913572 | 1368 | 220.2899 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 | 1.05
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 74710684 | 6117 | 146.808 | 6.117 | 6.7 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44914932 | 1360 | 222.3312 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 74716764 | 6080 | 145.92 | 6.08 | 6.2 | 6.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44916292 | 1360 | 223.6842 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 137 | 74722676 | 5912 | 141.888 | 5.912 | 5.7 | 5.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44917644 | 1352 | 228.6874 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 140 | 74728568 | 5892 | 141.408 | 5.892 | 5.3 | 5.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44918996 | 1352 | 229.4637 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 135 | 74734389 | 5821 | 139.704 | 5.821 | 5 | 5 | 3B+1S | 995 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44920300 | 1304 | 224.0165 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 142 | 141 | 74740237 | 5848 | 140.352 | 5.848 | 4.9 | 4.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44921628 | 1328 | 227.0862 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 141 | 74746090 | 5853 | 140.472 | 5.853 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44922960 | 1332 | 227.5756 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 144 | 74752020 | 5930 | 142.32 | 5.93 | 4.6 | 4.6 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44924308 | 1348 | 227.3187 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 141 | 74757924 | 5904 | 141.696 | 5.904 | 4.4 | 4.4 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44925652 | 1344 | 227.6423 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 131 | 74763474 | 5550 | 133.2 | 5.55 | 3.8 | 3.8 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44926748 | 1096 | 197.4775 | 100% | 0% | 100% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 132 | 74769052 | 5578 | 133.872 | 5.578 | 3.1 | 3.1 | 2B+1S | 1057 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44927816 | 1068 | 191.4665 | 100% | 0% | 0% | 100% | 100% | 0% | 10466109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 132 | 74774522 | 5470 | 131.28 | 5.47 | 2.4 | 2.4 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44928900 | 1084 | 198.1718 | 100% | 0% | 0% | 100% | 100% | 0% | 10466109 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 112 | 74779258 | 4736 | 113.664 | 4.736 | 3.2 | 3.2 | 2B | 0 | 0 | 0 | 1185 | 1128 | N/A | N/A | N/A | N/A | 44929796 | 896 | 189.1892 | 0% | 0% | 0% | 100% | 100% | 45% | 10466977 | 868 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 107 | 74783716 | 4458 | 106.992 | 4.458 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1057 | N/A | N/A | N/A | N/A | 44930604 | 808 | 181.2472 | 0% | 0% | 0% | 100% | 100% | 45% | 10468253 | 1276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129133 | 129.133 | 129.133 | [12 empty] | 26872 | 26872 | 208.0955 | [6 empty] | 6600 | 6600 | 1.045 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (50%)
XCV2- CLOSED @ 3:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## MAR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26624 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74783716 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44930604 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10468253 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 99 | 74788104 | 4388 | 105.312 | 4.388 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 44931372 | 768 | 175.0228 | 0% | 0% | 0% | 100% | 100% | 50% | 10469534 | 1281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 74791939 | 3835 | 92.04 | 3.835 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44932072 | 700 | 182.5293 | 0% | 0% | 0% | 100% | 100% | 50% | 10470861 | 1327 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 93 | 74796016 | 4077 | 97.848 | 4.077 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44932784 | 712 | 174.6382 | 0% | 0% | 0% | 100% | 100% | 50% | 10472288 | 1427 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 99 | 74799869 | 3853 | 92.472 | 3.853 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 917 | N/A | N/A | N/A | N/A | 44933460 | 676 | 175.4477 | 0% | 0% | 0% | 100% | 100% | 50% | 10473021 | 733 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 102 | 74804051 | 4182 | 100.368 | 4.182 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 44934140 | 680 | 162.6016 | 0% | 0% | 0% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 74808811 | 4760 | 114.24 | 4.76 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44934956 | 816 | 171.4286 | 0% | 0% | 0% | 100% | 100% | 0% | 10473021 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 74814723 | 5912 | 141.888 | 5.912 | 9.4 | 9.4 | 3B+1S | 1037 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44936240 | 1284 | 217.1854 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 74821048 | 6325 | 151.8 | 6.325 | 8.9 | 8.9 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44937652 | 1412 | 223.2411 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 149 | 74827196 | 6148 | 147.552 | 6.148 | 8.2 | 7.9 | 3B+1S | 1038 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44939012 | 1360 | 221.2101 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 74833585 | 6389 | 153.336 | 6.389 | 7.6 | 7.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44940422 | 1410 | 220.6918 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 | 1.25
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 74839050 | 5465 | 131.16 | 5.465 | 7.2 | 6.5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44941596 | 1174 | 214.8216 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 74845165 | 6115 | 146.76 | 6.115 | 6.8 | 6.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44942980 | 1384 | 226.3287 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 163 | 74851365 | 6200 | 148.8 | 6.2 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44944368 | 1388 | 223.871 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 74857104 | 5739 | 137.736 | 5.739 | 5.9 | 5.9 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44945651 | 1283 | 223.5581 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 74863012 | 5908 | 141.792 | 5.908 | 5.6 | 5.6 | 3B+1S | 1004 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44946944 | 1293 | 218.8558 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 74868922 | 5910 | 141.84 | 5.91 | 5.3 | 5.3 | 3B+1S | 1001 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44948324 | 1380 | 233.5025 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 74874756 | 5834 | 140.016 | 5.834 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44949652 | 1328 | 227.6311 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 143 | 74880678 | 5922 | 142.128 | 5.922 | 4.6 | 4.6 | 3B+1S | 1000 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44950992 | 1340 | 226.2749 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 141 | 74886545 | 5867 | 140.808 | 5.867 | 4.4 | 4.4 | 3B+1S | 1001 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44952324 | 1332 | 227.0326 | 100% | 0% | 100% | 100% | 100% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 133 | 74892157 | 5612 | 134.688 | 5.612 | 3.4 | 3.4 | 2B+1S | 1099 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44953420 | 1096 | 195.2958 | 100% | 0% | 100% | 100% | 0% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 128 | 74897686 | 5529 | 132.696 | 5.529 | 2.8 | 2.8 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44954484 | 1064 | 192.4399 | 100% | 0% | 100% | 100% | 0% | 0% | 10473021 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 127 | 74903096 | 5410 | 129.84 | 5.41 | 2.3 | 2.3 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 44955540 | 1056 | 195.1941 | 100% | 0% | 100% | 100% | 0% | 0% | 10473021 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 112 | 74907926 | 4830 | 115.92 | 4.83 | 3.1 | 3.1 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 44956448 | 908 | 187.9917 | 0% | 0% | 100% | 100% | 0% | 45% | 10473902 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 103 | 74912183 | 4257 | 102.168 | 4.257 | 4.3 | 4.3 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 44957228 | 780 | 183.2276 | 0% | 0% | 100% | 100% | 0% | 45% | 10474964 | 1062 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128467 | 128.467 | 128.467 | [12 empty] | 26624 | 26624 | 207.2439 | [6 empty] | 6711 | 6711 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (50%)
XCV1- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:22 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MERALCO POWER FLUCTUATION @ 10:02AM
ALL PUMP STOPPED DUE TO POWER FLUCTUATION @ 10:02AM
BP2 POWER RESUME @ 10:04AM
BP3 POWER RESUME @ 10:06AM
BP1 POWER RESUME @ 10:08AM
SP1 POWER RESUME @ 10:10AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## MAR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26844 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 74912183 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44957228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10474964 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 100 | 74916365 | 4182 | 100.368 | 4.182 | 5.6 | 5.6 | 2B | 0 | 0 | 1026 | 1185 | 0 | N/A | N/A | N/A | N/A | 44957972 | 744 | 177.9053 | 0% | 0% | 100% | 100% | 0% | 50% | 10476175 | 1211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 74920502 | 4137 | 99.288 | 4.137 | 6.6 | 6.6 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 44958708 | 736 | 177.9067 | 0% | 0% | 100% | 100% | 0% | 50% | 10477437 | 1262 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 98 | 74924522 | 4020 | 96.48 | 4.02 | 7.7 | 7.7 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 44959420 | 712 | 177.1144 | 0% | 0% | 100% | 100% | 0% | 50% | 10478244 | 807 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 112 | 94 | 74928684 | 4162 | 99.888 | 4.162 | 8.5 | 8.5 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 44960140 | 720 | 172.9938 | 0% | 0% | 100% | 100% | 0% | 50% | 10478976 | 732 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 122 | 101 | 74932586 | 3902 | 93.648 | 3.902 | 9.2 | 9.2 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 44960820 | 680 | 174.2696 | 0% | 0% | 100% | 100% | 0% | 50% | 10479638 | 662 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 124 | 121 | 74937501 | 4915 | 117.96 | 4.915 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 44961672 | 852 | 173.3469 | 0% | 0% | 100% | 100% | 0% | 0% | 10479638 | 0 | 1.34 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 138 | 74943202 | 5701 | 136.824 | 5.701 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44962876 | 1204 | 211.191 | 0% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 145 | 74949250 | 6048 | 145.152 | 6.048 | 9.4 | 9.4 | 3B+1S | 976 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44964220 | 1344 | 222.2222 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 146 | 74955427 | 6177 | 148.248 | 6.177 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44965572 | 1352 | 218.8765 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 74961721 | 6294 | 151.056 | 6.294 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44966968 | 1396 | 221.7985 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 | 1.05
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 74967930 | 6209 | 149.016 | 6.209 | 8 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44968340 | 1372 | 220.9696 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 151 | 74974077 | 6147 | 147.528 | 6.147 | 7.5 | 7.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44969716 | 1376 | 223.849 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 146 | 74980185 | 6108 | 146.592 | 6.108 | 7.1 | 7.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44971116 | 1400 | 229.2076 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 143 | 74986037 | 5852 | 140.448 | 5.852 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44972420 | 1304 | 222.8298 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 142 | 74991915 | 5878 | 141.072 | 5.878 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44973764 | 1344 | 228.6492 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 140 | 74997784 | 5869 | 140.856 | 5.869 | 5.8 | 5.8 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44975108 | 1344 | 228.9998 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 75003663 | 5879 | 141.096 | 5.879 | 5.4 | 5.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44976452 | 1344 | 228.6103 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 146 | 75009583 | 5920 | 142.08 | 5.92 | 4.9 | 4.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 44977800 | 1348 | 227.7027 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 75015541 | 5958 | 142.992 | 5.958 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44979140 | 1340 | 224.9077 | 100% | 0% | 100% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 129 | 75021059 | 5518 | 132.432 | 5.518 | 3.9 | 3.9 | 2B+1S | 1058 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44980260 | 1120 | 202.9721 | 100% | 0% | 0% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 133 | 75026615 | 5556 | 133.344 | 5.556 | 3.2 | 3.2 | 2B+1S | 1057 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44981336 | 1076 | 193.6645 | 100% | 0% | 0% | 100% | 100% | 0% | 10479638 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 129 | 75032132 | 5517 | 132.408 | 5.517 | 2.6 | 2.6 | 2B+1S | 1057 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44982420 | 1084 | 196.4836 | 100% | 0% | 0% | 100% | 100% | 0% | 10479638 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 107 | 75036732 | 4600 | 110.4 | 4.6 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 44983284 | 864 | 187.8261 | 0% | 0% | 0% | 100% | 100% | 45% | 10480771 | 1133 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 100 | 75041158 | 4426 | 106.224 | 4.426 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1028 | N/A | N/A | N/A | N/A | 44984072 | 788 | 178.0389 | 0% | 0% | 0% | 100% | 100% | 45% | 10481979 | 1208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128975 | 128.975 | 128.975 | [12 empty] | 26844 | 26844 | 208.1334 | [6 empty] | 7015 | 7015 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (50%)
XCV2- CLOSED @ 5:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## MAR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27140 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75041158 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 44984072 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10481979 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 100 | 75045182 | 4024 | 96.576 | 4.024 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 44984792 | 720 | 178.9264 | 0% | 0% | 0% | 100% | 100% | 50% | 10483126 | 1147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 97 | 75049583 | 4401 | 105.624 | 4.401 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 986 | N/A | N/A | N/A | N/A | 44985564 | 772 | 175.4147 | 0% | 0% | 0% | 100% | 100% | 50% | 10484492 | 1366 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 117 | 88 | 75053514 | 3931 | 94.344 | 3.931 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44986252 | 688 | 175.0191 | 0% | 0% | 0% | 100% | 100% | 50% | 10485752 | 1260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 108 | 88 | 75057202 | 3688 | 88.512 | 3.688 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44986908 | 656 | 177.8742 | 0% | 0% | 0% | 100% | 100% | 50% | 10486586 | 834 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 106 | 98 | 75061367 | 4165 | 99.96 | 4.165 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 936 | N/A | N/A | N/A | N/A | 44987596 | 688 | 165.1861 | 0% | 0% | 0% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 128 | 75066597 | 5230 | 125.52 | 5.23 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44988508 | 912 | 174.3786 | 0% | 0% | 0% | 100% | 100% | 0% | 10486586 | 0 | 1.24 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 141 | 75072692 | 6095 | 146.28 | 6.095 | 9.1 | 9.1 | 3B | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44989844 | 1336 | 219.1961 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 75078935 | 6243 | 149.832 | 6.243 | 8.4 | 8.4 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 44991232 | 1388 | 222.329 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 75085217 | 6282 | 150.768 | 6.282 | 7.8 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44992612 | 1380 | 219.6753 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 151 | 75091458 | 6241 | 149.784 | 6.241 | 7.2 | 7.2 | 3B+1S | 1045 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44993996 | 1384 | 221.7593 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 | 1.19
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 75097667 | 6209 | 149.016 | 6.209 | 6.7 | 6.5 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44995368 | 1372 | 220.9696 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 75103715 | 6048 | 145.152 | 6.048 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44996732 | 1364 | 225.5291 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 145 | 75109737 | 6022 | 144.528 | 6.022 | 5.7 | 5.7 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44998092 | 1360 | 225.8386 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 145 | 75115749 | 6012 | 144.288 | 6.012 | 5.1 | 5.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44999444 | 1352 | 224.8836 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 144 | 75121683 | 5934 | 142.416 | 5.934 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45000796 | 1352 | 227.8396 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 75127583 | 5900 | 141.6 | 5.9 | 4.4 | 4.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45002132 | 1336 | 226.4407 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 75133454 | 5871 | 140.904 | 5.871 | 4 | 4 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45003468 | 1336 | 227.5592 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 139 | 75139374 | 5920 | 142.08 | 5.92 | 3.6 | 3.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45004804 | 1336 | 225.6757 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 75145215 | 5841 | 140.184 | 5.841 | 3.4 | 3.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45006140 | 1336 | 228.728 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 140 | 75151063 | 5848 | 140.352 | 5.848 | 3.2 | 3.2 | 3B+1S | 994 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45007468 | 1328 | 227.0862 | 100% | 0% | 100% | 100% | 100% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 131 | 75156571 | 5508 | 132.192 | 5.508 | 2.7 | 2.7 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45008548 | 1080 | 196.0784 | 100% | 0% | 100% | 100% | 0% | 0% | 10486586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 124 | 75161766 | 5195 | 124.68 | 5.195 | 2.2 | 2.2 | 2B+1S | 1016 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45009568 | 1020 | 196.3426 | 100% | 0% | 100% | 100% | 0% | 0% | 10486586 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 106 | 75166352 | 4586 | 110.064 | 4.586 | 3 | 3 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 45010420 | 852 | 185.7828 | 0% | 0% | 100% | 100% | 0% | 50% | 10487480 | 894 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 106 | 75170743 | 4391 | 105.384 | 4.391 | 4.5 | 4.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45011212 | 792 | 180.3689 | 0% | 0% | 100% | 100% | 0% | 50% | 10488817 | 1337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129585 | 129.585 | 129.585 | [12 empty] | 27140 | 27140 | 209.4378 | [6 empty] | 6838 | 6838 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (50%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## MAR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27124 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75170743 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45011212 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10488817 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 101 | 75174835 | 4092 | 98.208 | 4.092 | 6.3 | 6.3 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 45011988 | 776 | 189.6383 | 0% | 0% | 100% | 100% | 0% | 60% | 10490182 | 1365 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 102 | 75178935 | 4100 | 98.4 | 4.1 | 7.6 | 7.6 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 45012773 | 785 | 191.4634 | 0% | 0% | 100% | 100% | 0% | 50% | 10491550 | 1368 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 99 | 75183055 | 4120 | 98.88 | 4.12 | 8.8 | 8.8 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45013576 | 803 | 194.9029 | 0% | 0% | 100% | 100% | 0% | 50% | 10492931 | 1381 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 101 | 75186998 | 3943 | 94.632 | 3.943 | 9.3 | 9.3 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45014158 | 582 | 147.6033 | 0% | 0% | 100% | 100% | 0% | 50% | 10493698 | 767 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 98 | 75190960 | 3962 | 95.088 | 3.962 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45014756 | 598 | 150.9339 | 0% | 0% | 100% | 100% | 0% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 125 | 75196203 | 5243 | 125.832 | 5.243 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45015404 | 648 | 123.5934 | 0% | 0% | 100% | 100% | 0% | 0% | 10493698 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 145 | 75202170 | 5967 | 143.208 | 5.967 | 9.1 | 9.1 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45016980 | 1576 | 264.1193 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 150 | 75208465 | 6295 | 151.08 | 6.295 | 8.5 | 8.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45018368 | 1388 | 220.4925 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 75214677 | 6212 | 149.088 | 6.212 | 7.9 | 9.1 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45019748 | 1380 | 222.1507 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 75220933 | 6256 | 150.144 | 6.256 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45021136 | 1388 | 221.867 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 | 1.25
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 75227184 | 6251 | 150.024 | 6.251 | 6.7 | 6.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45022508 | 1372 | 219.4849 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 75233255 | 6071 | 145.704 | 6.071 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45023876 | 1368 | 225.3336 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 75239260 | 6005 | 144.12 | 6.005 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45025220 | 1344 | 223.8135 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 128 | 75245195 | 5935 | 142.44 | 5.935 | 5.3 | 5.3 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45026568 | 1348 | 227.1272 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 75251049 | 5854 | 140.496 | 5.854 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45027900 | 1332 | 227.5367 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 75256861 | 5812 | 139.488 | 5.812 | 4.8 | 4.8 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45029228 | 1328 | 228.4928 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 145 | 75262702 | 5841 | 140.184 | 5.841 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45030556 | 1328 | 227.3583 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 143 | 75268630 | 5928 | 142.272 | 5.928 | 4.1 | 4.1 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45031896 | 1340 | 226.0459 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 123 | 75274438 | 5808 | 139.392 | 5.808 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45033228 | 1332 | 229.3388 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 75280143 | 5705 | 136.92 | 5.705 | 3.6 | 3.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45034484 | 1256 | 220.1578 | 100% | 0% | 100% | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 130 | 75285604 | 5461 | 131.064 | 5.461 | 3.2 | 3.2 | 2B+1S | 1058 | 0 |  | 1185 | 1188 | N/A | N/A | N/A | N/A | 45035548 | 1064 | 194.8361 | 100% | 0% |  | 100% | 100% | 0% | 10493698 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 129 | 75291077 | 5473 | 131.352 | 5.473 | 2.6 | 2.6 | 2B+1S | 1057 | 0 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 45036616 | 1068 | 195.1398 | 100% | 0% |  | 100% | 100% | 0% | 10493698 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 125 | 75295756 | 4679 | 112.296 | 4.679 | 3.2 | 3.2 | 2B | 0 | 0 |  | 1185 | 1117 | N/A | N/A | N/A | N/A | 45037500 | 884 | 188.9293 | 0% | 0% |  | 100% | 100% | 45% | 10494410 | 712 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 109 | 75300327 | 4571 | 109.704 | 4.571 | 4.2 | 4.2 | 2B | 0 | 0 |  | 1185 | 1077 | N/A | N/A | N/A | N/A | 45038336 | 836 | 182.8921 | 0% | 0% |  | 100% | 100% | 45% | 10495311 | 901 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129584 | 129.584 | 129.584 | [12 empty] | 27124 | 27124 | 209.316 | [6 empty] | 6494 | 6494 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (60%)
XCV2- CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## MAR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26952 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75300327 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45038336 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10495311 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 100 | 75304594 | 4267 | 102.408 | 4.267 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45039120 | 784 | 183.7356 | 0% | 0% | 0% | 100% | 100% | 55% | 10496408 | 1097 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 98 | 75308842 | 4248 | 101.952 | 4.248 | 6.6 | 6.6 | 2B | 0 | 0 | 0 | 1185 | 1006 | N/A | N/A | N/A | N/A | 45039884 | 764 | 179.8493 | 0% | 0% | 0% | 100% | 100% | 55% | 10497725 | 1317 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 95 | 75312933 | 4091 | 98.184 | 4.091 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45040600 | 716 | 175.0183 | 0% | 0% | 0% | 100% | 100% | 55% | 10499086 | 1361 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 94 | 75316985 | 4052 | 97.248 | 4.052 | 8.9 | 8.9 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45041308 | 708 | 174.7285 | 0% | 0% | 0% | 100% | 100% | 55% | 10499759 | 673 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 126 | 106 | 75321153 | 4168 | 100.032 | 4.168 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45042020 | 712 | 170.8253 | 0% | 0% | 0% | 100% | 100% | 55% | 10500270 | 511 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 133 | 75326187 | 5034 | 120.816 | 5.034 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45042848 | 828 | 164.4815 | 0% | 0% | 0% | 100% | 100% | 0% | 10500270 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 146 | 75332030 | 5843 | 140.232 | 5.843 | 9.2 | 9.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45044140 | 1292 | 221.1193 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 75338173 | 6143 | 147.432 | 6.143 | 8.7 | 8.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45045500 | 1360 | 221.3902 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 75344440 | 6267 | 150.408 | 6.267 | 8.2 | 8.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45046876 | 1376 | 219.5628 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 153 | 75350639 | 6199 | 148.776 | 6.199 | 7.6 | 7.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45048252 | 1376 | 221.9713 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 | 1.05
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 75356817 | 6178 | 148.272 | 6.178 | 7.1 | 6.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45049628 | 1376 | 222.7258 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 75363067 | 6250 | 150 | 6.25 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45051020 | 1392 | 222.72 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 144 | 75369009 | 5942 | 142.608 | 5.942 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45052368 | 1348 | 226.8596 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 145 | 75374890 | 5881 | 141.144 | 5.881 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45053724 | 1356 | 230.573 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 75380681 | 5791 | 138.984 | 5.791 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45055044 | 1320 | 227.9399 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 75386475 | 5794 | 139.056 | 5.794 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45056372 | 1328 | 229.2026 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 75392377 | 5902 | 141.648 | 5.902 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45057716 | 1344 | 227.7194 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 136 | 75398333 | 5956 | 142.944 | 5.956 | 4.5 | 4.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45059052 | 1336 | 224.3116 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 139 | 75404164 | 5831 | 139.944 | 5.831 | 4.3 | 4.3 | 3B+1S | 995 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45060380 | 1328 | 227.7482 | 100% | 0% | 100% | 100% | 100% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 131 | 75409674 | 5510 | 132.24 | 5.51 | 3.8 | 3.8 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45061460 | 1080 | 196.0073 | 100% | 0% | 100% | 100% | 0% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 130 | 75415096 | 5422 | 130.128 | 5.422 | 3.3 | 3.3 | 2B+1S | 1057 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45062500 | 1040 | 191.8111 | 100% | 0% | 100% | 100% | 0% | 0% | 10500270 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 108 | 75420546 | 5450 | 130.8 | 5.45 | 2.7 | 2.7 | 2B+1S | 1058 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45063572 | 1072 | 196.6972 | 100% | 0% | 100% | 100% | 0% | 0% | 10500270 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 110 | 75425062 | 4516 | 108.384 | 4.516 | 3.5 | 3.5 | 2B | 0 | 0 | 1138 | 1185 | 0 | N/A | N/A | N/A | N/A | 45064436 | 864 | 191.3198 | 0% | 0% | 100% | 100% | 0% | 50% | 10501136 | 866 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 100 | 75429713 | 4651 | 111.624 | 4.651 | 5 | 5 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 45065288 | 852 | 183.1864 | 0% | 0% | 100% | 100% | 0% | 50% | 10502445 | 1309 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129386 | 129.386 | 129.386 | [12 empty] | 26952 | 26952 | 208.3069 | [6 empty] | 7134 | 7134 | 1.0733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
XCV1- CLOSED @ 5:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## MAR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26268 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75429713 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45065288 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10502445 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 97 | 75433802 | 4089 | 98.136 | 4.089 | 6.3 | 6.3 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45066024 | 736 | 179.9951 | 0% | 0% | 100% | 100% | 0% | 55% | 10503757 | 1312 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 89 | 75437788 | 3986 | 95.664 | 3.986 | 7.7 | 7.7 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 45066736 | 712 | 178.6252 | 0% | 0% | 100% | 100% | 0% | 55% | 10505110 | 1353 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 92 | 75441653 | 3865 | 92.76 | 3.865 | 9 | 9 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45067420 | 684 | 176.9728 | 0% | 0% | 100% | 100% | 0% | 55% | 10506392 | 1282 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 92 | 75445486 | 3833 | 91.992 | 3.833 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45068077 | 657 | 171.4062 | 0% | 0% | 100% | 100% | 0% | 55% | 10506891 | 499 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 101 | 97 | 75449351 | 3865 | 92.76 | 3.865 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 45068756 | 679 | 175.6792 | 0% | 0% | 100% | 100% | 0% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 122 | 116 | 75454127 | 4776 | 114.624 | 4.776 | 9.5 | 9.5 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 45069524 | 768 | 160.804 | 0% | 0% | 100% | 100% | 0% | 0% | 10506891 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 140 | 75459574 | 5447 | 130.728 | 5.447 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45070648 | 1124 | 206.3521 | 0% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 143 | 75465580 | 6006 | 144.144 | 6.006 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45071896 | 1248 | 207.7922 | 0% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 148 | 145 | 75471610 | 6030 | 144.72 | 6.03 | 9.5 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45073141 | 1245 | 206.4677 | 0% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 152 | 75477860 | 6250 | 150 | 6.25 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45074552 | 1411 | 225.76 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 | 1.12
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 75484033 | 6173 | 148.152 | 6.173 | 8.8 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45075914 | 1362 | 220.6383 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 75490173 | 6140 | 147.36 | 6.14 | 8.4 | 8.4 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45077254 | 1340 | 218.241 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 75496256 | 6083 | 145.992 | 6.083 | 8 | 8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45078628 | 1374 | 225.8754 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 141 | 75502200 | 5944 | 142.656 | 5.944 | 7.6 | 7.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45079988 | 1360 | 228.8022 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 75508049 | 5849 | 140.376 | 5.849 | 7.2 | 7.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45081312 | 1324 | 226.3635 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 75513972 | 5923 | 142.152 | 5.923 | 6.8 | 6.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45082652 | 1340 | 226.2367 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 75519938 | 5966 | 143.184 | 5.966 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45084004 | 1352 | 226.6175 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 143 | 75525971 | 6033 | 144.792 | 6.033 | 5.9 | 5.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45085348 | 1344 | 222.7747 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 75531965 | 5994 | 143.856 | 5.994 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45086692 | 1344 | 224.2242 | 100% | 0% | 100% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 133 | 75537528 | 5563 | 133.512 | 5.563 | 4.9 | 4.9 | 2B+1S | 1068 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45087804 | 1112 | 199.8921 | 100% | 0% | 0% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 119 | 130 | 75543111 | 5583 | 133.992 | 5.583 | 4.2 | 4.2 | 2B+1S | 1067 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45088880 | 1076 | 192.7279 | 100% | 0% | 0% | 100% | 100% | 0% | 10506891 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 121 | 75548444 | 5333 | 127.992 | 5.333 | 3.7 | 3.7 | 2B+1S | 1005 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45089924 | 1044 | 195.7622 | 100% | 0% | 0% | 100% | 100% | 0% | 10506891 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 105 | 75553166 | 4722 | 113.328 | 4.722 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45090804 | 880 | 186.3617 | 0% | 0% | 0% | 100% | 100% | 45% | 10507794 | 903 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 133 | 98 | 75557465 | 4299 | 103.176 | 4.299 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 986 | N/A | N/A | N/A | N/A | 45091556 | 752 | 174.9244 | 0% | 0% | 0% | 100% | 100% | 45% | 10509110 | 1316 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127752 | 127.752 | 127.752 | [12 empty] | 26268 | 26268 | 205.6171 | [6 empty] | 6665 | 6665 | 1.1083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (55%)
XCV2- CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 9:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## MAR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24608 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75557465 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45091556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10509110 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 101 | 75561478 | 4013 | 96.312 | 4.013 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 987 | N/A | N/A | N/A | N/A | 45092260 | 704 | 175.4299 | 0% | 0% | 0% | 100% | 100% | 50% | 10510241 | 1131 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 106 | 75565463 | 3985 | 95.64 | 3.985 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 45092960 | 700 | 175.6587 | 0% | 0% | 0% | 100% | 100% | 50% | 10511467 | 1226 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 115 | 100 | 75569392 | 3929 | 94.296 | 3.929 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 926 | N/A | N/A | N/A | N/A | 45093631 | 671 | 170.7814 | 0% | 0% | 0% | 100% | 100% | 50% | 10512504 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 105 | 75573556 | 4164 | 99.936 | 4.164 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 45094320 | 689 | 165.4659 | 0% | 0% | 0% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 100 | 99 | 75577534 | 3978 | 95.472 | 3.978 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 916 | N/A | N/A | N/A | N/A | 45094980 | 660 | 165.9125 | 0% | 0% | 0% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 23 | 16.1972 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 117 | 109 | 75582134 | 4600 | 110.4 | 4.6 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 947 | N/A | N/A | N/A | N/A | 45095700 | 720 | 156.5217 | 0% | 0% | 0% | 100% | 100% | 0% | 10512504 | 0 | 0.97 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 141 | 75587647 | 5513 | 132.312 | 5.513 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 45096768 | 1068 | 193.7239 | 0% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 140 | 75593432 | 5785 | 138.84 | 5.785 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 45097940 | 1172 | 202.5929 | 0% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 146 | 151 | 75599394 | 5962 | 143.088 | 5.962 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45099172 | 1232 | 206.6421 | 0% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 146 | 75605520 | 6126 | 147.024 | 6.126 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45100524 | 1352 | 220.6987 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 | 1.24
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 75611485 | 5965 | 143.16 | 5.965 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45101852 | 1328 | 222.632 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 75617599 | 6114 | 146.736 | 6.114 | 8.7 | 8.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45103224 | 1372 | 224.403 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 133 | 75623430 | 5831 | 139.944 | 5.831 | 8.4 | 8.4 | 3B+1S | 996 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45104528 | 1304 | 223.6323 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 134 | 75629029 | 5599 | 134.376 | 5.599 | 8 | 8 | 3B+1S | 1015 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45105736 | 1208 | 215.7528 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 127 | 131 | 75634569 | 5540 | 132.96 | 5.54 | 7.6 | 7.6 | 3B+1S | 1016 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45106956 | 1220 | 220.2166 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 11 | 7.7465 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 127 | 135 | 75640082 | 5513 | 132.312 | 5.513 | 7.3 | 7.3 | 3B+1S | 1007 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45108168 | 1212 | 219.844 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 136 | 75645608 | 5526 | 132.624 | 5.526 | 7 | 7 | 3B+1S | 1006 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45109380 | 1212 | 219.3268 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 125 | 132 | 75651120 | 5512 | 132.288 | 5.512 | 6.7 | 6.7 | 3B+1S | 1005 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 45110556 | 1176 | 213.3527 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 10 | 7.0423 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 123 | 132 | 75656608 | 5488 | 131.712 | 5.488 | 6.3 | 6.3 | 3B+1S | 1006 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 45111720 | 1164 | 212.0991 | 100% | 0% | 100% | 100% | 100% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 127 | 75661866 | 5258 | 126.192 | 5.258 | 5.9 | 5.9 | 2B+1S | 1006 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 45112724 | 1004 | 190.9471 | 100% | 0% | 100% | 100% | 0% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 15 | 10.5634 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 124 | 75667154 | 5288 | 126.912 | 5.288 | 5.6 | 5.6 | 2B+1S | 1007 | 0 | 1158 | 1185 | 0 | N/A | N/A | N/A | N/A | 45113708 | 984 | 186.0817 | 100% | 0% | 100% | 100% | 0% | 0% | 10512504 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 17 | 11.9718 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 104 | 122 | 75672360 | 5206 | 124.944 | 5.206 | 5.3 | 5.3 | 2B+1S | 1006 | 0 | 1038 | 1185 | 0 | N/A | N/A | N/A | N/A | 45114684 | 976 | 187.476 | 100% | 0% | 100% | 100% | 0% | 0% | 10512504 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 128 | 105 | 75676735 | 4375 | 105 | 4.375 | 5.9 | 5.9 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45115436 | 752 | 171.8857 | 0% | 0% | 100% | 100% | 0% | 35% | 10513283 | 779 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 95 | 75681011 | 4276 | 102.624 | 4.276 | 6.8 | 6.8 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 45116164 | 728 | 170.2526 | 0% | 0% | 100% | 100% | 0% | 35% | 10514184 | 901 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123546 | 123.546 | 123.546 | [12 empty] | 24608 | 24608 | 199.1809 | [6 empty] | 5074 | 5074 | 1.1 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (50%)
XCV1- CLOSED @ 2:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 9:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (35%)

## MAR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25968 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75681011 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45116164 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10514184 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 91 | 75684975 | 3964 | 95.136 | 3.964 | 8 | 8 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 45116868 | 704 | 177.5984 | 0% | 0% | 100% | 100% | 0% | 45% | 10515301 | 1117 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 87 | 75688859 | 3884 | 93.216 | 3.884 | 9.2 | 9.2 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 45117540 | 672 | 173.0175 | 0% | 0% | 100% | 100% | 0% | 45% | 10516484 | 1183 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 18 | 12.6761 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 94 | 95 | 75692759 | 3900 | 93.6 | 3.9 | 9.5 | 9.5 | 2B | 0 | 0 | 887 | 1185 | 0 | N/A | N/A | N/A | N/A | 45118196 | 656 | 168.2051 | 0% | 0% | 100% | 100% | 0% | 45% | 10516651 | 167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 92 | 90 | 75696502 | 3743 | 89.832 | 3.743 | 9.5 | 9.5 | 2B | 0 | 0 | 887 | 1185 | 0 | N/A | N/A | N/A | N/A | 45118840 | 644 | 172.0545 | 0% | 0% | 100% | 100% | 0% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 24 | 16.9014 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 104 | 102 | 75700225 | 3723 | 89.352 | 3.723 | 9.5 | 9.5 | 2B | 0 | 0 | 887 | 1185 | 0 | N/A | N/A | N/A | N/A | 45119480 | 640 | 171.9044 | 0% | 0% | 100% | 100% | 0% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 20 | 14.0845 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 113 | 75704912 | 4687 | 112.488 | 4.687 | 9.5 | 9.5 | 2B | 0 | 0 | 1048 | 1185 | 0 | N/A | N/A | N/A | N/A | 45120196 | 716 | 152.763 | 0% | 0% | 100% | 100% | 0% | 0% | 10516651 | 0 | 1.23 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 139 | 75710461 | 5549 | 133.176 | 5.549 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45121348 | 1152 | 207.605 | 0% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 | 147 | 75716487 | 6026 | 144.624 | 6.026 | 9.3 | 9.3 | 3B | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45122668 | 1320 | 219.0508 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 75722714 | 6227 | 149.448 | 6.227 | 8.9 | 8.9 | 3B | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45124036 | 1368 | 219.6885 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 75728956 | 6242 | 149.808 | 6.242 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45125420 | 1384 | 221.7238 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 | 1.24
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 75735292 | 6336 | 152.064 | 6.336 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45126820 | 1400 | 220.9596 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 151 | 75741503 | 6211 | 149.064 | 6.211 | 7.4 | 7.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45128192 | 1372 | 220.8984 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 144 | 75747516 | 6013 | 144.312 | 6.013 | 7 | 7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45129540 | 1348 | 224.1809 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 75753277 | 5761 | 138.264 | 5.761 | 6.6 | 6.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45130856 | 1316 | 228.4326 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 75759075 | 5798 | 139.152 | 5.798 | 6.3 | 6.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45132144 | 1288 | 222.1456 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 75764881 | 5806 | 139.344 | 5.806 | 6.1 | 6.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45133516 | 1372 | 236.3073 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 75770588 | 5707 | 136.968 | 5.707 | 5.8 | 5.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45134832 | 1316 | 230.594 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 131 | 75776288 | 5700 | 136.8 | 5.7 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45136152 | 1320 | 231.5789 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 131 | 75781933 | 5645 | 135.48 | 5.645 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1126 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45137456 | 1304 | 231.0009 | 100% | 0% | 100% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 130 | 75787342 | 5409 | 129.816 | 5.409 | 4.7 | 4.7 | 2B+1S | 1027 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45138516 | 1060 | 195.9697 | 100% | 0% | 0% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 127 | 75792784 | 5442 | 130.608 | 5.442 | 4.2 | 4.2 | 2B+1S | 1016 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45139564 | 1048 | 192.5763 | 100% | 0% | 0% | 100% | 100% | 0% | 10516651 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 129 | 75798018 | 5234 | 125.616 | 5.234 | 3.7 | 3.7 | 2B+1S | 1006 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45140580 | 1016 | 194.1154 | 100% | 0% | 0% | 100% | 100% | 0% | 10516651 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 103 | 75802458 | 4440 | 106.56 | 4.44 | 4.7 | 4.7 |  | 0 | 0 | 0 | 1185 | 1037 | N/A | N/A | N/A | N/A | 45141364 | 784 | 176.5766 | 0% | 0% | 0% | 100% | 100% | 40% | 10517454 | 803 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 105 | 75806811 | 4353 | 104.472 | 4.353 | 5.8 | 5.8 |  | 0 | 0 | 0 | 1185 | 1037 | N/A | N/A | N/A | N/A | 45142132 | 768 | 176.43 | 0% | 0% | 0% | 100% | 100% | 40% | 10518549 | 1095 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 125800 | 125.8 | 125.8 | [12 empty] | 25968 | 25968 | 206.4229 | [6 empty] | 4365 | 4365 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 2:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (40%)

## MAR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25616 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75806811 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45142132 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10518549 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 101 | 75810916 | 4105 | 98.52 | 4.105 | 6.8 | 6.8 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45142848 | 716 | 174.4214 | 0% | 0% | 0% | 100% | 100% | 50% | 10519749 | 1200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 98 | 75815026 | 4110 | 98.64 | 4.11 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45143569 | 721 | 175.4258 | 0% | 0% | 0% | 100% | 100% | 50% | 10520929 | 1180 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 97 | 75819153 | 4127 | 99.048 | 4.127 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45144308 | 739 | 179.0647 | 0% | 0% | 0% | 100% | 100% | 50% | 10522106 | 1177 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 100 | 75823444 | 4291 | 102.984 | 4.291 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45145031 | 723 | 168.4922 | 0% | 0% | 0% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 19 | 13.3803 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 104 | 75827753 | 4309 | 103.416 | 4.309 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45145772 | 741 | 171.9657 | 0% | 0% | 0% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 19 | 13.3803 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 119 | 117 | 75832520 | 4767 | 114.408 | 4.767 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45146552 | 780 | 163.6249 | 0% | 0% | 0% | 100% | 100% | 0% | 10522106 | 0 | 0.99 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 136 | 75838045 | 5525 | 132.6 | 5.525 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 45147640 | 1088 | 196.9231 | 0% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 142 | 75843849 | 5804 | 139.296 | 5.804 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45148856 | 1216 | 209.5107 | 0% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 148 | 75849939 | 6090 | 146.16 | 6.09 | 9.2 | 9.2 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45150140 | 1284 | 210.8374 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 144 | 75856057 | 6118 | 146.832 | 6.118 | 8.9 | 8.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45151492 | 1352 | 220.9873 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 | 1.14
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 145 | 75862184 | 6127 | 147.048 | 6.127 | 8.6 | 8.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45152836 | 1344 | 219.3569 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Normal operation schedule
59:00 | 12:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 148 | 75868280 | 6096 | 146.304 | 6.096 | 8.4 | 8.4 | 3B+1S | 996 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45154196 | 1360 | 223.0971 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 75874186 | 5906 | 141.744 | 5.906 | 8.1 | 8.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45155516 | 1320 | 223.5015 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 146 | 75880077 | 5891 | 141.384 | 5.891 | 7.9 | 7.9 | 3B+1S | 996 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45156848 | 1332 | 226.1076 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 134 | 75885698 | 5621 | 134.904 | 5.621 | 7.6 | 7.6 | 3B+1S | 995 | 0 | 1168 | 1185 | 1147 | N/A | N/A | N/A | N/A | 45158100 | 1252 | 222.7362 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 9 | 6.338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 127 | 75891283 | 5585 | 134.04 | 5.585 | 7.4 | 7.4 | 3B+1S | 996 | 0 | 1147 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45159340 | 1240 | 222.0233 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 75896863 | 5580 | 133.92 | 5.58 | 7.1 | 7.1 | 3B+1S | 996 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 45160588 | 1248 | 223.6559 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 75902605 | 5742 | 137.808 | 5.742 | 6.8 | 6.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1096 | N/A | N/A | N/A | N/A | 45161844 | 1256 | 218.7391 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 127 | 75908198 | 5593 | 134.232 | 5.593 | 6.5 | 6.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1026 | N/A | N/A | N/A | N/A | 45163076 | 1232 | 220.2753 | 100% | 0% | 100% | 100% | 100% | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 11 | 7.7465 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 119 | 130 | 75913707 | 5509 | 132.216 | 5.509 | 5.9 | 5.9 | 2B+1S | 1038 | 0 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45164136 | 1060 | 192.4124 | 100% | 0% | 100% | 100% |  | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 12 | 8.4507 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 125 | 75919180 | 5473 | 131.352 | 5.473 | 5.4 | 5.4 | 2B+1S | 1036 | 0 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45165188 | 1052 | 192.2163 | 100% | 0% | 100% | 100% |  | 0% | 10522106 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 13 | 9.1549 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 110 | 122 | 75924509 | 5329 | 127.896 | 5.329 | 4.9 | 4.9 | 2B+1S | 1026 | 0 | 1128 | 1185 |  | N/A | N/A | N/A | N/A | 45166204 | 1016 | 190.6549 | 100% | 0% | 100% | 100% |  | 0% | 10522106 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 130 | 104 | 75929052 | 4543 | 109.032 | 4.543 | 5.5 | 5.5 | 2B | 0 | 0 | 1027 | 1185 |  | N/A | N/A | N/A | N/A | 45167020 | 816 | 179.617 | 0% | 0% | 100% | 100% |  | 40% | 10522815 | 709 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 127 | 100 | 75933334 | 4282 | 102.768 | 4.282 | 6.5 | 6.5 | 2B | 0 | 0 | 977 | 1185 |  | N/A | N/A | N/A | N/A | 45167748 | 728 | 170.014 | 0% | 0% | 100% | 100% |  | 40% | 10523884 | 1069 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126523 | 126.523 | 126.523 | [12 empty] | 25616 | 25616 | 202.4612 | [6 empty] | 5335 | 5335 | 1.0917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (45%)
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (40%)

## MAR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25880 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 75933334 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45167748 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10523884 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 124 | 95 | 75937386 | 4052 | 97.248 | 4.052 | 7.6 | 7.6 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45168460 | 712 | 175.7157 | 0% | 0% | 100% | 100% | 0% | 45% | 10524924 | 1040 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 75941393 | 4007 | 96.168 | 4.007 | 8.8 | 8.8 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 45169156 | 696 | 173.696 | 0% | 0% | 100% | 100% | 0% | 45% | 10526040 | 1116 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 17 | 11.9718 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 97 | 96 | 75945312 | 3919 | 94.056 | 3.919 | 9.5 | 9.5 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 45169820 | 664 | 169.431 | 0% | 0% | 100% | 100% | 0% | 45% | 10526595 | 555 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 99 | 96 | 75949226 | 3914 | 93.936 | 3.914 | 9.5 | 9.5 | 2B | 0 | 0 | 936 | 1185 | 0 | N/A | N/A | N/A | N/A | 45170474 | 654 | 167.0925 | 0% | 0% | 100% | 100% | 0% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 111 | 105 | 75953293 | 4067 | 97.608 | 4.067 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 45171140 | 666 | 163.7571 | 0% | 0% | 100% | 100% | 0% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 125 | 75958235 | 4942 | 118.608 | 4.942 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45171932 | 792 | 160.259 | 0% | 0% | 100% | 100% | 0% | 0% | 10526595 | 0 | 0.96 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 149 | 75964260 | 6025 | 144.6 | 6.025 | 9.2 | 9.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45173260 | 1328 | 220.4149 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 150 | 75970463 | 6203 | 148.872 | 6.203 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45174668 | 1408 | 226.9869 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 150 | 75976639 | 6176 | 148.224 | 6.176 | 8 | 8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45176012 | 1344 | 217.6166 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 153 | 75982955 | 6316 | 151.584 | 6.316 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45177404 | 1392 | 220.3927 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 | 1.19
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 144 | 75988254 | 5299 | 127.176 | 5.299 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45178516 | 1112 | 209.8509 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 75994232 | 5978 | 143.472 | 5.978 | 6.5 | 6.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45179876 | 1360 | 227.5008 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 76000048 | 5816 | 139.584 | 5.816 | 6.2 | 6.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45181208 | 1332 | 229.0234 | 100% | 0% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 76005819 | 5771 | 138.504 | 5.771 | 5.8 | 5.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45182556 | 1348 | 233.5817 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 76011550 | 5731 | 137.544 | 5.731 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45183868 | 1312 | 228.9304 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 76017217 | 5667 | 136.008 | 5.667 | 5.5 | 5.5 | 3B+1S | 0 | 1005 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45185180 | 1312 | 231.5158 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 76022913 | 5696 | 136.704 | 5.696 | 5.4 | 5.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45186484 | 1304 | 228.9326 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 134 | 76028533 | 5620 | 134.88 | 5.62 | 5.1 | 5.1 | 3B+1S | 0 | 1006 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 45187748 | 1264 | 224.911 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 9 | 6.338 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 125 | 134 | 76034088 | 5555 | 133.32 | 5.555 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1076 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45188976 | 1228 | 221.0621 | 0% | 100% | 100% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 117 | 125 | 76039347 | 5259 | 126.216 | 5.259 | 4.4 | 4.4 | 2B+1S | 0 | 1026 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45190028 | 1052 | 200.038 | 0% | 100% | 0% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 102 | 76044664 | 5317 | 127.608 | 5.317 | 3.7 | 3.7 | 2B+1S | 0 | 1037 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45191080 | 1052 | 197.8559 | 0% | 100% | 0% | 100% | 100% | 0% | 10526595 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 124 | 76049777 | 5113 | 122.712 | 5.113 | 3.3 | 3.3 | 2B+1S | 0 | 1006 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45192100 | 1020 | 199.4915 | 0% | 100% | 0% | 100% | 100% | 0% | 10526595 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 129 | 101 | 76054094 | 4317 | 103.608 | 4.317 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45192892 | 792 | 183.4607 | 0% | 0% | 0% | 100% | 100% | 47% | 10527480 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 98 | 76058311 | 4217 | 101.208 | 4.217 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45193628 | 736 | 174.5317 | 0% | 0% | 0% | 100% | 100% | 47% | 10528757 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124977 | 124.977 | 124.977 | [12 empty] | 25880 | 25880 | 207.0781 | [6 empty] | 4873 | 4873 | 1.0833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (45%)
XCV2- CLOSED @ 2:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MERALCO POWER FLUCTUATION @ 10:04AM DUE TO MAINTENACE INSTALLATION OF WIRING TO MOV STORAGE PUMP 2(SP2)
ALL PUMP STOPPED DUE TO POWER FLUCTUATION @ 10:04AM
BP2 POWER RESUME @ 10:04AM
BP3 POWER RESUME @ 10:06AM
BP1 POWER RESUME @ 10:07AM
SP1 POWER RESUME @ 10:08AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 1:00 PM DUE TO EXCESS CAPACITY
SP2 - STARTED @ 1:01 PM DUE TO WARM UP
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (47%)

## MAR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26888 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76058311 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45193628 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10528757 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 97 | 76062301 | 3990 | 95.76 | 3.99 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45194330 | 702 | 175.9398 | 0% | 0% | 0% | 100% | 100% | 57% | 10529877 | 1120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 96 | 76066296 | 3995 | 95.88 | 3.995 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45195032 | 702 | 175.7196 | 0% | 0% | 0% | 100% | 100% | 57% | 10531000 | 1123 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 95 | 76070307 | 4011 | 96.264 | 4.011 | 9.2 | 9.2 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45195760 | 728 | 181.5009 | 0% | 0% | 0% | 100% | 100% | 57% | 10532134 | 1134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 98 | 76074447 | 4140 | 99.36 | 4.14 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 45196459 | 699 | 168.8406 | 0% | 0% | 0% | 100% | 100% | 57% | 10532416 | 282 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 101 | 76078606 | 4159 | 99.816 | 4.159 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 45197176 | 717 | 172.3972 | 0% | 0% | 0% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 76083718 | 5112 | 122.688 | 5.112 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45198092 | 916 | 179.1862 | 0% | 0% | 0% | 100% | 100% | 0% | 10532416 | 0 | 0.98 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 146 | 76089743 | 6025 | 144.6 | 6.025 | 8.9 | 8.9 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45199440 | 1348 | 223.7344 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 76095924 | 6181 | 148.344 | 6.181 | 8.3 | 8.3 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45200836 | 1396 | 225.8534 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 151 | 76102066 | 6142 | 147.408 | 6.142 | 7.6 | 7.6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45202220 | 1384 | 225.3338 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 143 | 76108191 | 6125 | 147 | 6.125 | 7 | 7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45203596 | 1376 | 224.6531 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 | 1.03
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 144 | 76114355 | 6164 | 147.936 | 6.164 | 6.5 | 6.5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45204984 | 1388 | 225.1785 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 139 | 76120415 | 6060 | 145.44 | 6.06 | 6 | 6 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45206344 | 1360 | 224.4224 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 141 | 76126319 | 5904 | 141.696 | 5.904 | 5.8 | 5.8 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45207684 | 1340 | 226.9648 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 76131995 | 5676 | 136.224 | 5.676 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45208996 | 1312 | 231.1487 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 76137702 | 5707 | 136.968 | 5.707 | 5.6 | 5.6 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45210312 | 1316 | 230.594 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 133 | 76143459 | 5757 | 138.168 | 5.757 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45211640 | 1328 | 230.6757 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 76149285 | 5826 | 139.824 | 5.826 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45212972 | 1332 | 228.6303 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 76155126 | 5841 | 140.184 | 5.841 | 4.9 | 4.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45214308 | 1336 | 228.728 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 135 | 76160920 | 5794 | 139.056 | 5.794 | 4.6 | 4.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45215636 | 1328 | 229.2026 | 0% | 100% | 100% | 100% | 100% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 76166430 | 5510 | 132.24 | 5.51 | 3.9 | 3.9 | 2B+1S | 0 | 1099 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45216732 | 1096 | 198.9111 | 0% | 100% | 100% | 100% | 0% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 131 | 76171881 | 5451 | 130.824 | 5.451 | 3.2 | 3.2 | 2B+1S | 0 | 1066 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45217796 | 1064 | 195.1935 | 0% | 100% | 100% | 100% | 0% | 0% | 10532416 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 112 | 130 | 76177426 | 5545 | 133.08 | 5.545 | 2.5 | 2.5 | 2B+1S | 0 | 1067 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45218892 | 1096 | 197.6555 | 0% | 100% | 100% | 100% | 0% | 0% | 10532416 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 111 | 76181845 | 4419 | 106.056 | 4.419 | 3 | 3 | 2B | 0 | 0 | 1137 | 1185 | 0 | N/A | N/A | N/A | N/A | 45219732 | 840 | 190.0883 | 0% | 0% | 100% | 100% | 0% | 45% | 10533091 | 675 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 114 | 76186167 | 4322 | 103.728 | 4.322 | 4.4 | 4.4 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45220516 | 784 | 181.3975 | 0% | 0% | 100% | 100% | 0% | 45% | 10534245 | 1154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127856 | 127.856 | 127.856 | [12 empty] | 26888 | 26888 | 210.2991 | [6 empty] | 5488 | 5488 | 0.99833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (57%)
XCV1- CLOSED @ 3:27 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (45%)

## MAR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27256 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76186167 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45220516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10534245 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 96 | 76190513 | 4346 | 104.304 | 4.346 | 5.8 | 5.8 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 45221296 | 780 | 179.4754 | 0% | 0% | 100% | 100% | 0% | 50% | 10535656 | 1411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 94 | 76194606 | 4093 | 98.232 | 4.093 | 7.3 | 7.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 45222028 | 732 | 178.8419 | 0% | 0% | 100% | 100% | 0% | 50% | 10537086 | 1430 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 15 | 10.5634 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 96 | 76198524 | 3918 | 94.032 | 3.918 | 8.9 | 8.9 | 2B | 0 | 0 | 916 | 1185 | 0 | N/A | N/A | N/A | N/A | 45222708 | 680 | 173.5579 | 0% | 0% | 100% | 100% | 0% | 50% | 10538647 | 1561 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 96 | 93 | 76202448 | 3924 | 94.176 | 3.924 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 1185 | 0 | N/A | N/A | N/A | N/A | 45223372 | 664 | 169.2151 | 0% | 0% | 100% | 100% | 0% | 50% | 10539151 | 504 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 104 | 76206427 | 3979 | 95.496 | 3.979 | 9.5 | 9.5 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45224044 | 672 | 168.8867 | 0% | 0% | 100% | 100% | 0% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 127 | 76211505 | 5078 | 121.872 | 5.078 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45224948 | 904 | 178.0228 | 0% | 0% | 100% | 100% | 0% | 0% | 10539151 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 136 | 76217537 | 6032 | 144.768 | 6.032 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45226308 | 1360 | 225.4642 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 76223723 | 6186 | 148.464 | 6.186 | 8.3 | 8.3 | 3B+1S | 0 | 1064 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45227700 | 1392 | 225.0242 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 144 | 76229945 | 6222 | 149.328 | 6.222 | 7.6 | 7.6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45229092 | 1392 | 223.7223 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 76236107 | 6162 | 147.888 | 6.162 | 7 | 7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45230472 | 1380 | 223.9533 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 | 1.14
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 76242358 | 6251 | 150.024 | 6.251 | 6.4 | 6.4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45231884 | 1412 | 225.8839 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 76248328 | 5970 | 143.28 | 5.97 | 5.8 | 5.8 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45233236 | 1352 | 226.4657 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 145 | 76254234 | 5906 | 141.744 | 5.906 | 5.3 | 5.3 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45234604 | 1368 | 231.6289 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 76260114 | 5880 | 141.12 | 5.88 | 4.8 | 4.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45235948 | 1344 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 143 | 76265965 | 5851 | 140.424 | 5.851 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45237284 | 1336 | 228.337 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 76271732 | 5767 | 138.408 | 5.767 | 4.4 | 4.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45238612 | 1328 | 230.2757 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 76277588 | 5856 | 140.544 | 5.856 | 4 | 4 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45239948 | 1336 | 228.1421 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 76283497 | 5909 | 141.816 | 5.909 | 3.6 | 3.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45241292 | 1344 | 227.4497 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 76289387 | 5890 | 141.36 | 5.89 | 3.2 | 3.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45242636 | 1344 | 228.1834 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 141 | 139 | 76295119 | 5732 | 137.568 | 5.732 | 3.1 | 3.1 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45243964 | 1328 | 231.6818 | 0% | 100% | 100% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 128 | 76300569 | 5450 | 130.8 | 5.45 | 2.6 | 2.6 | 2B+1S | 0 | 1058 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45245044 | 1080 | 198.1651 | 0% | 100% | 0% | 100% | 100% | 0% | 10539151 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 128 | 76306034 | 5465 | 131.16 | 5.465 | 2 | 2 | 2B+1S | 0 | 1058 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45246116 | 1072 | 196.1574 | 0% | 100% | 0% | 100% | 100% | 0% | 10539151 | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 108 | 76310618 | 4584 | 110.016 | 4.584 | 2.6 | 2.6 | 2B | 0 | 0 | 0 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45247000 | 884 | 192.8447 | 0% | 0% | 0% | 100% | 100% | 45% | 10539900 | 749 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 131 | 76314846 | 4228 | 101.472 | 4.228 | 3.9 | 3.9 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45247772 | 772 | 182.5922 | 0% | 0% | 0% | 100% | 100% | 45% | 10541063 | 1163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128679 | 128.679 | 128.679 | [12 empty] | 27256 | 27256 | 211.8139 | [6 empty] | 6818 | 6818 | 1.0483 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (50%)
XCV2- CLOSED @ 3:33 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)
ALL PUMP STOPPED DUE TO GENSET WARM-UP WITH LOAD @ 12:00AM
BP2 POWER RESUME @ 12:02AM
BP3 POWER RESUME @ 12:04AM

## MAR 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-03-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25224 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76314846 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45247772 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10541063 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 134 | 101 | 76318985 | 4139 | 99.336 | 4.139 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 1037 | N/A | N/A | N/A | N/A | 45247772 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 55% | 10541890 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 107 | 76323304 | 4319 | 103.656 | 4.319 | 6.4 | 6.4 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45247772 | 0 | 0 | 0% | 0% | 0% | 100% | 100% | 55% | 10543243 | 1353 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 100 | 76327218 | 3914 | 93.936 | 3.914 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45248180 | 408 | 104.2412 | 0% | 0% | 0% | 100% | 100% | 55% | 10544498 | 1255 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 92 | 76331244 | 4026 | 96.624 | 4.026 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 956 | N/A | N/A | N/A | N/A | 45248900 | 720 | 178.8376 | 0% | 0% | 0% | 100% | 100% | 55% | 10545385 | 887 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 117 | 100 | 76335326 | 4082 | 97.968 | 4.082 | 9.3 | 9.3 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45249608 | 708 | 173.4444 | 0% | 0% | 0% | 100% | 100% | 55% | 10545916 | 531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 76340239 | 4913 | 117.912 | 4.913 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45250496 | 888 | 180.745 | 0% | 0% | 0% | 100% | 100% | 0% | 10545916 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 155 | 76346226 | 5987 | 143.688 | 5.987 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45251836 | 1340 | 223.8183 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 76352359 | 6133 | 147.192 | 6.133 | 8.8 | 8.8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45253196 | 1360 | 221.7512 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 154 | 76358441 | 6082 | 145.968 | 6.082 | 8.3 | 8.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45254556 | 1360 | 223.6107 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 76364604 | 6163 | 147.912 | 6.163 | 7.9 | 7.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45255924 | 1368 | 221.9698 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 | 1.23
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 76370684 | 6080 | 145.92 | 6.08 | 7.4 | 7.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45257244 | 1320 | 217.1053 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 76376788 | 6104 | 146.496 | 6.104 | 7.1 | 7.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45258652 | 1408 | 230.6684 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 76382777 | 5989 | 143.736 | 5.989 | 6.6 | 6.6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45260014 | 1362 | 227.4169 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 141 | 76388808 | 6031 | 144.744 | 6.031 | 6.2 | 6.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45261364 | 1350 | 223.8435 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 146 | 76394660 | 5852 | 140.448 | 5.852 | 5.8 | 5.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45262708 | 1344 | 229.6651 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 76400461 | 5801 | 139.224 | 5.801 | 5.6 | 5.6 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45264036 | 1328 | 228.926 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 145 | 76406375 | 5914 | 141.936 | 5.914 | 5.2 | 5.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45265388 | 1352 | 228.6101 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 76412251 | 5876 | 141.024 | 5.876 | 4.8 | 4.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45266732 | 1344 | 228.727 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 76418128 | 5877 | 141.048 | 5.877 | 4.5 | 4.5 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45268072 | 1340 | 228.0075 | 0% | 100% | 100% | 100% | 100% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 118 | 129 | 76423613 | 5485 | 131.64 | 5.485 | 3.7 | 3.7 | 2B+1S | 0 | 1048 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45269164 | 1092 | 199.0884 | 0% | 100% | 100% | 100% | 0% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 76429046 | 5433 | 130.392 | 5.433 | 3.1 | 3.1 | 2B+1S | 0 | 1047 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45270228 | 1064 | 195.8402 | 0% | 100% | 100% | 100% | 0% | 0% | 10545916 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 126 | 76434482 | 5436 | 130.464 | 5.436 | 2.5 | 2.5 | 2B+1S | 0 | 1046 | 1189 | 1185 | 0 | N/A | N/A | N/A | N/A | 45271292 | 1064 | 195.7322 | 0% | 100% | 100% | 100% | 0% | 0% | 10545916 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 123 | 76439066 | 4584 | 110.016 | 4.584 | 3.1 | 3.1 | 2B | 0 | 0 | 1118 | 1185 | 0 | N/A | N/A | N/A | N/A | 45272164 | 872 | 190.2269 | 0% | 0% | 100% | 100% | 0% | 50% | 10546899 | 983 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 139 | 101 | 76443602 | 4536 | 108.864 | 4.536 | 4.4 | 4.4 | 2B | 0 | 0 | 1036 | 1185 | 0 | N/A | N/A | N/A | N/A | 45272996 | 832 | 183.4215 | 0% | 0% | 100% | 100% | 0% | 50% | 10548041 | 1142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128756 | 128.756 | 128.756 | [12 empty] | 25224 | 25224 | 195.9054 | [6 empty] | 6978 | 6978 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
ALL PUMP STOPPED DUE TO POWER TRANSFER TO MERALCO @ 2:24AM
BP2 POWER RESUME @ 2:26AM
BP3 POWER RESUME @ 2:28AM
XCV1- CLOSED @ 5:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MARCH 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)