## APR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27056 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76443602 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45272996 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10548041 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 101 | 76447796 | 4194 | 100.656 | 4.194 | 5.7 | 5.7 | 2B | 0 | 0 | 1016 | 1185 | 0 | N/A | N/A | N/A | N/A | 45273760 | 764 | 182.165 | 0% | 0% | 100% | 100% | 0% | 55% | 10549253 | 1212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 100 | 76451843 | 4047 | 97.128 | 4.047 | 7 | 7 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 45274484 | 724 | 178.8979 | 0% | 0% | 100% | 100% | 0% | 55% | 10550561 | 1308 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 99 | 76455932 | 4089 | 98.136 | 4.089 | 8.4 | 8.4 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 45275204 | 720 | 176.0822 | 0% | 0% | 100% | 100% | 0% | 55% | 10551896 | 1335 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 133 | 104 | 76459996 | 4064 | 97.536 | 4.064 | 9.3 | 9.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 45275921 | 717 | 176.4272 | 0% | 0% | 100% | 100% | 0% | 55% | 10552889 | 993 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 105 | 102 | 76463994 | 3998 | 95.952 | 3.998 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 45276620 | 699 | 174.8374 | 0% | 0% | 100% | 100% | 0% | 55% | 10553051 | 162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 122 | 76469061 | 5067 | 121.608 | 5.067 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45277500 | 880 | 173.6728 | 0% | 0% | 100% | 100% | 0% | 0% | 10553051 | 0 | 1.31 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 140 | 76474798 | 5737 | 137.688 | 5.737 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45278722 | 1222 | 213.0033 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 76481027 | 6229 | 149.496 | 6.229 | 8.9 | 8.9 | 3B+1S | 1007 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45280150 | 1428 | 229.2503 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 76487116 | 6089 | 146.136 | 6.089 | 8.5 | 8.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45281508 | 1358 | 223.0251 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 76493404 | 6288 | 150.912 | 6.288 | 8.1 | 8.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45282904 | 1396 | 222.0102 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 | 1.45
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 76499296 | 5892 | 141.408 | 5.892 | 7.8 | 7.8 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45284220 | 1316 | 223.3537 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 76505493 | 6197 | 148.728 | 6.197 | 7.4 | 7.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45285588 | 1368 | 220.752 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 120 | 76511314 | 5821 | 139.704 | 5.821 | 7.1 | 7.1 | 3B+1S | 996 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45286892 | 1304 | 224.0165 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 76517547 | 6233 | 149.592 | 6.233 | 6.6 | 6.6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45288316 | 1424 | 228.4614 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 76523496 | 5949 | 142.776 | 5.949 | 6.1 | 6.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45289676 | 1360 | 228.6099 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 76529391 | 5895 | 141.48 | 5.895 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45291016 | 1340 | 227.3113 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 146 | 76535401 | 6010 | 144.24 | 6.01 | 5.3 | 5.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45292380 | 1364 | 226.9551 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 76541396 | 5995 | 143.88 | 5.995 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45293740 | 1360 | 226.8557 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 76547176 | 5780 | 138.72 | 5.78 | 4.5 | 4.5 | 3B+1S | 996 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45295068 | 1328 | 229.7578 | 100% | 0% | 100% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 128 | 76552648 | 5472 | 131.328 | 5.472 | 3.6 | 3.6 | 2B+1S | 1098 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45296172 | 1104 | 201.7544 | 100% | 0% | 0% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 132 | 76558091 | 5443 | 130.632 | 5.443 | 2.8 | 2.8 | 2B+1S | 1097 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45297268 | 1096 | 201.3595 | 100% | 0% | 0% | 100% | 100% | 0% | 10553051 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 128 | 76563488 | 5397 | 129.528 | 5.397 | 2.1 | 2.1 | 2B+1S | 1097 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45298340 | 1072 | 198.6289 | 100% | 0% | 0% | 100% | 100% | 0% | 10553051 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 110 | 76568126 | 4638 | 111.312 | 4.638 | 2.8 | 2.8 | 2B | 0 | 0 | 0 | 1185 | 1128 | N/A | N/A | N/A | N/A | 45299228 | 888 | 191.4618 | 0% | 0% | 0% | 100% | 100% | 45% | 10553849 | 798 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 105 | 76572608 | 4482 | 107.568 | 4.482 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 45300052 | 824 | 183.8465 | 0% | 0% | 0% | 100% | 100% | 45% | 10555045 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129006 | 129.006 | 129.006 | [12 empty] | 27056 | 27056 | 209.7267 | [6 empty] | 7004 | 7004 | 1.2283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (55%)
XCV2- CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (45%)

## APR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27112 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76572608 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45300052 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10555045 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 105 | 76577077 | 4469 | 107.256 | 4.469 | 5.4 | 5.4 | 2B | 0 | 0 | 0 | 1185 | 1078 | N/A | N/A | N/A | N/A | 45300868 | 816 | 182.5912 | 0% | 0% | 0% | 100% | 100% | 55% | 10556145 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 96 | 76581168 | 4091 | 98.184 | 4.091 | 6.6 | 6.6 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45301628 | 760 | 185.7736 | 0% | 0% | 0% | 100% | 100% | 55% | 10557301 | 1156 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 76585225 | 4057 | 97.368 | 4.057 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 986 | N/A | N/A | N/A | N/A | 45302356 | 728 | 179.4429 | 0% | 0% | 0% | 100% | 100% | 55% | 10558482 | 1181 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 135 | 98 | 76589207 | 3982 | 95.568 | 3.982 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 967 | N/A | N/A | N/A | N/A | 45303060 | 704 | 176.7956 | 0% | 0% | 0% | 100% | 100% | 55% | 10559361 | 879 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 114 | 109 | 76593572 | 4365 | 104.76 | 4.365 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 966 | N/A | N/A | N/A | N/A | 45303780 | 720 | 164.9485 | 0% | 0% | 0% | 100% | 100% | 55% | 10560073 | 712 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 145 | 76598634 | 5062 | 121.488 | 5.062 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45304636 | 856 | 169.1031 | 0% | 0% | 0% | 100% | 100% | 0% | 10560073 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 140 | 76604403 | 5769 | 138.456 | 5.769 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45305852 | 1216 | 210.7818 | 0% | 0% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 76610594 | 6191 | 148.584 | 6.191 | 9.2 | 9.2 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45307212 | 1360 | 219.6737 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 143 | 143 | 76616756 | 6162 | 147.888 | 6.162 | 8.8 | 8.8 | 3B+1S | 0 | 996 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45308572 | 1360 | 220.7076 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 153 | 76623168 | 6412 | 153.888 | 6.412 | 8.4 | 8.4 | 3B+1S | 0 | 996 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45309980 | 1408 | 219.5883 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 | 1.23
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 76629296 | 6128 | 147.072 | 6.128 | 8.1 | 8.1 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45311324 | 1344 | 219.3211 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 143 | 76635402 | 6106 | 146.544 | 6.106 | 7.7 | 7.7 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45312676 | 1352 | 221.4216 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 127 | 76641299 | 5897 | 141.528 | 5.897 | 7.3 | 7.3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45314016 | 1340 | 227.2342 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 146 | 76647192 | 5893 | 141.432 | 5.893 | 7.1 | 7.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45315344 | 1328 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 76653208 | 6016 | 144.384 | 6.016 | 6.7 | 6.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45316692 | 1348 | 224.0691 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 76659180 | 5972 | 143.328 | 5.972 | 6.3 | 6.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45318040 | 1348 | 225.72 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 143 | 76665143 | 5963 | 143.112 | 5.963 | 5.8 | 5.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45319396 | 1356 | 227.4023 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 141 | 76671066 | 5923 | 142.152 | 5.923 | 5.5 | 5.5 | 3B+1S | 0 | 1001 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45320740 | 1344 | 226.912 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 149 | 76676968 | 5902 | 141.648 | 5.902 | 5.1 | 5.1 | 3B+1S | 0 | 1001 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45322076 | 1336 | 226.3639 | 0% | 100% | 100% | 100% | 100% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 132 | 76682579 | 5611 | 134.664 | 5.611 | 4.3 | 4.3 | 2B+1S | 0 | 1099 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45323180 | 1104 | 196.7564 | 0% | 100% | 100% | 100% | 0% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 131 | 76688185 | 5606 | 134.544 | 5.606 | 3.3 | 3.3 | 2B+1S | 0 | 1099 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45324284 | 1104 | 196.9319 | 0% | 100% | 100% | 100% | 0% | 0% | 10560073 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 125 | 76693734 | 5549 | 133.176 | 5.549 | 2.6 | 2.6 | 2B+1S | 0 | 1098 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45325384 | 1100 | 198.2339 | 0% | 100% | 100% | 100% | 0% | 0% | 10560073 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 114 | 76698519 | 4785 | 114.84 | 4.785 | 3.1 | 3.1 | 2B | 0 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 45326308 | 924 | 193.1034 | 0% | 0% | 100% | 100% | 0% | 50% | 10560720 | 647 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 111 | 76703152 | 4633 | 111.192 | 4.633 | 4.3 | 4.3 | 2B | 0 | 0 | 1098 | 1185 | 0 | N/A | N/A | N/A | N/A | 45327164 | 856 | 184.7615 | 0% | 0% | 100% | 100% | 0% | 50% | 10561790 | 1070 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130544 | 130.544 | 130.544 | [12 empty] | 27112 | 27112 | 207.6848 | [6 empty] | 6745 | 6745 | 1.135 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## APR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26872 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76703152 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45327164 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10561790 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 104 | 76707570 | 4418 | 106.032 | 4.418 | 5.3 | 5.3 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 45327980 | 816 | 184.699 | 0% | 0% | 100% | 100% | 0% | 55% | 10562768 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 100 | 76711863 | 4293 | 103.032 | 4.293 | 6.4 | 6.4 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45328752 | 772 | 179.8276 | 0% | 0% | 100% | 100% | 0% | 55% | 10563969 | 1201 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 99 | 76715980 | 4117 | 98.808 | 4.117 | 7.8 | 7.8 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 45329484 | 732 | 177.7994 | 0% | 0% | 100% | 100% | 0% | 55% | 10565234 | 1265 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 127 | 97 | 76719869 | 3889 | 93.336 | 3.889 | 9.1 | 9.1 | 2B | 0 | 0 | 957 | 1185 | 0 | N/A | N/A | N/A | N/A | 45330180 | 696 | 178.9663 | 0% | 0% | 100% | 100% | 0% | 55% | 10566400 | 1166 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 103 | 76724054 | 4185 | 100.44 | 4.185 | 9.5 | 9.5 | 2B | 0 | 0 | 917 | 1185 | 0 | N/A | N/A | N/A | N/A | 45330868 | 688 | 164.3967 | 0% | 0% | 100% | 100% | 0% | 55% | 10566659 | 259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 128 | 76728777 | 4723 | 113.352 | 4.723 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45331632 | 764 | 161.7616 | 0% | 0% | 100% | 100% | 0% | 0% | 10566659 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 140 | 76734418 | 5641 | 135.384 | 5.641 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45332796 | 1164 | 206.3464 | 0% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 149 | 76740486 | 6068 | 145.632 | 6.068 | 9.3 | 9.3 | 3B+1S | 976 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45334136 | 1340 | 220.8306 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 148 | 76746598 | 6112 | 146.688 | 6.112 | 9.1 | 9.1 | 3B+1S | 976 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45335480 | 1344 | 219.8953 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 142 | 76752926 | 6328 | 151.872 | 6.328 | 8.7 | 8.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45336838 | 1358 | 214.6018 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 | 1.2
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 76759058 | 6132 | 147.168 | 6.132 | 8.3 | 8.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45338220 | 1382 | 225.3751 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 76765214 | 6156 | 147.744 | 6.156 | 7.9 | 7.9 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45339604 | 1384 | 224.8213 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 138 | 76771382 | 6168 | 148.032 | 6.168 | 7.5 | 7.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45340980 | 1376 | 223.0869 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 146 | 76777297 | 5915 | 141.96 | 5.915 | 7 | 7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45342316 | 1336 | 225.8664 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 138 | 76783230 | 5933 | 142.392 | 5.933 | 6.4 | 6.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45343708 | 1392 | 234.6199 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 142 | 76789154 | 5924 | 142.176 | 5.924 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45345036 | 1328 | 224.1729 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 76795120 | 5966 | 143.184 | 5.966 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45346396 | 1360 | 227.9584 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 76801006 | 5886 | 141.264 | 5.886 | 5 | 5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45347740 | 1344 | 228.3384 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 146 | 76806943 | 5937 | 142.488 | 5.937 | 4.6 | 4.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45349084 | 1344 | 226.377 | 100% | 0% | 100% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 140 | 76812571 | 5628 | 135.072 | 5.628 | 3.7 | 3.7 | 2B+1S | 1129 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45350188 | 1104 | 196.162 | 100% | 0% | 0% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 129 | 76818084 | 5513 | 132.312 | 5.513 | 3 | 3 | 2B+1S | 1067 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45351260 | 1072 | 194.4495 | 100% | 0% | 0% | 100% | 100% | 0% | 10566659 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 10 | 7.0423 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 126 | 76823451 | 5367 | 128.808 | 5.367 | 2.4 | 2.4 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45352312 | 1052 | 196.0127 | 100% | 0% | 0% | 100% | 100% | 0% | 10566659 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 105 | 76828160 | 4709 | 113.016 | 4.709 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1128 | N/A | N/A | N/A | N/A | 45353216 | 904 | 191.9728 | 0% | 0% | 0% | 100% | 100% | 50% | 10567459 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 142 | 104 | 76832604 | 4444 | 106.656 | 4.444 | 4.6 | 4.6 | 2B | 0 | 0 | 0 | 1185 | 1058 | N/A | N/A | N/A | N/A | 45354036 | 820 | 184.5185 | 0% | 0% | 0% | 100% | 100% | 50% | 10568754 | 1295 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129452 | 129.452 | 129.452 | [12 empty] | 26872 | 26872 | 207.5827 | [6 empty] | 6964 | 6964 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (55%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (50%)

## APR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26808 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76832604 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45354036 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10568754 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 101 | 76836805 | 4201 | 100.824 | 4.201 | 5.9 | 5.9 | 2B | 0 | 0 | 0 | 1185 | 1057 | N/A | N/A | N/A | N/A | 45354816 | 780 | 185.6701 | 0% | 0% | 0% | 100% | 100% | 55% | 10569927 | 1173 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 91 | 76840897 | 4092 | 98.208 | 4.092 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45355556 | 740 | 180.8407 | 0% | 0% | 0% | 100% | 100% | 55% | 10571262 | 1335 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 91 | 76844794 | 3897 | 93.528 | 3.897 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 45356260 | 704 | 180.6518 | 0% | 0% | 0% | 100% | 100% | 55% | 10572630 | 1368 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 103 | 96 | 76848836 | 4042 | 97.008 | 4.042 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 937 | N/A | N/A | N/A | N/A | 45356964 | 704 | 174.1712 | 0% | 0% | 0% | 100% | 100% | 55% | 10573681 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 104 | 76852948 | 4112 | 98.688 | 4.112 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 927 | N/A | N/A | N/A | N/A | 45357620 | 656 | 159.5331 | 0% | 0% | 0% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 106 | 76858041 | 5093 | 122.232 | 5.093 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45358460 | 840 | 164.9323 | 0% | 0% | 0% | 100% | 100% | 0% | 10573681 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 76863698 | 5657 | 135.768 | 5.657 | 9.5 | 9.5 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45359692 | 1232 | 217.7833 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 76870076 | 6378 | 153.072 | 6.378 | 9 | 9 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45361100 | 1408 | 220.7589 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 149 | 76876174 | 6098 | 146.352 | 6.098 | 8.5 | 8.5 | 3B+1S | 0 | 1007 | 1189 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45362448 | 1348 | 221.0561 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 149 | 76882730 | 6556 | 157.344 | 6.556 | 8 | 8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45363812 | 1364 | 208.0537 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 | 1.37
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 76888525 | 5795 | 139.08 | 5.795 | 7.7 | 7.7 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45365148 | 1336 | 230.5436 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 76894662 | 6137 | 147.288 | 6.137 | 7.4 | 7.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45366516 | 1368 | 222.9102 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 146 | 76900732 | 6070 | 145.68 | 6.07 | 6.9 | 6.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45367878 | 1362 | 224.3822 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 76906812 | 6080 | 145.92 | 6.08 | 6.4 | 6.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45369260 | 1382 | 227.3026 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 76912781 | 5969 | 143.256 | 5.969 | 5.9 | 5.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45370620 | 1360 | 227.8439 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 76918607 | 5826 | 139.824 | 5.826 | 5.5 | 5.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45371956 | 1336 | 229.3169 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 76924542 | 5935 | 142.44 | 5.935 | 5.1 | 5.1 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45373300 | 1344 | 226.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 144 | 76930492 | 5950 | 142.8 | 5.95 | 4.7 | 4.7 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45374644 | 1344 | 225.8824 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 76936397 | 5905 | 141.72 | 5.905 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45375988 | 1344 | 227.6037 | 0% | 100% | 100% | 100% | 100% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 127 | 76941766 | 5369 | 128.856 | 5.369 | 3.5 | 3.5 | 2B+1S | 0 | 1118 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45377068 | 1080 | 201.1548 | 0% | 100% | 100% | 100% | 0% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 76947160 | 5394 | 129.456 | 5.394 | 2.9 | 2.9 | 2B+1S | 0 | 1048 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45378124 | 1056 | 195.7731 | 0% | 100% | 100% | 100% | 0% | 0% | 10573681 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 127 | 76952415 | 5255 | 126.12 | 5.255 | 2.5 | 2.5 | 2B+1S | 0 | 1026 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45379164 | 1040 | 197.9068 | 0% | 100% | 100% | 100% | 0% | 0% | 10573681 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 109 | 76956992 | 4577 | 109.848 | 4.577 | 3.1 | 3.1 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 45380028 | 864 | 188.7699 | 0% | 0% | 100% | 100% | 0% | 50% | 10574422 | 741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 132 | 109 | 76961367 | 4375 | 105 | 4.375 | 4.5 | 4.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45380844 | 816 | 186.5143 | 0% | 0% | 100% | 100% | 0% | 50% | 10575625 | 1203 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128763 | 128.763 | 128.763 | [12 empty] | 26808 | 26808 | 208.1965 | [6 empty] | 6871 | 6871 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## APR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27088 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 76961367 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45380844 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10575625 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 127 | 85 | 76965454 | 4087 | 98.088 | 4.087 | 5.7 | 5.7 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 45381580 | 736 | 180.0832 | 0% | 0% | 100% | 100% | 0% | 55% | 10576776 | 1151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 91 | 76969382 | 3928 | 94.272 | 3.928 | 7 | 7 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 45382292 | 712 | 181.2627 | 0% | 0% | 100% | 100% | 0% | 55% | 10578022 | 1246 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 123 | 98 | 76973344 | 3962 | 95.088 | 3.962 | 8.3 | 8.3 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 45383004 | 712 | 179.7072 | 0% | 0% | 100% | 100% | 0% | 55% | 10579227 | 1205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 118 | 93 | 76977211 | 3867 | 92.808 | 3.867 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 45383688 | 684 | 176.8813 | 0% | 0% | 100% | 100% | 0% | 55% | 10580298 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 13 | 9.1549 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 112 | 108 | 76981361 | 4150 | 99.6 | 4.15 | 9.5 | 9.5 | 2B | 0 | 0 | 946 | 1185 | 0 | N/A | N/A | N/A | N/A | 45384388 | 700 | 168.6747 | 0% | 0% | 100% | 100% | 0% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 127 | 76986852 | 5491 | 131.784 | 5.491 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45385340 | 952 | 173.3746 | 0% | 0% | 100% | 100% | 0% | 0% | 10580298 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 140 | 76992455 | 5603 | 134.472 | 5.603 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45386584 | 1244 | 222.0239 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 76998642 | 6187 | 148.488 | 6.187 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45387964 | 1380 | 223.0483 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 144 | 77004864 | 6222 | 149.328 | 6.222 | 8.1 | 8.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45389344 | 1380 | 221.7936 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 77011006 | 6142 | 147.408 | 6.142 | 7.7 | 7.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45390720 | 1376 | 224.0313 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 | 1.31
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 125 | 142 | 77016998 | 5992 | 143.808 | 5.992 | 7.3 | 7.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45392060 | 1340 | 223.6315 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 143 | 77023088 | 6090 | 146.16 | 6.09 | 6.9 | 6.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45393420 | 1360 | 223.3169 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 137 | 77029018 | 5930 | 142.32 | 5.93 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45394776 | 1356 | 228.6678 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 77034974 | 5956 | 142.944 | 5.956 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45396120 | 1344 | 225.6548 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 137 | 77040934 | 5960 | 143.04 | 5.96 | 5.7 | 5.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45397468 | 1348 | 226.1745 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 77046793 | 5859 | 140.616 | 5.859 | 5.4 | 5.4 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45398788 | 1320 | 225.2944 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 77052668 | 5875 | 141 | 5.875 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45400132 | 1344 | 228.766 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 150 | 77058706 | 6038 | 144.912 | 6.038 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45401500 | 1368 | 226.5651 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | , | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 77064512 | 5806 | 139.344 | 5.806 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45402824 | 1324 | 228.04 | 100% | 0% | 100% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 133 | 77070185 | 5673 | 136.152 | 5.673 | 3.4 | 3.4 | 2B+1S | 1128 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45403968 | 1144 | 201.657 | 100% | 0% | 0% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 77075786 | 5601 | 134.424 | 5.601 | 2.6 | 2.6 | 2B+1S | 1128 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45405088 | 1120 | 199.9643 | 100% | 0% | 0% | 100% | 100% | 0% | 10580298 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 129 | 77081390 | 5604 | 134.496 | 5.604 | 1.8 | 1.8 | 2B+1S | 1098 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45406196 | 1108 | 197.7159 | 100% | 0% | 0% | 100% | 100% | 0% | 10580298 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 110 | 77086118 | 4728 | 113.472 | 4.728 | 2.4 | 2.4 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45407092 | 896 | 189.5093 | 0% | 0% | 0% | 100% | 100% | 50% | 10581202 | 904 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 107 | 77090586 | 4468 | 107.232 | 4.468 | 3.7 | 3.7 | 2B | 0 | 0 | 0 | 1185 | 1077 | N/A | N/A | N/A | N/A | 45407932 | 840 | 188.0036 | 0% | 0% | 0% | 100% | 100% | 50% | 10582479 | 1277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129219 | 129.219 | 129.219 | [12 empty] | 27088 | 27088 | 209.6286 | [6 empty] | 6854 | 6854 | 1.1083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (55%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## APR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27132 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77090586 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45407932 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10582479 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 129 | 100 | 77094890 | 4304 | 103.296 | 4.304 | 5 | 5 | 2B | 0 | 0 | 0 | 1185 | 1058 | N/A | N/A | N/A | N/A | 45408724 | 792 | 184.0149 | 0% | 0% | 0% | 100% | 100% | 55% | 10583535 | 1056 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 94 | 77098994 | 4104 | 98.496 | 4.104 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 1016 | N/A | N/A | N/A | N/A | 45409484 | 760 | 185.1852 | 0% | 0% | 0% | 100% | 100% | 55% | 10584706 | 1171 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 77103020 | 4026 | 96.624 | 4.026 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 976 | N/A | N/A | N/A | N/A | 45410204 | 720 | 178.8376 | 0% | 0% | 0% | 100% | 100% | 55% | 10585902 | 1196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 132 | 93 | 77106956 | 3936 | 94.464 | 3.936 | 8.5 | 8.5 | 2B | 0 | 0 | 0 | 1185 | 957 | N/A | N/A | N/A | N/A | 45410900 | 696 | 176.8293 | 0% | 0% | 0% | 100% | 100% | 55% | 10586936 | 1034 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 109 | 104 | 77111127 | 4171 | 100.104 | 4.171 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 978 | N/A | N/A | N/A | N/A | 45411616 | 716 | 171.6615 | 0% | 0% | 0% | 100% | 100% | 55% | 10587736 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 155 | 77116174 | 5047 | 121.128 | 5.047 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45412460 | 844 | 167.2281 | 0% | 0% | 0% | 100% | 100% | 0% | 10587736 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 146 | 77122208 | 6034 | 144.816 | 6.034 | 9.1 | 9.1 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45413788 | 1328 | 220.0862 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 77128472 | 6264 | 150.336 | 6.264 | 8.7 | 8.7 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45415172 | 1384 | 220.9451 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 77134674 | 6202 | 148.848 | 6.202 | 8.2 | 8.2 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45416540 | 1368 | 220.574 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 77140857 | 6183 | 148.392 | 6.183 | 7.7 | 7.7 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45417900 | 1360 | 219.9579 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 | 1.28
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 77146986 | 6129 | 147.096 | 6.129 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45419268 | 1368 | 223.2012 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 77153164 | 6178 | 148.272 | 6.178 | 6.8 | 6.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45420652 | 1384 | 224.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 144 | 77158966 | 5802 | 139.248 | 5.802 | 6.4 | 6.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45421960 | 1308 | 225.4395 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 142 | 77165098 | 6132 | 147.168 | 6.132 | 5.9 | 5.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45423344 | 1384 | 225.7012 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 77171038 | 5940 | 142.56 | 5.94 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45424696 | 1352 | 227.6094 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 77176986 | 5948 | 142.752 | 5.948 | 5 | 5 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45426044 | 1348 | 226.6308 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 145 | 77182987 | 6001 | 144.024 | 6.001 | 4.6 | 4.6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45427400 | 1356 | 225.9623 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 141 | 77188950 | 5963 | 143.112 | 5.963 | 4.2 | 4.2 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45428748 | 1348 | 226.0607 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | , | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 77194936 | 5986 | 143.664 | 5.986 | 3.9 | 3.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45430088 | 1340 | 223.8557 | 0% | 100% | 100% | 100% | 100% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 77200401 | 5465 | 131.16 | 5.465 | 3.1 | 3.1 | 2B+1S | 0 | 1119 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45431168 | 1080 | 197.6212 | 0% | 100% | 100% | 100% | 0% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 129 | 77205882 | 5481 | 131.544 | 5.481 | 2.4 | 2.4 | 2B+1S | 0 | 1129 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45432240 | 1072 | 195.5847 | 0% | 100% | 100% | 100% | 0% | 0% | 10587736 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 126 | 77211270 | 5388 | 129.312 | 5.388 | 1.8 | 1.8 | 2B+1S | 0 | 1047 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45433288 | 1048 | 194.5063 | 0% | 100% | 100% | 100% | 0% | 0% | 10587736 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 110 | 77216059 | 4789 | 114.936 | 4.789 | 2.4 | 2.4 | 2B | 0 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 45434212 | 924 | 192.9422 | 0% | 0% | 100% | 100% | 0% | 50% | 10588472 | 736 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 144 | 106 | 77220640 | 4581 | 109.944 | 4.581 | 3.8 | 3.8 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 45435064 | 852 | 185.9856 | 0% | 0% | 100% | 100% | 0% | 50% | 10589714 | 1242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130054 | 130.054 | 130.054 | [12 empty] | 27132 | 27132 | 208.621 | [6 empty] | 7235 | 7235 | 1.17 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (55%)
XCV2- CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (50%)

## APR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27596 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77220640 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45435064 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10589714 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 100 | 77224958 | 4318 | 103.632 | 4.318 | 5.1 | 5.1 | 2B | 0 | 0 | 1066 | 1185 | 0 | N/A | N/A | N/A | N/A | 45435868 | 804 | 186.1973 | 0% | 0% | 100% | 100% | 0% | 55% | 10590912 | 1198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 104 | 77229069 | 4111 | 98.664 | 4.111 | 6.6 | 6.6 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 45436612 | 744 | 180.9779 | 0% | 0% | 100% | 100% | 0% | 55% | 10592305 | 1393 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 95 | 77233106 | 4037 | 96.888 | 4.037 | 7.8 | 7.8 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 45437340 | 728 | 180.3319 | 0% | 0% | 100% | 100% | 0% | 55% | 10593497 | 1192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 95 | 77237088 | 3982 | 95.568 | 3.982 | 9 | 9 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 45438044 | 704 | 176.7956 | 0% | 0% | 100% | 100% | 0% | 55% | 10594579 | 1082 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 116 | 99 | 77241160 | 4072 | 97.728 | 4.072 | 9.5 | 9.5 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 45438740 | 696 | 170.9234 | 0% | 0% | 100% | 100% | 0% | 55% | 10595056 | 477 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 126 | 77246170 | 5010 | 120.24 | 5.01 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45439612 | 872 | 174.0519 | 0% | 0% | 100% | 100% | 0% | 0% | 10595056 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 145 | 77252222 | 6052 | 145.248 | 6.052 | 9.1 | 9.1 | 3B+1S | 1037 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45440948 | 1336 | 220.7535 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 77258467 | 6245 | 149.88 | 6.245 | 8.5 | 8.5 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45442332 | 1384 | 221.6173 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 158 | 77264653 | 6186 | 148.464 | 6.186 | 8 | 8 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45443711 | 1379 | 222.9227 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 77270874 | 6221 | 149.304 | 6.221 | 7.5 | 7.5 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45445054 | 1343 | 215.8817 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 | 1.21
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 141 | 77277076 | 6202 | 148.848 | 6.202 | 7.1 | 7.1 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45446424 | 1370 | 220.8965 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 77283224 | 6148 | 147.552 | 6.148 | 6.7 | 6.7 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45447744 | 1320 | 214.704 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 144 | 77289190 | 5966 | 143.184 | 5.966 | 6.4 | 6.4 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45449136 | 1392 | 233.3222 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 145 | 77295431 | 6241 | 149.784 | 6.241 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45450560 | 1424 | 228.1686 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 141 | 77301304 | 5873 | 140.952 | 5.873 | 5.5 | 5.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45451872 | 1312 | 223.3952 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 77307168 | 5864 | 140.736 | 5.864 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45453208 | 1336 | 227.8308 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 77313106 | 5938 | 142.512 | 5.938 | 4.9 | 4.9 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45454556 | 1348 | 227.0125 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 77319138 | 6032 | 144.768 | 6.032 | 4.4 | 4.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45455924 | 1368 | 226.7905 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 131 | 77325135 | 5997 | 143.928 | 5.997 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45457284 | 1360 | 226.7801 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 137 | 77330982 | 5847 | 140.328 | 5.847 | 3.5 | 3.5 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45458612 | 1328 | 227.125 | 100% | 0% | 100% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 77336663 | 5681 | 136.344 | 5.681 | 2.8 | 2.8 | 2B+1S | 1128 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45459736 | 1124 | 197.8525 | 100% | 0% | 0% | 100% | 100% | 0% | 10595056 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 134 | 77342237 | 5574 | 133.776 | 5.574 | 1.9 | 1.9 | 2B+1S | 1109 | 0 | 0 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45460844 | 1108 | 198.7801 | 100% | 0% | 0% | 100% | 100% | 0% | 10595056 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 126 | 77347168 | 4931 | 118.344 | 4.931 | 2.4 | 2.4 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 45461788 | 944 | 191.4419 | 0% | 0% | 0% | 100% | 100% | 50% | 10595691 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 105 | 77351779 | 4611 | 110.664 | 4.611 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 45462660 | 872 | 189.113 | 0% | 0% | 0% | 100% | 100% | 50% | 10596831 | 1140 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131139 | 131.139 | 131.139 | [12 empty] | 27596 | 27596 | 210.4332 | [6 empty] | 7117 | 7117 | 1.0767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (55%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (50%)

## APR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27708 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77351779 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45462660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10596831 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 110 | 77356200 | 4421 | 106.104 | 4.421 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 1067 | N/A | N/A | N/A | N/A | 45463472 | 812 | 183.6689 | 0% | 0% | 0% | 100% | 100% | 60% | 10597939 | 1108 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 99 | 77360477 | 4277 | 102.648 | 4.277 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 1026 | N/A | N/A | N/A | N/A | 45464248 | 776 | 181.4356 | 0% | 0% | 0% | 100% | 100% | 60% | 10599143 | 1204 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 116 | 77364629 | 4152 | 99.648 | 4.152 | 7.4 | 7.4 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 45464988 | 740 | 178.2274 | 0% | 0% | 0% | 100% | 100% | 60% | 10600380 | 1237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 99 | 77368725 | 4096 | 98.304 | 4.096 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45465713 | 725 | 177.002 | 0% | 0% | 0% | 100% | 100% | 60% | 10601322 | 942 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 147 | 115 | 77372852 | 4127 | 99.048 | 4.127 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45466420 | 707 | 171.3109 | 0% | 0% | 0% | 100% | 100% | 60% | 10602287 | 965 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 127 | 77377955 | 5103 | 122.472 | 5.103 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45467292 | 872 | 170.8799 | 0% | 0% | 0% | 100% | 100% | 0% | 10602287 | 0 | 0.95 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 145 | 77383995 | 6040 | 144.96 | 6.04 | 9.1 | 9.1 | 3B+1S | 0 | 1068 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45468644 | 1352 | 223.8411 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 77390214 | 6219 | 149.256 | 6.219 | 8.4 | 8.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45470032 | 1388 | 223.187 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 77396401 | 6187 | 148.488 | 6.187 | 7.8 | 7.8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45471412 | 1380 | 223.0483 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 77402637 | 6236 | 149.664 | 6.236 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45472800 | 1388 | 222.5786 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 | 1.15
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 77408857 | 6220 | 149.28 | 6.22 | 6.6 | 6.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45474188 | 1388 | 223.1511 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 146 | 77414891 | 6034 | 144.816 | 6.034 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45475548 | 1360 | 225.3895 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 145 | 77420777 | 5886 | 141.264 | 5.886 | 5.6 | 5.6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45476908 | 1360 | 231.0567 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 143 | 77426820 | 6043 | 145.032 | 6.043 | 4.9 | 4.9 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45478292 | 1384 | 229.0253 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 143 | 77432787 | 5967 | 143.208 | 5.967 | 4.4 | 4.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45479660 | 1368 | 229.2609 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 145 | 77438735 | 5948 | 142.752 | 5.948 | 3.8 | 3.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45481016 | 1356 | 227.9758 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 77444690 | 5955 | 142.92 | 5.955 | 3.4 | 3.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45482372 | 1356 | 227.7078 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 144 | 77450528 | 5838 | 140.112 | 5.838 | 3.1 | 3.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45483700 | 1328 | 227.4752 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 144 | 77456377 | 5849 | 140.376 | 5.849 | 2.9 | 2.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45485036 | 1336 | 228.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 134 | 77462267 | 5890 | 141.36 | 5.89 | 2.8 | 2.8 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45486392 | 1356 | 230.2207 | 0% | 100% | 100% | 100% | 100% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 129 | 77467698 | 5431 | 130.344 | 5.431 | 2.5 | 2.5 | 2B+1S | 0 | 1067 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45487500 | 1108 | 204.014 | 0% | 100% | 100% | 100% | 0% | 0% | 10602287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 128 | 77473143 | 5445 | 130.68 | 5.445 | 1.9 | 1.9 | 2B+1S | 0 | 1046 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45488568 | 1068 | 196.1433 | 0% | 100% | 100% | 100% | 0% | 0% | 10602287 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 112 | 77478039 | 4896 | 117.504 | 4.896 | 2.5 | 2.5 | 2B | 0 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 45489496 | 928 | 189.5425 | 0% | 0% | 100% | 100% | 0% | 55% | 10603038 | 751 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 108 | 77482688 | 4649 | 111.576 | 4.649 | 3.8 | 3.8 | 2B | 0 | 0 | 1107 | 1185 | 0 | N/A | N/A | N/A | N/A | 45490368 | 872 | 187.5672 | 0% | 0% | 100% | 100% | 0% | 55% | 10604259 | 1221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130909 | 130.909 | 130.909 | [12 empty] | 27708 | 27708 | 211.6585 | [6 empty] | 7428 | 7428 | 1.085 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (60%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (55%)
Note on P4: Fidel A. Ramos:

## APR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27068 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77482688 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45490368 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10604259 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 100 | 77487030 | 4342 | 104.208 | 4.342 | 5 | 5 | 2B | 0 | 0 | 1058 | 1185 | 0 | N/A | N/A | N/A | N/A | 45491176 | 808 | 186.0894 | 0% | 0% | 100% | 100% | 0% | 60% | 10605255 | 996 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 98 | 77491234 | 4204 | 100.896 | 4.204 | 6.2 | 6.2 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45491944 | 768 | 182.6832 | 0% | 0% | 100% | 100% | 0% | 60% | 10606402 | 1147 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 120 | 96 | 77495362 | 4128 | 99.072 | 4.128 | 7.4 | 7.4 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 45492692 | 748 | 181.2016 | 0% | 0% | 100% | 100% | 0% | 60% | 10607595 | 1193 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 114 | 93 | 77499293 | 3931 | 94.344 | 3.931 | 8.3 | 8.3 | 2B | 0 | 0 | 966 | 1185 | 0 | N/A | N/A | N/A | N/A | 45493412 | 720 | 183.1595 | 0% | 0% | 100% | 100% | 0% | 60% | 10608467 | 872 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 150 | 104 | 77503307 | 4014 | 96.336 | 4.014 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 1185 | 0 | N/A | N/A | N/A | N/A | 45494120 | 708 | 176.3827 | 0% | 0% | 100% | 100% | 0% | 60% | 10609763 | 1296 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 14 | 9.8592 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 108 | 77508146 | 4839 | 116.136 | 4.839 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45494900 | 780 | 161.1903 | 0% | 0% | 100% | 100% | 0% | 0% | 10609763 | 0 | 0.89 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 148 | 148 | 77514236 | 6090 | 146.16 | 6.09 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45496242 | 1342 | 220.3612 | 0% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 143 | 77520096 | 5860 | 140.64 | 5.86 | 9.5 | 9.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45497460 | 1218 | 207.8498 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 150 | 77526308 | 6212 | 149.088 | 6.212 | 9 | 9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45498832 | 1372 | 220.8628 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 77532624 | 6316 | 151.584 | 6.316 | 8.5 | 8.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45500220 | 1388 | 219.7593 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 | 1.41
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 77538958 | 6334 | 152.016 | 6.334 | 8 | 8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45501612 | 1392 | 219.7663 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 77545022 | 6064 | 145.536 | 6.064 | 7.6 | 7.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45502956 | 1344 | 221.6359 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 142 | 77551033 | 6011 | 144.264 | 6.011 | 7.2 | 7.2 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45504308 | 1352 | 224.921 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 146 | 77557003 | 5970 | 143.28 | 5.97 | 6.8 | 6.8 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45505622 | 1314 | 220.1005 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 144 | 77563058 | 6055 | 145.32 | 6.055 | 6.4 | 6.4 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45506944 | 1322 | 218.332 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 147 | 77568997 | 5939 | 142.536 | 5.939 | 6.1 | 6.1 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45508324 | 1380 | 232.3624 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 148 | 77575043 | 6046 | 145.104 | 6.046 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45509676 | 1352 | 223.6189 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 141 | 77580971 | 5928 | 142.272 | 5.928 | 5.2 | 5.2 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45511012 | 1336 | 225.3711 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 145 | 77587012 | 6041 | 144.984 | 6.041 | 4.9 | 4.9 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45512356 | 1344 | 222.4797 | 100% | 0% | 100% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 137 | 77592630 | 5618 | 134.832 | 5.618 | 4.1 | 4.1 | 2B+1S | 1087 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45513468 | 1112 | 197.9352 | 100% | 0% | 0% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 131 | 77598213 | 5583 | 133.992 | 5.583 | 3.2 | 3.2 | 2B+1S | 1067 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45514556 | 1088 | 194.8773 | 100% | 0% | 0% | 100% | 100% | 0% | 10609763 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 9 | 6.338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 115 | 129 | 77603809 | 5596 | 134.304 | 5.596 | 2.6 | 2.6 | 2B+1S | 1057 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45515652 | 1096 | 195.8542 | 100% | 0% | 0% | 100% | 100% | 0% | 10609763 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 114 | 77608612 | 4803 | 115.272 | 4.803 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45516576 | 924 | 192.3798 | 0% | 0% | 0% | 100% | 100% | 55% | 10610414 | 651 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 109 | 77613261 | 4649 | 111.576 | 4.649 | 4.3 | 4.3 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 45517436 | 860 | 184.986 | 0% | 0% | 0% | 100% | 100% | 55% | 10611467 | 1053 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130573 | 130.573 | 130.573 | [12 empty] | 27068 | 27068 | 207.3017 | [6 empty] | 7208 | 7208 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (60%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (55%)
Note on P4: Fidel A. Ramos:

## APR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26896 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77613261 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45517436 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10611467 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 104 | 77617775 | 4514 | 108.336 | 4.514 | 5.2 | 5.2 | 2B | 0 | 0 | 0 | 1185 | 1078 | N/A | N/A | N/A | N/A | 45518260 | 824 | 182.5432 | 0% | 0% | 0% | 100% | 100% | 60% | 10612265 | 798 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 97 | 77622046 | 4271 | 102.504 | 4.271 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 1016 | N/A | N/A | N/A | N/A | 45519044 | 784 | 183.5636 | 0% | 0% | 0% | 100% | 100% | 60% | 10613348 | 1083 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 97 | 77626171 | 4125 | 99 | 4.125 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45519780 | 736 | 178.4242 | 0% | 0% | 0% | 100% | 100% | 60% | 10614563 | 1215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 113 | 77630297 | 4126 | 99.024 | 4.126 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45520504 | 724 | 175.4726 | 0% | 0% | 0% | 100% | 100% | 60% | 10615372 | 809 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 146 | 103 | 77634443 | 4146 | 99.504 | 4.146 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45521220 | 716 | 172.6966 | 0% | 0% | 0% | 100% | 100% | 60% | 10616306 | 934 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 17 | 11.9718 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 121 | 77639218 | 4775 | 114.6 | 4.775 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45521980 | 760 | 159.1623 | 0% | 0% | 0% | 100% | 100% | 0% | 10616306 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 138 | 77644820 | 5602 | 134.448 | 5.602 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45523148 | 1168 | 208.497 | 0% | 0% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 148 | 140 | 77650836 | 6016 | 144.384 | 6.016 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45524420 | 1272 | 211.4362 | 0% | 0% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 77657364 | 6528 | 156.672 | 6.528 | 9.2 | 9.2 | 3B+1S | 0 | 997 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45525836 | 1416 | 216.9118 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 147 | 77663336 | 5972 | 143.328 | 5.972 | 8.8 | 8.8 | 3B+1S | 0 | 998 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45527148 | 1312 | 219.6919 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 | 1.15
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 77669368 | 6032 | 144.768 | 6.032 | 8.5 | 8.5 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45528476 | 1328 | 220.1592 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 77675614 | 6246 | 149.904 | 6.246 | 8.1 | 8.1 | 3B+1S | 0 | 997 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45529860 | 1384 | 221.5818 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 146 | 77681582 | 5968 | 143.232 | 5.968 | 7.6 | 7.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45531188 | 1328 | 222.5201 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 77687782 | 6200 | 148.8 | 6.2 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45532588 | 1400 | 225.8065 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 143 | 77693738 | 5956 | 142.944 | 5.956 | 6.7 | 6.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45533932 | 1344 | 225.6548 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 77699699 | 5961 | 143.064 | 5.961 | 6.3 | 6.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45535280 | 1348 | 226.1366 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 77705676 | 5977 | 143.448 | 5.977 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45536652 | 1372 | 229.5466 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 147 | 77711677 | 6001 | 144.024 | 6.001 | 5.3 | 5.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45538020 | 1368 | 227.962 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 143 | 77717580 | 5903 | 141.672 | 5.903 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45539364 | 1344 | 227.6808 | 0% | 100% | 100% | 100% | 100% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 132 | 77723122 | 5542 | 133.008 | 5.542 | 4.1 | 4.1 | 2B+1S | 0 | 1098 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45540468 | 1104 | 199.2061 | 0% | 100% | 100% | 100% | 0% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 127 | 77728626 | 5504 | 132.096 | 5.504 | 3.3 | 3.3 | 2B+1S | 0 | 1077 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45541512 | 1044 | 189.6802 | 0% | 100% | 100% | 100% | 0% | 0% | 10616306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 126 | 77733986 | 5360 | 128.64 | 5.36 | 2.7 | 2.7 | 2B+1S | 0 | 1047 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45542564 | 1052 | 196.2687 | 0% | 100% | 100% | 100% | 0% | 0% | 10616306 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 140 | 112 | 77738850 | 4864 | 116.736 | 4.864 | 3.4 | 3.4 | 2B | 0 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 45543492 | 928 | 190.7895 | 0% | 0% | 100% | 100% | 0% | 55% | 10617050 | 744 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 137 | 107 | 77743405 | 4555 | 109.32 | 4.555 | 4.9 | 4.9 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 45544332 | 840 | 184.4127 | 0% | 0% | 100% | 100% | 0% | 55% | 10618366 | 1316 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130144 | 130.144 | 130.144 | [12 empty] | 26896 | 26896 | 206.6634 | [6 empty] | 6899 | 6899 | 1.0717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (60%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 8:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (55%)

## APR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27304 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77743405 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45544332 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10618366 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 102 | 77747793 | 4388 | 105.312 | 4.388 | 6 | 6 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45545124 | 792 | 180.4923 | 0% | 0% | 100% | 100% | 0% | 60% | 10619423 | 1057 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 90 | 77751933 | 4140 | 99.36 | 4.14 | 7.3 | 7.3 | 2B | 0 | 0 | 1016 | 1185 | 0 | N/A | N/A | N/A | N/A | 45545872 | 748 | 180.6763 | 0% | 0% | 100% | 100% | 0% | 60% | 10620657 | 1234 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 95 | 77755970 | 4037 | 96.888 | 4.037 | 8.6 | 8.6 | 2B | 0 | 0 | 977 | 1185 | 0 | N/A | N/A | N/A | N/A | 45546604 | 732 | 181.3228 | 0% | 0% | 100% | 100% | 0% | 60% | 10621951 | 1294 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 98 | 94 | 77759901 | 3931 | 94.344 | 3.931 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 45547300 | 696 | 177.0542 | 0% | 0% | 100% | 100% | 0% | 60% | 10622748 | 797 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 14 | 9.8592 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 107 | 104 | 77764111 | 4210 | 101.04 | 4.21 | 9.5 | 9.5 | 2B | 0 | 0 | 947 | 1185 | 0 | N/A | N/A | N/A | N/A | 45547988 | 688 | 163.4204 | 0% | 0% | 100% | 100% | 0% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 124 | 77768866 | 4755 | 114.12 | 4.755 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45548808 | 820 | 172.4501 | 0% | 0% | 100% | 100% | 0% | 0% | 10622748 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 77775058 | 6192 | 148.608 | 6.192 | 9.1 | 9.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45550172 | 1364 | 220.2842 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 149 | 77781454 | 6396 | 153.504 | 6.396 | 8.7 | 8.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45551560 | 1388 | 217.0106 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 150 | 77787502 | 6048 | 145.152 | 6.048 | 8.2 | 8.2 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45552928 | 1368 | 226.1905 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 77793586 | 6084 | 146.016 | 6.084 | 7.7 | 7.7 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45554250 | 1322 | 217.2913 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 | 1.1
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 77799748 | 6162 | 147.888 | 6.162 | 7.3 | 7.3 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45555624 | 1374 | 222.9796 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 143 | 77805888 | 6140 | 147.36 | 6.14 | 6.9 | 6.9 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45556996 | 1372 | 223.4528 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 77811796 | 5908 | 141.792 | 5.908 | 6.6 | 6.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45558332 | 1336 | 226.1341 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 143 | 77817762 | 5966 | 143.184 | 5.966 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45559700 | 1368 | 229.2994 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 77823774 | 6012 | 144.288 | 6.012 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45561048 | 1348 | 224.2182 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 145 | 77829740 | 5966 | 143.184 | 5.966 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45562392 | 1344 | 225.2766 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 77835749 | 6009 | 144.216 | 6.009 | 5.1 | 5.1 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45563744 | 1352 | 224.9958 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 146 | 77841703 | 5954 | 142.896 | 5.954 | 4.7 | 4.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45565084 | 1340 | 225.0588 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 145 | 77847687 | 5984 | 143.616 | 5.984 | 4.4 | 4.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45566436 | 1352 | 225.9358 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 142 | 77853572 | 5885 | 141.24 | 5.885 | 4 | 4 | 2B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45567776 | 1340 | 227.6975 | 100% | 0% | 100% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 137 | 77859161 | 5589 | 134.136 | 5.589 | 3.1 | 3.1 | 2B+1S | 1149 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45568884 | 1108 | 198.2466 | 100% | 0% | 0% | 100% | 100% | 0% | 10622748 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 128 | 77864556 | 5395 | 129.48 | 5.395 | 2.4 | 2.4 | 2B+1S | 1047 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45569956 | 1072 | 198.7025 | 100% | 0% | 0% | 100% | 100% | 0% | 10622748 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 111 | 77869315 | 4759 | 114.216 | 4.759 | 2.9 | 2.9 | 2B | 0 | 0 | 0 | 1185 | 1127 | N/A | N/A | N/A | N/A | 45570832 | 876 | 184.0723 | 0% | 0% | 0% | 100% | 100% | 60% | 10623383 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 138 | 108 | 77873767 | 4452 | 106.848 | 4.452 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 45571636 | 804 | 180.593 | 0% | 0% | 0% | 100% | 100% | 60% | 10624576 | 1193 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130362 | 130.362 | 130.362 | [12 empty] | 27304 | 27304 | 209.4475 | [6 empty] | 6210 | 6210 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (60%)
XCV1- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (60%)

## APR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27688 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 77873767 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45571636 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10624576 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 100 | 77877969 | 4202 | 100.848 | 4.202 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 45572382 | 746 | 177.5345 | 0% | 0% | 0% | 100% | 100% | 72% | 10625651 | 1075 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 139 | 102 | 77882175 | 4206 | 100.944 | 4.206 | 6.8 | 6.8 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 45573130 | 748 | 177.8412 | 0% | 0% | 0% | 100% | 100% | 72% | 10626729 | 1078 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 138 | 101 | 77886377 | 4202 | 100.848 | 4.202 | 7.9 | 7.9 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 45573880 | 750 | 178.4864 | 0% | 0% | 0% | 100% | 100% | 72% | 10627809 | 1080 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 137 | 97 | 77890610 | 4233 | 101.592 | 4.233 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45574652 | 772 | 182.3766 | 0% | 0% | 0% | 100% | 100% | 72% | 10628918 | 1109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 108 | 106 | 77894871 | 4261 | 102.264 | 4.261 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45575372 | 720 | 168.9744 | 0% | 0% | 0% | 100% | 100% | 72% | 10629474 | 556 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 124 | 77900336 | 5465 | 131.16 | 5.465 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45576372 | 1000 | 182.9826 | 0% | 0% | 0% | 100% | 100% | 0% | 10629474 | 0 | 1.22 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 77906028 | 5692 | 136.608 | 5.692 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45577628 | 1256 | 220.6606 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 77912222 | 6194 | 148.656 | 6.194 | 8.4 | 8.4 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45578996 | 1368 | 220.8589 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 77918522 | 6300 | 151.2 | 6.3 | 7.9 | 7.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45580388 | 1392 | 220.9524 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 77924706 | 6184 | 148.416 | 6.184 | 7.4 | 7.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45581756 | 1368 | 221.216 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 | 1.17
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 77930748 | 6042 | 145.008 | 6.042 | 6.9 | 6.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45583104 | 1348 | 223.1049 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 143 | 77936946 | 6198 | 148.752 | 6.198 | 6.5 | 6.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45584484 | 1380 | 222.6525 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 145 | 77943052 | 6106 | 146.544 | 6.106 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45585860 | 1376 | 225.3521 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 144 | 77948992 | 5940 | 142.56 | 5.94 | 5.7 | 5.7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45587216 | 1356 | 228.2828 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 145 | 77954995 | 6003 | 144.072 | 6.003 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45588580 | 1364 | 227.2197 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 77960956 | 5961 | 143.064 | 5.961 | 4.7 | 4.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45589940 | 1360 | 228.1496 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 143 | 77966993 | 6037 | 144.888 | 6.037 | 4.2 | 4.2 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45591308 | 1368 | 226.6026 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 77973074 | 6081 | 145.944 | 6.081 | 3.6 | 3.6 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45592696 | 1388 | 228.2519 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 141 | 77978963 | 5889 | 141.336 | 5.889 | 3.2 | 3.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45594032 | 1336 | 226.8636 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 142 | 77984864 | 5901 | 141.624 | 5.901 | 3 | 3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45595368 | 1336 | 226.4023 | 0% | 100% | 100% | 100% | 100% | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 112 | 138 | 77990340 | 5476 | 131.424 | 5.476 | 2.3 | 2.3 | 2B+1S | 0 | 1149 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45596452 | 1084 | 197.9547 | 0% | 100% | 100% | 100% |  | 0% | 10629474 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 127 | 77995708 | 5368 | 128.832 | 5.368 | 1.7 | 1.7 | 2B+1S | 0 | 1047 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45597508 | 1056 | 196.7213 | 0% | 100% | 100% | 100% |  | 0% | 10629474 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 138 | 113 | 78000601 | 4893 | 117.432 | 4.893 | 2.3 | 2.3 | 2B | 0 | 0 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45598436 | 928 | 189.6587 | 0% | 0% | 100% | 100% |  | 55% | 10630132 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 143 | 107 | 78005253 | 4652 | 111.648 | 4.652 | 3.4 | 3.4 | 2B | 0 | 0 | 1117 | 1185 |  | N/A | N/A | N/A | N/A | 45599324 | 888 | 190.8856 | 0% | 0% | 100% | 100% |  | 55% | 10631289 | 1157 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131486 | 131.486 | 131.486 | [12 empty] | 27688 | 27688 | 210.5776 | [6 empty] | 6713 | 6713 | 1.085 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (72%)
XCV2- CLOSED @ 4:33 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (55%)

## APR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78005253 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45599324 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10631289 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 102 | 78009641 | 4388 | 105.312 | 4.388 | 4.8 | 4.8 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 45600156 | 832 | 189.608 | 0% | 0% | 100% | 100% | 0% | 65% | 10632468 | 1179 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 78014025 | 4384 | 105.216 | 4.384 | 6.2 | 6.2 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45600986 | 830 | 189.3248 | 0% | 0% | 100% | 100% | 0% | 65% | 10633880 | 1412 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 96 | 78018114 | 4089 | 98.136 | 4.089 | 7.5 | 7.5 | 2B | 0 | 0 | 996 | 1185 | 0 | N/A | N/A | N/A | N/A | 45601704 | 718 | 175.5931 | 0% | 0% | 100% | 100% | 0% | 65% | 10634978 | 1098 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 116 | 95 | 78021984 | 3870 | 92.88 | 3.87 | 8.4 | 8.4 | 2B | 0 | 0 | 976 | 1185 | 0 | N/A | N/A | N/A | N/A | 45602404 | 700 | 180.8786 | 0% | 0% | 100% | 100% | 0% | 65% | 10635861 | 883 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 149 | 107 | 78026198 | 4214 | 101.136 | 4.214 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45603128 | 724 | 171.8083 | 0% | 0% | 100% | 100% | 0% | 65% | 10636931 | 1070 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 123 | 78031256 | 5058 | 121.392 | 5.058 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45604020 | 892 | 176.3543 | 0% | 0% | 100% | 100% | 0% | 0% | 10636931 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 150 | 78037314 | 6058 | 145.392 | 6.058 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45605344 | 1324 | 218.554 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 149 | 78043656 | 6342 | 152.208 | 6.342 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45606732 | 1388 | 218.8584 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 151 | 78049898 | 6242 | 149.808 | 6.242 | 8 | 8 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45608112 | 1380 | 221.083 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 147 | 78056334 | 6436 | 154.464 | 6.436 | 7.5 | 7.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45609510 | 1398 | 217.2157 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 | 1.29
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 150 | 78062352 | 6018 | 144.432 | 6.018 | 7 | 7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45610844 | 1334 | 221.6683 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 78068492 | 6140 | 147.36 | 6.14 | 6.6 | 6.6 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45612204 | 1360 | 221.4984 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 146 | 78074438 | 5946 | 142.704 | 5.946 | 6.2 | 6.2 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45613552 | 1348 | 226.707 | 100% | 0% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 148 | 78080665 | 6227 | 149.448 | 6.227 | 5.7 | 5.7 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45614948 | 1396 | 224.185 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 146 | 78086783 | 6118 | 146.832 | 6.118 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45616324 | 1376 | 224.9101 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 78092809 | 6026 | 144.624 | 6.026 | 4.7 | 4.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45617688 | 1364 | 226.3525 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 78098879 | 6070 | 145.68 | 6.07 | 4.2 | 4.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45619052 | 1364 | 224.7117 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 143 | 78104951 | 6072 | 145.728 | 6.072 | 3.6 | 3.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45620420 | 1368 | 225.2964 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 78110982 | 6031 | 144.744 | 6.031 | 3.2 | 3.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45621772 | 1352 | 224.1751 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 142 | 78116932 | 5950 | 142.8 | 5.95 | 2.9 | 2.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45623116 | 1344 | 225.8824 | 0% | 100% | 100% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 138 | 78122461 | 5529 | 132.696 | 5.529 | 2.2 | 2.2 | 2B+1S | 0 | 1148 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45624208 | 1092 | 197.5041 | 0% | 100% | 0% | 100% | 100% | 0% | 10636931 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 127 | 78127883 | 5422 | 130.128 | 5.422 | 1.6 | 1.6 | 2B+1S | 0 | 1016 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45625264 | 1056 | 194.7621 | 0% | 100% | 0% | 100% | 100% | 0% | 10636931 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 114 | 78132272 | 4389 | 105.336 | 4.389 | 2 | 2 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45626204 | 940 | 214.1718 | 0% | 0% | 0% | 100% | 100% | 60% | 10637476 | 545 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 145 | 106 | 78137357 | 5085 | 122.04 | 5.085 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1117 | N/A | N/A | N/A | N/A | 45627092 | 888 | 174.6313 | 0% | 0% | 0% | 100% | 100% | 60% | 10638578 | 1102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132104 | 132.104 | 132.104 | [12 empty] | 27768 | 27768 | 210.198 | [6 empty] | 7289 | 7289 | 1.135 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (65%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP1 - STOPPED @1:10 PM DUE TO PREVENTIVE MAINTENANCE
SP2- STARTED @1:11PM DUE TO PREVENTIVE MAINTENANCE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (60%)

## APR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27816 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78137357 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45627092 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10638578 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 108 | 78142027 | 4670 | 112.08 | 4.67 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 1067 | N/A | N/A | N/A | N/A | 45627959 | 867 | 185.6531 | 0% | 0% | 0% | 100% | 100% | 70% | 10639804 | 1226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 134 | 103 | 78146235 | 4208 | 100.992 | 4.208 | 6.7 | 6.7 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45628705 | 746 | 177.2814 | 0% | 0% | 0% | 100% | 100% | 70% | 10641143 | 1339 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 102 | 78150178 | 3943 | 94.632 | 3.943 | 7.2 | 7.2 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45629452 | 747 | 189.4497 | 0% | 0% | 0% | 100% | 100% | 70% | 10642363 | 1220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 95 | 78154172 | 3994 | 95.856 | 3.994 | 8.2 | 8.2 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45630172 | 720 | 180.2704 | 0% | 0% | 0% | 100% | 100% | 70% | 10643327 | 964 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 11 | 7.7465 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 145 | 103 | 78158411 | 4239 | 101.736 | 4.239 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 977 | N/A | N/A | N/A | N/A | 45630896 | 724 | 170.795 | 0% | 0% | 0% | 100% | 100% | 70% | 10644380 | 1053 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 128 | 78163333 | 4922 | 118.128 | 4.922 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45631756 | 860 | 174.7257 | 0% | 0% | 0% | 100% | 100% | 0% | 10644380 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 146 | 78169374 | 6041 | 144.984 | 6.041 | 9.1 | 9.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45633092 | 1336 | 221.1554 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 153 | 78175653 | 6279 | 150.696 | 6.279 | 8.4 | 8.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45634444 | 1352 | 215.3209 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 146 | 78181904 | 6251 | 150.024 | 6.251 | 7.8 | 7.8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45635854 | 1410 | 225.5639 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 160 | 78188194 | 6290 | 150.96 | 6.29 | 7.3 | 7.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45637244 | 1390 | 220.9857 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 | 1.24
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 155 | 78194476 | 6282 | 150.768 | 6.282 | 6.8 | 6.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45638621 | 1377 | 219.1977 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 141 | 78200603 | 6127 | 147.048 | 6.127 | 6.4 | 6.4 | 3B+1S | 0 | 1008 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45639941 | 1320 | 215.4399 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 140 | 78206587 | 5984 | 143.616 | 5.984 | 6 | 6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45641332 | 1391 | 232.4532 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 144 | 78212852 | 6265 | 150.36 | 6.265 | 5.6 | 5.6 | 3B+1S | 0 | 1078 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45642784 | 1452 | 231.7638 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 145 | 78218922 | 6070 | 145.68 | 6.07 | 5 | 5 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45644092 | 1308 | 215.486 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 146 | 78224985 | 6063 | 145.512 | 6.063 | 4.5 | 4.5 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45645452 | 1360 | 224.3114 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 78231003 | 6018 | 144.432 | 6.018 | 3.8 | 3.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45646824 | 1372 | 227.9827 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 143 | 78237075 | 6072 | 145.728 | 6.072 | 3.3 | 3.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45648196 | 1372 | 225.9552 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 145 | 78243162 | 6087 | 146.088 | 6.087 | 2.8 | 2.8 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45649572 | 1376 | 226.0555 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 143 | 78249198 | 6036 | 144.864 | 6.036 | 2.5 | 2.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45650924 | 1352 | 223.9894 | 0% | 100% | 100% | 100% | 100% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 140 | 78254724 | 5526 | 132.624 | 5.526 | 1.8 | 1.8 | 2B+1S | 0 | 1098 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45652004 | 1080 | 195.4397 | 0% | 100% | 100% | 100% | 0% | 0% | 10644380 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 133 | 78260156 | 5432 | 130.368 | 5.432 | 1.3 | 1.3 | 2B+1S | 0 | 1017 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45653052 | 1048 | 192.9308 | 0% | 100% | 100% | 100% | 0% | 0% | 10644380 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 116 | 78265044 | 4888 | 117.312 | 4.888 | 1.7 | 1.7 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45653984 | 932 | 190.671 | 0% | 0% | 100% | 100% | 0% | 60% | 10644914 | 534 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 145 | 111 | 78269799 | 4755 | 114.12 | 4.755 | 2.7 | 2.7 | 2B | 0 | 0 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 45654908 | 924 | 194.3218 | 0% | 0% | 100% | 100% | 0% | 60% | 10645876 | 962 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132442 | 132.442 | 132.442 | [12 empty] | 27816 | 27816 | 210.024 | [6 empty] | 7298 | 7298 | 1.0383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (60%)

## APR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27636 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78269799 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45654908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10645876 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 102 | 78274343 | 4544 | 109.056 | 4.544 | 3.9 | 3.9 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 45655780 | 872 | 191.9014 | 0% | 0% | 100% | 100% | 0% | 70% | 10646832 | 956 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 107 | 78278843 | 4500 | 108 | 4.5 | 5.4 | 5.4 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 45656620 | 840 | 186.6667 | 0% | 0% | 100% | 100% | 0% | 70% | 10647937 | 1105 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 100 | 78283096 | 4253 | 102.072 | 4.253 | 6.5 | 6.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45657396 | 776 | 182.4594 | 0% | 0% | 100% | 100% | 0% | 70% | 10649119 | 1182 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 107 | 78287396 | 4300 | 103.2 | 4.3 | 7.6 | 7.6 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45658164 | 768 | 178.6047 | 0% | 0% | 100% | 100% | 0% | 70% | 10650164 | 1045 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 143 | 104 | 78291853 | 4457 | 106.968 | 4.457 | 8.5 | 8.5 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45658936 | 772 | 173.2107 | 0% | 0% | 100% | 100% | 0% | 70% | 10651008 | 844 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 121 | 78296555 | 4702 | 112.848 | 4.702 | 8.5 | 8.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45659780 | 844 | 179.4981 | 0% | 0% | 100% | 100% | 0% | 0% | 10651008 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 145 | 78302786 | 6231 | 149.544 | 6.231 | 8 | 8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45661132 | 1352 | 216.9796 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 148 | 78309118 | 6332 | 151.968 | 6.332 | 7.5 | 7.5 | 3B+1S | 1017 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45662520 | 1388 | 219.204 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 78315318 | 6200 | 148.8 | 6.2 | 7 | 7 | 3B+1S | 1017 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45663892 | 1372 | 221.2903 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 78321526 | 6208 | 148.992 | 6.208 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45665260 | 1368 | 220.3608 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 | 1.19
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 78327692 | 6166 | 147.984 | 6.166 | 6 | 6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45666616 | 1356 | 219.9157 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 78333877 | 6185 | 148.44 | 6.185 | 5.5 | 5.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45667976 | 1360 | 219.8868 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 163 | 78339968 | 6091 | 146.184 | 6.091 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45669332 | 1356 | 222.6235 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 160 | 78346106 | 6138 | 147.312 | 6.138 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45670692 | 1360 | 221.5705 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 143 | 78352146 | 6040 | 144.96 | 6.04 | 4.5 | 4.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45672040 | 1348 | 223.1788 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 78358122 | 5976 | 143.424 | 5.976 | 4.2 | 4.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45673376 | 1336 | 223.5609 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 78364145 | 6023 | 144.552 | 6.023 | 3.7 | 3.7 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45674724 | 1348 | 223.8087 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 145 | 78370195 | 6050 | 145.2 | 6.05 | 3.4 | 3.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45676076 | 1352 | 223.4711 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 141 | 78376130 | 5935 | 142.44 | 5.935 | 3.2 | 3.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45677412 | 1336 | 225.1053 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 138 | 78382065 | 5935 | 142.44 | 5.935 | 2.9 | 2.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45678748 | 1336 | 225.1053 | 100% | 0% | 100% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 78387437 | 5372 | 128.928 | 5.372 | 2.5 | 2.5 | 2B+1S | 1098 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45679796 | 1048 | 195.0856 | 100% | 0% | 0% | 100% | 100% | 0% | 10651008 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 107 | 123 | 78392705 | 5268 | 126.432 | 5.268 | 1.7 | 1.7 | 2B+1S | 1097 | 0 | 1098 | 0 | 1188 | N/A | N/A | N/A | N/A | 45680796 | 1000 | 189.8254 | 100% | 0% | 100% | 0% | 100% | 0% | 10651008 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 139 | 125 | 78397450 | 4745 | 113.88 | 4.745 | 2.1 | 2.1 | 2B | 0 | 0 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 45681652 | 856 | 180.4004 | 0% | 0% | 100% | 100% | 0% | 60% | 10651688 | 680 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 113 | 78402193 | 4743 | 113.832 | 4.743 | 3.2 | 3.2 | 2B | 0 | 0 | 1159 | 1185 | 0 | N/A | N/A | N/A | N/A | 45682544 | 892 | 188.0666 | 0% | 0% | 100% | 100% | 0% | 60% | 10652710 | 1022 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132394 | 132.394 | 132.394 | [12 empty] | 27636 | 27636 | 208.7406 | [6 empty] | 6834 | 6834 | 1.075 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 6:00 AM,WATER ELEVATION (8.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP2 - STOPPED @ 9:00 PM DUE TO QUARTERLY PREVENTIVE MAINTENANCE
BP1 - STARTED @ 9:02 PM DUE TO QUARTERLY PREVENTIVE MAINTENANCE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (60%)
BP3 - STOPPED @ 10:04 PM DUE TO QUARTERLY PREVENTIVE MAINTENANCE
BP2 - STARTED @ 10:06 PM DUE TO QUARTERLY PREVENTIVE MAINTENANCE

## APR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27808 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78402193 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45682544 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10652710 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 137 | 107 | 78406809 | 4616 | 110.784 | 4.616 | 4.3 | 4.3 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 45683412 | 868 | 188.0416 | 0% | 0% | 100% | 100% | 0% | 70% | 10653637 | 927 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 138 | 102 | 78411250 | 4441 | 106.584 | 4.441 | 5.5 | 5.5 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 45684220 | 808 | 181.941 | 0% | 0% | 100% | 100% | 0% | 70% | 10654837 | 1200 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 100 | 78415551 | 4301 | 103.224 | 4.301 | 6.8 | 6.8 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45684992 | 772 | 179.4931 | 0% | 0% | 100% | 100% | 0% | 70% | 10656073 | 1236 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 117 | 96 | 78419759 | 4208 | 100.992 | 4.208 | 7.8 | 7.8 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45685744 | 752 | 178.7072 | 0% | 0% | 100% | 100% | 0% | 70% | 10656894 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 136 | 106 | 78424151 | 4392 | 105.408 | 4.392 | 8.8 | 8.8 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45686508 | 764 | 173.9526 | 0% | 0% | 100% | 100% | 0% | 70% | 10657779 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 126 | 78429386 | 5235 | 125.64 | 5.235 | 8.8 | 8.8 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45687456 | 948 | 181.0888 | 0% | 0% | 100% | 100% | 0% | 0% | 10657779 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 78434968 | 5582 | 133.968 | 5.582 | 8.4 | 8.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45688668 | 1212 | 217.1265 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 154 | 78441304 | 6336 | 152.064 | 6.336 | 8 | 8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45690060 | 1392 | 219.697 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 152 | 78447496 | 6192 | 148.608 | 6.192 | 7.5 | 7.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45691428 | 1368 | 220.9302 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 78453836 | 6340 | 152.16 | 6.34 | 6.9 | 6.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45692808 | 1380 | 217.6656 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 | 1.22
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 78460018 | 6182 | 148.368 | 6.182 | 6.4 | 6.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45694164 | 1356 | 219.3465 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 78466144 | 6126 | 147.024 | 6.126 | 6 | 6 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45695524 | 1360 | 222.0046 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 153 | 78472286 | 6142 | 147.408 | 6.142 | 5.5 | 5.5 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45696892 | 1368 | 222.7288 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 142 | 78478348 | 6062 | 145.488 | 6.062 | 5.1 | 5.1 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45698236 | 1344 | 221.709 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 141 | 141 | 78484470 | 6122 | 146.928 | 6.122 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45699544 | 1308 | 213.6557 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 144 | 78490477 | 6007 | 144.168 | 6.007 | 4.5 | 4.5 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45700932 | 1388 | 231.0638 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 78496465 | 5988 | 143.712 | 5.988 | 4 | 4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45702276 | 1344 | 224.4489 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 78502427 | 5962 | 143.088 | 5.962 | 3.6 | 3.6 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45703612 | 1336 | 224.0859 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 141 | 135 | 78508386 | 5959 | 143.016 | 5.959 | 3.5 | 3.5 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45704940 | 1328 | 222.8562 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 140 | 138 | 78514337 | 5951 | 142.824 | 5.951 | 3.3 | 3.3 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45706276 | 1336 | 224.5001 | 0% | 100% | 100% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 132 | 78519995 | 5658 | 135.792 | 5.658 | 2.6 | 2.6 | 2B+1S | 0 | 1098 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45707392 | 1116 | 197.2428 | 0% | 100% | 0% | 100% | 100% | 0% | 10657779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 131 | 78525693 | 5698 | 136.752 | 5.698 | 1.8 | 1.8 | 2B+1S | 0 | 1078 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45708508 | 1116 | 195.8582 | 0% | 100% | 0% | 100% | 100% | 0% | 10657779 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 132 | 117 | 78530530 | 4837 | 116.088 | 4.837 | 2.2 | 2.2 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 45709452 | 944 | 195.1623 | 0% | 0% | 0% | 100% | 100% | 62% | 10658339 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 112 | 78535247 | 4717 | 113.208 | 4.717 | 3 | 3 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45710352 | 900 | 190.7992 | 0% | 0% | 0% | 100% | 100% | 62% | 10659123 | 784 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133054 | 133.054 | 133.054 | [12 empty] | 27808 | 27808 | 208.9979 | [6 empty] | 6413 | 6413 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (72%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (8.8M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (60%)

## APR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27556 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78535247 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45710352 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10659123 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 126 | 78539863 | 4616 | 110.784 | 4.616 | 4 | 4 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 45711212 | 860 | 186.3085 | 0% | 0% | 0% | 100% | 100% | 72% | 10659979 | 856 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 136 | 114 | 78544269 | 4406 | 105.744 | 4.406 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1057 | N/A | N/A | N/A | N/A | 45712020 | 808 | 183.3863 | 0% | 0% | 0% | 100% | 100% | 72% | 10661071 | 1092 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 131 | 109 | 78548393 | 4124 | 98.976 | 4.124 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 1058 | N/A | N/A | N/A | N/A | 45712788 | 768 | 186.227 | 0% | 0% | 0% | 100% | 100% | 72% | 10662344 | 1273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 119 | 107 | 78552748 | 4355 | 104.52 | 4.355 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 1036 | N/A | N/A | N/A | N/A | 45713542 | 754 | 173.1343 | 0% | 0% | 0% | 100% | 100% | 72% | 10663398 | 1054 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 146 | 105 | 78557246 | 4498 | 107.952 | 4.498 | 9.3 | 9.3 | 2B | 0 | 0 | 0 | 1185 | 1117 | N/A | N/A | N/A | N/A | 45714532 | 990 | 220.0978 | 0% | 0% | 0% | 100% | 100% | 70% | 10663986 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 129 | 78561552 | 4306 | 103.344 | 4.306 | 9.3 | 9.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45715496 | 964 | 223.8737 | 0% | 0% | 0% | 100% | 100% | 0% | 10663986 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 144 | 78567110 | 5558 | 133.392 | 5.558 | 9.3 | 9.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45716620 | 1124 | 202.231 | 0% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 124 | 78573266 | 6156 | 147.744 | 6.156 | 9.2 | 9.2 | 3B+1S | 955 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45717968 | 1348 | 218.9734 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 147 | 78579472 | 6206 | 148.944 | 6.206 | 9 | 9 | 3B+1S | 967 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45719328 | 1360 | 219.1428 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 144 | 78585777 | 6305 | 151.32 | 6.305 | 8.7 | 8.7 | 3B+1S | 966 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45720696 | 1368 | 216.9707 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 | 1.28
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 151 | 78591868 | 6091 | 146.184 | 6.091 | 8.4 | 8.4 | 3B+1S | 976 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45722036 | 1340 | 219.9967 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 139 | 78598092 | 6224 | 149.376 | 6.224 | 8.1 | 8.1 | 3B+1S | 986 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45723412 | 1376 | 221.0797 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 | 139 | 78603986 | 5894 | 141.456 | 5.894 | 7.7 | 7.7 | 3B+1S | 986 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45724740 | 1328 | 225.3139 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 78610189 | 6203 | 148.872 | 6.203 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45726104 | 1364 | 219.8936 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 78616300 | 6111 | 146.664 | 6.111 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45727468 | 1364 | 223.2041 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 78622356 | 6056 | 145.344 | 6.056 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45728824 | 1356 | 223.9102 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 78628523 | 6167 | 148.008 | 6.167 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45730184 | 1360 | 220.5286 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 78634590 | 6067 | 145.608 | 6.067 | 5.5 | 5.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45731532 | 1348 | 222.1856 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 141 | 78640560 | 5970 | 143.28 | 5.97 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45732868 | 1336 | 223.7856 | 100% | 0% | 100% | 100% | 100% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 134 | 78646128 | 5568 | 133.632 | 5.568 | 4.4 | 4.4 | 3B+1S | 1149 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45733952 | 1084 | 194.6839 | 100% | 0% | 100% | 100% | 0% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 137 | 78651662 | 5534 | 132.816 | 5.534 | 3.6 | 3.6 | 2B+1S | 1149 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45735028 | 1076 | 194.4344 | 100% | 0% | 100% | 100% | 0% | 0% | 10663986 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 131 | 78657230 | 5568 | 133.632 | 5.568 | 2.9 | 2.9 | 2B+1S | 1078 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45736100 | 1072 | 192.5287 | 100% | 0% | 100% | 100% | 0% | 0% | 10663986 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 137 | 110 | 78662105 | 4875 | 117 | 4.875 | 3.2 | 3.2 | 2B | 0 | 0 | 1168 | 1185 | 0 | N/A | N/A | N/A | N/A | 45737036 | 936 | 192 | 0% | 0% | 100% | 100% | 0% | 65% | 10664667 | 681 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 136 | 108 | 78666753 | 4648 | 111.552 | 4.648 | 4.4 | 4.4 | 2B | 0 | 0 | 1118 | 1185 | 0 | N/A | N/A | N/A | N/A | 45737908 | 872 | 187.6076 | 0% | 0% | 100% | 100% | 0% | 65% | 10665769 | 1102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131506 | 131.506 | 131.506 | [12 empty] | 27556 | 27556 | 209.5418 | [6 empty] | 6646 | 6646 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (72%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (65%)

## APR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27596 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78666753 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45737908 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10665769 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 132 | 105 | 78671205 | 4452 | 106.848 | 4.452 | 5.3 | 5.3 | 2B | 0 | 0 | 1077 | 1185 | 0 | N/A | N/A | N/A | N/A | 45738732 | 824 | 185.0854 | 0% | 0% | 100% | 100% | 0% | 73% | 10666775 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 104 | 78675452 | 4247 | 101.928 | 4.247 | 6.2 | 6.2 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 45739500 | 768 | 180.8335 | 0% | 0% | 100% | 100% | 0% | 73% | 10667787 | 1012 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 99 | 78679743 | 4291 | 102.984 | 4.291 | 7.4 | 7.4 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 45740272 | 772 | 179.9114 | 0% | 0% | 100% | 100% | 0% | 73% | 10668875 | 1088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 97 | 78683884 | 4141 | 99.384 | 4.141 | 8.3 | 8.3 | 2B | 0 | 0 | 1007 | 1185 | 0 | N/A | N/A | N/A | N/A | 45741012 | 740 | 178.7008 | 0% | 0% | 100% | 100% | 0% | 73% | 10669398 | 523 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 142 | 105 | 78688046 | 4162 | 99.888 | 4.162 | 9.5 | 9.5 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45741756 | 744 | 178.7602 | 0% | 0% | 100% | 100% | 0% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 128 | 78693014 | 4968 | 119.232 | 4.968 | 9.4 | 9.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45742668 | 912 | 183.5749 | 0% | 0% | 100% | 100% | 0% | 0% | 10669398 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 145 | 78699006 | 5992 | 143.808 | 5.992 | 9 | 9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45743992 | 1324 | 220.9613 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 78705186 | 6180 | 148.32 | 6.18 | 8.5 | 8.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45745344 | 1352 | 218.7702 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 140 | 78711434 | 6248 | 149.952 | 6.248 | 7.9 | 7.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45746732 | 1388 | 222.1511 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 78717866 | 6432 | 154.368 | 6.432 | 7.4 | 7.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45748124 | 1392 | 216.4179 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 | 1.29
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 78723786 | 5920 | 142.08 | 5.92 | 6.9 | 6.9 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45749460 | 1336 | 225.6757 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 145 | 78729989 | 6203 | 148.872 | 6.203 | 6.5 | 6.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45750836 | 1376 | 221.8281 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 143 | 78736416 | 6427 | 154.248 | 6.427 | 6 | 6 | 3B+1S | 0 | 1007 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45752254 | 1418 | 220.6317 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 145 | 78742248 | 5832 | 139.968 | 5.832 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45753564 | 1310 | 224.6228 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 78748304 | 6056 | 145.344 | 6.056 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45754916 | 1352 | 223.2497 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 78754356 | 6052 | 145.248 | 6.052 | 4.9 | 4.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45756264 | 1348 | 222.7363 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 145 | 78760421 | 6065 | 145.56 | 6.065 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45757612 | 1348 | 222.2589 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 147 | 78766450 | 6029 | 144.696 | 6.029 | 4.1 | 4.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45758960 | 1348 | 223.586 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 78772498 | 6048 | 145.152 | 6.048 | 3.6 | 3.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45760300 | 1340 | 221.5608 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 145 | 78778591 | 6093 | 146.232 | 6.093 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45761652 | 1352 | 221.894 | 0% | 100% | 100% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 146 | 78784113 | 5522 | 132.528 | 5.522 | 2.6 | 2.6 | 2B+1S | 0 | 1180 |  | 1185 | 1188 | N/A | N/A | N/A | N/A | 45762732 | 1080 | 195.5813 | 0% | 100% | 0% | 100% | 100% | 0% | 10669398 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 141 | 78789514 | 5401 | 129.624 | 5.401 | 2 | 2 | 2B+1S | 0 | 1036 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45763780 | 1048 | 194.0381 | 0% | 100% | 0% | 100% | 100% | 0% | 10669398 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 136 | 114 | 78794233 | 4719 | 113.256 | 4.719 | 2.5 | 2.5 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45764676 | 896 | 189.8707 | 0% | 0% | 0% | 100% | 100% | 70% | 10669615 | 217 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 145 | 103 | 78798696 | 4463 | 107.112 | 4.463 | 3.7 | 3.7 | 2B | 0 | 0 | 0 | 1185 | 1057 | N/A | N/A | N/A | N/A | 45765504 | 828 | 185.5254 | 0% | 0% | 0% | 100% | 100% | 70% | 10670831 | 1216 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131943 | 131.943 | 131.943 | [12 empty] | 27596 | 27596 | 209.1509 | [6 empty] | 5062 | 5062 | 1.115 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (73%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (70%)

## APR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27904 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78798696 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45765504 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10670831 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 137 | 102 | 78802998 | 4302 | 103.248 | 4.302 | 5.3 | 5.3 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45766269 | 765 | 177.8243 | 0% | 0% | 0% | 100% | 100% | 85% | 10671991 | 1160 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 99 | 78807240 | 4242 | 101.808 | 4.242 | 6.5 | 6.5 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45767039 | 770 | 181.5182 | 0% | 0% | 0% | 100% | 100% | 85% | 10673156 | 1165 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 101 | 78811540 | 4300 | 103.2 | 4.3 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 1047 | N/A | N/A | N/A | N/A | 45767828 | 789 | 183.4884 | 0% | 0% | 0% | 100% | 100% | 85% | 10674332 | 1176 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 125 | 92 | 78815356 | 3816 | 91.584 | 3.816 | 8.9 | 8.9 | 2B | 0 | 0 | 0 | 1185 | 1138 | N/A | N/A | N/A | N/A | 45768692 | 864 | 226.4151 | 0% | 0% | 0% | 100% | 100% | 85% | 10675004 | 672 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 118 | 112 | 78819528 | 4172 | 100.128 | 4.172 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45769448 | 756 | 181.2081 | 0% | 0% | 0% | 100% | 100% | 85% | 10675248 | 244 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 126 | 78825102 | 5574 | 133.776 | 5.574 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45770444 | 996 | 178.6868 | 0% | 0% | 0% | 100% | 100% | 0% | 10675248 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 150 | 78830932 | 5830 | 139.92 | 5.83 | 9 | 9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45771732 | 1288 | 220.9262 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 150 | 78837226 | 6294 | 151.056 | 6.294 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45773124 | 1392 | 221.163 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 78843338 | 6112 | 146.688 | 6.112 | 8 | 8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45774476 | 1352 | 221.2042 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 143 | 78849786 | 6448 | 154.752 | 6.448 | 7.4 | 7.4 | 3B+1S | 1017 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45775862 | 1386 | 214.9504 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 160 | 78855752 | 5966 | 143.184 | 5.966 | 7 | 7 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45777212 | 1350 | 226.2823 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 78861888 | 6136 | 147.264 | 6.136 | 6.5 | 6.5 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45778572 | 1360 | 221.6428 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 145 | 78867832 | 5944 | 142.656 | 5.944 | 6.1 | 6.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45779912 | 1340 | 225.4374 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 145 | 78874132 | 6300 | 151.2 | 6.3 | 5.6 | 5.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45781308 | 1396 | 221.5873 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 146 | 78880099 | 5967 | 143.208 | 5.967 | 5.2 | 5.2 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45782660 | 1352 | 226.5795 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 144 | 78886032 | 5933 | 142.392 | 5.933 | 4.9 | 4.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45783996 | 1336 | 225.1812 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 78892051 | 6019 | 144.456 | 6.019 | 4.6 | 4.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45785344 | 1348 | 223.9575 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 146 | 78898161 | 6110 | 146.64 | 6.11 | 4 | 4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45786712 | 1368 | 223.8953 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 144 | 78904233 | 6072 | 145.728 | 6.072 | 3.4 | 3.4 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45788076 | 1364 | 224.6377 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 141 | 78910194 | 5961 | 143.064 | 5.961 | 3.1 | 3.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45789412 | 1336 | 224.1235 | 100% | 0% | 100% | 100% | 100% | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 118 | 140 | 78915791 | 5597 | 134.328 | 5.597 | 2.5 | 2.5 | 2B+1S | 1098 | 0 | 1187 | 1185 |  | N/A | N/A | N/A | N/A | 45790508 | 1096 | 195.8192 | 100% | 0% | 100% | 100% |  | 0% | 10675248 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 126 | 78921198 | 5407 | 129.768 | 5.407 | 1.9 | 1.9 | 2B+1S | 1046 | 0 | 1188 | 1185 |  | N/A | N/A | N/A | N/A | 45791560 | 1052 | 194.5626 | 100% | 0% | 100% | 100% |  | 0% | 10675248 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 111 | 78926139 | 4941 | 118.584 | 4.941 | 2.3 | 2.3 | 2B | 0 | 0 | 1187 | 1185 |  | N/A | N/A | N/A | N/A | 45792516 | 956 | 193.4831 | 0% | 0% | 100% | 100% |  | 70% | 10675848 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 110 | 78930842 | 4703 | 112.872 | 4.703 | 3.4 | 3.4 | 2B | 0 | 0 | 1087 | 1185 |  | N/A | N/A | N/A | N/A | 45793408 | 892 | 189.6662 | 0% | 0% | 100% | 100% |  | 70% | 10676948 | 1100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132146 | 132.146 | 132.146 | [12 empty] | 27904 | 27904 | 211.1604 | [6 empty] | 6117 | 6117 | 1.1333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (85%)
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (70%)

## APR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 78930842 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45793408 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10676948 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 104 | 78935237 | 4395 | 105.48 | 4.395 | 4.6 | 4.6 | 2B | 0 | 0 | 1087 | 1185 | 0 | N/A | N/A | N/A | N/A | 45794224 | 816 | 185.6655 | 0% | 0% | 100% | 100% | 0% | 85% | 10678056 | 1108 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 103 | 78939501 | 4264 | 102.336 | 4.264 | 5.8 | 5.8 | 2B | 0 | 0 | 1057 | 1185 | 0 | N/A | N/A | N/A | N/A | 45795020 | 796 | 186.6792 | 0% | 0% | 100% | 100% | 0% | 85% | 10679088 | 1032 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 95 | 78943681 | 4180 | 100.32 | 4.18 | 7.2 | 7.2 | 2B | 0 | 0 | 1018 | 1185 | 0 | N/A | N/A | N/A | N/A | 45795780 | 760 | 181.8182 | 0% | 0% | 100% | 100% | 0% | 85% | 10680098 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 98 | 78947604 | 3923 | 94.152 | 3.923 | 8.1 | 8.1 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45796580 | 800 | 203.9256 | 0% | 0% | 100% | 100% | 0% | 85% | 10681046 | 948 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 128 | 102 | 78951716 | 4112 | 98.688 | 4.112 | 9.4 | 9.4 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 45797404 | 824 | 200.3891 | 0% | 0% | 100% | 100% | 0% | 85% | 10682165 | 1119 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 123 | 78956742 | 5026 | 120.624 | 5.026 | 9.4 | 9.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45798376 | 972 | 193.3943 | 0% | 0% | 100% | 100% | 0% | 0% | 10682165 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 149 | 78962522 | 5780 | 138.72 | 5.78 | 8.9 | 8.9 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45799648 | 1272 | 220.0692 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 154 | 78968878 | 6356 | 152.544 | 6.356 | 8.3 | 8.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45801044 | 1396 | 219.635 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 78975065 | 6187 | 148.488 | 6.187 | 7.8 | 7.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45802412 | 1368 | 221.1088 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 78981286 | 6221 | 149.304 | 6.221 | 7.3 | 7.3 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45803788 | 1376 | 221.1863 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 | 1.18
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 152 | 78987476 | 6190 | 148.56 | 6.19 | 6.9 | 6.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45805144 | 1356 | 219.063 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 78993784 | 6308 | 151.392 | 6.308 | 6.4 | 6.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45806540 | 1396 | 221.3063 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 78999692 | 5908 | 141.792 | 5.908 | 6 | 6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45807880 | 1340 | 226.8111 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 145 | 79005822 | 6130 | 147.12 | 6.13 | 5.5 | 5.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45809248 | 1368 | 223.1648 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 79011783 | 5961 | 143.064 | 5.961 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45810592 | 1344 | 225.4655 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 79017745 | 5962 | 143.088 | 5.962 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45811936 | 1344 | 225.4277 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 79023716 | 5971 | 143.304 | 5.971 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45813284 | 1348 | 225.7578 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 143 | 79029711 | 5995 | 143.88 | 5.995 | 4.1 | 4.1 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45814628 | 1344 | 224.1868 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 140 | 79035608 | 5897 | 141.528 | 5.897 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45815964 | 1336 | 226.5559 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 139 | 79041516 | 5908 | 141.792 | 5.908 | 3.4 | 3.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45817308 | 1344 | 227.4882 | 0% | 100% | 100% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 139 | 79047033 | 5517 | 132.408 | 5.517 | 2.8 | 2.8 | 2B+1S | 0 | 1129 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45818396 | 1088 | 197.2086 | 0% | 100% | 0% | 100% | 100% | 0% | 10682165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 125 | 79052438 | 5405 | 129.72 | 5.405 | 2.3 | 2.3 | 2B+1S | 0 | 1027 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45819452 | 1056 | 195.3747 | 0% | 100% | 0% | 100% | 100% | 0% | 10682165 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 131 | 116 | 79057261 | 4823 | 115.752 | 4.823 | 2.7 | 2.7 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 45820396 | 944 | 195.7288 | 0% | 0% | 0% | 100% | 100% | 70% | 10682863 | 698 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 147 | 108 | 79061917 | 4656 | 111.744 | 4.656 | 3.8 | 3.8 | 2B | 0 | 0 | 0 | 1185 | 1117 | N/A | N/A | N/A | N/A | 45821268 | 872 | 187.2852 | 0% | 0% | 0% | 100% | 100% | 70% | 10683946 | 1083 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131075 | 131.075 | 131.075 | [12 empty] | 27860 | 27860 | 212.5501 | [6 empty] | 6998 | 6998 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (85%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (70%)

## APR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27728 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79061917 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45821268 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10683946 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 135 | 107 | 79066357 | 4440 | 106.56 | 4.44 | 4.8 | 4.8 | 2B | 0 | 0 | 0 | 1185 | 1086 | N/A | N/A | N/A | N/A | 45822108 | 840 | 189.1892 | 0% | 0% | 0% | 100% | 100% | 85% | 10685049 | 1103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 101 | 79070720 | 4363 | 104.712 | 4.363 | 6.2 | 6.2 | 2B | 0 | 0 | 0 | 1185 | 1036 | N/A | N/A | N/A | N/A | 45822904 | 796 | 182.4433 | 0% | 0% | 0% | 100% | 100% | 85% | 10686102 | 1053 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 109 | 79074919 | 4199 | 100.776 | 4.199 | 7.3 | 7.3 | 2B | 0 | 0 | 0 | 1185 | 1117 | N/A | N/A | N/A | N/A | 45823668 | 764 | 181.9481 | 0% | 0% | 0% | 100% | 100% | 85% | 10687105 | 1003 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 100 | 79078905 | 3986 | 95.664 | 3.986 | 8.4 | 8.4 | 2B | 0 | 0 | 0 | 1185 | 1027 | N/A | N/A | N/A | N/A | 45824452 | 784 | 196.6884 | 0% | 0% | 0% | 100% | 100% | 85% | 10687863 | 758 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 139 | 107 | 79083226 | 4321 | 103.704 | 4.321 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45825212 | 760 | 175.8852 | 0% | 0% | 0% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 122 | 79087979 | 4753 | 114.072 | 4.753 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45826040 | 828 | 174.2058 | 0% | 0% | 0% | 100% | 100% | 0% | 10687863 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 149 | 79094029 | 6050 | 145.2 | 6.05 | 8.9 | 8.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45827392 | 1352 | 223.4711 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 148 | 79100205 | 6176 | 148.224 | 6.176 | 8.3 | 8.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45828764 | 1372 | 222.1503 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 145 | 79106428 | 6223 | 149.352 | 6.223 | 7.7 | 7.7 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45830148 | 1384 | 222.4008 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 150 | 79112579 | 6151 | 147.624 | 6.151 | 7.3 | 7.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45831511 | 1363 | 221.59 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 142 | 79118828 | 6249 | 149.976 | 6.249 | 6.9 | 6.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45832872 | 1361 | 217.7948 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 79124953 | 6125 | 147 | 6.125 | 6.5 | 6.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45834224 | 1352 | 220.7347 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 149 | 79131050 | 6097 | 146.328 | 6.097 | 6 | 6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45835544 | 1320 | 216.4999 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 147 | 79137314 | 6264 | 150.336 | 6.264 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45836980 | 1436 | 229.2465 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 145 | 79143275 | 5961 | 143.064 | 5.961 | 5.2 | 5.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45838328 | 1348 | 226.1366 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 146 | 79149233 | 5958 | 142.992 | 5.958 | 4.9 | 4.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45839668 | 1340 | 224.9077 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 79155182 | 5949 | 142.776 | 5.949 | 4.4 | 4.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45841008 | 1340 | 225.2479 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 145 | 79161257 | 6075 | 145.8 | 6.075 | 4 | 4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 45842364 | 1356 | 223.2099 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 143 | 79167221 | 5964 | 143.136 | 5.964 | 3.6 | 3.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45843708 | 1344 | 225.3521 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 79173165 | 5944 | 142.656 | 5.944 | 3.3 | 3.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45845044 | 1336 | 224.7645 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 138 | 79178629 | 5464 | 131.136 | 5.464 | 2.7 | 2.7 | 2B+1S | 1130 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 45846116 | 1072 | 196.1933 | 100% | 0% | 100% | 100% | 100% | 0% | 10687863 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 125 | 79183958 | 5329 | 127.896 | 5.329 | 2.3 | 2.3 | 2B+1S | 1077 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45847168 | 1052 | 197.4104 | 100% | 0% | 100% | 100% | 0% | 0% | 10687863 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 133 | 114 | 79188852 | 4894 | 117.456 | 4.894 | 2.7 | 2.7 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45848108 | 940 | 192.0719 | 0% | 0% | 100% | 100% | 0% | 70% | 10688536 | 673 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 110 | 79193493 | 4641 | 111.384 | 4.641 | 3.6 | 3.6 | 2B | 0 | 0 | 1128 | 1185 | 0 | N/A | N/A | N/A | N/A | 45848996 | 888 | 191.3381 | 0% | 0% | 100% | 100% | 0% | 70% | 10689563 | 1027 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131576 | 131.576 | 131.576 | [12 empty] | 27728 | 27728 | 210.7375 | [6 empty] | 5617 | 5617 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (90%)
XCV1- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (70%)

## APR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27832 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79193493 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45848996 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10689563 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 105 | 79198003 | 4510 | 108.24 | 4.51 | 4.8 | 4.8 | 2B | 0 | 0 | 1087 | 1185 | 0 | N/A | N/A | N/A | N/A | 45849836 | 840 | 186.2528 | 0% | 0% | 100% | 100% | 0% | 90% | 10690564 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 101 | 79202361 | 4358 | 104.592 | 4.358 | 6.2 | 6.2 | 2B | 0 | 0 | 1047 | 1185 | 0 | N/A | N/A | N/A | N/A | 45850636 | 800 | 183.5704 | 0% | 0% | 100% | 100% | 0% | 90% | 10691664 | 1100 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 116 | 96 | 79206540 | 4179 | 100.296 | 4.179 | 7.3 | 7.3 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45851404 | 768 | 183.776 | 0% | 0% | 100% | 100% | 0% | 90% | 10692664 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 101 | 79210692 | 4152 | 99.648 | 4.152 | 8 | 8 | 2B | 0 | 0 | 1027 | 1185 | 0 | N/A | N/A | N/A | N/A | 45852156 | 752 | 181.1175 | 0% | 0% | 100% | 100% | 0% | 90% | 10693206 | 542 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 137 | 105 | 79215005 | 4313 | 103.512 | 4.313 | 9 | 9 | 2B | 0 | 0 | 1030 | 1185 | 0 | N/A | N/A | N/A | N/A | 45852924 | 768 | 178.0663 | 0% | 0% | 100% | 100% | 0% | 90% | 10693948 | 742 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 121 | 79219608 | 4603 | 110.472 | 4.603 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45853876 | 952 | 206.8216 | 0% | 0% | 100% | 100% | 0% | 0% | 10693948 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 79225378 | 5770 | 138.48 | 5.77 | 9 | 9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45855140 | 1264 | 219.0641 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 79232036 | 6658 | 159.792 | 6.658 | 8.5 | 8.5 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45856496 | 1356 | 203.6648 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 79237874 | 5838 | 140.112 | 5.838 | 7.9 | 7.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45857890 | 1394 | 238.7804 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 148 | 79244296 | 6422 | 154.128 | 6.422 | 7.3 | 7.3 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45859296 | 1406 | 218.9349 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 | 0.86
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 146 | 79250534 | 6238 | 149.712 | 6.238 | 6.9 | 6.9 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45860656 | 1360 | 218.0186 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 79256694 | 6160 | 147.84 | 6.16 | 6.4 | 6.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45862028 | 1372 | 222.7273 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 152 | 79263008 | 6314 | 151.536 | 6.314 | 5.9 | 5.9 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45863424 | 1396 | 221.096 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 146 | 79269130 | 6122 | 146.928 | 6.122 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45864780 | 1356 | 221.4962 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 148 | 79275163 | 6033 | 144.792 | 6.033 | 5.1 | 5.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45866116 | 1336 | 221.4487 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 79281198 | 6035 | 144.84 | 6.035 | 4.8 | 4.8 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45867468 | 1352 | 224.0265 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 79287221 | 6023 | 144.552 | 6.023 | 4.4 | 4.4 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45868820 | 1352 | 224.4729 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 143 | 79293279 | 6058 | 145.392 | 6.058 | 4 | 4 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45870164 | 1344 | 221.8554 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 144 | 79299300 | 6021 | 144.504 | 6.021 | 3.6 | 3.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45871516 | 1352 | 224.5474 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 140 | 79305302 | 6002 | 144.048 | 6.002 | 3.3 | 3.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45872848 | 1332 | 221.926 | 0% | 100% | 100% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 135 | 79310772 | 5470 | 131.28 | 5.47 | 2.6 | 2.6 | 2B+1S | 0 | 1128 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45873940 | 1092 | 199.6344 | 0% | 100% | 0% | 100% | 100% | 0% | 10693948 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 127 | 79316173 | 5401 | 129.624 | 5.401 | 2.2 | 2.2 | 2B+1S | 0 | 1077 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45875004 | 1064 | 197.0006 | 0% | 100% | 0% | 100% | 100% | 0% | 10693948 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 134 | 116 | 79321036 | 4863 | 116.712 | 4.863 | 2.6 | 2.6 | 2B | 0 | 0 | 0 | 1185 | 1168 | N/A | N/A | N/A | N/A | 45875944 | 940 | 193.2963 | 0% | 0% | 0% | 100% | 100% | 75% | 10694372 | 424 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 111 | 79325662 | 4626 | 111.024 | 4.626 | 3.7 | 3.7 | 2B | 0 | 0 | 0 | 1185 | 1118 | N/A | N/A | N/A | N/A | 45876828 | 884 | 191.0938 | 0% | 0% | 0% | 100% | 100% | 75% | 10695272 | 900 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132169 | 132.169 | 132.169 | [12 empty] | 27832 | 27832 | 210.5789 | [6 empty] | 5709 | 5709 | 1.0567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (90%)
XCV2- CLOSED @ 5:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (75%)

## APR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27792 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79325662 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45876828 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10695272 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 107 | 79330131 | 4469 | 107.256 | 4.469 | 4.9 | 4.9 | 2B | 0 | 0 | 0 | 1185 | 1087 | N/A | N/A | N/A | N/A | 45877672 | 844 | 188.8566 | 0% | 0% | 0% | 100% | 100% | 90% | 10696283 | 1011 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 133 | 101 | 79334506 | 4375 | 105 | 4.375 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 1056 | N/A | N/A | N/A | N/A | 45878476 | 804 | 183.7714 | 0% | 0% | 0% | 100% | 100% | 90% | 10697343 | 1060 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 124 | 99 | 79338778 | 4272 | 102.528 | 4.272 | 7.7 | 7.7 | 2B | 0 | 0 | 0 | 1185 | 1026 | N/A | N/A | N/A | N/A | 45879260 | 784 | 183.5206 | 0% | 0% | 0% | 100% | 100% | 90% | 10698414 | 1071 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 124 | 98 | 79342865 | 4087 | 98.088 | 4.087 | 8.6 | 8.6 | 2B | 0 | 0 | 0 | 1185 | 997 | N/A | N/A | N/A | N/A | 45880004 | 744 | 182.0406 | 0% | 0% | 0% | 100% | 100% | 90% | 10699466 | 1052 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 142 | 106 | 79347130 | 4265 | 102.36 | 4.265 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45880748 | 744 | 174.4431 | 0% | 0% | 0% | 100% | 100% | 90% | 10700125 | 659 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 108 | 79351826 | 4696 | 112.704 | 4.696 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45881660 | 912 | 194.2078 | 0% | 0% | 0% | 100% | 100% | 0% | 10700125 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 147 | 79357994 | 6168 | 148.032 | 6.168 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45883004 | 1344 | 217.8988 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 79364256 | 6262 | 150.288 | 6.262 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45884380 | 1376 | 219.7381 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 149 | 79370558 | 6302 | 151.248 | 6.302 | 8.1 | 8.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45885772 | 1392 | 220.8823 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 79376796 | 6238 | 149.712 | 6.238 | 7.6 | 7.6 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45887140 | 1368 | 219.3011 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 | 1.15
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 151 | 79382974 | 6178 | 148.272 | 6.178 | 7.1 | 7.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45888500 | 1360 | 220.136 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 79389228 | 6254 | 150.096 | 6.254 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45889876 | 1376 | 220.0192 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 128 | 79395336 | 6108 | 146.592 | 6.108 | 6.2 | 6.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45891244 | 1368 | 223.9686 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 145 | 79401519 | 6183 | 148.392 | 6.183 | 5.7 | 5.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45892612 | 1368 | 221.2518 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 135 | 79407582 | 6063 | 145.512 | 6.063 | 5.4 | 5.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45893966 | 1354 | 223.3218 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 146 | 79413640 | 6058 | 145.392 | 6.058 | 5 | 5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45895308 | 1342 | 221.5253 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 79419703 | 6063 | 145.512 | 6.063 | 4.6 | 4.6 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45896660 | 1352 | 222.9919 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 129 | 79425654 | 5951 | 142.824 | 5.951 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45898012 | 1352 | 227.1887 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 79431877 | 6223 | 149.352 | 6.223 | 3.9 | 3.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45899356 | 1344 | 215.973 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 143 | 79437850 | 5973 | 143.352 | 5.973 | 3.6 | 3.6 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45900700 | 1344 | 225.0126 | 100% | 0% | 100% | 100% | 100% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 126 | 79443290 | 5440 | 130.56 | 5.44 | 3 | 3 | 2B+1S | 1056 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45901764 | 1064 | 195.5882 | 100% | 0% | 100% | 100% | 0% | 0% | 10700125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 115 | 79448648 | 5358 | 128.592 | 5.358 | 2.4 | 2.4 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45902812 | 1048 | 195.5954 | 100% | 0% | 100% | 100% | 0% | 0% | 10700125 | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 112 | 79453449 | 4801 | 115.224 | 4.801 | 2.9 | 2.9 | 2B | 0 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 45903748 | 936 | 194.9594 | 0% | 0% | 100% | 100% | 0% | 75% | 10700796 | 671 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 135 | 111 | 79458048 | 4599 | 110.376 | 4.599 | 4.1 | 4.1 | 2B | 0 | 0 | 1118 | 1185 | 0 | N/A | N/A | N/A | N/A | 45904620 | 872 | 189.6064 | 0% | 0% | 100% | 100% | 0% | 75% | 10701846 | 1050 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132386 | 132.386 | 132.386 | [12 empty] | 27792 | 27792 | 209.9316 | [6 empty] | 6574 | 6574 | 1.0617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (90%)
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (75%)

## APR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27064 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79458048 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45904620 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10701846 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 130 | 100 | 79462405 | 4357 | 104.568 | 4.357 | 5.2 | 5.2 | 2B | 0 | 0 | 1078 | 1185 | 0 | N/A | N/A | N/A | N/A | 45905440 | 820 | 188.2029 | 0% | 0% | 100% | 100% | 0% | 90% | 10702710 | 864 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 132 | 98 | 79466605 | 4200 | 100.8 | 4.2 | 6.3 | 6.3 | 2B | 0 | 0 | 1036 | 1185 | 0 | N/A | N/A | N/A | N/A | 45906220 | 780 | 185.7143 | 0% | 0% | 100% | 100% | 0% | 90% | 10703831 | 1121 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 128 | 95 | 79470638 | 4033 | 96.792 | 4.033 | 7.6 | 7.6 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 45906972 | 752 | 186.4617 | 0% | 0% | 100% | 100% | 0% | 90% | 10705050 | 1219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 123 | 95 | 79474633 | 3995 | 95.88 | 3.995 | 8.5 | 8.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 45907704 | 732 | 183.229 | 0% | 0% | 100% | 100% | 0% | 90% | 10705834 | 784 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 146 | 99 | 79478704 | 4071 | 97.704 | 4.071 | 9.5 | 9.5 | 2B | 0 | 0 | 997 | 1185 | 0 | N/A | N/A | N/A | N/A | 45908412 | 708 | 173.913 | 0% | 0% | 100% | 100% | 0% | 90% | 10706802 | 968 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 128 | 79483222 | 4518 | 108.432 | 4.518 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45909152 | 740 | 163.7893 | 0% | 0% | 100% | 100% | 0% | 0% | 10706802 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 140 | 79489174 | 5952 | 142.848 | 5.952 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45910428 | 1276 | 214.3817 | 0% | 0% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 142 | 79495288 | 6114 | 146.736 | 6.114 | 9.3 | 9.3 | 3B+1S | 0 | 998 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45911788 | 1360 | 222.4403 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 | 149 | 79501622 | 6334 | 152.016 | 6.334 | 8.9 | 8.9 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45913184 | 1396 | 220.3979 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 156 | 79507774 | 6152 | 147.648 | 6.152 | 8.5 | 8.5 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45914532 | 1348 | 219.1157 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 | 1.24
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 155 | 79513982 | 6208 | 148.992 | 6.208 | 8 | 8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45915906 | 1374 | 221.3273 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 79520048 | 6066 | 145.584 | 6.066 | 7.5 | 7.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45917268 | 1362 | 224.5302 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 156 | 79526122 | 6074 | 145.776 | 6.074 | 7 | 7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45918620 | 1352 | 222.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 147 | 79532454 | 6332 | 151.968 | 6.332 | 6.6 | 6.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45920032 | 1412 | 222.9943 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 146 | 79538541 | 6087 | 146.088 | 6.087 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45921396 | 1364 | 224.0841 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 79544574 | 6033 | 144.792 | 6.033 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45922756 | 1360 | 225.4268 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 147 | 79550547 | 5973 | 143.352 | 5.973 | 5.3 | 5.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45924100 | 1344 | 225.0126 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 145 | 79556606 | 6059 | 145.416 | 6.059 | 5 | 5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45925448 | 1348 | 222.479 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 141 | 79562597 | 5991 | 143.784 | 5.991 | 4.7 | 4.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45926796 | 1348 | 225.0042 | 0% | 100% | 100% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 138 | 79568175 | 5578 | 133.872 | 5.578 | 4 | 4 | 2B+1S | 0 | 1129 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45927872 | 1076 | 192.9007 | 0% | 100% | 0% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 137 | 79573726 | 5551 | 133.224 | 5.551 | 3.2 | 3.2 | 2B+1S | 0 | 1129 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45928940 | 1068 | 192.3978 | 0% | 100% | 0% | 100% | 100% | 0% | 10706802 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 117 | 129 | 79578963 | 5237 | 125.688 | 5.237 | 2.9 | 2.9 | 2B+1S | 0 | 1006 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45929948 | 1008 | 192.4766 | 0% | 100% | 0% | 100% | 100% | 0% | 10706802 | 0 | 1.023 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 113 | 79583718 | 4755 | 114.12 | 4.755 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1148 | N/A | N/A | N/A | N/A | 45930848 | 900 | 189.2744 | 0% | 0% | 0% | 100% | 100% | 80% | 10707272 | 470 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 140 | 103 | 79588243 | 4525 | 108.6 | 4.525 | 4.5 | 4.5 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 45931684 | 836 | 184.7514 | 0% | 0% | 0% | 100% | 100% | 80% | 10708293 | 1021 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130195 | 130.195 | 130.195 | [12 empty] | 27064 | 27064 | 207.8728 | [6 empty] | 6447 | 6447 | 1.1305 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (90%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (80%)

## APR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27676 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79588243 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45931684 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10708293 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 131 | 97 | 79592474 | 4231 | 101.544 | 4.231 | 5.4 | 5.4 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45932449 | 765 | 180.8083 | 0% | 0% | 0% | 100% | 100% | 93% | 10709308 | 1015 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 129 | 99 | 79596711 | 4237 | 101.688 | 4.237 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45933219 | 770 | 181.7324 | 0% | 0% | 0% | 100% | 100% | 93% | 10710326 | 1018 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 127 | 100 | 79600970 | 4259 | 102.216 | 4.259 | 7.5 | 7.5 | 2B | 0 | 0 | 0 | 1185 | 1017 | N/A | N/A | N/A | N/A | 45934012 | 793 | 186.1939 | 0% | 0% | 0% | 100% | 100% | 93% | 10711354 | 1028 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 115 | 100 | 79605161 | 4191 | 100.584 | 4.191 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 45934742 | 730 | 174.1828 | 0% | 0% | 0% | 100% | 100% | 93% | 10711931 | 577 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 131 | 107 | 79609368 | 4207 | 100.968 | 4.207 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 1007 | N/A | N/A | N/A | N/A | 45935488 | 746 | 177.3235 | 0% | 0% | 0% | 100% | 100% | 93% | 10712509 | 578 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 127 | 79614622 | 5254 | 126.096 | 5.254 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45936504 | 1016 | 193.3765 | 0% | 0% | 0% | 100% | 100% | 93% | 10712788 | 279 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 148 | 79620504 | 5882 | 141.168 | 5.882 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45937792 | 1288 | 218.9731 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 149 | 79626945 | 6441 | 154.584 | 6.441 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45939210 | 1418 | 220.1522 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 150 | 79632806 | 5861 | 140.664 | 5.861 | 8.1 | 8.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45940508 | 1298 | 221.4639 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 79639324 | 6518 | 156.432 | 6.518 | 7.5 | 7.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45941930 | 1422 | 218.1651 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 | 1.28
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 79645346 | 6022 | 144.528 | 6.022 | 7 | 7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45943268 | 1338 | 222.1853 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 150 | 79651628 | 6282 | 150.768 | 6.282 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45944672 | 1404 | 223.4957 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 137 | 79657684 | 6056 | 145.344 | 6.056 | 6 | 6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45946028 | 1356 | 223.9102 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 79663897 | 6213 | 149.112 | 6.213 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45947404 | 1376 | 221.4711 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 79669867 | 5970 | 143.28 | 5.97 | 5.2 | 5.2 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45948748 | 1344 | 225.1256 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 79675804 | 5937 | 142.488 | 5.937 | 4.9 | 4.9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45950092 | 1344 | 226.377 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 79681890 | 6086 | 146.064 | 6.086 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45951448 | 1356 | 222.8064 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 145 | 79687890 | 6000 | 144 | 6 | 4 | 4 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45952780 | 1332 | 222 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 137 | 79693829 | 5939 | 142.536 | 5.939 | 3.6 | 3.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45954116 | 1336 | 224.9537 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 140 | 79699851 | 6022 | 144.528 | 6.022 | 3.2 | 3.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45955468 | 1352 | 224.5101 | 100% | 0% | 100% | 100% | 100% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 137 | 79705334 | 5483 | 131.592 | 5.483 | 2.5 | 2.5 | 2B+1S | 1149 | 0 | 1187 | 1185 |  | N/A | N/A | N/A | N/A | 45956544 | 1076 | 196.2429 | 100% | 0% | 100% | 100% | 0% | 0% | 10712788 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 132 | 79710561 | 5227 | 125.448 | 5.227 | 1.9 | 1.9 | 2B+1S | 1049 | 0 | 1187 | 1185 |  | N/A | N/A | N/A | N/A | 45957560 | 1016 | 194.3754 | 100% | 0% | 100% | 100% | 0% | 0% | 10712788 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 114 | 79715383 | 4822 | 115.728 | 4.822 | 2.4 | 2.4 | 2B | 0 | 0 | 1187 | 1185 |  | N/A | N/A | N/A | N/A | 45958484 | 924 | 191.6217 | 0% | 0% | 100% | 100% | 0% | 90% | 10713348 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 134 | 112 | 79720026 | 4643 | 111.432 | 4.643 | 3.2 | 3.2 | 2B | 0 | 0 | 1117 | 1185 |  | N/A | N/A | N/A | N/A | 45959360 | 876 | 188.6711 | 0% | 0% | 100% | 100% | 0% | 90% | 10714117 | 769 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131783 | 131.783 | 131.783 | [12 empty] | 27676 | 27676 | 210.0119 | [6 empty] | 5824 | 5824 | 1.095 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (93%)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 5:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (90%)

## APR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28216 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79720026 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45959360 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10714117 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 133 | 99 | 79724324 | 4298 | 103.152 | 4.298 | 5.2 | 5.2 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 45960190 | 830 | 193.1131 | 0% | 0% | 100% | 100% | 0% | 96% | 10714857 | 740 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 135 | 111 | 79728096 | 3772 | 90.528 | 3.772 | 7.1 | 7.1 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 45961025 | 835 | 221.368 | 0% | 0% | 100% | 100% | 0% | 96% | 10715600 | 743 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 130 | 108 | 79732104 | 4008 | 96.192 | 4.008 | 8.9 | 8.9 | 2B | 0 | 0 | 1117 | 1185 | 0 | N/A | N/A | N/A | N/A | 45961884 | 859 | 214.3214 | 0% | 0% | 100% | 100% | 0% | 96% | 10716348 | 748 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 113 | 115 | 79736108 | 4004 | 96.096 | 4.004 | 9.5 | 9.5 | 2B | 0 | 0 | 1148 | 1185 | 0 | N/A | N/A | N/A | N/A | 45962761 | 877 | 219.031 | 0% | 0% | 100% | 100% | 0% | 96% | 10716469 | 121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 110 | 106 | 79739925 | 3817 | 91.608 | 3.817 | 9.5 | 9.5 | 2B | 0 | 0 | 1017 | 1185 | 0 | N/A | N/A | N/A | N/A | 45963652 | 891 | 233.4294 | 0% | 0% | 100% | 100% | 0% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 136 | 79745312 | 5387 | 129.288 | 5.387 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 45964644 | 992 | 184.147 | 0% | 0% | 100% | 100% | 0% | 0% | 10716469 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 145 | 79751156 | 5844 | 140.256 | 5.844 | 9 | 9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45965940 | 1296 | 221.7659 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 79757212 | 6056 | 145.344 | 6.056 | 8.4 | 8.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45967300 | 1360 | 224.5707 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 79763386 | 6174 | 148.176 | 6.174 | 7.9 | 7.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45968676 | 1376 | 222.8701 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 79769666 | 6280 | 150.72 | 6.28 | 7.4 | 7.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45970064 | 1388 | 221.0191 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 | 1.37
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 140 | 79775528 | 5862 | 140.688 | 5.862 | 7 | 7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45971380 | 1316 | 224.4968 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 79781508 | 5980 | 143.52 | 5.98 | 6.5 | 6.5 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45972724 | 1344 | 224.7492 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 79787596 | 6088 | 146.112 | 6.088 | 6 | 6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45974088 | 1364 | 224.0473 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 141 | 79793778 | 6182 | 148.368 | 6.182 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45975484 | 1396 | 225.8169 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 144 | 79799844 | 6066 | 145.584 | 6.066 | 5.2 | 5.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45976828 | 1344 | 221.5628 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 146 | 79805904 | 6060 | 145.44 | 6.06 | 4.9 | 4.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45978172 | 1344 | 221.7822 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 145 | 79811970 | 6066 | 145.584 | 6.066 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45979508 | 1336 | 220.244 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 143 | 79818102 | 6132 | 147.168 | 6.132 | 3.8 | 3.8 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45980888 | 1380 | 225.0489 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 140 | 79824051 | 5949 | 142.776 | 5.949 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45982220 | 1332 | 223.9032 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 141 | 79830076 | 6025 | 144.6 | 6.025 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45983556 | 1336 | 221.7427 | 0% | 100% | 100% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 140 | 79835608 | 5532 | 132.768 | 5.532 | 2.5 | 2.5 | 2B+1S | 0 | 1147 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45984652 | 1096 | 198.12 | 0% | 100% | 0% | 100% | 100% | 0% | 10716469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 131 | 79841062 | 5454 | 130.896 | 5.454 | 1.9 | 1.9 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45985708 | 1056 | 193.6194 | 0% | 100% | 0% | 100% | 100% | 0% | 10716469 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.9 | 135 | 111 | 79845942 | 4880 | 117.12 | 4.88 | 2.3 | 2.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45986652 | 944 | 193.4426 | 0% | 0% | 0% | 100% | 100% | 80% | 10716844 | 375 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A ONG | 11.5 | 139 | 141 | 79850747 | 4805 | 115.32 | 4.805 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1158 | N/A | N/A | N/A | N/A | 45987576 | 924 | 192.2997 | 0% | 0% | 0% | 100% | 100% | 80% | 10717858 | 1014 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130721 | 130.721 | 130.721 | [12 empty] | 28216 | 28216 | 215.849 | [6 empty] | 3741 | 3741 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (96%)
XCV2- CLOSED @ 3:21 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (80%)

## APR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27928 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79850747 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 45987576 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10717858 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.4 | 136 | 112 | 79855420 | 4673 | 112.152 | 4.673 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1137 | N/A | N/A | N/A | N/A | 45988464 | 888 | 190.0278 | 0% | 0% | 0% | 100% | 100% | 95% | 10718781 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 138 | 110 | 79860001 | 4581 | 109.944 | 4.581 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 45989324 | 860 | 187.7319 | 0% | 0% | 0% | 100% | 100% | 95% | 10719882 | 1101 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 126 | 106 | 79864484 | 4483 | 107.592 | 4.483 | 6.9 | 6.9 | 2B | 0 | 0 | 0 | 1185 | 1068 | N/A | N/A | N/A | N/A | 45990144 | 820 | 182.9132 | 0% | 0% | 0% | 100% | 100% | 95% | 10720892 | 1010 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 12.8 | 120 | 110 | 79868891 | 4407 | 105.768 | 4.407 | 7.8 | 7.8 | 2B | 0 | 0 | 0 | 1185 | 1067 | N/A | N/A | N/A | N/A | 45990940 | 796 | 180.6217 | 0% | 0% | 0% | 100% | 100% | 95% | 10721653 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 18 | A.ONG | 13.1 | 138 | 111 | 79873126 | 4235 | 101.64 | 4.235 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 1067 | N/A | N/A | N/A | N/A | 45991763 | 823 | 194.3329 | 0% | 0% | 0% | 100% | 100% | 95% | 10722332 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 119 | 79877824 | 4698 | 112.752 | 4.698 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45992756 | 993 | 211.3665 | 0% | 0% | 0% | 100% | 100% | 0% | 10722332 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 149 | 79883356 | 5532 | 132.768 | 5.532 | 8.8 | 8.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45993864 | 1108 | 200.2892 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 150 | 79889413 | 6057 | 145.368 | 6.057 | 8.3 | 8.3 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45995208 | 1344 | 221.892 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 151 | 79895832 | 6419 | 154.056 | 6.419 | 7.7 | 7.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45996604 | 1396 | 217.4794 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 137 | 79901986 | 6154 | 147.696 | 6.154 | 7.2 | 7.2 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45997956 | 1352 | 219.6945 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 149 | 79908288 | 6302 | 151.248 | 6.302 | 6.8 | 6.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 45999344 | 1388 | 220.2475 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 79914356 | 6068 | 145.632 | 6.068 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46000692 | 1348 | 222.149 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 79920527 | 6171 | 148.104 | 6.171 | 5.9 | 5.9 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46002060 | 1368 | 221.6821 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 79926694 | 6167 | 148.008 | 6.167 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46003436 | 1376 | 223.1231 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 144 | 79932747 | 6053 | 145.272 | 6.053 | 5.1 | 5.1 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46004788 | 1352 | 223.3603 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 146 | 79938765 | 6018 | 144.432 | 6.018 | 4.8 | 4.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46006128 | 1340 | 222.6653 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 146 | 79944874 | 6109 | 146.616 | 6.109 | 4.4 | 4.4 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46007476 | 1348 | 220.658 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 144 | 79950980 | 6106 | 146.544 | 6.106 | 3.9 | 3.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46008832 | 1356 | 222.0766 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 142 | 79956969 | 5989 | 143.736 | 5.989 | 3.5 | 3.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46010164 | 1332 | 222.4077 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 140 | 79962892 | 5923 | 142.152 | 5.923 | 3.2 | 3.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46011500 | 1336 | 225.5614 | 100% | 0% | 100% | 100% | 100% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 139 | 79968372 | 5480 | 131.52 | 5.48 | 2.5 | 2.5 | 2B+1S | 1148 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46012588 | 1088 | 198.5401 | 100% | 0% | 100% | 100% | 0% | 0% | 10722332 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 119 | 128 | 79973785 | 5413 | 129.912 | 5.413 | 2.1 | 2.1 | 2B+1S | 1129 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46013644 | 1056 | 195.0859 | 100% | 0% | 100% | 100% | 0% | 0% | 10722332 | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 132 | 115 | 79978737 | 4952 | 118.848 | 4.952 | 2.4 | 2.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46014580 | 936 | 189.0145 | 0% | 0% | 100% | 100% | 0% | 75% | 10722545 | 213 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 134 | 116 | 79983560 | 4823 | 115.752 | 4.823 | 3.2 | 3.2 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46015504 | 924 | 191.582 | 0% | 0% | 100% | 100% | 0% | 75% | 10723285 | 740 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132813 | 132.813 | 132.813 | [12 empty] | 27928 | 27928 | 210.2806 | [6 empty] | 5427 | 5427 | 1.06 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (95%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (75%)

## APR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27980 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 79983560 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46015504 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10723285 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 129 | 111 | 79988401 | 4841 | 116.184 | 4.841 | 4.4 | 4.4 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46016428 | 924 | 190.8697 | 0% | 0% | 100% | 100% | 0% | 95% | 10723907 | 622 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 110 | 79993216 | 4815 | 115.56 | 4.815 | 5.8 | 5.8 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46017364 | 936 | 194.3925 | 0% | 0% | 100% | 100% | 0% | 95% | 10724950 | 1043 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 119 | 122 | 79996397 | 3181 | 76.344 | 3.181 | 6.9 | 6.9 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46017788 | 424 | 133.2914 | 0% | 0% | 100% | 100% | 0% | 95% | 10725853 | 903 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 121 | 123 | 80001250 | 4853 | 116.472 | 4.853 | 7.3 | 7.3 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46018700 | 912 | 187.925 | 0% | 0% | 100% | 100% | 0% | 95% | 10726646 | 793 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 130 | 118 | 80006137 | 4887 | 117.288 | 4.887 | 9 | 9 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46019644 | 944 | 193.1655 | 0% | 0% | 100% | 100% | 0% | 95% | 10726939 | 293 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 125 | 120 | 80012088 | 5951 | 142.824 | 5.951 | 9 | 9 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46020556 | 912 | 153.2516 | 0% | 0% | 100% | 100% | 0% | 0% | 10726939 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 134 | 80017774 | 5686 | 136.464 | 5.686 | 8.5 | 8.5 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46021888 | 1332 | 234.2596 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 142 | 80023742 | 5968 | 143.232 | 5.968 | 8 | 8 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46023256 | 1368 | 229.2225 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 143 | 80030041 | 6299 | 151.176 | 6.299 | 7.5 | 7.5 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46024612 | 1356 | 215.2723 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 80036106 | 6065 | 145.56 | 6.065 | 7.1 | 7.1 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46025944 | 1332 | 219.6208 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 | 1.21
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 80042529 | 6423 | 154.152 | 6.423 | 6.7 | 6.7 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46027348 | 1404 | 218.5894 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 80048615 | 6086 | 146.064 | 6.086 | 6.2 | 6.2 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46028714 | 1366 | 224.4496 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 142 | 80054652 | 6037 | 144.888 | 6.037 | 5.7 | 5.7 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46030052 | 1338 | 221.6333 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 80060750 | 6098 | 146.352 | 6.098 | 5.3 | 5.3 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46031344 | 1292 | 211.8727 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 80066762 | 6012 | 144.288 | 6.012 | 5 | 5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46032792 | 1448 | 240.8516 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 143 | 80072937 | 6175 | 148.2 | 6.175 | 4.7 | 4.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46034140 | 1348 | 218.2996 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 80079067 | 6130 | 147.12 | 6.13 | 4.2 | 4.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46035452 | 1312 | 214.0294 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 80085103 | 6036 | 144.864 | 6.036 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46036796 | 1344 | 222.664 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 141 | 80091300 | 6197 | 148.728 | 6.197 | 3.4 | 3.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46038148 | 1352 | 218.1701 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 139 | 80097520 | 6220 | 149.28 | 6.22 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46039492 | 1344 | 216.0772 | 0% | 100% | 100% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 130 | 134 | 80103456 | 5936 | 142.464 | 5.936 | 2.4 | 2.4 | 2B+1S | 0 | 1148 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46040568 | 1076 | 181.2668 | 0% | 100% | 0% | 100% | 100% | 0% | 10726939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 121 | 80109200 | 5744 | 137.856 | 5.744 | 1.8 | 1.8 | 2B+1S | 0 | 1016 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46041612 | 1044 | 181.7549 | 0% | 100% | 0% | 100% | 100% | 0% | 10726939 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 129 | 114 | 80113978 | 4778 | 114.672 | 4.778 | 2.2 | 2.2 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46042548 | 936 | 195.8979 | 0% | 0% | 0% | 100% | 100% | 75% | 10727166 | 227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 135 | 110 | 80118059 | 4081 | 97.944 | 4.081 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46043484 | 936 | 229.3556 | 0% | 0% | 0% | 100% | 100% | 75% | 10728130 | 964 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134499 | 134.499 | 134.499 | [12 empty] | 27980 | 27980 | 208.0313 | [6 empty] | 4845 | 4845 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (90%)
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
MERALCO POWER FLUCTUATION @ 2:01AM
BP2 AND BP1 STOPPED @2:01
R N O G 2 @ 2:05 AM
RNOM @2:09AM
BP2 POWER RESUME @ 2:15AM
BP1 POWER RESUME @ 2:17 AM
MERALCO POWER FLUCTUATION @ 2:23AM
BP2 AND BP1 STOPPED @2:23 AM
R N O G 2 @ 2:27 AM
BP2 POWER RESUME @ 2:30AM
BP1 POWER RESUME @ 2:32 AM
R N O M @ 2:38AM
BP2 POWER RESUME @ 2:40AM
BP1 POWER RESUME @ 2:42 AM
NORMAL OPERATION @ 2:45 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (75%)

## APR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28508 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80118059 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46043484 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10728130 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 109 | 80122877 | 4818 | 115.632 | 4.818 | 5.1 | 5.1 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46044404 | 920 | 190.9506 | 0% | 0% | 0% | 100% | 100% | 95% | 10728902 | 772 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 109 | 80127507 | 4630 | 111.12 | 4.63 | 7 | 7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46045324 | 920 | 198.7041 | 0% | 0% | 0% | 100% | 100% | 95% | 10729775 | 873 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 127 | 108 | 80132128 | 4621 | 110.904 | 4.621 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46046264 | 940 | 203.4192 | 0% | 0% | 0% | 100% | 100% | 95% | 10730388 | 613 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 119 | 107 | 80136754 | 4626 | 111.024 | 4.626 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46047204 | 940 | 203.1993 | 0% | 0% | 0% | 100% | 100% | 95% | 10730501 | 113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 128 | 118 | 80141434 | 4680 | 112.32 | 4.68 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46048174 | 970 | 207.265 | 0% | 0% | 0% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 122 | 80146146 | 4712 | 113.088 | 4.712 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46049148 | 974 | 206.7063 | 0% | 0% | 0% | 100% | 100% | 0% | 10730501 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 139 | 80152372 | 6226 | 149.424 | 6.226 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46050412 | 1264 | 203.0196 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 80158396 | 6024 | 144.576 | 6.024 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46051800 | 1388 | 230.4117 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 80164566 | 6170 | 148.08 | 6.17 | 8 | 8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46053172 | 1372 | 222.3663 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 145 | 80170684 | 6118 | 146.832 | 6.118 | 7.5 | 7.5 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46054563 | 1391 | 227.3619 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 | 0.89
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 146 | 146 | 80176844 | 6160 | 147.84 | 6.16 | 7 | 7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46055932 | 1369 | 222.2403 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 80182852 | 6008 | 144.192 | 6.008 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46057292 | 1360 | 226.3648 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 146 | 80189004 | 6152 | 147.648 | 6.152 | 6.2 | 6.2 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46058644 | 1352 | 219.7659 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 140 | 80195020 | 6016 | 144.384 | 6.016 | 5.7 | 5.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46060020 | 1376 | 228.7234 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 80200986 | 5966 | 143.184 | 5.966 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46061356 | 1336 | 223.9356 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 80207079 | 6093 | 146.232 | 6.093 | 5.1 | 5.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46062692 | 1336 | 219.268 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 80213009 | 5930 | 142.32 | 5.93 | 4.8 | 4.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46064028 | 1336 | 225.2951 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 137 | 80219009 | 6000 | 144 | 6 | 4.3 | 4.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46065360 | 1332 | 222 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 80225028 | 6019 | 144.456 | 6.019 | 4.1 | 4.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46066692 | 1332 | 221.2992 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 80231228 | 6200 | 148.8 | 6.2 | 3.7 | 3.7 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46068028 | 1336 | 215.4839 | 100% | 0% | 100% | 100% | 100% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 | 123 | 80237328 | 6100 | 146.4 | 6.1 | 3.3 | 3.3 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46069084 | 1056 | 173.1148 | 100% | 0% | 100% | 100% | 0% | 0% | 10730501 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 121 | 80243428 | 6100 | 146.4 | 6.1 | 2.8 | 2.8 | 2B+1S | 1077 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46070132 | 1048 | 171.8033 | 100% | 0% | 100% | 100% | 0% | 0% | 10730501 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 127 | 110 | 80248428 | 5000 | 120 | 5 | 3.2 | 3.2 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46071068 | 936 | 187.2 | 0% | 0% | 100% | 100% | 0% | 75% | 10730711 | 210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 139 | 112 | 80253528 | 5100 | 122.4 | 5.1 | 4.1 | 4.1 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46071992 | 924 | 181.1765 | 0% | 0% | 100% | 100% | 0% | 75% | 10731734 | 1023 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135469 | 135.469 | 135.469 | [12 empty] | 28508 | 28508 | 210.4393 | [6 empty] | 3604 | 3604 | 1.0067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (95%)
XCV1- CLOSED @ 3:25 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 - OPENED @ 10:01 PM (75%)

## APR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-04-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80253528 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46071992 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10731734 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 124 | 97 | 80258385 | 4857 | 116.568 | 4.857 | 5.3 | 5.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46072916 | 924 | 190.2409 | 0% | 0% | 100% | 100% | 0% | 95% | 10732469 | 735 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 106 | 80262926 | 4541 | 108.984 | 4.541 | 7.5 | 7.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46073828 | 912 | 200.8368 | 0% | 0% | 100% | 100% | 0% | 95% | 10733303 | 834 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 104 | 80267548 | 4622 | 110.928 | 4.622 | 8.8 | 8.8 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46074740 | 912 | 197.3172 | 0% | 0% | 100% | 100% | 0% | 95% | 10734065 | 762 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 108 | 105 | 80272232 | 4684 | 112.416 | 4.684 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46075656 | 916 | 195.5594 | 0% | 0% | 100% | 100% | 0% | 95% | 10734253 | 188 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 116 | 105 | 80276882 | 4650 | 111.6 | 4.65 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46076570 | 914 | 196.5591 | 0% | 0% | 100% | 100% | 0% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 121 | 80282792 | 5910 | 141.84 | 5.91 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46077572 | 1002 | 169.5431 | 0% | 0% | 100% | 100% | 0% | 0% | 10734253 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 80289038 | 6246 | 149.904 | 6.246 | 9.1 | 9.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46078860 | 1288 | 206.212 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 80295216 | 6178 | 148.272 | 6.178 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46080212 | 1352 | 218.841 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 146 | 80301448 | 6232 | 149.568 | 6.232 | 8 | 8 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46081604 | 1392 | 223.3633 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 102 | 80307597 | 6149 | 147.576 | 6.149 | 7.4 | 7.4 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46082992 | 1388 | 225.7278 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 120 | 80313816 | 6219 | 149.256 | 6.219 | 6.9 | 6.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46084360 | 1368 | 219.9711 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 117 | 80319887 | 6071 | 145.704 | 6.071 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46085752 | 1392 | 229.2868 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 123 | 80326015 | 6128 | 147.072 | 6.128 | 5.8 | 5.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46087116 | 1364 | 222.5849 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 131 | 80332063 | 6048 | 145.152 | 6.048 | 5.5 | 5.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46088424 | 1308 | 216.2698 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 104 | 80338100 | 6037 | 144.888 | 6.037 | 5 | 5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46089741 | 1317 | 218.1547 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 110 | 80344103 | 6003 | 144.072 | 6.003 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46091132 | 1391 | 231.7175 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 80350190 | 6087 | 146.088 | 6.087 | 4 | 4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46092444 | 1312 | 215.5413 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 109 | 80356380 | 6190 | 148.56 | 6.19 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46093824 | 1380 | 222.9402 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 101 | 80362480 | 6100 | 146.4 | 6.1 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46095172 | 1348 | 220.9836 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 130 | 80368580 | 6100 | 146.4 | 6.1 | 3 | 3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46096524 | 1352 | 221.6393 | 0% | 100% | 100% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 123 | 127 | 80374690 | 6110 | 146.64 | 6.11 | 2.4 | 2.4 | 2B+1S | 0 | 1148 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46097664 | 1140 | 186.5794 | 0% | 100% | 0% | 100% | 100% | 0% | 10734253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 121 | 80379950 | 5260 | 126.24 | 5.26 | 2 | 2 | 2B+1S | 0 | 1149 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46098816 | 1152 | 219.0114 | 0% | 100% | 0% | 100% | 100% | 0% | 10734253 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 128 | 107 | 80384650 | 4700 | 112.8 | 4.7 | 2.3 | 2.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46099756 | 940 | 200 | 0% | 0% | 0% | 100% | 100% | 75% | 10734702 | 449 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 133 | 109 | 80389191 | 4541 | 108.984 | 4.541 | 3.1 | 3.1 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46100688 | 932 | 205.2411 | 0% | 0% | 0% | 100% | 100% | 75% | 10735472 | 770 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135663 | 135.663 | 135.663 | [12 empty] | 28696 | 28696 | 211.5241 | [6 empty] | 3738 | 3738 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (95%)
XCV2- CLOSED @ 3:25 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2 - STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (APRIL 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 66PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 - OPENED @ 10:01 PM (75%)