## MAY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28484 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80389191 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46100688 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10735472 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 105 | 80393885 | 4694 | 112.656 | 4.694 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46101636 | 948 | 201.9599 | 0% | 0% | 0% | 100% | 100% | 95% | 10736339 | 867 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 107 | 80398685 | 4800 | 115.2 | 4.8 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46102540 | 904 | 188.3333 | 0% | 0% | 0% | 100% | 100% | 95% | 10737167 | 828 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 109 | 80403385 | 4700 | 112.8 | 4.7 | 6.9 | 6.9 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46103440 | 900 | 191.4894 | 0% | 0% | 0% | 100% | 100% | 95% | 10738127 | 960 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 125 | 105 | 80408165 | 4780 | 114.72 | 4.78 | 8.3 | 8.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46104362 | 922 | 192.887 | 0% | 0% | 0% | 100% | 100% | 95% | 10738686 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 134 | 106 | 80412985 | 4820 | 115.68 | 4.82 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46105300 | 938 | 194.6058 | 0% | 0% | 0% | 100% | 100% | 95% | 10739010 | 324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 121 | 80418885 | 5900 | 141.6 | 5.9 | 9 | 9 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46106260 | 960 | 162.7119 | 0% | 0% | 0% | 100% | 100% | 0% | 10739010 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 137 | 80424985 | 6100 | 146.4 | 6.1 | 9 | 9 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46107484 | 1224 | 200.6557 | 0% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 141 | 80430985 | 6000 | 144 | 6 | 8.7 | 8.7 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46108804 | 1320 | 220 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 135 | 80436995 | 6010 | 144.24 | 6.01 | 8.4 | 8.4 | 3B+1S | 1030 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46110180 | 1376 | 228.9517 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 140 | 80443092 | 6097 | 146.328 | 6.097 | 7.8 | 7.8 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46111532 | 1352 | 221.7484 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 | 1.23
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 80449292 | 6200 | 148.8 | 6.2 | 7.2 | 7.2 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46112904 | 1372 | 221.2903 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 80455352 | 6060 | 145.44 | 6.06 | 6.6 | 6.6 | 3B+1S | 1099 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46114284 | 1380 | 227.7228 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 80461542 | 6190 | 148.56 | 6.19 | 5.9 | 5.9 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46115676 | 1392 | 224.8788 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 80467662 | 6120 | 146.88 | 6.12 | 5.1 | 5.1 | 3B+1S | 1098 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46117084 | 1408 | 230.0654 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 132 | 80473852 | 6190 | 148.56 | 6.19 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46118420 | 1336 | 215.832 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 144 | 80479895 | 6043 | 145.032 | 6.043 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46119772 | 1352 | 223.7299 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 132 | 80485995 | 6100 | 146.4 | 6.1 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46121128 | 1356 | 222.2951 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 148 | 80492141 | 6146 | 147.504 | 6.146 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46122460 | 1332 | 216.7263 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 144 | 80498341 | 6200 | 148.8 | 6.2 | 3.3 | 3.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46123796 | 1336 | 215.4839 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 96 | 80504373 | 6032 | 144.768 | 6.032 | 3.2 | 3.2 | 3B+1S | 955 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46125120 | 1324 | 219.496 | 100% | 0% | 100% | 100% | 100% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 128 | 80509973 | 5600 | 134.4 | 5.6 | 2.7 | 2.7 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46126244 | 1124 | 200.7143 | 100% | 0% | 100% | 100% | 0% | 0% | 10739010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 111 | 125 | 80515873 | 5900 | 141.6 | 5.9 | 1.9 | 1.9 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46127340 | 1096 | 185.7627 | 100% | 0% | 100% | 100% | 0% | 0% | 10739010 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 137 | 112 | 80520473 | 4600 | 110.4 | 4.6 | 2.5 | 2.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46128268 | 928 | 201.7391 | 0% | 0% | 100% | 100% | 0% | 60% | 10739576 | 566 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 134 | 108 | 80524473 | 4000 | 96 | 4 | 3.4 | 3.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46129172 | 904 | 226 | 0% | 0% | 100% | 100% | 0% | 60% | 10740621 | 1045 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135282 | 135.282 | 135.282 | [12 empty] | 28484 | 28484 | 210.5528 | [6 empty] | 5149 | 5149 | 1.1667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (95%)
XCV1- CLOSED @ 5:0 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 7:23 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (60%)

## MAY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80524473 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46129172 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10740621 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 107 | 80529313 | 4840 | 116.16 | 4.84 | 4.3 | 4.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46130116 | 944 | 195.0413 | 0% | 0% | 100% | 100% | 0% | 70% | 10741433 | 812 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 103 | 80534213 | 4900 | 117.6 | 4.9 | 5.3 | 5.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46131020 | 904 | 184.4898 | 0% | 0% | 100% | 100% | 0% | 70% | 10742156 | 723 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 102 | 80539014 | 4801 | 115.224 | 4.801 | 6.5 | 6.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46131948 | 928 | 193.2931 | 0% | 0% | 100% | 100% | 0% | 70% | 10742995 | 839 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 121 | 104 | 80543914 | 4900 | 117.6 | 4.9 | 7.2 | 7.2 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46132872 | 924 | 188.5714 | 0% | 0% | 100% | 100% | 0% | 70% | 10743426 | 431 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 137 | 110 | 80549736 | 5822 | 139.728 | 5.822 | 7.5 | 7.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46133796 | 924 | 158.7083 | 0% | 0% | 100% | 100% | 0% | 70% | 10743471 | 45 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 129 | 80555736 | 6000 | 144 | 6 | 9 | 9 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46134756 | 960 | 160 | 0% | 0% | 100% | 100% | 0% | 0% | 10743471 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 80561836 | 6100 | 146.4 | 6.1 | 8.5 | 8.5 | 3B+1S | 0 | 1068 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46136076 | 1320 | 216.3934 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 80567846 | 6010 | 144.24 | 6.01 | 8 | 8 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46137444 | 1368 | 227.6206 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 143 | 80573756 | 5910 | 141.84 | 5.91 | 7.4 | 7.4 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46138820 | 1376 | 232.8257 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 108 | 80579866 | 6110 | 146.64 | 6.11 | 6.8 | 6.8 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46140220 | 1400 | 229.1326 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 | 1.27
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 107 | 80585876 | 6010 | 144.24 | 6.01 | 6.1 | 6.1 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46141632 | 1412 | 234.9418 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 80591796 | 5920 | 142.08 | 5.92 | 5.5 | 5.5 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46143009 | 1377 | 232.6014 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 103 | 80597916 | 6120 | 146.88 | 6.12 | 4.9 | 4.9 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46144372 | 1363 | 222.7124 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 102 | 80604049 | 6133 | 147.192 | 6.133 | 4.3 | 4.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46145758 | 1386 | 225.9905 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 139 | 80610192 | 6143 | 147.432 | 6.143 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46147074 | 1316 | 214.2276 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 142 | 80616237 | 6045 | 145.08 | 6.045 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46148436 | 1362 | 225.3102 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 109 | 80622392 | 6155 | 147.72 | 6.155 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46149768 | 1332 | 216.4094 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 100 | 80628559 | 6167 | 148.008 | 6.167 | 2.9 | 2.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46151140 | 1372 | 222.4745 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 98 | 80634735 | 6176 | 148.224 | 6.176 | 2.6 | 2.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46152468 | 1328 | 215.0259 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 90 | 80640611 | 5876 | 141.024 | 5.876 | 2.2 | 2.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46153808 | 1340 | 228.0463 | 0% | 100% | 100% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 133 | 80646387 | 5776 | 138.624 | 5.776 | 1.5 | 1.5 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46154956 | 1148 | 198.7535 | 0% | 100% | 0% | 100% | 100% | 0% | 10743471 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 118 | 80652063 | 5676 | 136.224 | 5.676 | 1.3 | 1.3 | 2B+1S | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46155924 | 968 | 170.5426 | 0% | 0% | 0% | 100% | 100% | 0% | 10743471 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 135 | 114 | 80656439 | 4376 | 105.024 | 4.376 | 1.8 | 1.8 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46156856 | 932 | 212.9799 | 0% | 0% | 0% | 100% | 100% | 60% | 10744005 | 534 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 136 | 107 | 80660115 | 3676 | 88.224 | 3.676 | 2.6 | 2.6 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46157772 | 916 | 249.1839 | 0% | 0% | 0% | 100% | 100% | 60% | 10744813 | 808 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135642 | 135.642 | 135.642 | [12 empty] | 28600 | 28600 | 210.8491 | [6 empty] | 4192 | 4192 | 1.2183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 5:30 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:14 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (60%)

## MAY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28788 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80660115 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46157772 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10744813 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 110 | 80664926 | 4811 | 115.464 | 4.811 | 3.6 | 3.6 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46158716 | 944 | 196.217 | 0% | 0% | 0% | 100% | 100% | 90% | 10745695 | 882 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 109 | 80669856 | 4930 | 118.32 | 4.93 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46159628 | 912 | 184.9899 | 0% | 0% | 0% | 100% | 100% | 90% | 10746666 | 971 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 107 | 80674667 | 4811 | 115.464 | 4.811 | 5.7 | 5.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46160548 | 920 | 191.2284 | 0% | 0% | 0% | 100% | 100% | 90% | 10747653 | 987 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 122 | 86 | 80679578 | 4911 | 117.864 | 4.911 | 7.7 | 7.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46161524 | 976 | 198.7375 | 0% | 0% | 0% | 100% | 100% | 90% | 10747666 | 13 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 132 | 89 | 80685389 | 5811 | 139.464 | 5.811 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46162476 | 952 | 163.8272 | 0% | 0% | 0% | 100% | 1000% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 120 | 80691430 | 6041 | 144.984 | 6.041 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46163448 | 972 | 160.9005 | 0% | 0% | 0% | 100% | 100% | 0% | 10747666 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 115 | 80697578 | 6148 | 147.552 | 6.148 | 9.2 | 9.2 | 3B+1S | 1099 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46164803 | 1355 | 220.3969 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 135 | 80703766 | 6188 | 148.512 | 6.188 | 8.7 | 8.7 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46166194 | 1391 | 224.7899 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 141 | 80709974 | 6208 | 148.992 | 6.208 | 8.1 | 8.1 | 3B+1S | 1077 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46167544 | 1350 | 217.4613 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 101 | 80716162 | 6188 | 148.512 | 6.188 | 7.5 | 7.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46168920 | 1376 | 222.3659 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 | 1.21
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 80722210 | 6048 | 145.152 | 6.048 | 6.9 | 6.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46170248 | 1328 | 219.5767 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 105 | 80728228 | 6018 | 144.432 | 6.018 | 6.3 | 6.3 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46171676 | 1428 | 237.2881 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 139 | 114 | 80734376 | 6148 | 147.552 | 6.148 | 5.6 | 5.6 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46173044 | 1368 | 222.5114 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 86 | 80740612 | 6236 | 149.664 | 6.236 | 4.8 | 4.8 | 3B+1S | 1078 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46174492 | 1448 | 232.2001 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 109 | 80746748 | 6136 | 147.264 | 6.136 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1189 | N/A | N/A | N/A | N/A | 46175844 | 1352 | 220.339 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 104 | 80752684 | 5936 | 142.464 | 5.936 | 4 | 4 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46177140 | 1296 | 218.3288 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 89 | 80758720 | 6036 | 144.864 | 6.036 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46178500 | 1360 | 225.3148 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 108 | 80764766 | 6046 | 145.104 | 6.046 | 3.3 | 3.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46179860 | 1360 | 224.9421 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 119 | 80770711 | 5945 | 142.68 | 5.945 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46181220 | 1360 | 228.7637 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 100 | 80776552 | 5841 | 140.184 | 5.841 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46182524 | 1304 | 223.2494 | 100% | 0% | 100% | 100% | 100% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 80782283 | 5731 | 137.544 | 5.731 | 1.9 | 1.9 | 2B+1S | 1088 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46183644 | 1120 | 195.4284 | 100% | 0% | 100% | 100% | 0% | 0% | 10747666 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 122 | 80787794 | 5511 | 132.264 | 5.511 | 1.3 | 1.3 | 2B |  | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46184692 | 1048 | 190.1651 | 0% | 0% | 100% | 100% | 0% | 0% | 10747666 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 134 | 78 | 80792205 | 4411 | 105.864 | 4.411 | 1.8 | 1.8 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46185648 | 956 | 216.7309 | 0% | 0% | 100% | 100% | 0% | 60% | 10748215 | 549 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 142 | 112 | 80795816 | 3611 | 86.664 | 3.611 | 2.6 | 2.6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46186560 | 912 | 252.5616 | 0% | 0% | 100% | 100% | 0% | 60% | 10748942 | 727 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135701 | 135.701 | 135.701 | [12 empty] | 28788 | 28788 | 212.1429 | [6 empty] | 4129 | 4129 | 1.2217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (90%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 9:37 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (60%)

## MAY 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 80795816 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46186560 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10748942 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 100 | 80800679 | 4863 | 116.712 | 4.863 | 3.7 | 3.7 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46187508 | 948 | 194.9414 | 0% | 0% | 100% | 100% | 0% | 70% | 10749243 | 301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 104 | 80805665 | 4986 | 119.664 | 4.986 | 4.8 | 4.8 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46188480 | 972 | 194.9458 | 0% | 0% | 100% | 100% | 0% | 70% | 10749507 | 264 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 107 | 80810541 | 4876 | 117.024 | 4.876 | 5.6 | 5.6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46189404 | 924 | 189.4996 | 0% | 0% | 100% | 100% | 0% | 70% | 10749707 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 120 | 97 | 80815522 | 4981 | 119.544 | 4.981 | 6.4 | 6.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46190348 | 944 | 189.5202 | 0% | 0% | 100% | 100% | 0% | 70% | 10749807 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 120 | 89 | 80821303 | 5781 | 138.744 | 5.781 | 7.9 | 7.9 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46191324 | 976 | 168.8289 | 0% | 0% | 100% | 100% | 0% | 70% | 10749817 | 10 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 121 | 80827284 | 5981 | 143.544 | 5.981 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46192244 | 920 | 153.8204 | 0% | 0% | 100% | 100% | 0% | 0% | 10749817 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 139 | 80833465 | 6181 | 148.344 | 6.181 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46193588 | 1344 | 217.4405 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 135 | 80839547 | 6082 | 145.968 | 6.082 | 8.6 | 8.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46194952 | 1364 | 224.2683 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 101 | 80845727 | 6180 | 148.32 | 6.18 | 8.1 | 8.1 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46196308 | 1356 | 219.4175 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 85 | 80851929 | 6202 | 148.848 | 6.202 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46197668 | 1360 | 219.2841 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 98 | 80858035 | 6106 | 146.544 | 6.106 | 7.1 | 7.1 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46199052 | 1384 | 226.6623 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 135 | 80864041 | 6006 | 144.144 | 6.006 | 6.6 | 6.6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46200423 | 1371 | 228.2717 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 101 | 80870037 | 5996 | 143.904 | 5.996 | 5.9 | 5.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46201788 | 1365 | 227.6518 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 123 | 80876049 | 6012 | 144.288 | 6.012 | 5.5 | 5.5 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46203156 | 1368 | 227.5449 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 130 | 80882046 | 5997 | 143.928 | 5.997 | 5 | 5 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46204540 | 1384 | 230.7821 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 120 | 80888058 | 6012 | 144.288 | 6.012 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46205928 | 1388 | 230.8716 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 89 | 80894083 | 6025 | 144.6 | 6.025 | 4.3 | 4.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46207204 | 1276 | 211.7842 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 0 | 80900038 | 5955 | 142.92 | 5.955 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46208528 | 1324 | 222.3342 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 87 | 80905893 | 5855 | 140.52 | 5.855 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46209844 | 1316 | 224.7652 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 7 | 80911644 | 5751 | 138.024 | 5.751 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46211208 | 1364 | 237.1761 | 0% | 100% | 100% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 90 | 80917292 | 5648 | 135.552 | 5.648 | 2.5 | 2.5 | 2B+1S | 0 | 1047 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46212288 | 1080 | 191.2181 | 0% | 100% | 0% | 100% | 100% | 0% | 10749817 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 114 | 87 | 80922780 | 5488 | 131.712 | 5.488 | 1.9 | 1.9 | 2B+1S | 0 | 1048 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 46213396 | 1108 | 201.895 | 0% | 100% | 0% | 100% | 100% | 0% | 10749817 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 131 | 114 | 80927268 | 4488 | 107.712 | 4.488 | 2.2 | 2.2 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46214324 | 928 | 206.7736 | 0% | 0% | 0% | 100% | 100% | 85% | 10750275 | 458 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 139 | 113 | 80931474 | 4206 | 100.944 | 4.206 | 2.9 | 2.9 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46215260 | 936 | 222.5392 | 0% | 0% | 0% | 100% | 100% | 85% | 10750981 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135658 | 135.658 | 135.658 | [12 empty] | 28700 | 28700 | 211.5614 | [6 empty] | 2039 | 2039 | 1.23 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 5:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (85%)

## MAY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28636 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O | [6 empty] | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46215260 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10750981 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 112 | 4804 | 4804 | 115.296 | 4.804 | 3.9 | 3.9 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46216196 | 936 | 194.8376 | 0% | 0% | 0% | 100% | 100% | 90% | 10751552 | 571 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 111 | 9454 | 4650 | 111.6 | 4.65 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46217124 | 928 | 199.5699 | 0% | 0% | 0% | 100% | 100% | 90% | 10752219 | 667 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 113 | 14130 | 4676 | 112.224 | 4.676 | 6.1 | 6.1 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46218052 | 928 | 198.4602 | 0% | 0% | 0% | 100% | 100% | 90% | 10752960 | 741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 123 | 109 | 18797 | 4667 | 112.008 | 4.667 | 7.6 | 7.6 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46218972 | 920 | 197.1288 | 0% | 0% | 0% | 100% | 100% | 90% | 10753462 | 502 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 124 | 110 | 23964 | 5167 | 124.008 | 5.167 | 8 | 8 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46219948 | 976 | 188.891 | 0% | 0% | 0% | 100% | 100% | 90% | 10753580 | 118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 124 | 29971 | 6007 | 144.168 | 6.007 | 8 | 8 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46220844 | 896 | 149.1593 | 0% | 0% | 0% | 100% | 100% | 0% | 10753580 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 36098 | 6127 | 147.048 | 6.127 | 7.6 | 7.6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46222208 | 1364 | 222.6212 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 147 | 42375 | 6277 | 150.648 | 6.277 | 7.2 | 7.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46223552 | 1344 | 214.115 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 140 | 48562 | 6187 | 148.488 | 6.187 | 6.8 | 6.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46224914 | 1362 | 220.139 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 132 | 54629 | 6067 | 145.608 | 6.067 | 6.3 | 6.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46226294 | 1380 | 227.46 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 | 1.21
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 136 | 60598 | 5969 | 143.256 | 5.969 | 5.8 | 5.8 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46227652 | 1358 | 227.5088 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 137 | 66667 | 6069 | 145.656 | 6.069 | 5.1 | 5.1 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46229016 | 1364 | 224.7487 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 138 | 72836 | 6169 | 148.056 | 6.169 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46230372 | 1356 | 219.8087 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 96 | 78891 | 6055 | 145.32 | 6.055 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46231756 | 1384 | 228.5714 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 85122 | 6231 | 149.544 | 6.231 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46233112 | 1356 | 217.6216 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 91156 | 6034 | 144.816 | 6.034 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46234420 | 1308 | 216.7716 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 120 | 97199 | 6043 | 145.032 | 6.043 | 3.3 | 3.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46235796 | 1376 | 227.7015 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 116 | 103172 | 5973 | 143.352 | 5.973 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46237160 | 1364 | 228.361 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 136 | 109242 | 6070 | 145.68 | 6.07 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46238484 | 1324 | 218.1219 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 88 | 115112 | 5870 | 140.88 | 5.87 | 2.4 | 2.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46239828 | 1344 | 228.9608 | 0% | 100% | 100% | 100% | 100% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 129 | 120888 | 5776 | 138.624 | 5.776 | 1.8 | 1.8 | 2B+1S | 0 | 1047 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46240972 | 1144 | 198.0609 | 0% | 100% | 100% | 100% | 0% | 0% | 10753580 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 128 | 126464 | 5576 | 133.824 | 5.576 | 1.4 | 1.4 | 2B+1S | 0 | 1047 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46242036 | 1064 | 190.8178 | 0% | 100% | 100% | 100% | 0% | 0% | 10753580 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 136 | 115 | 131047 | 4583 | 109.992 | 4.583 | 3 | 3 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46242972 | 936 | 204.233 | 0% | 0% | 100% | 100% | 0% | 75% | 10754380 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 138 | 112 | 135530 | 4483 | 107.592 | 4.483 | 4.9 | 4.9 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46243896 | 924 | 206.112 | 0% | 0% | 100% | 100% | 0% | 75% | 10755302 | 922 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135530 | 135.53 | 135.53 | [12 empty] | 28636 | 28636 | 211.289 | [6 empty] | 4321 | 4321 | 1.1217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (90%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (8.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (75%)

## MAY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28608 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 135530 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46243896 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10755302 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 134 | 110 | 140230 | 4700 | 112.8 | 4.7 | 6.6 | 6.6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46244812 | 916 | 194.8936 | 0% | 0% | 100% | 100% | 0% | 80% | 10756032 | 730 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 112 | 145070 | 4840 | 116.16 | 4.84 | 8.3 | 8.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46245732 | 920 | 197.13 | 0% | 0% | 100% | 100% | 0% | 80% | 10756891 | 859 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 124 | 111 | 149810 | 4740 | 113.76 | 4.74 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46246652 | 920 | 197.13 | 0% | 0% | 100% | 100% | 0% | 80% | 10757692 | 801 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 126 | 110 | 155690 | 5880 | 141.12 | 5.88 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46247604 | 952 | 161.9048 | 0% | 0% | 100% | 100% | 0% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ANDRO MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 124 | 116 | 161770 | 6080 | 145.92 | 6.08 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46248536 | 932 | 153.2895 | 0% | 0% | 100% | 100% | 0% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 122 | 167782 | 6012 | 144.288 | 6.012 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46249468 | 932 | 155.0233 | 0% | 0% | 100% | 100% | 0% | 0% | 10757692 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 126 | 173843 | 6061 | 145.464 | 6.061 | 9 | 9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46250768 | 1300 | 214.4861 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 179955 | 6112 | 146.688 | 6.112 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46252140 | 1372 | 224.4764 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 106 | 185915 | 5960 | 143.04 | 5.96 | 7.7 | 7.7 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46253508 | 1368 | 229.5302 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 141 | 191946 | 6031 | 144.744 | 6.031 | 7 | 7 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46254909 | 1401 | 232.2998 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 | 1.23
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 135 | 198012 | 6066 | 145.584 | 6.066 | 6.5 | 6.5 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46256284 | 1375 | 226.6733 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 121 | 203979 | 5967 | 143.208 | 5.967 | 6.1 | 6.1 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46257644 | 1360 | 227.9202 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 210082 | 6103 | 146.472 | 6.103 | 5.6 | 5.6 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46259000 | 1356 | 222.1858 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 216068 | 5986 | 143.664 | 5.986 | 5.2 | 5.2 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46260352 | 1352 | 225.8603 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 222077 | 6009 | 144.216 | 6.009 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46261745 | 1393 | 231.8189 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 228069 | 5992 | 143.808 | 5.992 | 4.5 | 4.5 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46263044 | 1299 | 216.7891 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 234078 | 6009 | 144.216 | 6.009 | 4.2 | 4.2 | 3B+1S | 1056 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46264388 | 1344 | 223.6645 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 128 | 240036 | 5958 | 142.992 | 5.958 | 3.7 | 3.7 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46265756 | 1368 | 229.6073 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 143 | 245864 | 5828 | 139.872 | 5.828 | 3.4 | 3.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46267112 | 1356 | 232.6699 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 132 | 251562 | 5698 | 136.752 | 5.698 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46268456 | 1344 | 235.8722 | 100% | 0% | 100% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 121 | 128 | 257115 | 5553 | 133.272 | 5.553 | 2.7 | 2.7 | 2B+1S | 1078 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46269548 | 1092 | 196.6505 | 100% | 0% | 0% | 100% | 100% | 0% | 10757692 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 130 | 262625 | 5510 | 132.24 | 5.51 | 2.4 | 2.4 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46270612 | 1064 | 193.1034 | 100% | 0% | 0% | 100% | 100% | 0% | 10757692 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 139 | 120 | 267135 | 4510 | 108.24 | 4.51 | 3.3 | 3.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46271564 | 952 | 211.0865 | 0% | 0% | 0% | 100% | 100% | 70% | 10758201 | 509 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 148 | 113 | 271225 | 4090 | 98.16 | 4.09 | 4.2 | 4.2 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46272504 | 940 | 229.8289 | 0% | 0% | 0% | 100% | 100% | 70% | 10758917 | 716 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135695 | 135.695 | 135.695 | [12 empty] | 28608 | 28608 | 210.8257 | [6 empty] | 3615 | 3615 | 1.1133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (80%)
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28288 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 271225 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46272504 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10758917 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 129 | 113 | 275952 | 4727 | 113.448 | 4.727 | 6.6 | 6.6 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46273436 | 932 | 197.1652 | 0% | 0% | 0% | 100% | 100% | 75% | 10759618 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 112 | 280759 | 4807 | 115.368 | 4.807 | 7.4 | 7.4 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46274372 | 936 | 194.716 | 0% | 0% | 0% | 100% | 100% | 75% | 10760613 | 995 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 124 | 110 | 285668 | 4909 | 117.816 | 4.909 | 8.7 | 8.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46275296 | 924 | 188.2257 | 0% | 0% | 0% | 100% | 100% | 75% | 10761309 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 126 | 111 | 290589 | 4921 | 118.104 | 4.921 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46276256 | 960 | 195.0823 | 0% | 0% | 0% | 100% | 100% | 75% | 10761709 | 400 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 123 | 116 | 296316 | 5727 | 137.448 | 5.727 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46277204 | 948 | 165.5317 | 0% | 0% | 0% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 123 | 302443 | 6127 | 147.048 | 6.127 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46278104 | 900 | 146.8908 | 0% | 0% | 0% | 100% | 100% | 0% | 10761709 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 148 | 308870 | 6427 | 154.248 | 6.427 | 9.3 | 9.3 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46279456 | 1352 | 210.3625 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 140 | 315207 | 6337 | 152.088 | 6.337 | 8.9 | 8.9 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46280816 | 1360 | 214.6126 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 145 | 321344 | 6137 | 147.288 | 6.137 | 8.3 | 8.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46282214 | 1398 | 227.7986 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 141 | 327471 | 6127 | 147.048 | 6.127 | 7.8 | 7.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46283572 | 1358 | 221.6419 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 | 1.21
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 144 | 333758 | 6287 | 150.888 | 6.287 | 7.3 | 7.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46284944 | 1372 | 218.2281 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 143 | 340115 | 6357 | 152.568 | 6.357 | 6.8 | 6.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46286312 | 1368 | 215.1958 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 346092 | 5977 | 143.448 | 5.977 | 6.5 | 6.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46287651 | 1339 | 224.0254 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 145 | 352104 | 6012 | 144.288 | 6.012 | 6.1 | 6.1 | 3B+1S | 0 | 1078 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46289060 | 1409 | 234.3646 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 358107 | 6003 | 144.072 | 6.003 | 5.7 | 5.7 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46290404 | 1344 | 223.8881 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 364093 | 5986 | 143.664 | 5.986 | 5.3 | 5.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46291740 | 1336 | 223.1874 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 125 | 370069 | 5976 | 143.424 | 5.976 | 5 | 5 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46293072 | 1332 | 222.8916 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 123 | 375941 | 5872 | 140.928 | 5.872 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46294352 | 1280 | 217.9837 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 120 | 381612 | 5671 | 136.104 | 5.671 | 4.4 | 4.4 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46295692 | 1340 | 236.2899 | 0% | 100% | 100% | 100% | 100% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 125 | 387187 | 5575 | 133.8 | 5.575 | 3.5 | 3.5 | 2B+1S | 0 | 1026 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46296809 | 1117 | 200.3587 | 0% | 100% | 100% | 100% | 0% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 120 | 124 | 392563 | 5376 | 129.024 | 5.376 | 2.8 | 2.8 | 2B+1S | 0 | 1067 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46297884 | 1075 | 199.9628 | 0% | 100% | 100% | 100% | 0% | 0% | 10761709 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 118 | 123 | 397737 | 5174 | 124.176 | 5.174 | 2.3 | 2.3 | 2B | 0 | 1067 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46298940 | 1056 | 204.0974 | 0% | 100% | 100% | 100% | 0% | 0% | 10761709 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 132 | 114 | 402511 | 4774 | 114.576 | 4.774 | 3.2 | 3.2 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46299872 | 932 | 195.2241 | 0% | 0% | 100% | 100% | 0% | 70% | 10762192 | 483 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 137 | 112 | 406654 | 4143 | 99.432 | 4.143 | 4.3 | 4.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46300792 | 920 | 222.0613 | 0% | 0% | 100% | 100% | 0% | 70% | 10762706 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135429 | 135.429 | 135.429 | [12 empty] | 28288 | 28288 | 208.877 | [6 empty] | 3789 | 3789 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
POWER FLUCTUATION @ 5:30PM
3 BOOSTER STOPPED @ 5:30 PM
GENSET RESUMED @ 5:30 PM
MERALCO RESUMED @ 5:33 PM
BP1 - STARTED @5:35 PM
BP3 - STARTED @5:37 PM
SP2- STARTED @ 5:39 PM
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (70%)

## MAY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28100 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 406654 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46300792 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10762706 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 110 | 411356 | 4702 | 112.848 | 4.702 | 6 | 6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46301700 | 908 | 193.1093 | 0% | 0% | 100% | 100% | 0% | 75% | 10763619 | 913 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 108 | 415964 | 4608 | 110.592 | 4.608 | 7.2 | 7.2 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46302612 | 912 | 197.9167 | 0% | 0% | 100% | 100% | 0% | 75% | 10764654 | 1035 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 106 | 420773 | 4809 | 115.416 | 4.809 | 8.7 | 8.7 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46303524 | 912 | 189.6444 | 0% | 0% | 100% | 100% | 0% | 75% | 10765693 | 1039 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 126 | 111 | 425691 | 4918 | 118.032 | 4.918 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46304472 | 948 | 192.7613 | 0% | 0% | 100% | 100% | 0% | 75% | 10766148 | 455 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 115 | 112 | 431309 | 5618 | 134.832 | 5.618 | 9.5 | 9.5 | 2B | 0 | 0 | 1128 | 1185 | 0 | N/A | N/A | N/A | N/A | 46305372 | 900 | 160.1994 | 0% | 0% | 100% | 100% | 0% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 129 | 129 | 437323 | 6014 | 144.336 | 6.014 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46306292 | 920 | 152.9764 | 0% | 0% | 100% | 100% | 0% | 0% | 10766148 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 139 | 443434 | 6111 | 146.664 | 6.111 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46307548 | 1256 | 205.531 | 0% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 145 | 449645 | 6211 | 149.064 | 6.211 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46308908 | 1360 | 218.9664 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 144 | 455758 | 6113 | 146.712 | 6.113 | 8.8 | 8.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46310364 | 1456 | 238.1809 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 461887 | 6129 | 147.096 | 6.129 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46311692 | 1328 | 216.6748 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 | 1.12 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 467918 | 6031 | 144.744 | 6.031 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46313092 | 1400 | 232.134 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 138 | 473945 | 6027 | 144.648 | 6.027 | 7 | 7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46314456 | 1364 | 226.3149 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 480050 | 6105 | 146.52 | 6.105 | 6.5 | 6.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46315820 | 1364 | 223.4234 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 486108 | 6058 | 145.392 | 6.058 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46317172 | 1352 | 223.176 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 492097 | 5989 | 143.736 | 5.989 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46318524 | 1352 | 225.7472 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 498048 | 5951 | 142.824 | 5.951 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46319824 | 1300 | 218.4507 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 504034 | 5986 | 143.664 | 5.986 | 5 | 5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46321172 | 1348 | 225.1921 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 510004 | 5970 | 143.28 | 5.97 | 4.7 | 4.7 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46322508 | 1336 | 223.7856 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 515978 | 5974 | 143.376 | 5.974 | 4.5 | 4.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46323848 | 1340 | 224.3053 | 100% | 0% | 100% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 121 | 521843 | 5865 | 140.76 | 5.865 | 3.7 | 3.7 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46324936 | 1088 | 185.5072 | 100% | 0% | 0% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 129 | 527467 | 5624 | 134.976 | 5.624 | 3.2 | 3.2 | 2B+1S | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46325964 | 1028 | 182.7881 | 100% | 0% | 0% | 100% | 100% | 0% | 10766148 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 123 | 532971 | 5504 | 132.096 | 5.504 | 2.9 | 2.9 | 2B | 1047 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46327056 | 1092 | 198.4012 | 100% | 0% | 0% | 100% | 100% | 0% | 10766148 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 131 | 116 | 537475 | 4504 | 108.096 | 4.504 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46327988 | 932 | 206.9272 | 0% | 0% | 0% | 100% | 100% | 70% | 10766566 | 418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 134 | 114 | 541765 | 4290 | 102.96 | 4.29 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46328892 | 904 | 210.7226 | 0% | 0% | 0% | 100% | 100% | 70% | 10767167 | 601 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135111 | 135.111 | 135.111 | [12 empty] | 28100 | 28100 | 207.9771 | [6 empty] | 4461 | 4461 | 1.1417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 541765 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46328892 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10767167 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 108 | 546492 | 4727 | 113.448 | 4.727 | 5.6 | 5.6 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46329808 | 916 | 193.7804 | 0% | 0% | 0% | 100% | 100% | 75% | 10768125 | 958 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 104 | 551313 | 4821 | 115.704 | 4.821 | 6.8 | 6.8 | 2B | 0 | 0 | 0 | 1185 | 1138 | N/A | N/A | N/A | N/A | 46330668 | 860 | 178.3862 | 0% | 0% | 0% | 100% | 100% | 75% | 10769041 | 916 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 118 | 96 | 556237 | 4924 | 118.176 | 4.924 | 8 | 8 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46331476 | 808 | 164.0942 | 0% | 0% | 0% | 100% | 100% | 75% | 10770170 | 1129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 121 | 100 | 561265 | 5028 | 120.672 | 5.028 | 8.8 | 8.8 | 2B | 0 | 0 | 0 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46332304 | 828 | 164.6778 | 0% | 0% | 0% | 100% | 100% | 75% | 10771133 | 963 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 123 | 114 | 566836 | 5571 | 133.704 | 5.571 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1098 | N/A | N/A | N/A | N/A | 46333184 | 880 | 157.9609 | 0% | 0% | 0% | 100% | 100% | 75% | 10771714 | 581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 128 | 572857 | 6021 | 144.504 | 6.021 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46334116 | 932 | 154.7916 | 0% | 0% | 0% | 100% | 100% | 0% | 10771714 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 139 | 578949 | 6092 | 146.208 | 6.092 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46335308 | 1192 | 195.6664 | 0% | 0% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 144 | 144 | 585237 | 6288 | 150.912 | 6.288 | 9.3 | 9.3 | 3B+1S | 0 | 986 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46336672 | 1364 | 216.9211 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 145 | 146 | 591424 | 6187 | 148.488 | 6.187 | 9 | 9 | 3B+1S | 0 | 986 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46338004 | 1332 | 215.2901 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 129 | 597637 | 6213 | 149.112 | 6.213 | 8.7 | 8.7 | 3B+1S | 0 | 986 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46339400 | 1396 | 224.6902 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 | 1.27 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 145 | 603793 | 6156 | 147.744 | 6.156 | 8.4 | 8.4 | 3B+1S | 0 | 986 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46340764 | 1364 | 221.5724 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 138 | 609953 | 6160 | 147.84 | 6.16 | 8.1 | 8.1 | 3B+1S | 0 | 985 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46342108 | 1344 | 218.1818 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 146 | 143 | 616175 | 6222 | 149.328 | 6.222 | 7.7 | 7.7 | 3B+1S | 0 | 986 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46343476 | 1368 | 219.865 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 138 | 622412 | 6237 | 149.688 | 6.237 | 7.3 | 7.3 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46344836 | 1360 | 218.0536 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 141 | 628526 | 6114 | 146.736 | 6.114 | 6.9 | 6.9 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46346152 | 1316 | 215.2437 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 634652 | 6126 | 147.024 | 6.126 | 6.5 | 6.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46347516 | 1364 | 222.6575 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 640537 | 5885 | 141.24 | 5.885 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46348836 | 1320 | 224.2991 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 646446 | 5909 | 141.816 | 5.909 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46350204 | 1368 | 231.5113 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 652223 | 5777 | 138.648 | 5.777 | 5.3 | 5.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46351532 | 1328 | 229.8771 | 0% | 100% | 100% | 100% | 100% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 134 | 657735 | 5512 | 132.288 | 5.512 | 4.6 | 4.6 | 2B+1S | 0 | 1068 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46352628 | 1096 | 198.8389 | 0% | 100% | 100% | 100% | 0% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 132 | 663353 | 5618 | 134.832 | 5.618 | 3.7 | 3.7 | 2B+1S | 0 | 1068 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46353692 | 1064 | 189.3912 | 0% | 100% | 100% | 100% | 0% | 0% | 10771714 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 129 | 668871 | 5518 | 132.432 | 5.518 | 3.1 | 3.1 | 2B+1S | 0 | 1006 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46354708 | 1016 | 184.1247 | 0% | 100% | 100% | 100% | 0% | 0% | 10771714 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 133 | 109 | 673289 | 4418 | 106.032 | 4.418 | 3.6 | 3.6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46355628 | 920 | 208.239 | 0% | 0% | 100% | 100% | 0% | 88% | 10772313 | 599 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 139 | 106 | 677500 | 4211 | 101.064 | 4.211 | 4.6 | 4.6 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46356540 | 912 | 216.5756 | 0% | 0% | 100% | 100% | 0% | 88% | 10773100 | 787 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135735 | 135.735 | 135.735 | [12 empty] | 27648 | 27648 | 203.691 | [6 empty] | 5933 | 5933 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (88%)

## MAY 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 677500 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46356540 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10773100 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 106 | 682200 | 4700 | 112.8 | 4.7 | 6.3 | 6.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46357427 | 887 | 188.7234 | 0% | 0% | 100% | 100% | 0% | 95% | 10774099 | 999 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 102 | 687032 | 4832 | 115.968 | 4.832 | 8.1 | 8.1 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46358322 | 895 | 185.2235 | 0% | 0% | 100% | 100% | 0% | 95% | 10775099 | 1000 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 104 | 692044 | 5012 | 120.288 | 5.012 | 9.5 | 9.5 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46359240 | 918 | 183.1604 | 0% | 0% | 100% | 100% | 0% | 95% | 10776092 | 993 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 105 | 103 | 697311 | 5267 | 126.408 | 5.267 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 46360164 | 924 | 175.4319 | 0% | 0% | 100% | 100% | 0% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 117 | 110 | 702991 | 5680 | 136.32 | 5.68 | 9.5 | 9.5 | 2B | 0 | 0 | 1067 | 1185 | 0 | N/A | N/A | N/A | N/A | 46360968 | 804 | 141.5493 | 0% | 0% | 100% | 100% | 0% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 128 | 123 | 708886 | 5895 | 141.48 | 5.895 | 9.4 | 9.4 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46361900 | 932 | 158.1001 | 0% | 0% | 100% | 100% | 0% | 0% | 10776092 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 149 | 715024 | 6138 | 147.312 | 6.138 | 9 | 9 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46363276 | 1376 | 224.1773 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 721184 | 6160 | 147.84 | 6.16 | 8.6 | 8.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46364660 | 1384 | 224.6753 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 142 | 727422 | 6238 | 149.712 | 6.238 | 8.1 | 8.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46366016 | 1356 | 217.3774 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 733658 | 6236 | 149.664 | 6.236 | 7.6 | 7.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46367388 | 1372 | 220.0128 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 | 1.26 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 140 | 739824 | 6166 | 147.984 | 6.166 | 7.2 | 7.2 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46368748 | 1360 | 220.5644 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 138 | 745964 | 6140 | 147.36 | 6.14 | 6.7 | 6.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46370068 | 1320 | 214.9837 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 135 | 752128 | 6164 | 147.936 | 6.164 | 6.2 | 6.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46371456 | 1388 | 225.1785 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 758236 | 6108 | 146.592 | 6.108 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46372800 | 1344 | 220.0393 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 764332 | 6096 | 146.304 | 6.096 | 5.4 | 5.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46374132 | 1332 | 218.5039 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 134 | 770492 | 6160 | 147.84 | 6.16 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46375496 | 1364 | 221.4286 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 98 | 776602 | 6110 | 146.64 | 6.11 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46376823 | 1327 | 217.1849 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 141 | 782813 | 6211 | 149.064 | 6.211 | 4.3 | 4.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46378188 | 1365 | 219.7714 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 140 | 788953 | 6140 | 147.36 | 6.14 | 3.9 | 3.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46379524 | 1336 | 217.5896 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 137 | 795188 | 6235 | 149.64 | 6.235 | 3.4 | 3.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46380860 | 1336 | 214.2743 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 135 | 126 | 800702 | 5514 | 132.336 | 5.514 | 3.1 | 3.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46382224 | 1364 | 247.3703 | 100% | 0% | 100% | 100% | 100% | 0% | 10776092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 129 | 805409 | 4707 | 112.968 | 4.707 | 2.8 | 2.8 | 2B+1S | 1099 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46383324 | 1100 | 233.6945 | 100% | 0% | 0% | 100% | 100% | 0% | 10776092 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 131 | 113 | 809809 | 4400 | 105.6 | 4.4 | 3.2 | 3.2 | 2B | 0 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46384256 | 932 | 211.8182 | 0% | 0% | 0% | 100% | 100% | 70% | 10776786 | 694 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 137 | 110 | 813128 | 3319 | 79.656 | 3.319 | 4.4 | 4.4 | 2B | 0 | 0 | 0 | 1185 | 1189 | N/A | N/A | N/A | N/A | 46385188 | 932 | 280.8075 | 0% | 0% | 0% | 100% | 100% | 70% | 10777709 | 923 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135628 | 135.628 | 135.628 | [12 empty] | 28648 | 28648 | 211.2248 | [6 empty] | 4609 | 4609 | 1.1917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (95%)
XCV2- CLOSED @ 2:51 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP3 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 9:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 75PSI @ 10:01 PM TO 12:01 PM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29256 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 813128 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46385188 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10777709 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 128 | 105 | 817839 | 4711 | 113.064 | 4.711 | 6.3 | 6.3 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46386092 | 904 | 191.8913 | 0% | 0% | 0% | 100% | 100% | 75% | 10778517 | 808 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 104 | 822657 | 4818 | 115.632 | 4.818 | 8.1 | 8.1 | 2B | 0 | 0 | 0 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46386968 | 876 | 181.8182 | 0% | 0% | 0% | 100% | 100% | 75% | 10779525 | 1008 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 106 | 827577 | 4920 | 118.08 | 4.92 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46387824 | 856 | 173.9837 | 0% | 0% | 0% | 100% | 100% | 75% | 10780572 | 1047 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 111 | 110 | 832697 | 5120 | 122.88 | 5.12 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46388740 | 916 | 178.9062 | 0% | 0% | 0% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 124 | 113 | 838238 | 5541 | 132.984 | 5.541 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46389656 | 916 | 165.3131 | 0% | 0% | 0% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 125 | 844276 | 6038 | 144.912 | 6.038 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46390580 | 924 | 153.0308 | 0% | 0% | 0% | 100% | 100% | 0% | 10780572 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 143 | 850415 | 6139 | 147.336 | 6.139 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46391924 | 1344 | 218.9282 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 856459 | 6044 | 145.056 | 6.044 | 8.3 | 8.3 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46393336 | 1412 | 233.6201 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 151 | 862705 | 6246 | 149.904 | 6.246 | 7.7 | 7.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46394700 | 1364 | 218.3798 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 141 | 868853 | 6148 | 147.552 | 6.148 | 7 | 7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46396120 | 1420 | 230.9694 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 | 1.32 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 874907 | 6054 | 145.296 | 6.054 | 6.4 | 6.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46397492 | 1372 | 226.627 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 880967 | 6060 | 145.44 | 6.06 | 5.8 | 5.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46398864 | 1372 | 226.4026 | 0% | 100% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 136 | 887127 | 6160 | 147.84 | 6.16 | 5.3 | 5.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46400228 | 1364 | 221.4286 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 893246 | 6119 | 146.856 | 6.119 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46401616 | 1388 | 226.8345 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 899453 | 6207 | 148.968 | 6.207 | 4.2 | 4.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46402960 | 1344 | 216.5297 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 905668 | 6215 | 149.16 | 6.215 | 3.6 | 3.6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46404316 | 1356 | 218.1818 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 911858 | 6190 | 148.56 | 6.19 | 3.1 | 3.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46405668 | 1352 | 218.4168 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 93 | 917978 | 6120 | 146.88 | 6.12 | 2.8 | 2.8 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46407036 | 1368 | 223.5294 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 88 | 923989 | 6011 | 144.264 | 6.011 | 2.6 | 2.6 | 3B+1S | 995 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46408340 | 1304 | 216.9356 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 90 | 929976 | 5987 | 143.688 | 5.987 | 2.3 | 2.3 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46409696 | 1356 | 226.4907 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 138 | 82 | 935488 | 5512 | 132.288 | 5.512 | 2.1 | 2.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46411040 | 1344 | 243.8316 | 100% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 104 | 940800 | 5312 | 127.488 | 5.312 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46412324 | 1284 | 241.7169 | 0% | 0% | 100% | 100% | 100% | 0% | 10780572 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 125 | 945115 | 4315 | 103.56 | 4.315 | 2.2 | 2.2 | 3B | 0 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 46413452 | 1128 | 261.4137 | 0% | 0% | 100% | 100% | 100% | 70% | 10780849 | 277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 123 | 949379 | 4264 | 102.336 | 4.264 | 3.4 | 3.4 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46414444 | 992 | 232.6454 | 0% | 0% | 100% | 100% | 100% | 70% | 10781676 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136251 | 136.251 | 136.251 | [12 empty] | 29256 | 29256 | 214.7214 | [6 empty] | 3967 | 3967 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
BP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP2- STOPPED @ 12:00 PM DUE TO PREVENTIVE MAINTENACE
SP1- STARTED @ 12:01 PM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 9:00 PM DUE TO PREVENTIVE MAINTENACE
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (70%)

## MAY 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29240 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 949379 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46414444 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10781676 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 122 | 954343 | 4964 | 119.136 | 4.964 | 6.3 | 6.3 | 3B | 0 | 0 | 1147 | 1185 | 1148 | N/A | N/A | N/A | N/A | 46415384 | 940 | 189.3634 | 0% | 0% | 100% | 100% | 100% | 75% | 10782496 | 820 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 119 | 959205 | 4862 | 116.688 | 4.862 | 8.1 | 8.1 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46416372 | 988 | 203.2086 | 0% | 0% | 100% | 100% | 100% | 75% | 10783767 | 1271 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 117 | 964168 | 4963 | 119.112 | 4.963 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46417204 | 832 | 167.6405 | 0% | 0% | 100% | 100% | 100% | 75% | 10784827 | 1060 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 127 | 969032 | 4864 | 116.736 | 4.864 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46418244 | 1040 | 213.8158 | 0% | 0% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 135 | 126 | 974091 | 5059 | 121.416 | 5.059 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46419344 | 1100 | 217.4343 | 0% | 0% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 127 | 979550 | 5459 | 131.016 | 5.459 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46420436 | 1092 | 200.0366 | 0% | 0% | 100% | 100% | 100% | 0% | 10784827 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 146 | 985508 | 5958 | 142.992 | 5.958 | 9 | 9 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46421796 | 1360 | 228.2645 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 991862 | 6354 | 152.496 | 6.354 | 8.4 | 8.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46423141 | 1345 | 211.6777 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 998120 | 6258 | 150.192 | 6.258 | 7.9 | 7.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46424544 | 1403 | 224.193 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 1004180 | 6060 | 145.44 | 6.06 | 7.3 | 7.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46425924 | 1380 | 227.7228 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 142 | 1010545 | 6365 | 152.76 | 6.365 | 6.8 | 6.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46427316 | 1392 | 218.696 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 1016804 | 6259 | 150.216 | 6.259 | 6.3 | 6.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46428654 | 1338 | 213.7722 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 145 | 1023000 | 6196 | 148.704 | 6.196 | 5.8 | 5.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46430044 | 1390 | 224.3383 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 148 | 1029194 | 6194 | 148.656 | 6.194 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46431480 | 1436 | 231.8373 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 1035245 | 6051 | 145.224 | 6.051 | 5 | 5 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46432804 | 1324 | 218.8068 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 143 | 1041438 | 6193 | 148.632 | 6.193 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46434164 | 1360 | 219.6028 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 92 | 1047575 | 6137 | 147.288 | 6.137 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46435520 | 1356 | 220.9549 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 96 | 1053718 | 6143 | 147.432 | 6.143 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46436876 | 1356 | 220.7391 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 1059854 | 6136 | 147.264 | 6.136 | 3.4 | 3.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46438204 | 1328 | 216.4276 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 131 | 1065936 | 6082 | 145.968 | 6.082 | 3.1 | 3.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46439532 | 1328 | 218.3492 | 0% | 100% | 100% | 100% | 100% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 124 | 1071898 | 5962 | 143.088 | 5.962 | 2.4 | 2.4 | 2B+1S | 0 | 1098 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46440684 | 1152 | 193.2238 | 0% | 100% | 100% | 100% | 0% | 0% | 10784827 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 125 | 1076861 | 4963 | 119.112 | 4.963 | 2.2 | 2.2 | 2B+1S | 0 | 1097 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46441732 | 1048 | 211.1626 | 0% | 100% | 100% | 100% | 0% | 0% | 10784827 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 128 | 1081631 | 4770 | 114.48 | 4.77 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46442740 | 1008 | 211.3208 | 0% | 0% | 100% | 100% | 100% | 70% | 10785262 | 435 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 116 | 1086603 | 4972 | 119.328 | 4.972 | 3.7 | 3.7 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 46443684 | 944 | 189.8632 | 0% | 0% | 100% | 100% | 100% | 70% | 10785673 | 411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 137224 | 137.224 | 137.224 | [12 empty] | 29240 | 29240 | 213.0823 | [6 empty] | 3997 | 3997 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 75psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
BP3 - STARTED @ 10:01 PM DUE TO HIGH DISCHARGE
XCV2 -OPENED @ 10:02 PM (70%)

## MAY 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1086603 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46443684 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10785673 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 106 | 1091475 | 4872 | 116.928 | 4.872 | 6.3 | 6.3 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46444628 | 944 | 193.7603 | 0% | 0% | 100% | 100% | 100% | 75% | 10786630 | 957 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 118 | 1096421 | 4946 | 118.704 | 4.946 | 7.9 | 7.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46445588 | 960 | 194.0962 | 0% | 0% | 100% | 100% | 100% | 75% | 10787416 | 786 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 120 | 1101232 | 4811 | 115.464 | 4.811 | 8.6 | 8.6 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46446540 | 952 | 197.8799 | 0% | 0% | 100% | 100% | 100% | 75% | 10788411 | 995 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 128 | 1106154 | 4922 | 118.128 | 4.922 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46447592 | 1052 | 213.7343 | 0% | 0% | 100% | 100% | 100% | 75% | 10789236 | 825 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 120 | 1111276 | 5122 | 122.928 | 5.122 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 46448692 | 1100 | 214.7599 | 0% | 0% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 | 130 | 1116688 | 5412 | 129.888 | 5.412 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46449772 | 1080 | 199.5565 | 0% | 0% | 100% | 100% | 100% | 0% | 10789236 | 0 | 1.03 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 1122611 | 5923 | 142.152 | 5.923 | 9.1 | 9.1 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46451084 | 1312 | 221.5094 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 1128825 | 6214 | 149.136 | 6.214 | 8.6 | 8.6 | 3B+1S | 0 | 1048 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46452448 | 1364 | 219.5043 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 1134961 | 6136 | 147.264 | 6.136 | 8 | 8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46453828 | 1380 | 224.9022 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 139 | 1141154 | 6193 | 148.632 | 6.193 | 7.4 | 7.4 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46455196 | 1368 | 220.8946 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 | 1.14 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 1147385 | 6231 | 149.544 | 6.231 | 6.9 | 6.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46456558 | 1362 | 218.5845 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 135 | 1153601 | 6216 | 149.184 | 6.216 | 6.4 | 6.4 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46457928 | 1370 | 220.399 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 145 | 1159770 | 6169 | 148.056 | 6.169 | 5.8 | 5.8 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46459316 | 1388 | 224.9959 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 1165896 | 6126 | 147.024 | 6.126 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46460636 | 1320 | 215.475 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 145 | 1172049 | 6153 | 147.672 | 6.153 | 4.7 | 4.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46462054 | 1418 | 230.4567 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 147 | 1178098 | 6049 | 145.176 | 6.049 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46463388 | 1334 | 220.5323 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 98 | 1184197 | 6099 | 146.376 | 6.099 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46464740 | 1352 | 221.6757 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 92 | 1190338 | 6141 | 147.384 | 6.141 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46466096 | 1356 | 220.8109 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 88 | 1196444 | 6106 | 146.544 | 6.106 | 3.1 | 3.1 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46467444 | 1348 | 220.7665 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 112 | 1202618 | 6174 | 148.176 | 6.174 | 2.8 | 2.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46468796 | 1352 | 218.9828 | 0% | 100% | 100% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 1208292 | 5674 | 136.176 | 5.674 | 2 | 2 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46469940 | 1144 | 201.6214 | 0% | 100% | 0% | 100% | 100% | 0% | 10789236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 | 124 | 1213566 | 5274 | 126.576 | 5.274 | 1.8 | 1.8 | 2B+1S | 0 | 1099 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46470992 | 1052 | 199.4691 | 0% | 100% | 0% | 100% | 100% | 0% | 10789236 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 125 | 1218242 | 4676 | 112.224 | 4.676 | 2.5 | 2.5 | 2B+1S | 1099 | 0 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46472096 | 1104 | 236.0992 | 100% | 0% | 0% | 100% | 100% | 70% | 10790348 | 1112 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 120 | 1222838 | 4596 | 110.304 | 4.596 | 3.5 | 3.5 | 2B+1S | 1099 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46472916 | 820 | 178.416 | 100% | 0% | 100% | 100% | 0% | 70% | 10791332 | 984 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136235 | 136.235 | 136.235 | [12 empty] | 29232 | 29232 | 214.5704 | [6 empty] | 5659 | 5659 | 1.0317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
SP1 - STARTED @ 10:01 PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
XCV2 -OPENED @ 10:02 PM (70%)
BP3 - STOPPED @ 11:00 PM DUE MONTHLY PREVENTIVE MAINTENANCE
BP1 - STARTED @ 11:01 PM DUE MONTHLY PREVENTIVE MAINTENANCE

## MAY 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29512 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1222838 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46472916 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10791332 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 114 | 1227834 | 4996 | 119.904 | 4.996 | 6.5 | 6.5 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46473860 | 944 | 188.9512 | 100% | 0% | 100% | 100% | 0% | 75% | 10792542 | 1210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 110 | 1232726 | 4892 | 117.408 | 4.892 | 8 | 8 | 2B+1S | 1047 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 46474534 | 674 | 137.776 | 100% | 0% | 100% | 0% | 100% | 75% | 10794010 | 1468 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 123 | 113 | 1237720 | 4994 | 119.856 | 4.994 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46475468 | 934 | 187.0244 | 0% | 0% | 100% | 100% | 100% | 75% | 10795061 | 1051 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 112 | 1242793 | 5073 | 121.752 | 5.073 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46476536 | 1068 | 210.5263 | 0% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 114 | 1247987 | 5194 | 124.656 | 5.194 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46477684 | 1148 | 221.0243 | 0% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 127 | 1253286 | 5299 | 127.176 | 5.299 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46478788 | 1104 | 208.3412 | 0% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 142 | 1258753 | 5467 | 131.208 | 5.467 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46480124 | 1336 | 244.3753 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 148 | 1264669 | 5916 | 141.984 | 5.916 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46481488 | 1364 | 230.5612 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 1270686 | 6017 | 144.408 | 6.017 | 8.2 | 8.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46482852 | 1364 | 226.691 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 140 | 1276822 | 6136 | 147.264 | 6.136 | 7.5 | 7.5 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46484244 | 1392 | 226.8579 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 | 1.26 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 143 | 1283025 | 6203 | 148.872 | 6.203 | 6.9 | 6.9 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46485636 | 1392 | 224.4075 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 1289193 | 6168 | 148.032 | 6.168 | 6.4 | 6.4 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46487012 | 1376 | 223.0869 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 146 | 1295277 | 6084 | 146.016 | 6.084 | 5.8 | 5.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46488388 | 1376 | 226.167 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 147 | 1301560 | 6283 | 150.792 | 6.283 | 5.2 | 5.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46489711 | 1323 | 210.5682 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 1307948 | 6388 | 153.312 | 6.388 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46491044 | 1333 | 208.6725 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 134 | 1313992 | 6044 | 145.056 | 6.044 | 4.4 | 4.4 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46492392 | 1348 | 223.0311 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 131 | 1320158 | 6166 | 147.984 | 6.166 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46493740 | 1348 | 218.6182 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 139 | 1326152 | 5994 | 143.856 | 5.994 | 3.6 | 3.6 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46495084 | 1344 | 224.2242 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 136 | 1332257 | 6105 | 146.52 | 6.105 | 3.3 | 3.3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46496428 | 1344 | 220.1474 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 130 | 1338263 | 6006 | 144.144 | 6.006 | 3 | 3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46497760 | 1332 | 221.7782 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 136 | 128 | 1343970 | 5707 | 136.968 | 5.707 | 2.8 | 2.8 | 2B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46499092 | 1332 | 233.3976 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 | 129 | 1349486 | 5516 | 132.384 | 5.516 | 2.5 | 2.5 | 2B+1S | 996 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46500340 | 1248 | 226.2509 | 100% | 0% | 100% | 100% | 100% | 0% | 10795061 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 128 | 1354708 | 5222 | 125.328 | 5.222 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46501400 | 1060 | 202.9874 | 0% | 0% | 100% | 100% | 100% | 70% | 10795600 | 539 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 129 | 126 | 1359880 | 5172 | 124.128 | 5.172 | 4.2 | 4.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46502428 | 1028 | 198.7626 | 0% | 0% | 100% | 100% | 100% | 70% | 10796175 | 575 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 137042 | 137.042 | 137.042 | [12 empty] | 29512 | 29512 | 215.35 | [6 empty] | 4843 | 4843 | 1.17 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
BP3 - STARTED @ 1:00 AM DUE MONTHLY PREVENTIVE MAINTENANCE
BP2 - STOPPED @ 1:01 AM DUE MONTHLY PREVENTIVE MAINTENANCE
BP2 - STARTED @ 2:00 AM DUE MONTHLY PREVENTIVE MAINTENANCE
SP1 - STOPPED @ 2:01 AM DUE MONTHLY PREVENTIVE MAINTENANCE
XCV2- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29048 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1359880 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46502428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10796175 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 128 | 120 | 1364252 | 4372 | 104.928 | 4.372 | 6 | 6 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46503432 | 1004 | 229.6432 | 0% | 0% | 100% | 100% | 100% | 75% | 10796810 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 123 | 1369081 | 4829 | 115.896 | 4.829 | 8.1 | 8.1 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46504380 | 948 | 196.3139 | 0% | 0% | 100% | 100% | 100% | 75% | 10797597 | 787 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 120 | 1374015 | 4934 | 118.416 | 4.934 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46505288 | 908 | 184.0292 | 0% | 0% | 100% | 100% | 100% | 75% | 10798124 | 527 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 135 | 121 | 1379041 | 5026 | 120.624 | 5.026 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46506280 | 992 | 197.3737 | 0% | 0% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 119 | 1384177 | 5136 | 123.264 | 5.136 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46507268 | 988 | 192.3676 | 0% | 0% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 131 | 123 | 1389320 | 5143 | 123.432 | 5.143 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46508284 | 1016 | 197.5501 | 0% | 0% | 100% | 100% | 100% | 0% | 10798124 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 148 | 138 | 1394632 | 5312 | 127.488 | 5.312 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46509556 | 1272 | 239.4578 | 0% | 0% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 144 | 1400018 | 5386 | 129.264 | 5.386 | 9.4 | 9.4 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46510868 | 1312 | 243.5945 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 1405652 | 5634 | 135.216 | 5.634 | 8.8 | 8.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46512256 | 1388 | 246.3614 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 133 | 1411735 | 6083 | 145.992 | 6.083 | 8.2 | 8.2 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46513644 | 1388 | 228.1769 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 | 1.15 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 1417876 | 6141 | 147.384 | 6.141 | 7.5 | 7.5 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46515048 | 1404 | 228.6273 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 1423967 | 6091 | 146.184 | 6.091 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46516420 | 1372 | 225.2504 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 1430025 | 6058 | 145.392 | 6.058 | 6.3 | 6.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46517804 | 1384 | 228.4582 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 96 | 1436146 | 6121 | 146.904 | 6.121 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46519188 | 1384 | 226.1068 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 1442234 | 6088 | 146.112 | 6.088 | 5.3 | 5.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46520500 | 1312 | 215.5059 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 1448386 | 6152 | 147.648 | 6.152 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46521900 | 1400 | 227.5683 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 103 | 1454488 | 6102 | 146.448 | 6.102 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46523212 | 1312 | 215.0115 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 99 | 1460664 | 6176 | 148.224 | 6.176 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46524548 | 1336 | 216.3212 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 96 | 1466862 | 6198 | 148.752 | 6.198 | 3.7 | 3.7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46525912 | 1364 | 220.071 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 100 | 1472972 | 6110 | 146.64 | 6.11 | 3.5 | 3.5 | 3B+1S | 0 | 995 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46527244 | 1332 | 218.0033 | 0% | 100% | 100% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 125 | 1479096 | 6124 | 146.976 | 6.124 | 2.9 | 2.9 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46528352 | 1108 | 180.9275 | 0% | 100% | 0% | 100% | 100% | 0% | 10798124 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 125 | 1485122 | 6026 | 144.624 | 6.026 | 2.5 | 2.5 | 2B+1S | 0 | 1048 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46529404 | 1052 | 174.5768 | 0% | 100% | 0% | 100% | 100% | 0% | 10798124 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 121 | 1490548 | 5426 | 130.224 | 5.426 | 3.2 | 3.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46530436 | 1032 | 190.1954 | 0% | 0% | 100% | 100% | 100% | 70% | 10798532 | 408 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 116 | 1495384 | 4836 | 116.064 | 4.836 | 4 | 4 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46531476 | 1040 | 215.0538 | 0% | 0% | 100% | 100% | 100% | 70% | 10798980 | 448 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135504 | 135.504 | 135.504 | [12 empty] | 29048 | 29048 | 214.3701 | [6 empty] | 2805 | 2805 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30000 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1495384 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46531476 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10798980 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 127 | 120 | 1500320 | 4936 | 118.464 | 4.936 | 6.1 | 6.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46532464 | 988 | 200.1621 | 0% | 0% | 100% | 100% | 100% | 75% | 10799519 | 539 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 115 | 1505152 | 4832 | 115.968 | 4.832 | 7.6 | 7.6 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46533448 | 984 | 203.6424 | 0% | 0% | 100% | 100% | 100% | 75% | 10799990 | 471 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 116 | 1510097 | 4945 | 118.68 | 4.945 | 8.7 | 8.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46534452 | 1004 | 203.0334 | 0% | 0% | 100% | 100% | 100% | 75% | 10800515 | 525 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 132 | 122 | 1515186 | 5089 | 122.136 | 5.089 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46535552 | 1100 | 216.1525 | 0% | 0% | 100% | 100% | 100% | 75% | 10801197 | 682 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 123 | 1520379 | 5193 | 124.632 | 5.193 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46536676 | 1124 | 216.4452 | 0% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 143 | 135 | 1525598 | 5219 | 125.256 | 5.219 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1168 | N/A | N/A | N/A | N/A | 46537716 | 1040 | 199.2719 | 0% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 1531116 | 5518 | 132.432 | 5.518 | 9.3 | 9.3 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46539048 | 1332 | 241.3918 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 1536825 | 5709 | 137.016 | 5.709 | 8.7 | 8.7 | 3B+1S | 1058 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46540436 | 1388 | 243.1249 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 1542693 | 5868 | 140.832 | 5.868 | 8 | 8 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46541820 | 1384 | 235.8555 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 1548631 | 5938 | 142.512 | 5.938 | 7.4 | 7.4 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46543212 | 1392 | 234.4224 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 1554652 | 6021 | 144.504 | 6.021 | 6.8 | 6.8 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46544596 | 1384 | 229.8621 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 1560725 | 6073 | 145.752 | 6.073 | 6.1 | 6.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46545980 | 1384 | 227.894 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 148 | 1566828 | 6103 | 146.472 | 6.103 | 5.4 | 5.4 | 3B+1S | 1078 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46547372 | 1392 | 228.0845 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 151 | 1572958 | 6130 | 147.12 | 6.13 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46548768 | 1396 | 227.7325 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 152 | 1579136 | 6178 | 148.272 | 6.178 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46550068 | 1300 | 210.4241 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 142 | 140 | 1585383 | 6247 | 149.928 | 6.247 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46551440 | 1372 | 219.6254 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 1342180 | 6120 | 146.88 | 6.12 | 3.6 | 3.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46552788 | 1348 | 220.2614 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 142 | 1348084 | 5904 | 141.696 | 5.904 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46554140 | 1352 | 228.9973 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 133 | 1354052 | 5968 | 143.232 | 5.968 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46555492 | 1352 | 226.5416 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 132 | 1359875 | 5823 | 139.752 | 5.823 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46556848 | 1356 | 232.8697 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 130 | 1365278 | 5403 | 129.672 | 5.403 | 1.9 | 1.9 | 2B+1S | 1058 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46557940 | 1092 | 202.1099 | 100% | 0% | 100% | 100% | 100% | 0% | 10801197 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 136 | 129 | 1370640 | 5362 | 128.688 | 5.362 | 1.3 | 1.3 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46559008 | 1068 | 199.1794 | 100% | 0% | 100% | 100% | 0% | 0% | 10801197 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 141 | 128 | 1375972 | 5332 | 127.968 | 5.332 | 1.5 | 1.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46560244 | 1236 | 231.808 | 0% | 0% | 100% | 100% | 100% | 80% | 10801408 | 211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 122 | 1381404 | 5432 | 130.368 | 5.432 | 1.8 | 1.8 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46561476 | 1232 | 226.8041 | 0% | 0% | 100% | 100% | 100% | 80% | 10801843 | 435 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135343 | 135.343 | 135.343 | [12 empty] | 30000 | 30000 | 221.659 | [6 empty] | 2863 | 2863 | 1.135 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
RESET THE FLOW METERS @ 5:00PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (80%)
Note on Q27: RESET THE FLOW METERS AT 5PM

## MAY 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30352 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1381404 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46561476 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10801843 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 118 | 1385905 | 4501 | 108.024 | 4.501 | 4.2 | 4.2 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46562615 | 1139 | 253.0549 | 0% | 0% | 100% | 100% | 100% | 93% | 10802332 | 489 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 109 | 1390330 | 4425 | 106.2 | 4.425 | 5.9 | 5.9 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46563747 | 1132 | 255.8192 | 0% | 0% | 100% | 100% | 100% | 93% | 10802922 | 590 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 115 | 1394946 | 4616 | 110.784 | 4.616 | 7.7 | 7.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46564889 | 1142 | 247.4003 | 0% | 0% | 100% | 100% | 100% | 93% | 10803517 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 110 | 1399485 | 4539 | 108.936 | 4.539 | 8.9 | 8.9 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 46566092 | 1203 | 265.0364 | 0% | 0% | 100% | 100% | 100% | 93% | 10804036 | 519 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 120 | 1403781 | 4296 | 103.104 | 4.296 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46567324 | 1232 | 286.7784 | 0% | 0% | 100% | 100% | 100% | 93% | 10804236 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 141 | 132 | 1409171 | 5390 | 129.36 | 5.39 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46568420 | 1096 | 203.3395 | 0% | 0% | 100% | 100% | 100% | 0% | 10804236 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 145 | 1415403 | 6232 | 149.568 | 6.232 | 9.1 | 9.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46569728 | 1308 | 209.8845 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 1421688 | 6285 | 150.84 | 6.285 | 8.6 | 8.6 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46571104 | 1376 | 218.934 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 1427963 | 6275 | 150.6 | 6.275 | 8 | 8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46572548 | 1444 | 230.1195 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 1434218 | 6255 | 150.12 | 6.255 | 7.3 | 7.3 | 3B+1S | 0 | 1067 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46573980 | 1432 | 228.9369 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 | 1.27 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 1440332 | 6114 | 146.736 | 6.114 | 6.7 | 6.7 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46575364 | 1384 | 226.3657 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 1446326 | 5994 | 143.856 | 5.994 | 6.2 | 6.2 | 3B+1S | 0 | 1068 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46576744 | 1380 | 230.2302 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 144 | 1452509 | 6183 | 148.392 | 6.183 | 5.5 | 5.5 | 3B+1S | 0 | 1088 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46578132 | 1388 | 224.4865 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 1458781 | 6272 | 150.528 | 6.272 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46579516 | 1384 | 220.6633 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 1465021 | 6240 | 149.76 | 6.24 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46580844 | 1328 | 212.8205 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 1471289 | 6268 | 150.432 | 6.268 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46582188 | 1344 | 214.4225 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 1477581 | 6292 | 151.008 | 6.292 | 3.6 | 3.6 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46583544 | 1356 | 215.5118 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 133 | 1483874 | 6293 | 151.032 | 6.293 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46584880 | 1336 | 212.2994 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 136 | 1489792 | 5918 | 142.032 | 5.918 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46586220 | 1340 | 226.4278 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 140 | 1496074 | 6282 | 150.768 | 6.282 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46587600 | 1380 | 219.6753 | 0% | 100% | 100% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 151 | 1502372 | 6298 | 151.152 | 6.298 | 2 | 2 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46588684 | 1084 | 172.1181 | 0% | 100% | 0% | 100% | 100% | 0% | 10804236 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 153 | 1508384 | 6012 | 144.288 | 6.012 | 1.7 | 1.7 | 2B+1S | 0 | 1050 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46589748 | 1064 | 176.9794 | 0% | 100% | 0% | 100% | 100% | 0% | 10804236 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 134 | 1514361 | 5977 | 143.448 | 5.977 | 2.3 | 2.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46590836 | 1088 | 182.0311 | 0% | 0% | 100% | 100% | 100% | 70% | 10804834 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 123 | 1520215 | 5854 | 140.496 | 5.854 | 3.5 | 3.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46591828 | 992 | 169.4568 | 0% | 0% | 100% | 100% | 100% | 70% | 10805421 | 587 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 138811 | 138.811 | 138.811 | [12 empty] | 30352 | 30352 | 218.657 | [6 empty] | 3578 | 3578 | 1.115 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (93%)
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29724 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1520215 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46591828 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10805421 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 117 | 1525772 | 5557 | 133.368 | 5.557 | 5.8 | 5.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46592836 | 1008 | 181.3928 | 0% | 0% | 100% | 100% | 100% | 75% | 10806036 | 615 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 115 | 1531439 | 5667 | 136.008 | 5.667 | 7.5 | 7.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46593888 | 1052 | 185.6361 | 0% | 0% | 100% | 100% | 100% | 75% | 10806836 | 800 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 113 | 1536888 | 5449 | 130.776 | 5.449 | 8.6 | 8.6 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46594940 | 1052 | 193.0629 | 0% | 0% | 100% | 100% | 100% | 75% | 10807632 | 796 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 123 | 1542456 | 5568 | 133.632 | 5.568 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46596092 | 1152 | 206.8966 | 0% | 0% | 100% | 100% | 100% | 75% | 10808227 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 125 | 1547964 | 5508 | 132.192 | 5.508 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46597196 | 1104 | 200.4357 | 0% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 142 | 137 | 1553934 | 5970 | 143.28 | 5.97 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1184 | N/A | N/A | N/A | N/A | 46598372 | 1176 | 196.9849 | 0% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 1560065 | 6131 | 147.144 | 6.131 | 9.3 | 9.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46599700 | 1328 | 216.6041 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 143 | 1566247 | 6182 | 148.368 | 6.182 | 8.9 | 8.9 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46601064 | 1364 | 220.6406 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 1572496 | 6249 | 149.976 | 6.249 | 8.3 | 8.3 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46602448 | 1384 | 221.4754 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 1578588 | 6092 | 146.208 | 6.092 | 7.7 | 7.7 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46603838 | 1390 | 228.1681 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 1584739 | 6151 | 147.624 | 6.151 | 7.1 | 7.1 | 3B+1S | 1057 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46605212 | 1374 | 223.3783 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 1590788 | 6049 | 145.176 | 6.049 | 6.5 | 6.5 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46606592 | 1380 | 228.1369 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 146 | 1597021 | 6233 | 149.592 | 6.233 | 6 | 6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46607968 | 1376 | 220.7605 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 1603112 | 6091 | 146.184 | 6.091 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46609336 | 1368 | 224.5937 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 1608773 | 5661 | 135.864 | 5.661 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46610644 | 1308 | 231.0546 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 143 | 1614643 | 5870 | 140.88 | 5.87 | 5 | 5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46611984 | 1340 | 228.2794 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 142 | 1620263 | 5620 | 134.88 | 5.62 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46613156 | 1172 | 208.5409 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 140 | 1626295 | 6032 | 144.768 | 6.032 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46614532 | 1376 | 228.1167 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 1632348 | 6053 | 145.272 | 6.053 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46615880 | 1348 | 222.6995 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 139 | 1638389 | 6041 | 144.984 | 6.041 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46617236 | 1356 | 224.4661 | 100% | 0% | 100% | 100% | 100% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 132 | 1644332 | 5943 | 142.632 | 5.943 | 2.5 | 2.5 | 2B+1S | 1098 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46618532 | 1296 | 218.0717 | 100% | 0% | 100% | 100% | 0% | 0% | 10808227 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 124 | 127 | 1648984 | 4652 | 111.648 | 4.652 | 2.3 | 2.3 | 2B+1S | 1149 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46619432 | 900 | 193.4652 | 100% | 0% | 100% | 100% | 0% | 0% | 10808227 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 125 | 1653934 | 4950 | 118.8 | 4.95 | 3 | 3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46620476 | 1044 | 210.9091 | 0% | 0% | 100% | 100% | 100% | 70% | 10808815 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 1658821 | 4887 | 117.288 | 4.887 | 4.3 | 4.3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46621552 | 1076 | 220.176 | 0% | 0% | 100% | 100% | 100% | 70% | 10809327 | 512 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 138606 | 138.606 | 138.606 | [12 empty] | 29724 | 29724 | 214.4496 | [6 empty] | 3906 | 3906 | 1.1483 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29720 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1658821 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46621552 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10809327 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 116 | 1663671 | 4850 | 116.4 | 4.85 | 5.6 | 5.6 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46622612 | 1060 | 218.5567 | 0% | 0% | 100% | 100% | 100% | 75% | 10810082 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 115 | 1668424 | 4753 | 114.072 | 4.753 | 6.9 | 6.9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46623664 | 1052 | 221.3339 | 0% | 0% | 100% | 100% | 100% | 75% | 10810691 | 609 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 118 | 113 | 1673054 | 4630 | 111.12 | 4.63 | 8 | 8 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46624704 | 1040 | 224.622 | 0% | 0% | 100% | 100% | 100% | 75% | 10811525 | 834 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 114 | 1676250 | 3196 | 76.704 | 3.196 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46625880 | 1176 | 367.9599 | 0% | 0% | 100% | 100% | 100% | 75% | 10812232 | 707 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 120 | 1681284 | 5034 | 120.816 | 5.034 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46626972 | 1092 | 216.9249 | 0% | 0% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 141 | 138 | 1686584 | 5300 | 127.2 | 5.3 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46628180 | 1208 | 227.9245 | 0% | 0% | 100% | 100% | 100% | 0% | 10812232 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 1692507 | 5923 | 142.152 | 5.923 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46629432 | 1252 | 211.3794 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 1698768 | 6261 | 150.264 | 6.261 | 8.7 | 8.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46630814 | 1382 | 220.7315 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 145 | 1704973 | 6205 | 148.92 | 6.205 | 8.1 | 8.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46632172 | 1358 | 218.8558 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 152 | 1711293 | 6320 | 151.68 | 6.32 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46633548 | 1376 | 217.7215 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 | 1.25 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 1717450 | 6157 | 147.768 | 6.157 | 7.1 | 7.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46634916 | 1368 | 222.1861 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 1723648 | 6198 | 148.752 | 6.198 | 6.7 | 6.7 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46636244 | 1328 | 214.2627 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 145 | 1729720 | 6072 | 145.728 | 6.072 | 6.1 | 6.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46637652 | 1408 | 231.8841 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 1735906 | 6186 | 148.464 | 6.186 | 5.6 | 5.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46639060 | 1408 | 227.6107 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 1741738 | 5832 | 139.968 | 5.832 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46640400 | 1340 | 229.7668 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 1747684 | 5946 | 142.704 | 5.946 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46641740 | 1340 | 225.3616 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 143 | 1753578 | 5894 | 141.456 | 5.894 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46643080 | 1340 | 227.3498 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 136 | 1759486 | 5908 | 141.792 | 5.908 | 3.9 | 3.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46644436 | 1356 | 229.5193 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 132 | 1765264 | 5778 | 138.672 | 5.778 | 3.5 | 3.5 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46645758 | 1322 | 228.7989 | 0% | 100% | 100% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 1770972 | 5708 | 136.992 | 5.708 | 2.8 | 2.8 | 2B+1S | 0 | 1118 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46646876 | 1118 | 195.8655 | 0% | 100% | 0% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 135 | 1776574 | 5602 | 134.448 | 5.602 | 1.9 | 1.9 | 2B+1S | 0 | 1119 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46648004 | 1128 | 201.3567 | 0% | 100% | 0% | 100% | 100% | 0% | 10812232 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 123 | 128 | 1781998 | 5424 | 130.176 | 5.424 | 1.7 | 1.7 | 2B+1S | 0 | 1149 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46649108 | 1104 | 203.5398 | 0% | 100% | 0% | 100% | 100% | 0% | 10812232 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 122 | 1786998 | 5000 | 120 | 5 | 3 | 3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46650188 | 1080 | 216 | 0% | 0% | 100% | 100% | 100% | 70% | 10812862 | 630 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 145 | 115 | 1791906 | 4908 | 117.792 | 4.908 | 4.8 | 4.8 | 3B | 0 | 0 | 1147 | 1185 | 1148 | N/A | N/A | N/A | N/A | 46651272 | 1084 | 220.8639 | 0% | 0% | 100% | 100% | 100% | 70% | 10813528 | 666 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133085 | 133.085 | 133.085 | [12 empty] | 29720 | 29720 | 223.3159 | [7 empty] | 4201 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## MAY 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29564 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1791906 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46651272 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10813528 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 112 | 1796665 | 4759 | 114.216 | 4.759 | 5.9 | 5.9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46652332 | 1060 | 222.7359 | 0% | 0% | 100% | 100% | 100% | 75% | 10814123 | 595 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 110 | 1801318 | 4653 | 111.672 | 4.653 | 7 | 7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46653376 | 1044 | 224.3714 | 0% | 0% | 100% | 100% | 100% | 75% | 10814891 | 768 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 107 | 1805749 | 4431 | 106.344 | 4.431 | 8.6 | 8.6 | 3B | 0 | 0 | 1048 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46654372 | 996 | 224.78 | 0% | 0% | 100% | 100% | 100% | 75% | 10815615 | 724 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 12.8 | 122 | 108 | 1809052 | 3303 | 79.272 | 3.303 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46655572 | 1200 | 363.3061 | 0% | 0% | 100% | 100% | 100% | 75% | 10816275 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A.ONG | 13.1 | 121 | 113 | 1813532 | 4480 | 107.52 | 4.48 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46656616 | 1044 | 233.0357 | 0% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 139 | 135 | 1818754 | 5222 | 125.328 | 5.222 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 46657644 | 1028 | 196.8594 | 0% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 145 | 1824739 | 5985 | 143.64 | 5.985 | 9.2 | 9.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46658988 | 1344 | 224.5614 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 1831029 | 6290 | 150.96 | 6.29 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46660380 | 1392 | 221.3037 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 146 | 1837303 | 6274 | 150.576 | 6.274 | 8 | 8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46661756 | 1376 | 219.3178 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 1843515 | 6212 | 149.088 | 6.212 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46663144 | 1388 | 223.4385 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 | 1.3 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 1849650 | 6135 | 147.24 | 6.135 | 6.8 | 6.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46664524 | 1380 | 224.9389 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 1855727 | 6077 | 145.848 | 6.077 | 6.4 | 6.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46665892 | 1368 | 225.1111 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 1861805 | 6078 | 145.872 | 6.078 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46667268 | 1376 | 226.3903 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 1867708 | 5903 | 141.672 | 5.903 | 5.3 | 5.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46668620 | 1352 | 229.0361 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 138 | 1873654 | 5946 | 142.704 | 5.946 | 4.9 | 4.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46669972 | 1352 | 227.3798 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 1879523 | 5869 | 140.856 | 5.869 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46671296 | 1324 | 225.5921 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 139 | 1885662 | 6139 | 147.336 | 6.139 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46672672 | 1376 | 224.1407 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 1891392 | 5730 | 137.52 | 5.73 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46673988 | 1316 | 229.6684 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 1897354 | 5962 | 143.088 | 5.962 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46675332 | 1344 | 225.4277 | 100% | 0% | 100% | 100% | 100% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 130 | 1902818 | 5464 | 131.136 | 5.464 | 2.9 | 2.9 | 2B+1S | 1058 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46676422 | 1090 | 199.4876 | 100% | 0% | 100% | 100% | 0% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 121 | 1908156 | 5338 | 128.112 | 5.338 | 2.2 | 2.2 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46677476 | 1054 | 197.4522 | 100% | 0% | 100% | 100% | 0% | 0% | 10816275 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 120 | 1913439 | 5283 | 126.792 | 5.283 | 1.9 | 1.9 | 2B+1S | 1046 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46678548 | 1072 | 202.915 | 100% | 0% | 100% | 100% | 0% | 0% | 10816275 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 143 | 122 | 1918534 | 5095 | 122.28 | 5.095 | 3 | 3 | 3B | 0 | 0 | 1146 | 1185 | 1148 | N/A | N/A | N/A | N/A | 46679684 | 1136 | 222.9637 | 0% | 0% | 100% | 100% | 100% | 70% | 10817052 | 777 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 143 | 118 | 1923603 | 5069 | 121.656 | 5.069 | 4.5 | 4.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46680836 | 1152 | 227.2638 | 0% | 0% | 100% | 100% | 100% | 70% | 10817651 | 599 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131697 | 131.697 | 131.697 | [12 empty] | 29564 | 29564 | 224.485 | [7 empty] | 4123 | 1.1633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
Change operation as per advise sir Alvin Cruz effective May 20, 2016 ONLY from 3am to 5am the PSI is 75psi and the change operation will be waiting the advised of SPM.
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (70%)

## MAY 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29988 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 1923603 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46680836 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10817651 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 114 | 1928526 | 4923 | 118.152 | 4.923 | 5.8 | 5.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46681980 | 1144 | 232.3786 | 0% | 0% | 100% | 100% | 100% | 75% | 10818516 | 865 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 112 | 1933142 | 4616 | 110.784 | 4.616 | 7 | 7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46683020 | 1040 | 225.3033 | 0% | 0% | 100% | 100% | 100% | 75% | 10819381 | 865 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 114 | 1937803 | 4661 | 111.864 | 4.661 | 8.5 | 8.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46684080 | 1060 | 227.419 | 0% | 0% | 100% | 100% | 100% | 75% | 10820127 | 746 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 119 | 1941324 | 3521 | 84.504 | 3.521 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46685204 | 1124 | 319.2275 | 0% | 0% | 100% | 100% | 100% | 75% | 10820954 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 117 | 1946218 | 4894 | 117.456 | 4.894 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46686284 | 1080 | 220.6784 | 0% | 0% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 132 | 128 | 1951209 | 4991 | 119.784 | 4.991 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46687224 | 940 | 188.339 | 0% | 0% | 100% | 100% | 100% | 0% | 10820954 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 141 | 1957096 | 5887 | 141.288 | 5.887 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46688480 | 1256 | 213.3515 | 0% | 0% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 1963333 | 6237 | 149.688 | 6.237 | 9.2 | 9.2 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46689840 | 1360 | 218.0536 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 1969630 | 6297 | 151.128 | 6.297 | 8.6 | 8.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46691228 | 1388 | 220.4224 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 150 | 1976029 | 6399 | 153.576 | 6.399 | 7.9 | 7.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46692628 | 1400 | 218.7842 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 | 1.11 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 151 | 1982294 | 6265 | 150.36 | 6.265 | 7.3 | 7.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46694024 | 1396 | 222.8252 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 1988550 | 6256 | 150.144 | 6.256 | 6.6 | 6.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46695424 | 1400 | 223.7852 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 146 | 1994836 | 6286 | 150.864 | 6.286 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46696788 | 1364 | 216.9901 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 2000942 | 6106 | 146.544 | 6.106 | 5.6 | 5.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46698092 | 1304 | 213.5604 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 142 | 2006431 | 5489 | 131.736 | 5.489 | 5.2 | 5.2 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46699448 | 1356 | 247.0395 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 145 | 2012430 | 5999 | 143.976 | 5.999 | 4.8 | 4.8 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46700796 | 1348 | 224.7041 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 2018498 | 6068 | 145.632 | 6.068 | 4.4 | 4.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46702156 | 1360 | 224.1266 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 138 | 2024469 | 5971 | 143.304 | 5.971 | 4 | 4 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46703500 | 1344 | 225.0879 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 139 | 2030384 | 5915 | 141.96 | 5.915 | 3.7 | 3.7 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46704840 | 1340 | 226.5427 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 136 | 2036153 | 5769 | 138.456 | 5.769 | 3.4 | 3.4 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46706180 | 1340 | 232.276 | 0% | 100% | 100% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 131 | 2041626 | 5473 | 131.352 | 5.473 | 2.7 | 2.7 | 2B+1S | 0 | 1079 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46707272 | 1092 | 199.5249 | 0% | 100% | 0% | 100% | 100% | 0% | 10820954 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 125 | 2047396 | 5770 | 138.48 | 5.77 | 2.1 | 2.1 | 2B+1S | 0 | 1046 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46708388 | 1116 | 193.4142 | 0% | 100% | 0% | 100% | 100% | 0% | 10820954 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 128 | 2052689 | 5293 | 127.032 | 5.293 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46709596 | 1208 | 228.226 | 0% | 0% | 100% | 100% | 100% | 75% | 10821527 | 573 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 2057852 | 5163 | 123.912 | 5.163 | 4.4 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46710824 | 1228 | 237.8462 | 0% | 0% | 100% | 100% | 100% | 75% | 10822313 | 786 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134249 | 134.249 | 134.249 | [12 empty] | 29988 | 29988 | 223.376 | [7 empty] | 4662 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (75%)

## MAY 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30404 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2057852 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46710824 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10822313 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 121 | 2062932 | 5080 | 121.92 | 5.08 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46712040 | 1216 | 239.3701 | 0% | 0% | 100% | 100% | 100% | 85% | 10823186 | 873 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 115 | 2067853 | 4921 | 118.104 | 4.921 | 7 | 7 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46713252 | 1212 | 246.2914 | 0% | 0% | 100% | 100% | 100% | 85% | 10824069 | 883 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 113 | 2072694 | 4841 | 116.184 | 4.841 | 8.7 | 8.7 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 46714420 | 1168 | 241.2725 | 0% | 0% | 100% | 100% | 100% | 85% | 10824863 | 794 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 142 | 117 | 2077333 | 4639 | 111.336 | 4.639 | 9.3 | 9.3 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 46715701 | 1281 | 276.1371 | 0% | 0% | 100% | 100% | 100% | 85% | 10825447 | 584 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 120 | 2081191 | 3858 | 92.592 | 3.858 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 46716952 | 1251 | 324.2613 | 0% | 0% | 100% | 100% | 100% | 85% | 10825593 | 146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 130 | 127 | 2086300 | 5109 | 122.616 | 5.109 | 9.5 | 9.5 | 3B | 0 | 0 | 1037 | 1185 | 1037 | N/A | N/A | N/A | N/A | 46717944 | 992 | 194.1672 | 0% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 142 | 2092014 | 5714 | 137.136 | 5.714 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46719156 | 1212 | 212.1106 | 0% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 146 | 2098104 | 6090 | 146.16 | 6.09 | 9.3 | 9.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46720492 | 1336 | 219.376 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 2104282 | 6178 | 148.272 | 6.178 | 8.8 | 8.8 | 3B+1S | 1058 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46721860 | 1368 | 221.4309 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 2110581 | 6299 | 151.176 | 6.299 | 8.2 | 8.2 | 3B+1S | 1058 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46723235 | 1375 | 218.2886 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 2116830 | 6249 | 149.976 | 6.249 | 7.6 | 7.6 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46724628 | 1393 | 222.9157 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 2122951 | 6121 | 146.904 | 6.121 | 7 | 7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46726000 | 1372 | 224.1464 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 2129090 | 6139 | 147.336 | 6.139 | 6.5 | 6.5 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46727368 | 1368 | 222.8376 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 2135207 | 6117 | 146.808 | 6.117 | 5.9 | 5.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46728740 | 1372 | 224.293 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 143 | 2141260 | 6053 | 145.272 | 6.053 | 5.4 | 5.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46730124 | 1384 | 228.647 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 146 | 2147259 | 5999 | 143.976 | 5.999 | 4.9 | 4.9 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46731468 | 1344 | 224.0373 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 149 | 2153262 | 6003 | 144.072 | 6.003 | 4.5 | 4.5 | 3B+1S | 1059 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46732836 | 1368 | 227.8861 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 143 | 2159321 | 6059 | 145.416 | 6.059 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46734180 | 1344 | 221.8188 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 2165357 | 6036 | 144.864 | 6.036 | 3.7 | 3.7 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46735524 | 1344 | 222.664 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 132 | 2171233 | 5876 | 141.024 | 5.876 | 3.5 | 3.5 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46736852 | 1328 | 226.0041 | 100% | 0% | 100% | 100% | 100% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 123 | 125 | 2176660 | 5427 | 130.248 | 5.427 | 3.2 | 3.2 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46737936 | 1084 | 199.742 | 100% | 0% | 100% | 100% | 0% | 0% | 10825593 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 127 | 2181872 | 5212 | 125.088 | 5.212 | 2.9 | 2.9 | 2B+1S | 1098 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46738996 | 1060 | 203.3768 | 100% | 0% | 100% | 100% | 0% | 0% | 10825593 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 126 | 2187111 | 5239 | 125.736 | 5.239 | 3.5 | 3.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46740124 | 1128 | 215.3083 | 0% | 0% | 100% | 100% | 100% | 75% | 10826106 | 513 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 2192121 | 5010 | 120.24 | 5.01 | 4.9 | 4.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46741228 | 1104 | 220.3593 | 0% | 0% | 100% | 100% | 100% | 75% | 10826620 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134269 | 134.269 | 134.269 | [12 empty] | 30404 | 30404 | 226.441 | [7 empty] | 4307 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (85%)
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (75%)

## MAY 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29392 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2192121 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46741228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10826620 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 110 | 2196813 | 4692 | 112.608 | 4.692 | 6 | 6 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46742220 | 992 | 211.4237 | 0% | 0% | 100% | 100% | 100% | 80% | 10827457 | 837 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 107 | 2201298 | 4485 | 107.64 | 4.485 | 7.9 | 7.9 | 3B | 0 | 0 | 1046 | 1185 | 1045 | N/A | N/A | N/A | N/A | 46743188 | 968 | 215.8305 | 0% | 0% | 100% | 100% | 100% | 80% | 10828265 | 808 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 109 | 2205799 | 4501 | 108.024 | 4.501 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46744152 | 964 | 214.1746 | 0% | 0% | 100% | 100% | 100% | 80% | 10829194 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 127 | 106 | 2210401 | 4602 | 110.448 | 4.602 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46745100 | 948 | 205.9974 | 0% | 0% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 117 | 2214350 | 3949 | 94.776 | 3.949 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1197 | N/A | N/A | N/A | N/A | 46746272 | 1172 | 296.784 | 0% | 0% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 133 | 2219687 | 5337 | 128.088 | 5.337 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46747324 | 1052 | 197.1145 | 0% | 0% | 100% | 100% | 100% | 0% | 10829194 | 0 | 1.3 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 2225669 | 5982 | 143.568 | 5.982 | 9.2 | 9.2 | 3B+1S | 0 | 997 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46748636 | 1312 | 219.3246 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 149 | 2231859 | 6190 | 148.56 | 6.19 | 8.7 | 8.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46749988 | 1352 | 218.4168 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 151 | 2238126 | 6267 | 150.408 | 6.267 | 8 | 8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46751384 | 1396 | 222.7541 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 152 | 2244425 | 6299 | 151.176 | 6.299 | 7.4 | 7.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46752772 | 1388 | 220.3524 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 | 1.26 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 2250697 | 6272 | 150.528 | 6.272 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46754156 | 1384 | 220.6633 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 145 | 2256982 | 6285 | 150.84 | 6.285 | 6.2 | 6.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46755540 | 1384 | 220.2068 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 144 | 2262904 | 5922 | 142.128 | 5.922 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46756884 | 1344 | 226.9504 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 145 | 2269242 | 6338 | 152.112 | 6.338 | 5.1 | 5.1 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46758308 | 1424 | 224.6766 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 144 | 2275222 | 5980 | 143.52 | 5.98 | 4.7 | 4.7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46759635 | 1327 | 221.9064 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 2281092 | 5870 | 140.88 | 5.87 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46760964 | 1329 | 226.4055 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 2287096 | 6004 | 144.096 | 6.004 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46762312 | 1348 | 224.517 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 141 | 2293294 | 6198 | 148.752 | 6.198 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46763656 | 1344 | 216.8441 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 134 | 2299132 | 5838 | 140.112 | 5.838 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46764984 | 1328 | 227.4752 | 0% | 100% | 100% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 137 | 2304749 | 5617 | 134.808 | 5.617 | 2.4 | 2.4 | 3B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46766120 | 1136 | 202.2432 | 0% | 100% | 0% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 131 | 2310277 | 5528 | 132.672 | 5.528 | 1.6 | 1.6 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46767208 | 1088 | 196.8162 | 0% | 100% | 0% | 100% | 100% | 0% | 10829194 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 129 | 2315476 | 5199 | 124.776 | 5.199 | 1.3 | 1.3 | 2B+1S | 0 | 1016 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46768228 | 1020 | 196.1916 | 0% | 100% | 0% | 100% | 100% | 0% | 10829194 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 131 | 2320961 | 5485 | 131.64 | 5.485 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46769468 | 1240 | 226.0711 | 0% | 0% | 100% | 100% | 100% | 80% | 10829542 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 143 | 118 | 2326006 | 5045 | 121.08 | 5.045 | 2.2 | 4.1 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46770620 | 1152 | 228.3449 | 0% | 0% | 100% | 100% | 100% | 80% | 10830201 | 659 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133885 | 133.885 | 133.885 | [12 empty] | 29392 | 29392 | 219.5317 | [7 empty] | 3581 | 1.1933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (80%)
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (80%)

## MAY 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29652 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2326006 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46770620 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10830201 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 108 | 2330374 | 4368 | 104.832 | 4.368 | 4.9 | 4.9 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 46771690 | 1070 | 244.9634 | 0% | 0% | 100% | 100% | 100% | 90% | 10831078 | 877 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 115 | 2334694 | 4320 | 103.68 | 4.32 | 7.3 | 7.3 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 46772769 | 1079 | 249.7685 | 0% | 0% | 100% | 100% | 100% | 90% | 10832100 | 1022 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 110 | 2338999 | 4305 | 103.32 | 4.305 | 8.9 | 8.9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46773864 | 1095 | 254.3554 | 0% | 0% | 100% | 100% | 100% | 90% | 10833197 | 1097 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 116 | 2343540 | 4541 | 108.984 | 4.541 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46775052 | 1188 | 261.6164 | 0% | 0% | 100% | 100% | 100% | 90% | 10833397 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 114 | 2348329 | 4789 | 114.936 | 4.789 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46776100 | 1048 | 218.8348 | 0% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 134 | 127 | 2353622 | 5293 | 127.032 | 5.293 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46777160 | 1060 | 200.2645 | 0% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 145 | 2359885 | 6263 | 150.312 | 6.263 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46778560 | 1400 | 223.535 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 146 | 2366099 | 6214 | 149.136 | 6.214 | 8.6 | 8.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46779936 | 1376 | 221.4355 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 148 | 2372301 | 6202 | 148.848 | 6.202 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46781324 | 1388 | 223.7988 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 150 | 2378626 | 6325 | 151.8 | 6.325 | 7.4 | 7.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46782708 | 1384 | 218.8142 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 | 1.23 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 2384903 | 6277 | 150.648 | 6.277 | 6.8 | 6.8 | 3B+1S | 1057 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46784092 | 1384 | 220.4875 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 2391001 | 6098 | 146.352 | 6.098 | 6.2 | 6.2 | 3B+1S | 1098 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46785476 | 1384 | 226.9597 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 2397098 | 6097 | 146.328 | 6.097 | 5.4 | 5.4 | 3B+1S | 1098 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46786860 | 1384 | 226.9969 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 2402928 | 5830 | 139.92 | 5.83 | 5 | 5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46788200 | 1340 | 229.8456 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 137 | 2408984 | 6056 | 145.344 | 6.056 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46789556 | 1356 | 223.9102 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 2414664 | 5680 | 136.32 | 5.68 | 4.3 | 4.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46790856 | 1300 | 228.8732 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 140 | 2420506 | 5842 | 140.208 | 5.842 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46792212 | 1356 | 232.1123 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 2426394 | 5888 | 141.312 | 5.888 | 3.5 | 3.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46793556 | 1344 | 228.2609 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 2432386 | 5992 | 143.808 | 5.992 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46794920 | 1364 | 227.6368 | 100% | 0% | 100% | 100% | 100% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 128 | 2437784 | 5398 | 129.552 | 5.398 | 2.6 | 2.6 | 2B+1S | 1027 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46795980 | 1060 | 196.369 | 100% | 0% | 100% | 100% | 0% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 117 | 134 | 2443066 | 5282 | 126.768 | 5.282 | 2 | 2 | 2B+1S | 1027 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46797012 | 1032 | 195.3805 | 100% | 0% | 100% | 100% | 0% | 0% | 10833397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 123 | 2448514 | 5448 | 130.752 | 5.448 | 1.7 | 1.7 | 2B+1S | 1027 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46798084 | 1072 | 196.7695 | 100% | 0% | 100% | 100% | 0% | 0% | 10833397 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 125 | 2453601 | 5087 | 122.088 | 5.087 | 2.9 | 2.9 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 46799164 | 1080 | 212.3059 | 0% | 0% | 100% | 100% | 100% | 70% | 10833956 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 117 | 2458728 | 5127 | 123.048 | 5.127 | 3.8 | 3.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46800272 | 1108 | 216.1108 | 0% | 0% | 100% | 100% | 100% | 70% | 10834537 | 581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132722 | 132.722 | 132.722 | [12 empty] | 29652 | 29652 | 223.4144 | [7 empty] | 4336 | 1.15 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (90%)
XCV1- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (70%)

## MAY 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29516 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2458728 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46800272 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10834537 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 115 | 2463377 | 4649 | 111.576 | 4.649 | 5.6 | 5.6 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46801292 | 1020 | 219.402 | 0% | 0% | 100% | 100% | 100% | 75% | 10835099 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 112 | 2468039 | 4662 | 111.888 | 4.662 | 6.9 | 6.9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46802336 | 1044 | 223.9382 | 0% | 0% | 100% | 100% | 100% | 75% | 10835834 | 735 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 111 | 2472712 | 4673 | 112.152 | 4.673 | 8.4 | 8.4 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46803384 | 1048 | 224.2671 | 0% | 0% | 100% | 100% | 100% | 75% | 10836752 | 918 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 123 | 2475864 | 3152 | 75.648 | 3.152 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46804604 | 1220 | 387.0558 | 0% | 0% | 100% | 100% | 100% | 75% | 10837518 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 113 | 2480626 | 4762 | 114.288 | 4.762 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46805676 | 1072 | 225.1155 | 0% | 0% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 134 | 2485862 | 5236 | 125.664 | 5.236 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46806752 | 1076 | 205.5004 | 0% | 0% | 100% | 100% | 100% | 0% | 10837518 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 147 | 2491842 | 5980 | 143.52 | 5.98 | 9.3 | 9.3 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46808076 | 1324 | 221.4047 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 2497978 | 6136 | 147.264 | 6.136 | 8.8 | 8.8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46809444 | 1368 | 222.9465 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 2504079 | 6101 | 146.424 | 6.101 | 8.2 | 8.2 | 3B+1S | 0 | 1058 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46810820 | 1376 | 225.5368 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 2510143 | 6064 | 145.536 | 6.064 | 7.6 | 7.6 | 3B+1S | 0 | 1058 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46812180 | 1360 | 224.2744 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 | 1.28 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 2516221 | 6078 | 145.872 | 6.078 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46813548 | 1368 | 225.074 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 2522422 | 6201 | 148.824 | 6.201 | 6.6 | 6.6 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46814928 | 1380 | 222.5448 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 144 | 2528498 | 6076 | 145.824 | 6.076 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46816284 | 1356 | 223.1731 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 2534354 | 5856 | 140.544 | 5.856 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46817628 | 1344 | 229.5082 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 2540377 | 6023 | 144.552 | 6.023 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46819004 | 1376 | 228.4576 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 2546262 | 5885 | 141.24 | 5.885 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46820340 | 1336 | 227.0178 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 2551996 | 5734 | 137.616 | 5.734 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46821644 | 1304 | 227.4154 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 132 | 2557834 | 5838 | 140.112 | 5.838 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46822992 | 1348 | 230.901 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 2563954 | 6120 | 146.88 | 6.12 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46824374 | 1382 | 225.817 | 0% | 100% | 100% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 126 | 2569182 | 5228 | 125.472 | 5.228 | 3.2 | 3.2 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46825436 | 1062 | 203.137 | 0% | 100% | 0% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 127 | 2574604 | 5422 | 130.128 | 5.422 | 2.5 | 2.5 | 2B+1S | 0 | 1046 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46826516 | 1080 | 199.1885 | 0% | 100% | 0% | 100% | 100% | 0% | 10837518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 130 | 124 | 2579863 | 5259 | 126.216 | 5.259 | 2.3 | 2.3 | 2B+1S | 0 | 1047 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46827584 | 1068 | 203.0804 | 0% | 100% | 0% | 100% | 100% | 0% | 10837518 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 118 | 2585047 | 5184 | 124.416 | 5.184 | 3.7 | 3.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46828720 | 1136 | 219.1358 | 0% | 0% | 100% | 100% | 100% | 75% | 10838227 | 709 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 146 | 113 | 2589881 | 4834 | 116.016 | 4.834 | 4.9 | 4.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46829788 | 1068 | 220.935 | 0% | 0% | 100% | 100% | 100% | 75% | 10838973 | 746 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131153 | 131.153 | 131.153 | [12 empty] | 29516 | 29516 | 225.0501 | [7 empty] | 4436 | 1.08 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (75%)

## MAY 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29232 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2589881 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46829788 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10838973 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 139 | 113 | 2594658 | 4777 | 114.648 | 4.777 | 6.2 | 6.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46830836 | 1048 | 219.3846 | 0% | 0% | 100% | 100% | 100% | 80% | 10839779 | 806 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 112 | 2599258 | 4600 | 110.4 | 4.6 | 7.5 | 7.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46831974 | 1138 | 247.3913 | 0% | 0% | 100% | 100% | 100% | 80% | 10840563 | 784 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 115 | 2602863 | 3605 | 86.52 | 3.605 | 8.7 | 8.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46833036 | 1062 | 294.5908 | 0% | 0% | 100% | 100% | 100% | 80% | 10841360 | 797 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 | 112 | 2607460 | 4597 | 110.328 | 4.597 | 9.5 | 9.5 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 46834044 | 1008 | 219.2734 | 0% | 0% | 100% | 100% | 100% | 80% | 10842026 | 666 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 113 | 2612256 | 4796 | 115.104 | 4.796 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46835104 | 1060 | 221.0175 | 0% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 130 | 2617337 | 5081 | 121.944 | 5.081 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46836008 | 904 | 177.9177 | 0% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 | 1.37 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 141 | 2623278 | 5941 | 142.584 | 5.941 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46837340 | 1332 | 224.2047 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 2629427 | 6149 | 147.576 | 6.149 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46838732 | 1392 | 226.3783 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 2635702 | 6275 | 150.6 | 6.275 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46840148 | 1416 | 225.6574 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 2641699 | 5997 | 143.928 | 5.997 | 7.4 | 7.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46841484 | 1336 | 222.7781 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 | 1.28 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 2647889 | 6190 | 148.56 | 6.19 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46842880 | 1396 | 225.525 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 2653885 | 5996 | 143.904 | 5.996 | 6.2 | 6.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46844244 | 1364 | 227.485 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 140 | 2659927 | 6042 | 145.008 | 6.042 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46845612 | 1368 | 226.4151 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 2665934 | 6007 | 144.168 | 6.007 | 5.1 | 5.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46846968 | 1356 | 225.7366 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 2671846 | 5912 | 141.888 | 5.912 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46848312 | 1344 | 227.3342 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 146 | 2677808 | 5962 | 143.088 | 5.962 | 4.4 | 4.4 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46849668 | 1356 | 227.4405 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 141 | 2683526 | 5718 | 137.232 | 5.718 | 4 | 4 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46850964 | 1296 | 226.6527 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 134 | 2689506 | 5980 | 143.52 | 5.98 | 3.6 | 3.6 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46852332 | 1368 | 228.7625 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 2695366 | 5860 | 140.64 | 5.86 | 3.3 | 3.3 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46853684 | 1352 | 230.7167 | 100% | 0% | 100% | 100% | 100% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 134 | 2700772 | 5406 | 129.744 | 5.406 | 2.6 | 2.6 | 2B+1S | 1047 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46854788 | 1104 | 204.2175 | 100% | 0% | 100% | 100% | 0% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 122 | 2706172 | 5400 | 129.6 | 5.4 | 2 | 2 | 2B+1S | 1027 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46855856 | 1068 | 197.7778 | 100% | 0% | 100% | 100% | 0% | 0% | 10842026 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 134 | 120 | 2711350 | 5178 | 124.272 | 5.178 | 1.8 | 1.8 | 2B+1S | 1027 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46856892 | 1036 | 200.0772 | 100% | 0% | 100% | 100% | 0% | 0% | 10842026 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 119 | 2716286 | 4936 | 118.464 | 4.936 | 2.9 | 2.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46857952 | 1060 | 214.7488 | 0% | 0% | 100% | 100% | 100% | 75% | 10842537 | 511 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 147 | 116 | 2721159 | 4873 | 116.952 | 4.873 | 4 | 4.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46859020 | 1068 | 219.1668 | 0% | 0% | 100% | 100% | 100% | 75% | 10843233 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131278 | 131.278 | 131.278 | [12 empty] | 29232 | 29232 | 222.6725 | [7 empty] | 4260 | 1.255 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (75%)

## MAY 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29044 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2721159 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46859020 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10843233 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 114 | 2725883 | 4724 | 113.376 | 4.724 | 5.9 | 5.9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46860092 | 1072 | 226.9263 | 0% | 0% | 100% | 100% | 100% | 80% | 10843973 | 740 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 108 | 2730390 | 4507 | 108.168 | 4.507 | 6.7 | 6.7 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46861044 | 952 | 211.227 | 0% | 0% | 100% | 100% | 100% | 80% | 10844969 | 996 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 106 | 2734854 | 4464 | 107.136 | 4.464 | 8.6 | 8.6 | 3B | 0 | 0 | 1046 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46862020 | 976 | 218.638 | 0% | 0% | 100% | 100% | 100% | 80% | 10845951 | 982 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 | 110 | 2738145 | 3291 | 78.984 | 3.291 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46863108 | 1088 | 330.5986 | 0% | 0% | 100% | 100% | 100% | 80% | 10846957 | 1006 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 112 | 2742942 | 4797 | 115.128 | 4.797 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 46864096 | 988 | 205.9621 | 0% | 0% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 131 | 2748168 | 5226 | 125.424 | 5.226 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46865116 | 1020 | 195.178 | 0% | 0% | 100% | 100% | 100% | 0% | 10846957 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 2754043 | 5875 | 141 | 5.875 | 9.2 | 9.2 | 3B+1S | 0 | 1058 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46866424 | 1308 | 222.6383 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 2760147 | 6104 | 146.496 | 6.104 | 8.6 | 8.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46867796 | 1372 | 224.7706 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 140 | 2766271 | 6124 | 146.976 | 6.124 | 8 | 8 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46869164 | 1368 | 223.3834 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 2772486 | 6215 | 149.16 | 6.215 | 7.3 | 7.3 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46870556 | 1392 | 223.9743 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 | 1.22 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 2778740 | 6254 | 150.096 | 6.254 | 6.6 | 6.6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46871948 | 1392 | 222.5776 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 2784832 | 6092 | 146.208 | 6.092 | 6 | 6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46873316 | 1368 | 224.5568 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 146 | 2790844 | 6012 | 144.288 | 6.012 | 5.4 | 5.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46874680 | 1364 | 226.8796 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 2796652 | 5808 | 139.392 | 5.808 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46876012 | 1332 | 229.3388 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 2802584 | 5932 | 142.368 | 5.932 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46877364 | 1352 | 227.9164 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 2808392 | 5808 | 139.392 | 5.808 | 4.1 | 4.1 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46878700 | 1336 | 230.0275 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 141 | 2814222 | 5830 | 139.92 | 5.83 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46880044 | 1344 | 230.5317 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 2820044 | 5822 | 139.728 | 5.822 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46881388 | 1344 | 230.8485 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 | 0.71 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 2826068 | 6024 | 144.576 | 6.024 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46882760 | 1372 | 227.7556 | 0% | 100% | 100% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 129 | 2831342 | 5274 | 126.576 | 5.274 | 2.5 | 2.5 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46883820 | 1060 | 200.986 | 0% | 100% | 0% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 126 | 2836652 | 5310 | 127.44 | 5.31 | 1.8 | 1.8 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46884876 | 1056 | 198.8701 | 0% | 100% | 0% | 100% | 100% | 0% | 10846957 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 137 | 122 | 2841993 | 5341 | 128.184 | 5.341 | 1.5 | 1.5 | 2B+1S | 0 | 995 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46885940 | 1064 | 199.2136 | 0% | 100% | 0% | 100% | 100% | 0% | 10846957 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 116 | 2846942 | 4949 | 118.776 | 4.949 | 3 | 3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46887004 | 1064 | 214.9929 | 0% | 0% | 100% | 100% | 100% | 75% | 10847891 | 934 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 115 | 2851828 | 4886 | 117.264 | 4.886 | 4.5 | 4.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46888064 | 1060 | 216.9464 | 0% | 0% | 100% | 100% | 100% | 75% | 10848451 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130669 | 130.669 | 130.669 | [12 empty] | 29044 | 29044 | 222.2715 | [7 empty] | 5218 | 1.0867 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (80%)
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (75%)

## MAY 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29644 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2851828 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46888064 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10848451 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 112 | 2856629 | 4801 | 115.224 | 4.801 | 6 | 6 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46889128 | 1064 | 221.6205 | 0% | 0% | 100% | 100% | 100% | 80% | 10849368 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 109 | 2861232 | 4603 | 110.472 | 4.603 | 7.4 | 7.4 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46890172 | 1044 | 226.8086 | 0% | 0% | 100% | 100% | 100% | 80% | 10850117 | 749 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 110 | 2865837 | 4605 | 110.52 | 4.605 | 8.6 | 8.6 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46891212 | 1040 | 225.8415 | 0% | 0% | 100% | 100% | 100% | 80% | 10850988 | 871 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 116 | 2869260 | 3423 | 82.152 | 3.423 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46892348 | 1136 | 331.8726 | 0% | 0% | 100% | 100% | 100% | 80% | 10851905 | 917 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 115 | 2874157 | 4897 | 117.528 | 4.897 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46893412 | 1064 | 217.2759 | 0% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 134 | 125 | 2879146 | 4989 | 119.736 | 4.989 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 46894380 | 968 | 194.0269 | 0% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 141 | 2885005 | 5859 | 140.616 | 5.859 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46895708 | 1328 | 226.6598 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 146 | 2891177 | 6172 | 148.128 | 6.172 | 8.8 | 8.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46897076 | 1368 | 221.6461 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 147 | 2897235 | 6058 | 145.392 | 6.058 | 8.3 | 8.3 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46898432 | 1356 | 223.8362 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 2903407 | 6172 | 148.128 | 6.172 | 7.8 | 7.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46899800 | 1368 | 221.6461 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 | 1.29 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 2909682 | 6275 | 150.6 | 6.275 | 7.2 | 7.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46901188 | 1388 | 221.1952 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 2915760 | 6078 | 145.872 | 6.078 | 6.7 | 6.7 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46902556 | 1368 | 225.074 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 144 | 2921732 | 5972 | 143.328 | 5.972 | 6.1 | 6.1 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46903932 | 1376 | 230.4086 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 2927646 | 5914 | 141.936 | 5.914 | 5.4 | 5.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46905300 | 1368 | 231.3155 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 147 | 2933605 | 5959 | 143.016 | 5.959 | 5 | 5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46906660 | 1360 | 228.2262 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 2939457 | 5852 | 140.448 | 5.852 | 4.6 | 4.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46908000 | 1340 | 228.9815 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 2945260 | 5803 | 139.272 | 5.803 | 4.2 | 4.2 | 3B+1S | 1058 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46909340 | 1340 | 230.915 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 2951052 | 5792 | 139.008 | 5.792 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46910684 | 1344 | 232.0442 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 2956853 | 5801 | 139.224 | 5.801 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46912020 | 1336 | 230.3051 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 136 | 2962675 | 5822 | 139.728 | 5.822 | 3.1 | 3.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46913372 | 1352 | 232.2226 | 100% | 0% | 100% | 100% | 100% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 131 | 2967995 | 5320 | 127.68 | 5.32 | 2.6 | 2.6 | 2B+1S | 1079 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 46914420 | 1048 | 196.9925 | 100% | 0% | 100% | 100% | 0% | 0% | 10851905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 125 | 2973162 | 5167 | 124.008 | 5.167 | 2.3 | 2.3 | 2B+1S | 1048 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 46915480 | 1060 | 205.1481 | 100% | 0% | 100% | 100% | 0% | 0% | 10851905 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 124 | 2978328 | 5166 | 123.984 | 5.166 | 3.7 | 3.7 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46916636 | 1156 | 223.7708 | 0% | 0% | 100% | 100% | 100% | 75% | 10852567 | 662 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 116 | 2983232 | 4904 | 117.696 | 4.904 | 4.5 | 4.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46917708 | 1072 | 218.5971 | 0% | 0% | 100% | 100% | 100% | 75% | 10853218 | 651 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131404 | 131.404 | 131.404 | [12 empty] | 29644 | 29644 | 225.5944 | [7 empty] | 4767 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (75%)

## MAY 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29204 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 2983232 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46917708 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10853218 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 112 | 2988082 | 4850 | 116.4 | 4.85 | 6.3 | 6.3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46918800 | 1092 | 225.1546 | 0% | 0% | 100% | 100% | 100% | 80% | 10853865 | 647 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 111 | 2992794 | 4712 | 113.088 | 4.712 | 7.7 | 7.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46919820 | 1020 | 216.4686 | 0% | 0% | 100% | 100% | 100% | 80% | 10854520 | 655 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 109 | 2997274 | 4480 | 107.52 | 4.48 | 8.4 | 8.4 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 46920796 | 976 | 217.8571 | 0% | 0% | 100% | 100% | 100% | 80% | 10855390 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 | 110 | 3000698 | 3424 | 82.176 | 3.424 | 9.5 | 9.5 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 46921900 | 1104 | 322.4299 | 0% | 0% | 100% | 100% | 100% | 80% | 10856375 | 985 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 | 113 | 3005372 | 4674 | 112.176 | 4.674 | 9.5 | 9.5 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 46922900 | 1000 | 213.9495 | 0% | 0% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 134 | 130 | 3010670 | 5298 | 127.152 | 5.298 | 9.5 | 9.5 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 46923940 | 1040 | 196.3005 | 0% | 0% | 100% | 100% | 100% | 0% | 10856375 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 150 | 140 | 3016443 | 5773 | 138.552 | 5.773 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46925172 | 1232 | 213.4072 | 0% | 0% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 135 | 3022577 | 6134 | 147.216 | 6.134 | 9.3 | 9.3 | 3B+1S | 0 | 975 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46926508 | 1336 | 217.8024 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 3028776 | 6199 | 148.776 | 6.199 | 9 | 9 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46927876 | 1368 | 220.6808 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 142 | 3034992 | 6216 | 149.184 | 6.216 | 8.3 | 8.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46929272 | 1396 | 224.5817 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 3041050 | 6058 | 145.392 | 6.058 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46930620 | 1348 | 222.5157 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 3047092 | 6042 | 145.008 | 6.042 | 7.2 | 7.2 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46931996 | 1376 | 227.7392 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 143 | 3053150 | 6058 | 145.392 | 6.058 | 6.7 | 6.7 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46933368 | 1372 | 226.4774 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 149 | 3058956 | 5806 | 139.344 | 5.806 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46934712 | 1344 | 231.4847 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 3065024 | 6068 | 145.632 | 6.068 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46936068 | 1356 | 223.4674 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 3070968 | 5944 | 142.656 | 5.944 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46937436 | 1368 | 230.148 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 3076800 | 5832 | 139.968 | 5.832 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46938776 | 1340 | 229.7668 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 3082522 | 5722 | 137.328 | 5.722 | 4.5 | 4.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46940100 | 1324 | 231.3876 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 | 1.38 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 3088202 | 5680 | 136.32 | 5.68 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46941412 | 1312 | 230.9859 | 0% | 100% | 100% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 128 | 3093628 | 5426 | 130.224 | 5.426 | 3.5 | 3.5 | 2B+1S | 0 | 1046 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46942532 | 1120 | 206.4136 | 0% | 100% | 0% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 131 | 3099112 | 5484 | 131.616 | 5.484 | 2.7 | 2.7 | 2B+1S | 0 | 1078 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46943632 | 1100 | 200.5835 | 0% | 100% | 0% | 100% | 100% | 0% | 10856375 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 139 | 120 | 3104314 | 5202 | 124.848 | 5.202 | 2.5 | 2.5 | 2B+1S | 0 | 1048 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46944700 | 1068 | 205.3057 | 0% | 100% | 0% | 100% | 100% | 0% | 10856375 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 141 | 122 | 3109471 | 5157 | 123.768 | 5.157 | 3.9 | 3.9 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 46945844 | 1144 | 221.8344 | 0% | 0% | 100% | 100% | 100% | 75% | 10857296 | 921 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 145 | 115 | 3114320 | 4849 | 116.376 | 4.849 | 4.8 | 4.8 | 3B | 0 | 0 | 1047 | 1185 | 147 | N/A | N/A | N/A | N/A | 46946912 | 1068 | 220.2516 | 0% | 0% | 100% | 100% | 100% | 75% | 10857905 | 609 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131088 | 131.088 | 131.088 | [12 empty] | 29204 | 29204 | 222.7816 | [7 empty] | 4687 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (80%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (75%)

## MAY 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29604 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3114320 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46946912 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10857905 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 114 | 3119169 | 4849 | 116.376 | 4.849 | 6.4 | 6.4 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46947987 | 1075 | 221.6952 | 0% | 0% | 100% | 100% | 100% | 80% | 10858802 | 897 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 112 | 3123894 | 4725 | 113.4 | 4.725 | 7.3 | 7.3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46949028 | 1041 | 220.3175 | 0% | 0% | 100% | 100% | 100% | 80% | 10859569 | 767 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 123 | 110 | 3128562 | 4668 | 112.032 | 4.668 | 8.6 | 8.6 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46950076 | 1048 | 224.5073 | 0% | 0% | 100% | 100% | 100% | 80% | 10860397 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 | 113 | 3132159 | 3597 | 86.328 | 3.597 | 9.5 | 9.5 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 46951172 | 1096 | 304.6984 | 0% | 0% | 100% | 100% | 100% | 80% | 10861181 | 784 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 116 | 3137036 | 4877 | 117.048 | 4.877 | 9.5 | 9.5 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 46952196 | 1024 | 209.9651 | 0% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 131 | 3142340 | 5304 | 127.296 | 5.304 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46953260 | 1064 | 200.6033 | 0% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 146 | 3148295 | 5955 | 142.92 | 5.955 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46954580 | 1320 | 221.6625 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 3154445 | 6150 | 147.6 | 6.15 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46955900 | 1320 | 214.6341 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 3160519 | 6074 | 145.776 | 6.074 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46957296 | 1396 | 229.8321 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 147 | 3166707 | 6188 | 148.512 | 6.188 | 7.9 | 7.9 | 3B+1S | 1037 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46958668 | 1372 | 221.7195 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 | 1.21 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 148 | 3172903 | 6196 | 148.704 | 6.196 | 7.4 | 7.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46960036 | 1368 | 220.7876 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 3178916 | 6013 | 144.312 | 6.013 | 6.9 | 6.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46961396 | 1360 | 226.1766 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 144 | 3184917 | 6001 | 144.024 | 6.001 | 6.4 | 6.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46962752 | 1356 | 225.9623 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 3190715 | 5798 | 139.152 | 5.798 | 5.8 | 5.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46964088 | 1336 | 230.4243 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 3196704 | 5989 | 143.736 | 5.989 | 5.4 | 5.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46965452 | 1364 | 227.7509 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 3202562 | 5858 | 140.592 | 5.858 | 5 | 5 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46966796 | 1344 | 229.4298 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 3208522 | 5960 | 143.04 | 5.96 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46968148 | 1352 | 226.8456 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 3214222 | 5700 | 136.8 | 5.7 | 4.2 | 4.2 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46969460 | 1312 | 230.1754 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 3220156 | 5934 | 142.416 | 5.934 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46970828 | 1368 | 230.5359 | 100% | 0% | 100% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 132 | 3225674 | 5518 | 132.432 | 5.518 | 2.9 | 2.9 | 2B+1S | 1099 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46971940 | 1112 | 201.5223 | 100% | 0% | 0% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 130 | 3231152 | 5478 | 131.472 | 5.478 | 2.1 | 2.1 | 2B+1S | 1099 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46973036 | 1096 | 200.073 | 100% | 0% | 0% | 100% | 100% | 0% | 10861181 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 120 | 124 | 3236328 | 5176 | 124.224 | 5.176 | 1.5 | 1.5 | 2B+1S | 1099 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46974080 | 1044 | 201.7002 | 100% | 0% | 0% | 100% | 100% | 0% | 10861181 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 123 | 3241660 | 5332 | 127.968 | 5.332 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46975312 | 1232 | 231.0578 | 0% | 0% | 100% | 100% | 100% | 80% | 10861691 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 124 | 3246824 | 5164 | 123.936 | 5.164 | 2.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46976516 | 1204 | 233.1526 | 0% | 0% | 100% | 100% | 100% | 80% | 10862380 | 689 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132504 | 132.504 | 132.504 | [12 empty] | 29604 | 29604 | 223.4197 | [7 empty] | 4475 | 1.104 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (80%)

## MAY 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-05-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30184 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3246824 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 46976516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10862380 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 143 | 115 | 3251428 | 4604 | 110.496 | 4.604 | 3.9 | 3.9 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46977736 | 1220 | 264.987 | 0% | 0% | 100% | 100% | 100% | 83% | 10863083 | 703 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 110 | 3256020 | 4592 | 110.208 | 4.592 | 5.8 | 5.8 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 46978857 | 1121 | 244.1202 | 0% | 0% | 100% | 100% | 100% | 83% | 10863869 | 786 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 113 | 3260638 | 4618 | 110.832 | 4.618 | 8.3 | 8.3 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 46979996 | 1139 | 246.6436 | 0% | 0% | 100% | 100% | 100% | 83% | 10864592 | 723 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 116 | 3265256 | 4618 | 110.832 | 4.618 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 46981244 | 1248 | 270.2469 | 0% | 0% | 100% | 100% | 100% | 83% | 10865048 | 456 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 | 117 | 3269923 | 4667 | 112.008 | 4.667 | 9.5 | 9.5 | 3B | 0 | 0 | 1078 | 1185 | 1077 | N/A | N/A | N/A | N/A | 46982392 | 1148 | 245.9824 | 0% | 0% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 | 136 | 3275168 | 5245 | 125.88 | 5.245 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 46983476 | 1084 | 206.673 | 0% | 0% | 100% | 100% | 100% | 0% | 10865048 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 144 | 3281500 | 6332 | 151.968 | 6.332 | 9.1 | 9.1 | 3B+1S | 0 | 1049 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46984859 | 1383 | 218.4144 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 3287675 | 6175 | 148.2 | 6.175 | 8.6 | 8.6 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46986268 | 1409 | 228.1781 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 3293794 | 6119 | 146.856 | 6.119 | 8.1 | 8.1 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46987636 | 1368 | 223.5659 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 3300025 | 6231 | 149.544 | 6.231 | 7.5 | 7.5 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46989020 | 1384 | 222.1152 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 | 1.31 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 3306192 | 6167 | 148.008 | 6.167 | 7 | 7 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46990396 | 1376 | 223.1231 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 140 | 3312132 | 5940 | 142.56 | 5.94 | 6.3 | 6.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 46991772 | 1376 | 231.6498 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 139 | 3317966 | 5834 | 140.016 | 5.834 | 5.7 | 5.7 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46993128 | 1356 | 232.4306 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 138 | 3323702 | 5736 | 137.664 | 5.736 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46994452 | 1324 | 230.8229 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 139 | 3329604 | 5902 | 141.648 | 5.902 | 4.9 | 4.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 46995796 | 1344 | 227.7194 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 3335584 | 5980 | 143.52 | 5.98 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46997156 | 1360 | 227.4247 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 3341438 | 5854 | 140.496 | 5.854 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46998488 | 1332 | 227.5367 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 145 | 3347056 | 5618 | 134.832 | 5.618 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46999788 | 1300 | 231.3991 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 | 1.38 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 3352877 | 5821 | 139.704 | 5.821 | 3.5 | 3.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47001124 | 1336 | 229.5138 | 0% | 100% | 100% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 128 | 3358340 | 5463 | 131.112 | 5.463 | 2.9 | 2.9 | 2B+1S | 0 | 1047 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47002240 | 1116 | 204.2834 | 0% | 100% | 0% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 130 | 3363683 | 5343 | 128.232 | 5.343 | 2.2 | 2.2 | 2B+1S | 0 | 1068 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47003308 | 1068 | 199.8877 | 0% | 100% | 0% | 100% | 100% | 0% | 10865048 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 | 126 | 3369039 | 5356 | 128.544 | 5.356 | 2 | 2 | 2B+1S | 0 | 1069 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47004404 | 1096 | 204.6303 | 0% | 100% | 0% | 100% | 100% | 0% | 10865048 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 123 | 3374181 | 5142 | 123.408 | 5.142 | 3 | 3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47005564 | 1160 | 225.5932 | 0% | 0% | 100% | 100% | 100% | 80% | 10865932 | 884 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 119 | 3379152 | 4971 | 119.304 | 4.971 | 4.5 | 4.5 | 3B | 0 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 47006700 | 1136 | 228.5254 | 0% | 0% | 100% | 100% | 100% | 80% | 10866489 | 557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132328 | 132.328 | 132.328 | [12 empty] | 30184 | 30184 | 228.0999 | [7 empty] | 4109 | 1.2383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (83%)
XCV2- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (MAY 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (80%)