## JUNE 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29664 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3379152 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47006700 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10866489 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 113 | 3383794 | 4642 | 111.408 | 4.642 | 5.9 | 5.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 47007748 | 1048 | 225.7648 | 0% | 0% | 100% | 100% | 100% | 85% | 10867165 | 676 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 111 | 3388455 | 4661 | 111.864 | 4.661 | 7.4 | 7.4 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47008788 | 1040 | 223.1281 | 0% | 0% | 100% | 100% | 100% | 85% | 10868151 | 986 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 109 | 3393034 | 4579 | 109.896 | 4.579 | 8.6 | 8.6 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47009828 | 1040 | 227.1238 | 0% | 0% | 100% | 100% | 100% | 85% | 10869054 | 903 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 112 | 3396566 | 3532 | 84.768 | 3.532 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47010964 | 1136 | 321.6308 | 0% | 0% | 100% | 100% | 100% | 85% | 10869847 | 793 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 114 | 3401993 | 5427 | 130.248 | 5.427 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47012028 | 1064 | 196.0568 | 0% | 0% | 100% | 100% | 100% | 85% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 126 | 3406537 | 4544 | 109.056 | 4.544 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47013052 | 1024 | 225.3521 | 0% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 | 1.37 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 3412445 | 5908 | 141.792 | 5.908 | 9.3 | 9.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47014388 | 1336 | 226.1341 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 3418613 | 6168 | 148.032 | 6.168 | 8.6 | 8.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47015772 | 1384 | 224.3839 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 143 | 3424837 | 6224 | 149.376 | 6.224 | 8 | 8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47017140 | 1368 | 219.7943 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 3431080 | 6243 | 149.832 | 6.243 | 7.3 | 7.3 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47018540 | 1400 | 224.2512 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 | 1.24
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 3437239 | 6159 | 147.816 | 6.159 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47019908 | 1368 | 222.114 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 3443320 | 6081 | 145.944 | 6.081 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47021276 | 1368 | 224.963 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 3449225 | 5905 | 141.72 | 5.905 | 5.6 | 5.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47022636 | 1360 | 230.3133 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 140 | 3455202 | 5977 | 143.448 | 5.977 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47024004 | 1368 | 228.8774 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 139 | 3461038 | 5836 | 140.064 | 5.836 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47025328 | 1324 | 226.8677 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 3466926 | 5888 | 141.312 | 5.888 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47026660 | 1332 | 226.2228 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 3472775 | 5849 | 140.376 | 5.849 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47027988 | 1328 | 227.0474 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 3478574 | 5799 | 139.176 | 5.799 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47029320 | 1332 | 229.6948 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 140 | 3484422 | 5848 | 140.352 | 5.848 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47030644 | 1324 | 226.4022 | 100% | 0% | 100% | 100% | 100% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 135 | 3489948 | 5526 | 132.624 | 5.526 | 2.9 | 2.9 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47031760 | 1116 | 201.9544 | 100% | 0% | 100% | 100% | 0% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 129 | 3495622 | 5674 | 136.176 | 5.674 | 2.2 | 2.2 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47032872 | 1112 | 195.9817 | 100% | 0% | 100% | 100% | 0% | 0% | 10869847 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 | 122 | 3500792 | 5170 | 124.08 | 5.17 | 2 | 2 | 2B+1S | 1097 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 47033932 | 1060 | 205.029 | 100% | 0% | 100% | 100% | 0% | 0% | 10869847 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 139 | 124 | 3506164 | 5372 | 128.928 | 5.372 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47035156 | 1224 | 227.8481 | 0% | 0% | 100% | 100% | 100% | 65% | 10871002 | 1155 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 168 | 123 | 3511256 | 5092 | 122.208 | 5.092 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47036364 | 1208 | 237.2349 | 0% | 0% | 100% | 100% | 100% | 65% | 10871799 | 797 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132104 | 132.104 | 132.104 | [12 empty] | 29664 | 29664 | 224.5504 | [6 empty] | 5310 | 5310 | 1.232 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (85%)
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.0M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3 - STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (65%)

## JUNE 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3511256 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47036364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10871799 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 180 | 121 | 3516466 | 5210 | 125.04 | 5.21 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1086 | N/A | N/A | N/A | N/A | 47037604 | 1240 | 238.0038 | 0% | 0% | 100% | 100% | 100% | 75% | 10873998 | 2199 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 167 | 117 | 3521302 | 4836 | 116.064 | 4.836 | 7.7 | 7.7 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 47038732 | 1128 | 233.2506 | 0% | 0% | 100% | 100% | 100% | 75% | 10876096 | 2098 | 0.71 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 116 | 3526162 | 4860 | 116.64 | 4.86 | 8.9 | 8.9 | 3B | 0 | 0 | 1187 | 1185 | 1047 | N/A | N/A | N/A | N/A | 47039844 | 1112 | 228.8066 | 0% | 0% | 100% | 100% | 100% | 75% | 10877200 | 1104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 120 | 3531060 | 4898 | 117.552 | 4.898 | 9.2 | 9.2 | 3B | 0 | 0 | 1188 | 1185 | 1047 | N/A | N/A | N/A | N/A | 47040972 | 1128 | 230.2981 | 0% | 0% | 100% | 100% | 100% | 75% | 10877392 | 192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 116 | 3535779 | 4719 | 113.256 | 4.719 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1047 | N/A | N/A | N/A | N/A | 47042068 | 1096 | 232.2526 | 0% | 0% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 142 | 129 | 3540937 | 5158 | 123.792 | 5.158 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1046 | N/A | N/A | N/A | N/A | 47043172 | 1104 | 214.0364 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 3546910 | 5973 | 143.352 | 5.973 | 9.2 | 9.2 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47044504 | 1332 | 223.0035 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 144 | 3553050 | 6140 | 147.36 | 6.14 | 8.7 | 8.7 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47045841 | 1337 | 217.7524 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 3559173 | 6123 | 146.952 | 6.123 | 8.1 | 8.1 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47047244 | 1403 | 229.136 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 3565435 | 6262 | 150.288 | 6.262 | 7.6 | 7.6 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47048624 | 1380 | 220.3769 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 3571760 | 6325 | 151.8 | 6.325 | 7.1 | 7.1 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47050014 | 1390 | 219.7628 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 135 | 3577747 | 5987 | 143.688 | 5.987 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47051354 | 1340 | 223.8183 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 3583868 | 6121 | 146.904 | 6.121 | 5.9 | 5.9 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47052736 | 1382 | 225.7801 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 3590123 | 6255 | 150.12 | 6.255 | 5.3 | 5.3 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47054152 | 1416 | 226.3789 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 3596286 | 6163 | 147.912 | 6.163 | 4.8 | 4.8 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47055540 | 1388 | 225.215 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 3602229 | 5943 | 142.632 | 5.943 | 4.4 | 4.4 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47056892 | 1352 | 227.4945 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 3608068 | 5839 | 140.136 | 5.839 | 4 | 4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47058228 | 1336 | 228.8063 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 136 | 3613880 | 5812 | 139.488 | 5.812 | 3.6 | 3.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47059572 | 1344 | 231.2457 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 3619794 | 5914 | 141.936 | 5.914 | 3.2 | 3.2 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47060928 | 1356 | 229.2864 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 133 | 3625603 | 5809 | 139.416 | 5.809 | 3 | 3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47062252 | 1324 | 227.9222 | 0% | 100% | 100% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 114 | 133 | 3631089 | 5486 | 131.664 | 5.486 | 2.4 | 2.4 | 2B+1S | 0 | 1098 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47063356 | 1104 | 201.2395 | 0% | 100% | 0% | 100% | 100% | 0% | 10877392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 121 | 124 | 3636356 | 5267 | 126.408 | 5.267 | 1.9 | 1.9 | 2B+1S | 0 | 1048 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47064412 | 1056 | 200.4936 | 0% | 100% | 0% | 100% | 100% | 0% | 10877392 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 142 | 123 | 3641642 | 5286 | 126.864 | 5.286 | 2.3 | 2.3 | 3B | 0 | 0 | 1148 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47065612 | 1200 | 227.0148 | 0% | 0% | 100% | 100% | 100% | 65% | 10878092 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 143 | 120 | 3647662 | 6020 | 144.48 | 6.02 | 3.1 | 3.1 | 3B | 0 | 0 | 1147 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47067004 | 1392 | 231.2292 | 0% | 0% | 100% | 100% | 100% | 65% | 10878858 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136406 | 136.406 | 136.406 | [12 empty] | 30640 | 30640 | 224.6236 | [6 empty] | 7059 | 7059 | 1.1467 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:18 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (65%)

## JUNE 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30516 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3647662 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47067004 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10878858 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 147 | 117 | 3652922 | 5260 | 126.24 | 5.26 | 4.3 | 4.3 | 3B | 0 | 0 | 1147 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47068230 | 1226 | 233.0798 | 0% | 0% | 100% | 100% | 100% | 75% | 10879859 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 147 | 113 | 3656526 | 3604 | 86.496 | 3.604 | 5.1 | 5.1 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47069108 | 878 | 243.6182 | 0% | 0% | 100% | 100% | 100% | 75% | 10880762 | 903 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 113 | 3661492 | 4966 | 119.184 | 4.966 | 6.1 | 6.1 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47070264 | 1156 | 232.7829 | 0% | 0% | 100% | 100% | 100% | 75% | 10881643 | 881 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 156 | 114 | 3666142 | 4650 | 111.6 | 4.65 | 7.9 | 7.9 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47071426 | 1162 | 249.8925 | 0% | 0% | 100% | 100% | 100% | 75% | 10881796 | 153 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 126 | 3669678 | 3536 | 84.864 | 3.536 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47072516 | 1090 | 308.2579 | 0% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 | 130 | 3675151 | 5473 | 131.352 | 5.473 | 9.5 | 9.5 | 3B | 0 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 47073788 | 1272 | 232.4137 | 0% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 140 | 3681224 | 6073 | 145.752 | 6.073 | 9.4 | 9.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47075148 | 1360 | 223.942 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 3687401 | 6177 | 148.248 | 6.177 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47076528 | 1380 | 223.4094 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 3693547 | 6146 | 147.504 | 6.146 | 8 | 8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47077908 | 1380 | 224.5363 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 3699849 | 6302 | 151.248 | 6.302 | 7.4 | 7.4 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47079300 | 1392 | 220.8823 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 | 1.35
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 3706007 | 6158 | 147.792 | 6.158 | 6.7 | 6.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47080692 | 1392 | 226.0474 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 147 | 3712146 | 6139 | 147.336 | 6.139 | 6.1 | 6.1 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47082072 | 1380 | 224.7923 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 143 | 3718193 | 6047 | 145.128 | 6.047 | 5.5 | 5.5 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47083448 | 1376 | 227.5509 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 140 | 3724218 | 6025 | 144.6 | 6.025 | 5 | 5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47084808 | 1360 | 225.7261 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 137 | 3730274 | 6056 | 145.344 | 6.056 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47086156 | 1348 | 222.5892 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 3736217 | 5943 | 142.632 | 5.943 | 4.3 | 4.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47087512 | 1356 | 228.1676 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 3742226 | 6009 | 144.216 | 6.009 | 3.9 | 3.9 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47088852 | 1340 | 222.9988 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 140 | 3748049 | 5823 | 139.752 | 5.823 | 3.5 | 3.5 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47090180 | 1328 | 228.0611 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 3753944 | 5895 | 141.48 | 5.895 | 3.2 | 3.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47091516 | 1336 | 226.6327 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 139 | 3759885 | 5941 | 142.584 | 5.941 | 3 | 3 | 3B+1S | 1005 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47092876 | 1360 | 228.9177 | 100% | 0% | 100% | 100% | 100% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 116 | 126 | 3765289 | 5404 | 129.696 | 5.404 | 2.4 | 2.4 | 2B+1S | 1078 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47093960 | 1084 | 200.5922 | 100% | 0% | 100% | 100% | 0% | 0% | 10881796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 113 | 130 | 3770652 | 5363 | 128.712 | 5.363 | 1.6 | 1.6 | 2B+1S | 1080 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 47095028 | 1068 | 199.1423 | 100% | 0% | 100% | 100% | 0% | 0% | 10881796 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 139 | 126 | 3776126 | 5474 | 131.376 | 5.474 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47096276 | 1248 | 227.9868 | 0% | 0% | 100% | 100% | 100% | 65% | 10881947 | 151 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 117 | 3781378 | 5252 | 126.048 | 5.252 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47097520 | 1244 | 236.8621 | 0% | 0% | 100% | 100% | 100% | 65% | 10882425 | 478 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133716 | 133.716 | 133.716 | [12 empty] | 30516 | 30516 | 228.215 | [6 empty] | 3567 | 3567 | 1.2133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:18 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (65%)

## JUNE 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30476 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3781378 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47097520 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10882425 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 147 | 124 | 3786555 | 5177 | 124.248 | 5.177 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47098760 | 1240 | 239.521 | 0% | 0% | 100% | 100% | 100% | 75% | 10883311 | 886 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 121 | 3791326 | 4771 | 114.504 | 4.771 | 4 | 4 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47099900 | 1140 | 238.9436 | 0% | 0% | 100% | 100% | 100% | 75% | 10884169 | 858 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 123 | 3796302 | 4976 | 119.424 | 4.976 | 4.8 | 4.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47101068 | 1168 | 234.7267 | 0% | 0% | 100% | 100% | 100% | 75% | 10884898 | 729 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 135 | 126 | 3799980 | 3678 | 88.272 | 3.678 | 9 | 9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47102100 | 1032 | 280.5873 | 0% | 0% | 100% | 100% | 100% | 75% | 10885524 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 125 | 3804228 | 4248 | 101.952 | 4.248 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47103340 | 1240 | 291.9021 | 0% | 0% | 100% | 100% | 100% | 75% | 10885724 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 134 | 3809339 | 5111 | 122.664 | 5.111 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47104672 | 1332 | 260.6144 | 0% | 0% | 100% | 100% | 100% | 0% | 10885724 | 0 | 1.25 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 3815186 | 5847 | 140.328 | 5.847 | 9.3 | 9.3 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47106020 | 1348 | 230.5456 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 3821195 | 6009 | 144.216 | 6.009 | 8.7 | 8.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47107380 | 1360 | 226.3272 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 3827155 | 5960 | 143.04 | 5.96 | 8.2 | 8.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47108740 | 1360 | 228.1879 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 3833347 | 6192 | 148.608 | 6.192 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47110128 | 1388 | 224.1602 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 | 1.32
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 140 | 3839349 | 6002 | 144.048 | 6.002 | 6.8 | 6.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47111504 | 1376 | 229.2569 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 3845355 | 6006 | 144.144 | 6.006 | 6.1 | 6.1 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47112844 | 1340 | 223.1102 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 3851267 | 5912 | 141.888 | 5.912 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47114252 | 1408 | 238.1597 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 144 | 3856907 | 5640 | 135.36 | 5.64 | 5 | 5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47115536 | 1284 | 227.6596 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 3862807 | 5900 | 141.6 | 5.9 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47116844 | 1308 | 221.6949 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 3868588 | 5781 | 138.744 | 5.781 | 4.4 | 4.4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47118212 | 1368 | 236.6373 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 3874391 | 5803 | 139.272 | 5.803 | 4.1 | 4.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47119548 | 1336 | 230.2257 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 131 | 3880068 | 5677 | 136.248 | 5.677 | 3.7 | 3.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47120876 | 1328 | 233.9264 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 133 | 3885716 | 5648 | 135.552 | 5.648 | 3.5 | 3.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47122196 | 1320 | 233.711 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 133 | 3891335 | 5619 | 134.856 | 5.619 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47123520 | 1324 | 235.6291 | 0% | 100% | 100% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 113 | 131 | 3896718 | 5383 | 129.192 | 5.383 | 2.5 | 2.5 | 2B+1S | 0 | 1078 | 0 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47124608 | 1088 | 202.1178 | 0% | 100% | 0% | 100% | 100% | 0% | 10885724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 122 | 125 | 3902426 | 5708 | 136.992 | 5.708 | 2.2 | 2.2 | 2B+1S | 0 | 1078 | 0 | 1885 | 1188 | N/A | N/A | N/A | N/A | 47125760 | 1152 | 201.822 | 0% | 100% | 0% | 100% | 100% | 0% | 10885724 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 121 | 3907322 | 4896 | 117.504 | 4.896 | 2.4 | 2.4 | 3B | 0 | 0 | 1065 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47126852 | 1092 | 223.0392 | 0% | 0% | 100% | 100% | 100% | 65% | 10885896 | 172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 117 | 3912418 | 5096 | 122.304 | 5.096 | 3 | 3 | 3B | 0 | 0 | 1065 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47127996 | 1144 | 224.4898 | 0% | 0% | 100% | 100% | 100% | 65% | 10886231 | 335 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131040 | 131.04 | 131.04 | [12 empty] | 30476 | 30476 | 232.5702 | [6 empty] | 3806 | 3806 | 1.23 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP1 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (65%)

## JUNE 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30720 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 3912418 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47127996 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10886231 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 145 | 123 | 3917588 | 5170 | 124.08 | 5.17 | 3.7 | 3.7 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47129212 | 1216 | 235.2031 | 0% | 0% | 100% | 100% | 100% | 75% | 10886665 | 434 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 119 | 3922579 | 4991 | 119.784 | 4.991 | 4.4 | 4.4 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47130404 | 1192 | 238.8299 | 0% | 0% | 100% | 100% | 100% | 75% | 10887107 | 442 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 120 | 3927812 | 5233 | 125.592 | 5.233 | 5 | 5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47131646 | 1242 | 237.34 | 0% | 0% | 100% | 100% | 100% | 75% | 10887437 | 330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 154 | 110 | 3931584 | 3772 | 90.528 | 3.772 | 7.4 | 7.4 | 3B | 0 | 0 | 1138 | 1185 | 1138 | N/A | N/A | N/A | N/A | 47132842 | 1196 | 317.0732 | 0% | 0% | 100% | 100% | 100% | 75% | 10888014 | 577 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 122 | 3935688 | 4104 | 98.496 | 4.104 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 47134060 | 1218 | 296.7836 | 0% | 0% | 100% | 100% | 100% | 75% | 10888097 | 83 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 133 | 130 | 3941014 | 5326 | 127.824 | 5.326 | 9.5 | 9.5 | 3B | 0 | 0 | 1138 | 1185 | 1037 | N/A | N/A | N/A | N/A | 47135144 | 1084 | 203.5299 | 0% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 138 | 3946784 | 5770 | 138.48 | 5.77 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47136408 | 1264 | 219.0641 | 0% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 143 | 3952782 | 5998 | 143.952 | 5.998 | 9.2 | 9.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47137768 | 1360 | 226.7422 | 0% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 3958860 | 6078 | 145.872 | 6.078 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47139132 | 1364 | 224.4159 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 3965017 | 6157 | 147.768 | 6.157 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47140516 | 1384 | 224.7848 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 3971175 | 6158 | 147.792 | 6.158 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47141892 | 1376 | 223.4492 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 142 | 3977215 | 6040 | 144.96 | 6.04 | 6.6 | 6.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47143280 | 1388 | 229.8013 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 144 | 3983325 | 6110 | 146.64 | 6.11 | 5.9 | 5.9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47144658 | 1378 | 225.5319 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 145 | 3989266 | 5941 | 142.584 | 5.941 | 5.3 | 5.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47146028 | 1370 | 230.6009 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 3995194 | 5928 | 142.272 | 5.928 | 4.9 | 4.9 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47147388 | 1360 | 229.4197 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 4001121 | 5927 | 142.248 | 5.927 | 4.4 | 4.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47148740 | 1352 | 228.1087 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 4007016 | 5895 | 141.48 | 5.895 | 3.9 | 3.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47150092 | 1352 | 229.3469 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 132 | 4012859 | 5843 | 140.232 | 5.843 | 3.5 | 3.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47151432 | 1340 | 229.3342 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 | 142 | 4018729 | 5870 | 140.88 | 5.87 | 3.3 | 3.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47152764 | 1332 | 226.9165 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 135 | 4024534 | 5805 | 139.32 | 5.805 | 3.1 | 3.1 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47154108 | 1344 | 231.5245 | 100% | 0% | 100% | 100% | 100% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 115 | 123 | 4029919 | 5385 | 129.24 | 5.385 | 2.6 | 2.6 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47155196 | 1088 | 202.0427 | 100% | 0% | 100% | 100% | 0% | 0% | 10888097 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 116 | 126 | 4035014 | 5095 | 122.28 | 5.095 | 2 | 2 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47156216 | 1020 | 200.1963 | 100% | 0% | 100% | 100% | 0% | 0% | 10888097 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 125 | 4040896 | 5882 | 141.168 | 5.882 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47157544 | 1328 | 225.7735 | 0% | 0% | 100% | 100% | 100% | 65% | 10888487 | 390 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 120 | 4045706 | 4810 | 115.44 | 4.81 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47158716 | 1172 | 243.659 | 0% | 0% | 100% | 100% | 100% | 65% | 10889073 | 586 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133288 | 133.288 | 133.288 | [12 empty] | 30720 | 30720 | 230.4784 | [6 empty] | 2842 | 2842 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (75%)
XCV1- CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3- STOPPED @ 8:00 PM DUE TO HIGH DISCHARGE
BP3 - STARTED @ 10:00 PM DUE TO HIGH DISCHARGE
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
Change operation as per advise sir Alvin Cruz effective May 11, 2016 from 10pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (65%)

## JUNE 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30776 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4045706 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47158716 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10889073 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 149 | 116 | 4050672 | 4966 | 119.184 | 4.966 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47159920 | 1204 | 242.4487 | 0% | 0% | 100% | 100% | 100% | 75% | 10889720 | 647 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 148 | 116 | 4055834 | 5162 | 123.888 | 5.162 | 5 | 5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47161172 | 1252 | 242.5417 | 0% | 0% | 100% | 100% | 100% | 75% | 10890469 | 749 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 118 | 4060576 | 4742 | 113.808 | 4.742 | 6 | 6 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47162300 | 1128 | 237.8743 | 0% | 0% | 100% | 100% | 100% | 75% | 10891249 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 136 | 119 | 4064122 | 3546 | 85.104 | 3.546 | 8.6 | 8.6 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47163412 | 1112 | 313.5928 | 0% | 0% | 100% | 100% | 100% | 75% | 10891919 | 670 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 126 | 4070074 | 5952 | 142.848 | 5.952 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47164690 | 1278 | 214.7177 | 0% | 0% | 100% | 100% | 100% | 75% | 10892129 | 210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 129 | 4074183 | 4109 | 98.616 | 4.109 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 47165884 | 1194 | 290.5817 | 0% | 0% | 100% | 100% | 100% | 0% | 10892129 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 138 | 4080106 | 5923 | 142.152 | 5.923 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47167236 | 1352 | 228.2627 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 4086092 | 5986 | 143.664 | 5.986 | 8.5 | 8.5 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47168600 | 1364 | 227.865 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 142 | 4092027 | 5935 | 142.44 | 5.935 | 7.8 | 7.8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47169964 | 1364 | 229.8231 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 140 | 4098020 | 5993 | 143.832 | 5.993 | 7.2 | 7.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47171332 | 1368 | 228.2663 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 | 1.32
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 4104042 | 6022 | 144.528 | 6.022 | 6.6 | 6.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47172708 | 1376 | 228.4955 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 4110150 | 6108 | 146.592 | 6.108 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47174044 | 1336 | 218.7295 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 4116027 | 5877 | 141.048 | 5.877 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47175428 | 1384 | 235.4943 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 4121856 | 5829 | 139.896 | 5.829 | 5.1 | 5.1 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47176768 | 1340 | 229.8851 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 4127605 | 5749 | 137.976 | 5.749 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47178100 | 1332 | 231.6925 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 4133340 | 5735 | 137.64 | 5.735 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47179436 | 1336 | 232.9555 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 4139050 | 5710 | 137.04 | 5.71 | 4.3 | 4.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47180760 | 1324 | 231.8739 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 4144798 | 5748 | 137.952 | 5.748 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47182092 | 1332 | 231.7328 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 4150503 | 5705 | 136.92 | 5.705 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47183420 | 1328 | 232.7783 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 123 | 4155818 | 5315 | 127.56 | 5.315 | 3.1 | 3.1 | 2B+1S | 0 | 1048 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47184492 | 1072 | 201.6933 | 0% | 100% | 0% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 138 | 4161452 | 5634 | 135.216 | 5.634 | 2.7 | 2.7 | 3B+1S | 0 | 1077 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47185804 | 1312 | 232.8718 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 139 | 125 | 4166640 | 5188 | 124.512 | 5.188 | 2.5 | 2.5 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47187060 | 1256 | 242.0971 | 0% | 100% | 100% | 100% | 100% | 0% | 10892129 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 126 | 4171862 | 5222 | 125.328 | 5.222 | 2.6 | 2.6 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47188292 | 1232 | 235.9249 | 0% | 0% | 100% | 100% | 100% | 55% | 10892242 | 113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 121 | 4176981 | 5119 | 122.856 | 5.119 | 2.9 | 2.9 | 3B | 0 | 0 | 1177 | 1185 | 1136 | N/A | N/A | N/A | N/A | 47189492 | 1200 | 234.4208 | 0% | 0% | 100% | 100% | 100% | 55% | 10892668 | 426 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131275 | 131.275 | 131.275 | [12 empty] | 30776 | 30776 | 234.4392 | [6 empty] | 3595 | 3595 | 1.2317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (55%)

## JUNE 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | A.MIRAFLOR/P. LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30812 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4176981 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47189492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10892668 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 114 | 4181588 | 4607 | 110.568 | 4.607 | 4.5 | 4.5 | 3B | 0 | 0 | 1137 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47190597 | 1105 | 239.8524 | 0% | 0% | 100% | 100% | 100% | 65% | 10893500 | 832 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 116 | 4186173 | 4585 | 110.04 | 4.585 | 7.1 | 7.1 | 3B | 0 | 0 | 1137 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47191722 | 1125 | 245.3653 | 0% | 0% | 100% | 100% | 100% | 65% | 10894300 | 800 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 115 | 4190843 | 4670 | 112.08 | 4.67 | 8.8 | 8.8 | 3B | 0 | 0 | 1137 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47192892 | 1170 | 250.5353 | 0% | 0% | 100% | 100% | 100% | 65% | 10895077 | 777 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 131 | 118 | 4195438 | 4595 | 110.28 | 4.595 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47194136 | 1244 | 270.7291 | 0% | 0% | 100% | 100% | 100% | 65% | 10895277 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 117 | 116 | 4200018 | 4580 | 109.92 | 4.58 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47195300 | 1164 | 254.1485 | 0% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 136 | 127 | 4205560 | 5542 | 133.008 | 5.542 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47196460 | 1160 | 209.3107 | 0% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 | 1.31 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 4211466 | 5906 | 141.744 | 5.906 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47197812 | 1352 | 228.9197 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 4217471 | 6005 | 144.12 | 6.005 | 8.4 | 8.4 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47199180 | 1368 | 227.8102 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 4223449 | 5978 | 143.472 | 5.978 | 7.8 | 7.8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47200556 | 1376 | 230.1773 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 4229587 | 6138 | 147.312 | 6.138 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47201940 | 1384 | 225.4806 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 | 1.27
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 4235446 | 5859 | 140.616 | 5.859 | 6.6 | 6.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47203276 | 1336 | 228.0253 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 4241856 | 6410 | 153.84 | 6.41 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47204644 | 1368 | 213.4165 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 4247335 | 5479 | 131.496 | 5.479 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47206004 | 1360 | 248.2205 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 4253274 | 5939 | 142.536 | 5.939 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47207356 | 1352 | 227.6478 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 143 | 4259110 | 5836 | 140.064 | 5.836 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47208708 | 1352 | 231.6655 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 4264972 | 5862 | 140.688 | 5.862 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47210052 | 1344 | 229.2733 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 4270758 | 5786 | 138.864 | 5.786 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47211392 | 1340 | 231.5935 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 4276629 | 5871 | 140.904 | 5.871 | 3.2 | 3.2 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47212756 | 1364 | 232.3284 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 131 | 4282490 | 5861 | 140.664 | 5.861 | 2.9 | 2.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47214052 | 1296 | 221.1227 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 4287861 | 5371 | 128.904 | 5.371 | 2.3 | 2.3 | 2B+1S | 1070 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47215148 | 1096 | 204.0588 | 100% | 0% | 100% | 100% | 0% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 140 | 4293570 | 5709 | 137.016 | 5.709 | 1.9 | 1.9 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47216480 | 1332 | 233.3158 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 139 | 4299192 | 5622 | 134.928 | 5.622 | 1.4 | 1.4 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47217824 | 1344 | 239.0608 | 100% | 0% | 100% | 100% | 100% | 0% | 10895277 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 126 | 4304586 | 5394 | 129.456 | 5.394 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47219084 | 1260 | 233.5929 | 0% | 0% | 100% | 100% | 100% | 70% | 10895411 | 134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 127 | 4309824 | 5238 | 125.712 | 5.238 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47220304 | 1220 | 232.9133 | 0% | 0% | 100% | 100% | 100% | 70% | 10895814 | 403 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132843 | 132.843 | 132.843 | [12 empty] | 30812 | 30812 | 231.943 | [6 empty] | 3146 | 3146 | 1.2533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV1- INCREASE OPENING @ 12:00 AM (65%)
XCV1- CLOSED @ 3:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:01 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:02 PM (70%)

## JUNE 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31396 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4309824 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47220304 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10895814 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 143 | 124 | 4314986 | 5162 | 123.888 | 5.162 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47221540 | 1236 | 239.4421 | 0% | 0% | 100% | 100% | 100% | 75% | 10896379 | 565 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 120 | 4320012 | 5026 | 120.624 | 5.026 | 4.5 | 4.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47222752 | 1212 | 241.146 | 0% | 0% | 100% | 100% | 100% | 75% | 10897098 | 719 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 118 | 4325032 | 5020 | 120.48 | 5.02 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47223972 | 1220 | 243.0279 | 0% | 0% | 100% | 100% | 100% | 75% | 10897844 | 746 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 136 | 120 | 4329948 | 4916 | 117.984 | 4.916 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47225184 | 1212 | 246.5419 | 0% | 0% | 100% | 100% | 100% | 75% | 10898209 | 365 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 147 | 117 | 4334579 | 4631 | 111.144 | 4.631 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47226408 | 1224 | 264.3058 | 0% | 0% | 100% | 100% | 100% | 75% | 10898385 | 176 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 137 | 128 | 4338834 | 4255 | 102.12 | 4.255 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47227812 | 1404 | 329.9647 | 0% | 0% | 100% | 100% | 100% | 0% | 10898385 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 4344586 | 5752 | 138.048 | 5.752 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47229124 | 1312 | 228.0946 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 4350588 | 6002 | 144.048 | 6.002 | 8.6 | 8.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47230496 | 1372 | 228.5905 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 146 | 4356625 | 6037 | 144.888 | 6.037 | 7.9 | 7.9 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47231876 | 1380 | 228.5904 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 4362841 | 6216 | 149.184 | 6.216 | 7 | 7 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47233276 | 1400 | 225.2252 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 | 1.32
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 148 | 4368902 | 6061 | 145.464 | 6.061 | 6.5 | 6.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47234652 | 1376 | 227.0252 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 146 | 4374904 | 6002 | 144.048 | 6.002 | 5.8 | 5.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47236028 | 1376 | 229.2569 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 4380902 | 5998 | 143.952 | 5.998 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47237404 | 1376 | 229.4098 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 143 | 4386818 | 5916 | 141.984 | 5.916 | 4.7 | 4.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47238760 | 1356 | 229.2089 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 4392738 | 5920 | 142.08 | 5.92 | 4.1 | 4.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47240124 | 1364 | 230.4054 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 4398522 | 5784 | 138.816 | 5.784 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47241428 | 1304 | 225.4495 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 4404168 | 5646 | 135.504 | 5.646 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47242760 | 1332 | 235.9192 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 136 | 4409960 | 5792 | 139.008 | 5.792 | 3.5 | 3.5 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47244092 | 1332 | 229.9724 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 129 | 4415563 | 5603 | 134.472 | 5.603 | 3.3 | 3.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47245412 | 1320 | 235.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 130 | 4420979 | 5416 | 129.984 | 5.416 | 2.6 | 2.6 | 2B+1S | 0 | 1067 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47246516 | 1104 | 203.8405 | 0% | 100% | 0% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 135 | 140 | 4426766 | 5787 | 138.888 | 5.787 | 2.2 | 2.2 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47247836 | 1320 | 228.0975 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 135 | 4433004 | 6238 | 149.712 | 6.238 | 1.7 | 1.7 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47249160 | 1324 | 212.2475 | 0% | 100% | 100% | 100% | 100% | 0% | 10898385 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 139 | 131 | 4438242 | 5238 | 125.712 | 5.238 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47250482 | 1322 | 252.3864 | 0% | 0% | 100% | 100% | 100% | 70% | 10898507 | 122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 149 | 126 | 4443444 | 5202 | 124.848 | 5.202 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47251700 | 1218 | 234.1407 | 0% | 0% | 100% | 100% | 100% | 70% | 10899029 | 522 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133620 | 133.62 | 133.62 | [12 empty] | 31396 | 31396 | 234.9648 | [6 empty] | 3215 | 3215 | 1.2567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
XCV2- INCREASE OPENING @ 12:00 AM (75%)
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:02 PM (70%)

## JUNE 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31680 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4443444 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47251700 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10899029 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 146 | 125 | 4448608 | 5164 | 123.936 | 5.164 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47252924 | 1224 | 237.0256 | 0% | 0% | 100% | 100% | 100% | 80% | 10899641 | 612 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 148 | 121 | 4453686 | 5078 | 121.872 | 5.078 | 3.7 | 3.7 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47254116 | 1192 | 234.7381 | 0% | 0% | 100% | 100% | 100% | 80% | 10900477 | 836 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 122 | 4458954 | 5268 | 126.432 | 5.268 | 5 | 5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47255344 | 1228 | 233.1055 | 0% | 0% | 100% | 100% | 100% | 80% | 10901270 | 793 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 147 | 92 | 4462524 | 3570 | 85.68 | 3.57 | 7.8 | 7.8 | 3B | 0 | 0 | 1158 | 1185 | 1158 | N/A | N/A | N/A | N/A | 47256502 | 1158 | 324.3697 | 0% | 0% | 100% | 100% | 100% | 80% | 10901498 | 228 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 131 | 4467294 | 4770 | 114.48 | 4.77 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1158 | N/A | N/A | N/A | N/A | 47257814 | 1312 | 275.0524 | 0% | 0% | 100% | 100% | 100% | 80% | 10901598 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 142 | 135 | 4472360 | 5066 | 121.584 | 5.066 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1158 | N/A | N/A | N/A | N/A | 47258940 | 1126 | 222.2661 | 0% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 146 | 4478479 | 6119 | 146.856 | 6.119 | 9.2 | 9.2 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47260300 | 1360 | 222.2585 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 147 | 4484735 | 6256 | 150.144 | 6.256 | 8.5 | 8.5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47261700 | 1400 | 223.7852 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 147 | 4490961 | 6226 | 149.424 | 6.226 | 7.8 | 7.8 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47263092 | 1392 | 223.5785 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 151 | 4497378 | 6417 | 154.008 | 6.417 | 7.1 | 7.1 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47264516 | 1424 | 221.9106 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 | 1.29
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 4503365 | 5987 | 143.688 | 5.987 | 6.4 | 6.4 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47265872 | 1356 | 226.4907 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 148 | 4509494 | 6129 | 147.096 | 6.129 | 5.7 | 5.7 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47267264 | 1392 | 227.117 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 148 | 4515579 | 6085 | 146.04 | 6.085 | 5 | 5 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47268651 | 1387 | 227.9376 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 144 | 4521822 | 6243 | 149.832 | 6.243 | 4.5 | 4.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47270008 | 1357 | 217.3634 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 144 | 4528072 | 6250 | 150 | 6.25 | 3.8 | 3.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47271448 | 1440 | 230.4 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 142 | 4534027 | 5955 | 142.92 | 5.955 | 3.5 | 3.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47272812 | 1364 | 229.0512 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 4539898 | 5871 | 140.904 | 5.871 | 3.3 | 3.3 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47274152 | 1340 | 228.2405 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 138 | 4545812 | 5914 | 141.936 | 5.914 | 3 | 3 | 3B+1S | 996 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47275512 | 1360 | 229.9628 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 140 | 4551580 | 5768 | 138.432 | 5.768 | 2.8 | 2.8 | 3B+1S | 966 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47276832 | 1320 | 228.8488 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 140 | 4557449 | 5869 | 140.856 | 5.869 | 2.6 | 2.6 | 3B+1S | 996 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47278172 | 1340 | 228.3183 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 140 | 4563256 | 5807 | 139.368 | 5.807 | 2.3 | 2.3 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47279524 | 1352 | 232.8225 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 138 | 4568876 | 5620 | 134.88 | 5.62 | 1.9 | 1.9 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47280840 | 1316 | 234.1637 | 100% | 0% | 100% | 100% | 100% | 0% | 10901598 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 125 | 4574548 | 5672 | 136.128 | 5.672 | 1.8 | 1.8 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47282140 | 1300 | 229.1961 | 0% | 0% | 1000% | 100% | 100% | 50% | 10901634 | 36 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 144 | 126 | 4579922 | 5374 | 128.976 | 5.374 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47283380 | 1240 | 230.7406 | 0% | 0% | 100% | 100% | 100% | 50% | 10901968 | 334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136478 | 136.478 | 136.478 | [12 empty] | 31680 | 31680 | 232.1253 | [6 empty] | 2939 | 2939 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JUNE 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29872 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4579922 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47283380 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10901968 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 148 | 125 | 4585280 | 5358 | 128.592 | 5.358 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47284652 | 1272 | 237.402 | 0% | 0% | 100% | 100% | 100% | 70% | 10902596 | 628 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 150 | 120 | 4590264 | 4984 | 119.616 | 4.984 | 3.8 | 3.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47285828 | 1176 | 235.9551 | 0% | 0% | 100% | 100% | 100% | 70% | 10903420 | 824 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 119 | 4595452 | 5188 | 124.512 | 5.188 | 5 | 5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47287044 | 1216 | 234.387 | 0% | 0% | 100% | 100% | 100% | 70% | 10904207 | 787 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 150 | 110 | 4598789 | 3337 | 80.088 | 3.337 | 8.8 | 8.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47288056 | 1012 | 303.2664 | 0% | 0% | 100% | 100% | 100% | 70% | 10904431 | 224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 127 | 4602888 | 4099 | 98.376 | 4.099 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47289302 | 1246 | 303.9766 | 0% | 0% | 100% | 100% | 100% | 70% | 10904631 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 140 | 134 | 4608334 | 5446 | 130.704 | 5.446 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47290604 | 1302 | 239.0746 | 0% | 0% | 100% | 100% | 100% | 0% | 10904631 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 147 | 4614329 | 5995 | 143.88 | 5.995 | 9.3 | 9.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47291972 | 1368 | 228.1902 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 4620442 | 6113 | 146.712 | 6.113 | 8.8 | 8.8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47293360 | 1388 | 227.0571 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 144 | 4626631 | 6189 | 148.536 | 6.189 | 8.1 | 8.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47294740 | 1380 | 222.9762 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 4632802 | 6171 | 148.104 | 6.171 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47296132 | 1392 | 225.5712 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 | 1.23
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 4638972 | 6170 | 148.08 | 6.17 | 6.8 | 6.8 | 3B+1S | 0 | 1048 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47297508 | 1376 | 223.0146 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 4645037 | 6065 | 145.56 | 6.065 | 6.2 | 6.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47298876 | 1368 | 225.5565 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 4651032 | 5995 | 143.88 | 5.995 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47300248 | 1372 | 228.8574 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 |  | 0 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 |  |  | 4654447 | 3415 | 81.96 | 3.415 | 5.4 | 5.4 |  | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 47300934 | 686 | 200.8785 | 0% | 0% | 0% | 0% | 0% | 0% | 10904631 | 0 | 1.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 4657862 | 3415 | 81.96 | 3.415 | 5.1 | 5.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47301696 | 762 | 223.1332 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 4663826 | 5964 | 143.136 | 5.964 | 4.7 | 4.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47303064 | 1368 | 229.3763 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 4669553 | 5727 | 137.448 | 5.727 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47304414 | 1350 | 235.7255 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 4674944 | 5391 | 129.384 | 5.391 | 4.3 | 4.3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47305684 | 1270 | 235.5778 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 4680558 | 5614 | 134.736 | 5.614 | 4.1 | 4.1 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47307020 | 1336 | 237.9765 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 122 | 4685846 | 5288 | 126.912 | 5.288 | 3.6 | 3.6 | 2B+1S | 0 | 1048 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47308096 | 1076 | 203.4796 | 0% | 100% | 100% | 100% | 0% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 126 | 140 | 4691452 | 5606 | 134.544 | 5.606 | 3 | 3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 47309400 | 1304 | 232.6079 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 121 | 136 | 4697286 | 5834 | 140.016 | 5.834 | 2.4 | 2.4 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47310796 | 1396 | 239.2869 | 0% | 100% | 100% | 100% | 100% | 0% | 10904631 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 121 | 4702486 | 5200 | 124.8 | 5.2 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47312020 | 1224 | 235.3846 | 0% | 0% | 100% | 100% | 100% | 50% | 10904680 | 49 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 124 | 4707708 | 5222 | 125.328 | 5.222 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47313252 | 1232 | 235.9249 | 0% | 0% | 100% | 100% | 100% | 50% | 10904933 | 253 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 127786 | 127.786 | 127.786 | [12 empty] | 29872 | 29872 | 233.7658 | [6 empty] | 2965 | 2965 | 1.3117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 4:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
ALL BOOSTER AND STORAGE PUMP STOPPED OPERATION @1:30PM DUE TO SHORT CIRCUIT ELECTRICAL WIRING @ JUNCTION BOX.
MAINTENANCE ARRIVE @ 2:12PM
MAINTENANCE TEAM START TO CHECK ELECTRICAL PANEL BREAKER @ 2:14PM AND FINISHED @ 2:18PM
BP2- STARTED @ 2:20PM
BP3-STARTED @ 2:22PM
BP1- STARTED @ 2:23PM
SP2- STARTED @2:24PM
BACK TO NORMAL OPERATION @ 2:25PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JUNE 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30928 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4707708 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47313252 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10904933 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 144 | 121 | 4712822 | 5114 | 122.736 | 5.114 | 3.1 | 3.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47314476 | 1224 | 239.343 | 0% | 0% | 100% | 100% | 100% | 80% | 10905427 | 494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 144 | 122 | 4717856 | 5034 | 120.816 | 5.034 | 4 | 4 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47315668 | 1192 | 236.7898 | 0% | 0% | 100% | 100% | 100% | 80% | 10906268 | 841 | 0.79 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 122 | 4723266 | 5410 | 129.84 | 5.41 | 4.9 | 4.9 | 3B | 0 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47316932 | 1264 | 233.6414 | 0% | 0% | 100% | 100% | 100% | 80% | 10907076 | 808 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 122 | 4728016 | 4750 | 114 | 4.75 | 5.1 | 5.1 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47318044 | 1112 | 234.1053 | 0% | 0% | 100% | 100% | 100% | 80% | 10907230 | 154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 121 | 4733062 | 5046 | 121.104 | 5.046 | 5.1 | 5.1 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47319212 | 1168 | 231.4705 | 0% | 0% | 100% | 100% | 100% | 80% | 10907247 | 17 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 135 | 136 | 4738589 | 5527 | 132.648 | 5.527 | 5.1 | 5.1 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47320412 | 1200 | 217.116 | 0% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 | 1.24 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 4744736 | 6147 | 147.528 | 6.147 | 5 | 5 | 38+1S | 994 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47321756 | 1344 | 218.6432 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 4750167 | 5431 | 130.344 | 5.431 | 4.9 | 4.9 | 38+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47323044 | 1288 | 237.1571 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 4755968 | 5801 | 139.224 | 5.801 | 4.8 | 4.8 | 38+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47324372 | 1328 | 228.926 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 4761815 | 5847 | 140.328 | 5.847 | 4.7 | 4.7 | 38+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47325700 | 1328 | 227.125 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 | 1.49
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 4767887 | 6072 | 145.728 | 6.072 | 4.4 | 4.4 | 38+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47327060 | 1360 | 223.9789 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 4773749 | 5862 | 140.688 | 5.862 | 3.9 | 3.9 | 38+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47328412 | 1352 | 230.638 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 4779523 | 5774 | 138.576 | 5.774 | 3.5 | 3.5 | 38+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47329752 | 1340 | 232.0748 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 138 | 4784983 | 5460 | 131.04 | 5.46 | 3.2 | 3.2 | 38+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47331012 | 1260 | 230.7692 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 4790731 | 5748 | 137.952 | 5.748 | 2.9 | 2.9 | 38+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47332352 | 1340 | 233.1246 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 133 | 4796432 | 5701 | 136.824 | 5.701 | 2.6 | 2.6 | 38+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47333644 | 1292 | 226.6269 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 4802160 | 5728 | 137.472 | 5.728 | 2.3 | 2.3 | 38+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47335020 | 1376 | 240.2235 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 136 | 4807820 | 5660 | 135.84 | 5.66 | 2.2 | 2.2 | 38+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47336348 | 1328 | 234.629 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 4813506 | 5686 | 136.464 | 5.686 | 2.1 | 2.1 | 38+1S | 1000 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47337672 | 1324 | 232.8526 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 131 | 4819058 | 5552 | 133.248 | 5.552 | 2 | 2 | 38+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47338996 | 1324 | 238.4726 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 133 | 4824618 | 5560 | 133.44 | 5.56 | 1.9 | 1.9 | 38+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47340316 | 1320 | 237.4101 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 134 | 4830594 | 5976 | 143.424 | 5.976 | 1.7 | 1.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47341740 | 1424 | 238.2865 | 100% | 0% | 100% | 100% | 100% | 0% | 10907247 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 125 | 4835700 | 5106 | 122.544 | 5.106 | 1.7 | 1.7 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47342940 | 1200 | 235.0176 | 0% | 0% | 100% | 100% | 100% | 20% | 10907307 | 60 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 120 | 4840966 | 5266 | 126.384 | 5.266 | 1.9 | 1.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47344180 | 1240 | 235.4728 | 0% | 0% | 100% | 100% | 100% | 20% | 10907515 | 208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133258 | 133.258 | 133.258 | [12 empty] | 30928 | 30928 | 232.0911 | [6 empty] | 2582 | 2582 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (5.1M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:00 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (20%)

## JUNE 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31120 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4840966 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47344180 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10907515 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 145 | 126 | 4846336 | 5370 | 128.88 | 5.37 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47345444 | 1264 | 235.3818 | 0% | 0% | 100% | 100% | 100% | 70% | 10908029 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 149 | 119 | 4851332 | 4996 | 119.904 | 4.996 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47346692 | 1248 | 249.7998 | 0% | 0% | 100% | 100% | 100% | 70% | 10908636 | 607 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 149 | 122 | 4856314 | 4982 | 119.568 | 4.982 | 4.3 | 4.3 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47347860 | 1168 | 234.444 | 0% | 0% | 100% | 100% | 100% | 70% | 10909411 | 775 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 150 | 110 | 4858794 | 2480 | 59.52 | 2.48 | 7.8 | 7.8 | 3B | 0 | 0 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 47349000 | 1140 | 459.6774 | 0% | 0% | 100% | 100% | 100% | 70% | 10909732 | 321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 133 | 127 | 4863279 | 4485 | 107.64 | 4.485 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47350260 | 1260 | 280.9365 | 0% | 0% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 134 | 130 | 4868905 | 5626 | 135.024 | 5.626 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47351472 | 1212 | 215.4284 | 0% | 0% | 100% | 100% | 100% | 0% | 10909732 | 0 | 1.31 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 141 | 4874587 | 5682 | 136.368 | 5.682 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47352737 | 1265 | 222.6329 | 0% | 0% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 147 | 4880748 | 6161 | 147.864 | 6.161 | 9.3 | 9.3 | 3B+1S | 0 | 1099 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47354132 | 1395 | 226.4243 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 146 | 4886841 | 6093 | 146.232 | 6.093 | 8.7 | 8.7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47355524 | 1392 | 228.4589 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 148 | 4892915 | 6074 | 145.776 | 6.074 | 8 | 8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47356916 | 1392 | 229.1735 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 | 1.38
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 147 | 4898970 | 6055 | 145.32 | 6.055 | 7.3 | 7.3 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47358292 | 1376 | 227.2502 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 147 | 4905128 | 6158 | 147.792 | 6.158 | 6.5 | 6.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47359732 | 1440 | 233.8422 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 4910810 | 5682 | 136.368 | 5.682 | 6 | 6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47361024 | 1292 | 227.3847 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 141 | 4916757 | 5947 | 142.728 | 5.947 | 5.4 | 5.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47362396 | 1372 | 230.7046 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 4922557 | 5800 | 139.2 | 5.8 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47363740 | 1344 | 231.7241 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 4928278 | 5721 | 137.304 | 5.721 | 4.7 | 4.7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47365064 | 1324 | 231.4281 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 4933993 | 5715 | 137.16 | 5.715 | 4.4 | 4.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47366396 | 1332 | 233.0709 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 132 | 4939693 | 5700 | 136.8 | 5.7 | 4.1 | 4.1 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47367716 | 1320 | 231.5789 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 137 | 4945431 | 5738 | 137.712 | 5.738 | 3.9 | 3.9 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47369036 | 1320 | 230.0453 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 127 | 4950840 | 5409 | 129.816 | 5.409 | 3.3 | 3.3 | 2B+1S | 0 | 1078 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47370132 | 1096 | 202.6253 | 0% | 100% | 0% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 138 | 4956546 | 5706 | 136.944 | 5.706 | 2.7 | 2.7 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47371476 | 1344 | 235.5415 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 137 | 4962154 | 5608 | 134.592 | 5.608 | 2.3 | 2.3 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47372816 | 1340 | 238.9444 | 0% | 100% | 100% | 100% | 100% | 0% | 10909732 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 128 | 4967604 | 5450 | 130.8 | 5.45 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47374092 | 1276 | 234.1284 | 0% | 0% | 100% | 100% | 100% | 30% | 10909879 | 147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 125 | 4972762 | 5158 | 123.792 | 5.158 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47375300 | 1208 | 234.1993 | 0% | 0% | 100% | 100% | 100% | 30% | 10910168 | 289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131796 | 131.796 | 131.796 | [12 empty] | 31120 | 31120 | 236.1225 | [6 empty] | 2653 | 2653 | 1.2533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (20%)

## JUNE 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31156 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 4972762 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47375300 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10910168 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 146 | 123 | 4978086 | 5324 | 127.776 | 5.324 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47376564 | 1264 | 237.4155 | 0% | 0% | 100% | 100% | 100% | 80% | 10910727 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 149 | 124 | 4983166 | 5080 | 121.92 | 5.08 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47377772 | 1208 | 237.7953 | 0% | 0% | 100% | 100% | 100% | 80% | 10911433 | 706 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 143 | 120 | 4988412 | 5246 | 125.904 | 5.246 | 5.2 | 5.2 | 3B | 0 | 0 | 1157 | 1185 | 1158 | N/A | N/A | N/A | N/A | 47378988 | 1216 | 231.7957 | 0% | 0% | 100% | 100% | 100% | 80% | 10912209 | 776 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 150 | 105 | 4991646 | 3234 | 77.616 | 3.234 | 8.1 | 8.1 | 3B | 0 | 0 | 1138 | 1185 | 1137 | N/A | N/A | N/A | N/A | 47380152 | 1164 | 359.9258 | 0% | 0% | 100% | 100% | 100% | 80% | 10912510 | 301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 129 | 4996466 | 4820 | 115.68 | 4.82 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47381324 | 1172 | 243.1535 | 0% | 0% | 100% | 100% | 100% | 80% | 10912530 | 20 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 140 | 139 | 5002122 | 5656 | 135.744 | 5.656 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47382572 | 1248 | 220.6506 | 0% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 | 1.4 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 145 | 5008104 | 5982 | 143.568 | 5.982 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47383928 | 1356 | 226.68 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 147 | 5014158 | 6054 | 145.296 | 6.054 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47385308 | 1380 | 227.9485 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 5020289 | 6131 | 147.144 | 6.131 | 7.7 | 7.7 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47386692 | 1384 | 225.7381 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 5026467 | 6178 | 148.272 | 6.178 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47388092 | 1400 | 226.6106 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 | 1.42
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 5032584 | 6117 | 146.808 | 6.117 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47389494 | 1402 | 229.1973 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 142 | 5038621 | 6037 | 144.888 | 6.037 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47390832 | 1338 | 221.6333 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 143 | 5044523 | 5902 | 141.648 | 5.902 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47392180 | 1348 | 228.3972 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 5050302 | 5779 | 138.696 | 5.779 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47393508 | 1328 | 229.7975 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 142 | 5056133 | 5831 | 139.944 | 5.831 | 5 | 5 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47394852 | 1344 | 230.4922 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 5062005 | 5872 | 140.928 | 5.872 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47396188 | 1336 | 227.5204 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 5067890 | 5885 | 141.24 | 5.885 | 4.5 | 4.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47397556 | 1368 | 232.4554 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 142 | 5073796 | 5906 | 141.744 | 5.906 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47398876 | 1320 | 223.5015 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 142 | 5079661 | 5865 | 140.76 | 5.865 | 3.8 | 3.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47400220 | 1344 | 229.156 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 112 | 128 | 5085173 | 5512 | 132.288 | 5.512 | 3.1 | 3.1 | 2B+1S | 1097 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47401324 | 1104 | 200.2903 | 100% | 0% | 100% | 100% | 0% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 141 | 5091003 | 5830 | 139.92 | 5.83 | 2.5 | 2.5 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47402672 | 1348 | 231.2178 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 134 | 5096504 | 5501 | 132.024 | 5.501 | 2 | 2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47403972 | 1300 | 236.3207 | 100% | 0% | 100% | 100% | 100% | 0% | 10912530 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 129 | 5101942 | 5438 | 130.512 | 5.438 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47405220 | 1248 | 229.4961 | 0% | 0% | 100% | 100% | 100% | 20% | 10912580 | 50 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 123 | 5107259 | 5317 | 127.608 | 5.317 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47406456 | 1236 | 232.4619 | 0% | 0% | 100% | 100% | 100% | 20% | 10912670 | 90 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134497 | 134.497 | 134.497 | [12 empty] | 31156 | 31156 | 231.6483 | [6 empty] | 2502 | 2502 | 1.2333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (80%)
XCV1- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## JUNE 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31164 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5107259 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47406456 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10912670 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 140 | 123 | 5111722 | 4463 | 107.112 | 4.463 | 3.5 | 3.5 | 3B | 0 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47407610 | 1154 | 258.5705 | 0% | 0% | 100% | 100% | 100% | 70% | 10913248 | 578 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 143 | 120 | 5116150 | 4428 | 106.272 | 4.428 | 5.1 | 5.1 | 3B | 0 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47408775 | 1165 | 263.0985 | 0% | 0% | 100% | 100% | 100% | 70% | 10913808 | 560 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 119 | 5120605 | 4455 | 106.92 | 4.455 | 6.8 | 6.8 | 3B | 0 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47409972 | 1197 | 268.6869 | 0% | 0% | 100% | 100% | 100% | 70% | 10914320 | 512 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 140 | 110 | 5125137 | 4532 | 108.768 | 4.532 | 8.7 | 8.7 | 3B | 0 | 0 | 1167 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47411228 | 1256 | 277.1403 | 0% | 0% | 100% | 100% | 100% | 70% | 10914840 | 520 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 135 | 125 | 5129699 | 4562 | 109.488 | 4.562 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47412436 | 1208 | 264.7961 | 0% | 0% | 100% | 100% | 100% | 70% | 10915055 | 215 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 138 | 5135493 | 5794 | 139.056 | 5.794 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47413720 | 1284 | 221.6086 | 0% | 0% | 100% | 100% | 100% | 0% | 10915055 | 0 | 1.32 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 144 | 5141550 | 6057 | 145.368 | 6.057 | 9.1 | 9.1 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47415108 | 1388 | 229.1563 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 5147640 | 6090 | 146.16 | 6.09 | 8.7 | 8.7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47416496 | 1388 | 227.9146 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 140 | 5153846 | 6206 | 148.944 | 6.206 | 7.9 | 7.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47417892 | 1396 | 224.9436 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 5159906 | 6060 | 145.44 | 6.06 | 7.3 | 7.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47419268 | 1376 | 227.0627 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 | 1.34
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 5165984 | 6078 | 145.872 | 6.078 | 6.7 | 6.7 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47420635 | 1367 | 224.9095 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 5171960 | 5976 | 143.424 | 5.976 | 6.2 | 6.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47422004 | 1369 | 229.083 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 134 | 5177725 | 5765 | 138.36 | 5.765 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47423348 | 1344 | 233.131 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 5183537 | 5812 | 139.488 | 5.812 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47424684 | 1336 | 229.8692 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 5189299 | 5762 | 138.288 | 5.762 | 4.9 | 4.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47426016 | 1332 | 231.1697 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 5195131 | 5832 | 139.968 | 5.832 | 4.7 | 4.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47427352 | 1336 | 229.0809 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 5200987 | 5856 | 140.544 | 5.856 | 4.4 | 4.4 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47428692 | 1340 | 228.8251 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 5206863 | 5876 | 141.024 | 5.876 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47430028 | 1336 | 227.3656 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 144 | 5212685 | 5822 | 139.728 | 5.822 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47431372 | 1344 | 230.8485 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 128 | 5218147 | 5462 | 131.088 | 5.462 | 2.9 | 2.9 | 2B+1S | 0 | 1088 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47432476 | 1104 | 202.1238 | 0% | 100% | 0% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 140 | 5223820 | 5673 | 136.152 | 5.673 | 2.4 | 2.4 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47433796 | 1320 | 232.6811 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 134 | 5229624 | 5804 | 139.296 | 5.804 | 1.8 | 1.8 | 3B+1S | 0 | 1055 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47435156 | 1360 | 234.3212 | 0% | 100% | 100% | 100% | 100% | 0% | 10915055 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 130 | 5235016 | 5392 | 129.408 | 5.392 | 1.9 | 1.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47436412 | 1256 | 232.9377 | 0% | 0% | 100% | 100% | 100% | 30% | 10915117 | 62 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 122 | 5240112 | 5096 | 122.304 | 5.096 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47437620 | 1208 | 237.0487 | 0% | 0% | 100% | 100% | 100% | 30% | 10915327 | 210 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132853 | 132.853 | 132.853 | [12 empty] | 31164 | 31164 | 234.5751 | [6 empty] | 2657 | 2657 | 1.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31668 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5240112 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47437620 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10915327 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 139 | 117 | 5245206 | 5094 | 122.256 | 5.094 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47438860 | 1240 | 243.4236 | 0% | 0% | 100% | 100% | 100% | 70% | 10915763 | 436 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 | 118 | 5249998 | 4792 | 115.008 | 4.792 | 3.3 | 3.3 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 47440020 | 1160 | 242.0701 | 0% | 0% | 100% | 100% | 100% | 70% | 10916379 | 616 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 112 | 5254754 | 4756 | 114.144 | 4.756 | 4.3 | 4.3 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47441172 | 1152 | 242.2204 | 0% | 0% | 100% | 100% | 100% | 70% | 10917061 | 682 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 140 | 114 | 5258446 | 3692 | 88.608 | 3.692 | 6.7 | 6.7 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47442300 | 1128 | 305.5255 | 0% | 0% | 100% | 100% | 100% | 70% | 10917335 | 274 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 133 | 5262163 | 3717 | 89.208 | 3.717 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47443516 | 1216 | 327.1455 | 0% | 0% | 100% | 100% | 100% | 70% | 10917535 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 135 | 5267891 | 5728 | 137.472 | 5.728 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47444948 | 1432 | 250 | 0% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 | 1.25 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 5274071 | 6180 | 148.32 | 6.18 | 9.2 | 9.2 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47446340 | 1392 | 225.2427 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 5280183 | 6112 | 146.688 | 6.112 | 8.4 | 8.4 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47447756 | 1416 | 231.6754 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 5286281 | 6098 | 146.352 | 6.098 | 7.7 | 7.7 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47449116 | 1360 | 223.0239 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 5292431 | 6150 | 147.6 | 6.15 | 7 | 7 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47450508 | 1392 | 226.3415 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 | 1.3
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 5298601 | 6170 | 148.08 | 6.17 | 6.3 | 6.3 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47451896 | 1388 | 224.9595 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 5304635 | 6034 | 144.816 | 6.034 | 5.6 | 5.6 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47453276 | 1380 | 228.704 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 5310764 | 6129 | 147.096 | 6.129 | 5 | 5 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47454716 | 1440 | 234.9486 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 143 | 5316580 | 5816 | 139.584 | 5.816 | 4.4 | 4.4 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47456028 | 1312 | 225.5846 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 5322399 | 5819 | 139.656 | 5.819 | 3.9 | 3.9 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47457372 | 1344 | 230.9675 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 5328227 | 5828 | 139.872 | 5.828 | 3.5 | 3.5 | 3B+1S | 1025 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47458712 | 1340 | 229.9245 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 139 | 5334119 | 5892 | 141.408 | 5.892 | 3.2 | 3.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47460060 | 1348 | 228.7848 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 139 | 5340023 | 5904 | 141.696 | 5.904 | 2.9 | 2.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47461404 | 1344 | 227.6423 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 5346061 | 6038 | 144.912 | 6.038 | 2.7 | 2.7 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47462784 | 1380 | 228.5525 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 140 | 5351682 | 5621 | 134.904 | 5.621 | 2.5 | 2.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47464084 | 1300 | 231.2756 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 140 | 5357547 | 5865 | 140.76 | 5.865 | 2 | 2 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47465448 | 1364 | 232.5661 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 143 | 5363368 | 5821 | 139.704 | 5.821 | 1.5 | 1.5 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47466812 | 1364 | 234.324 | 100% | 0% | 100% | 100% | 100% | 0% | 10917535 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 127 | 5368811 | 5443 | 130.632 | 5.443 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47468060 | 1248 | 229.2853 | 0% | 0% | 100% | 100% | 100% | 30% | 10917653 | 118 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 142 | 122 | 5374094 | 5283 | 126.792 | 5.283 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47469288 | 1228 | 232.4437 | 0% | 0% | 100% | 100% | 100% | 30% | 10918015 | 362 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133982 | 133.982 | 133.982 | [12 empty] | 31668 | 31668 | 236.3601 | [6 empty] | 2688 | 2688 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31580 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5374094 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47469288 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10918015 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 144 | 123 | 5379258 | 5164 | 123.936 | 5.164 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47470508 | 1220 | 236.251 | 0% | 0% | 100% | 100% | 100% | 70% | 10918554 | 539 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 148 | 123 | 5384512 | 5254 | 126.096 | 5.254 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47471756 | 1248 | 237.5333 | 0% | 0% | 100% | 100% | 100% | 70% | 10919256 | 702 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 145 | 121 | 5389655 | 5143 | 123.432 | 5.143 | 4.5 | 4.5 | 3B | 0 | 0 | 1168 | 1185 | 1168 | N/A | N/A | N/A | N/A | 47472964 | 1208 | 234.8824 | 0% | 0% | 100% | 100% | 100% | 70% | 10920017 | 761 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 143 | 120 | 5392978 | 3323 | 79.752 | 3.323 | 7.4 | 7.4 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47474136 | 1172 | 352.6933 | 0% | 0% | 100% | 100% | 100% | 70% | 10920365 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 131 | 5397392 | 4414 | 105.936 | 4.414 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47475368 | 1232 | 279.1119 | 0% | 0% | 100% | 100% | 100% | 70% | 10920465 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 127 | 140 | 5402972 | 5580 | 133.92 | 5.58 | 9.1 | 9.1 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47476676 | 1308 | 234.4086 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 143 | 5408924 | 5952 | 142.848 | 5.952 | 8.3 | 8.3 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47478052 | 1376 | 231.1828 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 5415146 | 6222 | 149.328 | 6.222 | 7.6 | 7.6 | 3B+1S | 0 | 1068 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47479450 | 1398 | 224.6866 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 5421082 | 5936 | 142.464 | 5.936 | 7 | 7 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47480844 | 1394 | 234.8383 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 5427056 | 5974 | 143.376 | 5.974 | 6.3 | 6.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47482204 | 1360 | 227.6532 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 | 1.06
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 137 | 5433082 | 6026 | 144.624 | 6.026 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47483572 | 1368 | 227.0163 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 5439165 | 6083 | 145.992 | 6.083 | 5.3 | 5.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47484954 | 1382 | 227.1905 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 5444754 | 5589 | 134.136 | 5.589 | 4.9 | 4.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47486252 | 1298 | 232.2419 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 5450876 | 6122 | 146.928 | 6.122 | 4.5 | 4.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47487630 | 1378 | 225.0898 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 | 0.72 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 142 | 5456753 | 5877 | 141.048 | 5.877 | 4.2 | 4.2 | 3B+1S | 0 | 1023 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47488996 | 1366 | 232.4315 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 137 | 5462568 | 5815 | 139.56 | 5.815 | 4 | 4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47490332 | 1336 | 229.7506 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 5468427 | 5859 | 140.616 | 5.859 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47491668 | 1336 | 228.0253 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 140 | 5474230 | 5803 | 139.272 | 5.803 | 3.6 | 3.6 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47493004 | 1336 | 230.2257 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 | 1.36 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 5480052 | 5822 | 139.728 | 5.822 | 3.3 | 3.3 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47494344 | 1340 | 230.1615 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 135 | 5485922 | 5870 | 140.88 | 5.87 | 2.9 | 2.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47495700 | 1356 | 231.0051 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 139 | 5491715 | 5793 | 139.032 | 5.793 | 2.4 | 2.4 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47497060 | 1360 | 234.7661 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 138 | 5497318 | 5603 | 134.472 | 5.603 | 1.9 | 1.9 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47498380 | 1320 | 235.5881 | 0% | 100% | 100% | 100% | 100% | 0% | 10920465 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 127 | 5502984 | 5666 | 135.984 | 5.666 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47499692 | 1312 | 231.5567 | 0% | 0% | 100% | 100% | 100% | 30% | 10920521 | 56 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 122 | 5507954 | 4970 | 119.28 | 4.97 | 2.2 | 2.2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47500868 | 1176 | 236.6197 | 0% | 0% | 100% | 100% | 100% | 30% | 10920787 | 266 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133860 | 133.86 | 133.86 | [12 empty] | 31580 | 31580 | 235.9181 | [6 empty] | 2772 | 2772 | 1.0967 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
SP2- STARTED @ 5:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31440 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5507954 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47500868 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10920787 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 145 | 125 | 5513142 | 5188 | 124.512 | 5.188 | 2.7 | 2.7 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47502108 | 1240 | 239.0131 | 0% | 0% | 100% | 100% | 100% | 70% | 10921412 | 625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 145 | 124 | 5518152 | 5010 | 120.24 | 5.01 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47503358 | 1250 | 249.501 | 0% | 0% | 100% | 100% | 100% | 70% | 10922112 | 700 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 144 | 125 | 5523324 | 5172 | 124.128 | 5.172 | 4.6 | 4.6 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47504600 | 1242 | 240.1392 | 0% | 0% | 100% | 100% | 100% | 70% | 10922831 | 719 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 142 | 122 | 5526832 | 3508 | 84.192 | 3.508 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47505836 | 1236 | 352.3375 | 0% | 0% | 100% | 100% | 100% | 70% | 10923021 | 190 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 137 | 130 | 5531454 | 4622 | 110.928 | 4.622 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47507166 | 1330 | 287.7542 | 0% | 0% | 100% | 100% | 100% | 70% | 10923081 | 60 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 141 | 5537139 | 5685 | 136.44 | 5.685 | 9.2 | 9.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47508492 | 1326 | 233.2454 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 | 1.27 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 140 | 5543024 | 5885 | 141.24 | 5.885 | 8.6 | 8.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47509840 | 1348 | 229.0569 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 5548990 | 5966 | 143.184 | 5.966 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47511188 | 1348 | 225.947 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 143 | 5555040 | 6050 | 145.2 | 6.05 | 7.6 | 7.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47512552 | 1364 | 225.4545 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 5561064 | 6024 | 144.576 | 6.024 | 7 | 7 | 3B+1S | 1069 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47513912 | 1360 | 225.7636 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 | 1.31
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 5567241 | 6177 | 148.248 | 6.177 | 6.4 | 6.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47515312 | 1400 | 226.6472 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 5573163 | 5922 | 142.128 | 5.922 | 5.9 | 5.9 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47516660 | 1348 | 227.6258 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 5579085 | 5922 | 142.128 | 5.922 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47518020 | 1360 | 229.6521 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 5584865 | 5780 | 138.72 | 5.78 | 5 | 5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47519348 | 1328 | 229.7578 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 5590622 | 5757 | 138.168 | 5.757 | 4.8 | 4.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47520675 | 1327 | 230.502 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 5596480 | 5858 | 140.592 | 5.858 | 4.6 | 4.6 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47522016 | 1341 | 228.9177 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 142 | 5602399 | 5919 | 142.056 | 5.919 | 4.2 | 4.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47523364 | 1348 | 227.7412 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 135 | 5608321 | 5922 | 142.128 | 5.922 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47524712 | 1348 | 227.6258 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 140 | 5614147 | 5826 | 139.824 | 5.826 | 3.5 | 3.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47526056 | 1344 | 230.69 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 5619632 | 5485 | 131.64 | 5.485 | 2.8 | 2.8 | 2B+1S | 1067 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47527156 | 1100 | 200.5469 | 100% | 0% | 100% | 100% | 0% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 140 | 5625414 | 5782 | 138.768 | 5.782 | 2.4 | 2.4 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47528452 | 1296 | 224.1439 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 134 | 5630958 | 5544 | 133.056 | 5.544 | 2 | 2 | 3B+1S | 1056 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47529812 | 1360 | 245.3102 | 100% | 0% | 100% | 100% | 100% | 0% | 10923081 | 0 | 1.4 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 128 | 5636312 | 5354 | 128.496 | 5.354 | 2.1 | 2.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47531068 | 1256 | 234.591 | 0% | 0% | 100% | 100% | 100% | 30% | 10923179 | 98 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 125 | 5641604 | 5292 | 127.008 | 5.292 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47532308 | 1240 | 234.3159 | 0% | 0% | 100% | 100% | 100% | 30% | 10923422 | 243 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133650 | 133.65 | 133.65 | [12 empty] | 31440 | 31440 | 235.2413 | [6 empty] | 2635 | 2635 | 1.2617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
SP1- STARTED @ 5:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:01 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 32168 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5641604 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47532308 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10923422 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 124 | 5646846 | 5242 | 125.808 | 5.242 | 3 | 3 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47533548 | 1240 | 236.5509 | 0% | 0% | 100% | 100% | 100% | 70% | 10924082 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 151 | 125 | 5651788 | 4942 | 118.608 | 4.942 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47534724 | 1176 | 237.9603 | 0% | 0% | 100% | 100% | 100% | 70% | 10924930 | 848 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 148 | 122 | 5657074 | 5286 | 126.864 | 5.286 | 5.1 | 5.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47535980 | 1256 | 237.6088 | 0% | 0% | 100% | 100% | 100% | 70% | 10925713 | 783 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 150 | 118 | 5660318 | 3244 | 77.856 | 3.244 | 8.1 | 8.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47537171 | 1191 | 367.1393 | 0% | 0% | 100% | 100% | 100% | 70% | 10926011 | 298 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 133 | 128 | 5665308 | 4990 | 119.76 | 4.99 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47538432 | 1261 | 252.7054 | 0% | 0% | 100% | 100% | 100% | 70% | 10926111 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 137 | 5670988 | 5680 | 136.32 | 5.68 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47539708 | 1276 | 224.6479 | 0% | 0% | 100% | 100% | 100% | 0% | 10926111 | 0 | 1.32 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 5676924 | 5936 | 142.464 | 5.936 | 9.2 | 9.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47541052 | 1344 | 226.4151 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 5683057 | 6133 | 147.192 | 6.133 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47542436 | 1384 | 225.6644 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 5689205 | 6148 | 147.552 | 6.148 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47543824 | 1388 | 225.7645 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 144 | 149 | 5695414 | 6209 | 149.016 | 6.209 | 7.3 | 7.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47545212 | 1388 | 223.5465 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 | 1.36
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 5701726 | 6312 | 151.488 | 6.312 | 6.7 | 6.7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47546596 | 1384 | 219.2649 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 5707796 | 6070 | 145.68 | 6.07 | 6.1 | 6.1 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47547972 | 1376 | 226.6886 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 144 | 5713850 | 6054 | 145.296 | 6.054 | 5.5 | 5.5 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47549348 | 1376 | 227.2877 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 142 | 5719650 | 5800 | 139.2 | 5.8 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47550621 | 1273 | 219.4828 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 143 | 5725538 | 5888 | 141.312 | 5.888 | 4.5 | 4.5 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47551992 | 1371 | 232.8465 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 142 | 141 | 5731582 | 6044 | 145.056 | 6.044 | 4 | 4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47553364 | 1372 | 227.002 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 143 | 5737495 | 5913 | 141.912 | 5.913 | 3.6 | 3.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47554700 | 1336 | 225.9428 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 140 | 139 | 5743499 | 6004 | 144.096 | 6.004 | 3.3 | 3.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47556052 | 1352 | 225.1832 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 141 | 5749466 | 5967 | 143.208 | 5.967 | 3.1 | 3.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47557392 | 1340 | 224.5685 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 | 144 | 5755291 | 5825 | 139.8 | 5.825 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47558732 | 1340 | 230.0429 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 140 | 5761207 | 5916 | 141.984 | 5.916 | 2.4 | 2.4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47560092 | 1360 | 229.8851 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 135 | 5767756 | 6549 | 157.176 | 6.549 | 2.2 | 2.2 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47561580 | 1488 | 227.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 10926111 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 130 | 5774056 | 6300 | 151.2 | 6.3 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47563020 | 1440 | 228.5714 | 0% | 0% | 100% | 100% | 100% | 30% | 10926191 | 80 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 128 | 5780341 | 6285 | 150.84 | 6.285 | 2.4 | 2.4 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47564476 | 1456 | 231.6627 | 0% | 0% | 100% | 100% | 100% | 30% | 10926305 | 114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 138737 | 138.737 | 138.737 | [12 empty] | 32168 | 32168 | 231.8632 | [6 empty] | 2883 | 2883 | 1.2183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30872 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5780341 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47564476 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10926305 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 139 | 126 | 5783675 | 3334 | 80.016 | 3.334 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47565260 | 784 | 235.153 | 0% | 0% | 100% | 100% | 100% | 70% | 10926529 | 224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 123 | 5788556 | 4881 | 117.144 | 4.881 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47566424 | 1164 | 238.4757 | 0% | 0% | 100% | 100% | 100% | 70% | 10927078 | 549 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 144 | 121 | 5793666 | 5110 | 122.64 | 5.11 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47567648 | 1224 | 239.5303 | 0% | 0% | 100% | 100% | 100% | 70% | 10927713 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 140 | 120 | 5796912 | 3246 | 77.904 | 3.246 | 7.1 | 7.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47568918 | 1270 | 391.2508 | 0% | 0% | 100% | 100% | 100% | 70% | 10927800 | 87 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 123 | 5800572 | 3660 | 87.84 | 3.66 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47570064 | 1146 | 313.1148 | 0% | 0% | 100% | 100% | 100% | 70% | 10927807 | 7 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 133 | 5806382 | 5810 | 139.44 | 5.81 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47571340 | 1276 | 219.6213 | 0% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 | 1.29 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 138 | 5812171 | 5789 | 138.936 | 5.789 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47572604 | 1264 | 218.3451 | 0% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 5818148 | 5977 | 143.448 | 5.977 | 9.4 | 9.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47573936 | 1332 | 222.8543 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 148 | 5824310 | 6162 | 147.888 | 6.162 | 8.7 | 8.7 | 3B+1S | 1069 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47575308 | 1372 | 222.655 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 5830543 | 6233 | 149.592 | 6.233 | 8 | 8 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47576700 | 1392 | 223.3275 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 | 1.33
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 145 | 5836683 | 6140 | 147.36 | 6.14 | 7.3 | 7.3 | 3B+1S | 1078 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47578084 | 1384 | 225.4072 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 5842744 | 6061 | 145.464 | 6.061 | 6.6 | 6.6 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47579452 | 1368 | 225.7053 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 143 | 5848717 | 5973 | 143.352 | 5.973 | 6 | 6 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47580812 | 1360 | 227.6913 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 5854642 | 5925 | 142.2 | 5.925 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47582156 | 1344 | 226.8354 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 142 | 5860675 | 6033 | 144.792 | 6.033 | 5 | 5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47583512 | 1356 | 224.7638 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 143 | 5866700 | 6025 | 144.6 | 6.025 | 4.6 | 4.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47584864 | 1352 | 224.3983 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 5872630 | 5930 | 142.32 | 5.93 | 4.1 | 4.1 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47586208 | 1344 | 226.6442 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 142 | 5878594 | 5964 | 143.136 | 5.964 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47587552 | 1344 | 225.3521 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 | 1.37 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 140 | 143 | 5884546 | 5952 | 142.848 | 5.952 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47588888 | 1336 | 224.4624 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 137 | 5890369 | 5823 | 139.752 | 5.823 | 3 | 3 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47590216 | 1328 | 228.0611 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 141 | 5896258 | 5889 | 141.336 | 5.889 | 2.6 | 2.6 | 3B+1S | 1086 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47591552 | 1336 | 226.8636 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 140 | 5901782 | 5524 | 132.576 | 5.524 | 2.1 | 2.1 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47592876 | 1324 | 239.6814 | 100% | 0% | 100% | 100% | 100% | 0% | 10927807 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 128 | 5907304 | 5522 | 132.528 | 5.522 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47594140 | 1264 | 228.9026 | 0% | 0% | 100% | 100% | 100% | 30% | 10927932 | 125 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 142 | 126 | 5912523 | 5219 | 125.256 | 5.219 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47595348 | 1208 | 231.462 | 0% | 0% | 100% | 100% | 100% | 30% | 10928266 | 334 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132182 | 132.182 | 132.182 | [12 empty] | 30872 | 30872 | 233.5568 | [6 empty] | 1961 | 1961 | 1.29 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31016 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 5912523 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47595348 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10928266 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 144 | 126 | 5917784 | 5261 | 126.264 | 5.261 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47596580 | 1232 | 234.176 | 0% | 0% | 100% | 100% | 100% | 70% | 10928826 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 118 | 5923040 | 5256 | 126.144 | 5.256 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47597820 | 1240 | 235.9209 | 0% | 0% | 100% | 100% | 100% | 70% | 10929500 | 674 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 119 | 5928006 | 4966 | 119.184 | 4.966 | 4.7 | 4.7 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47598972 | 1152 | 231.9774 | 0% | 0% | 100% | 100% | 100% | 70% | 10930114 | 614 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 140 | 118 | 5931176 | 3170 | 76.08 | 3.17 | 7.6 | 7.6 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47600134 | 1162 | 366.5615 | 0% | 0% | 100% | 100% | 100% | 70% | 10930337 | 223 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 127 | 5935796 | 4620 | 110.88 | 4.62 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47601408 | 1274 | 275.7576 | 0% | 0% | 100% | 100% | 100% | 70% | 10930437 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 136 | 5941576 | 5780 | 138.72 | 5.78 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47602756 | 1348 | 233.218 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 5947504 | 5928 | 142.272 | 5.928 | 8.6 | 8.6 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47604116 | 1360 | 229.4197 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 5953558 | 6054 | 145.296 | 6.054 | 8 | 8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47605484 | 1368 | 225.9663 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 5959669 | 6111 | 146.664 | 6.111 | 7.4 | 7.4 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47606852 | 1368 | 223.8586 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 5965687 | 6018 | 144.432 | 6.018 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47608228 | 1376 | 228.6474 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 | 1.34
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 5971655 | 5968 | 143.232 | 5.968 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47609540 | 1312 | 219.8391 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 5977401 | 5746 | 137.904 | 5.746 | 6 | 6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47610924 | 1384 | 240.8632 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 143 | 5983421 | 6020 | 144.48 | 6.02 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47612276 | 1352 | 224.5847 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 137 | 5989221 | 5800 | 139.2 | 5.8 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47613612 | 1336 | 230.3448 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 144 | 5995028 | 5807 | 139.368 | 5.807 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47614940 | 1328 | 228.6895 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 144 | 6000911 | 5883 | 141.192 | 5.883 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47616280 | 1340 | 227.7749 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 141 | 6006827 | 5916 | 141.984 | 5.916 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47617624 | 1344 | 227.1805 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 141 | 6012748 | 5921 | 142.104 | 5.921 | 4.1 | 4.1 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47618972 | 1348 | 227.6642 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 139 | 6018556 | 5808 | 139.392 | 5.808 | 3.8 | 3.8 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47620316 | 1344 | 231.405 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 130 | 6024010 | 5454 | 130.896 | 5.454 | 3.1 | 3.1 | 2B+1S | 0 | 1077 |  | 1185 | 1187 | N/A | N/A | N/A | N/A | 47621396 | 1080 | 198.0198 | 0% | 100% | 0% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 140 | 6029612 | 5602 | 134.448 | 5.602 | 2.4 | 2.4 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47622620 | 1224 | 218.4934 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 136 | 6034983 | 5371 | 128.904 | 5.371 | 2 | 2 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47623900 | 1280 | 238.3169 | 0% | 100% | 100% | 100% | 100% | 0% | 10930437 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 127 | 6040360 | 5377 | 129.048 | 5.377 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47625140 | 1240 | 230.6119 | 0% | 0% | 100% | 100% | 100% | 20% | 10930478 | 41 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 121 | 6045595 | 5235 | 125.64 | 5.235 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47626364 | 1224 | 233.8109 | 0% | 0% | 100% | 100% | 100% | 20% | 10930650 | 172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133072 | 133.072 | 133.072 | [12 empty] | 31016 | 31016 | 233.0768 | [6 empty] | 2384 | 2384 | 1.2317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2- STARTED @ 5:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
BP2- STOPPED @ 8:01PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP2- STARTED @ 8:20PM DUE TO MONTHLY PREVENTIVE MAINTENANCE
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## JUNE 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31316 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6045595 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47626364 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10930650 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 146 | 120 | 6050174 | 4579 | 109.896 | 4.579 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47627561 | 1197 | 261.4108 | 0% | 0% | 100% | 100% | 100% | 60% | 10931297 | 647 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 150 | 122 | 6054762 | 4588 | 110.112 | 4.588 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47628771 | 1210 | 263.7315 | 0% | 0% | 100% | 100% | 100% | 60% | 10932000 | 703 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 145 | 119 | 6059393 | 4631 | 111.144 | 4.631 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47630032 | 1261 | 272.2954 | 0% | 0% | 100% | 100% | 100% | 60% | 10932600 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 138 | 125 | 6063923 | 4530 | 108.72 | 4.53 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47631300 | 1268 | 279.9117 | 0% | 0% | 100% | 100% | 100% | 60% | 10932922 | 322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 128 | 6068618 | 4695 | 112.68 | 4.695 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47632548 | 1248 | 265.8147 | 0% | 0% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 140 | 6074641 | 6023 | 144.552 | 6.023 | 9.3 | 9.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47633912 | 1364 | 226.4652 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 | 1.42 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 141 | 6080571 | 5930 | 142.32 | 5.93 | 8.7 | 8.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47635268 | 1356 | 228.6678 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 6086609 | 6038 | 144.912 | 6.038 | 8.1 | 8.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47636628 | 1360 | 225.2401 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 143 | 6092733 | 6124 | 146.976 | 6.124 | 7.4 | 7.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47638028 | 1400 | 228.6088 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 6098591 | 5858 | 140.592 | 5.858 | 6.9 | 6.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47639348 | 1320 | 225.3329 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 | 1.44
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 6104607 | 6016 | 144.384 | 6.016 | 6.5 | 6.5 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47640712 | 1364 | 226.7287 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 6110354 | 5747 | 137.928 | 5.747 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47642028 | 1316 | 228.989 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 6116117 | 5763 | 138.312 | 5.763 | 5.7 | 5.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47643364 | 1336 | 231.8237 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 6121804 | 5687 | 136.488 | 5.687 | 5.4 | 5.4 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47644676 | 1312 | 230.7016 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 141 | 6127540 | 5736 | 137.664 | 5.736 | 5.2 | 5.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47646004 | 1328 | 231.5202 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 6133267 | 5727 | 137.448 | 5.727 | 5 | 5 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47647328 | 1324 | 231.1856 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 6139096 | 5829 | 139.896 | 5.829 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47648660 | 1332 | 228.5126 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 139 | 6144973 | 5877 | 141.048 | 5.877 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47649996 | 1336 | 227.3269 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 | 1.37 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 6150782 | 5809 | 139.416 | 5.809 | 4.3 | 4.3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47651324 | 1328 | 228.6108 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 130 | 6156265 | 5483 | 131.592 | 5.483 | 3.5 | 3.5 | 2B+1S | 0 | 1078 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 47652436 | 1112 | 202.8087 | 0% | 100% | 100% | 100% | 0% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 142 | 6162117 | 5852 | 140.448 | 5.852 | 2.8 | 2.8 | 3B+1S | 0 | 1097 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47653796 | 1360 | 232.3992 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 122 | 138 | 6167802 | 5685 | 136.44 | 5.685 | 2.2 | 2.2 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47655148 | 1352 | 237.8188 | 0% | 100% | 100% | 100% | 100% | 0% | 10932922 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 127 | 6173038 | 5236 | 125.664 | 5.236 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47656364 | 1216 | 232.2383 | 0% | 0% | 100% | 100% | 100% | 30% | 10932965 | 43 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 143 | 119 | 6178905 | 5867 | 140.808 | 5.867 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47657680 | 1316 | 224.3054 | 0% | 0% | 100% | 100% | 100% | 30% | 10933477 | 512 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133310 | 133.31 | 133.31 | [12 empty] | 31316 | 31316 | 234.9111 | [6 empty] | 2827 | 2827 | 1.295 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (60%)
XCV2- CLOSED @ 3:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2- STARTED @ 5:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31068 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6178905 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47657680 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10933477 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 145 | 126 | 6183348 | 4443 | 106.632 | 4.443 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47658792 | 1112 | 250.2813 | 0% | 0% | 100% | 100% | 100% | 70% | 10933950 | 473 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 118 | 6188362 | 5014 | 120.336 | 5.014 | 4 | 4 | 3B | 0 | 0 | 1157 | 1185 | 115 | N/A | N/A | N/A | N/A | 47659952 | 1160 | 231.3522 | 0% | 0% | 100% | 100% | 100% | 70% | 10934525 | 575 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 119 | 6193414 | 5052 | 121.248 | 5.052 | 4.7 | 4.7 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47661116 | 1164 | 230.4038 | 0% | 0% | 100% | 100% | 100% | 70% | 10935152 | 627 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 136 | 120 | 6196906 | 3492 | 83.808 | 3.492 | 8 | 8 | 3B | 0 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47662246 | 1130 | 323.5968 | 0% | 0% | 100% | 100% | 100% | 70% | 10935299 | 147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 131 | 6201728 | 4822 | 115.728 | 4.822 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47663530 | 1284 | 266.2796 | 0% | 0% | 100% | 100% | 100% | 70% | 10935374 | 75 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 145 | 6207618 | 5890 | 141.36 | 5.89 | 9 | 9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47664980 | 1450 | 246.18 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 | 1.38 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 6213661 | 6043 | 145.032 | 6.043 | 8.4 | 8.4 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47666348 | 1368 | 226.3776 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 6219688 | 6027 | 144.648 | 6.027 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47667708 | 1360 | 225.6512 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 6225687 | 5999 | 143.976 | 5.999 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47669060 | 1352 | 225.3709 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 6231814 | 6127 | 147.048 | 6.127 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47670436 | 1376 | 224.5797 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 | 1.42
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 6237895 | 6081 | 145.944 | 6.081 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47671804 | 1368 | 224.963 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 6243837 | 5942 | 142.608 | 5.942 | 5.8 | 5.8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47673172 | 1368 | 230.2255 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 6249692 | 5855 | 140.52 | 5.855 | 5.3 | 5.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47674524 | 1352 | 230.9137 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 6255416 | 5724 | 137.376 | 5.724 | 4.9 | 4.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47675848 | 1324 | 231.3068 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 143 | 6261337 | 5921 | 142.104 | 5.921 | 4.7 | 4.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47677192 | 1344 | 226.9887 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 142 | 6267235 | 5898 | 141.552 | 5.898 | 4.5 | 4.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47678536 | 1344 | 227.8739 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 142 | 6273100 | 5865 | 140.76 | 5.865 | 4.2 | 4.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47679876 | 1340 | 228.474 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 138 | 6278960 | 5860 | 140.64 | 5.86 | 3.8 | 3.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47681216 | 1340 | 228.6689 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 136 | 6284784 | 5824 | 139.776 | 5.824 | 3.7 | 3.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47682536 | 1320 | 226.6484 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 126 | 6290284 | 5500 | 132 | 5.5 | 3 | 3 | 2B+1S | 1077 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47683652 | 1116 | 202.9091 | 100% | 0% | 0% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 137 | 6296100 | 5816 | 139.584 | 5.816 | 2.5 | 2.5 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47684988 | 1336 | 229.7111 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 132 | 6301766 | 5666 | 135.984 | 5.666 | 2.1 | 2.1 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47686304 | 1316 | 232.2626 | 100% | 0% | 100% | 100% | 100% | 0% | 10935374 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 129 | 6306952 | 5186 | 124.464 | 5.186 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47687508 | 1204 | 232.1635 | 0% | 0% | 100% | 100% | 100% | 30% | 10935447 | 73 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 125 | 6312232 | 5280 | 126.72 | 5.28 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47688748 | 1240 | 234.8485 | 0% | 0% | 100% | 100% | 100% | 30% | 10935773 | 326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133327 | 133.327 | 133.327 | [12 empty] | 31068 | 31068 | 233.0211 | [6 empty] | 2296 | 2296 | 1.3167 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1- STARTED @ 5:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUNE 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30968 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6312232 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47688748 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10935773 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 120 | 6317374 | 5142 | 123.408 | 5.142 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47689980 | 1232 | 239.5955 | 0% | 0% | 100% | 100% | 100% | 70% | 10936087 | 314 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 119 | 6322286 | 4912 | 117.888 | 4.912 | 3.5 | 3.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47691132 | 1152 | 234.5277 | 0% | 0% | 100% | 100% | 100% | 70% | 10936560 | 473 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 116 | 6327156 | 4870 | 116.88 | 4.87 | 4.2 | 4.2 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47692272 | 1140 | 234.0862 | 0% | 0% | 100% | 100% | 100% | 70% | 10937150 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 136 | 110 | 6330422 | 3266 | 78.384 | 3.266 | 7.2 | 7.2 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47693404 | 1132 | 346.6013 | 0% | 0% | 100% | 100% | 100% | 70% | 10937298 | 148 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 128 | 6334606 | 4184 | 100.416 | 4.184 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 47694686 | 1282 | 306.4054 | 0% | 0% | 100% | 100% | 100% | 70% | 10937368 | 70 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 140 | 6340175 | 5569 | 133.656 | 5.569 | 9.3 | 9.3 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47695972 | 1286 | 230.9212 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 | 1.28 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 6346106 | 5931 | 142.344 | 5.931 | 8.8 | 8.8 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47697316 | 1344 | 226.606 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 6352160 | 6054 | 145.296 | 6.054 | 8.3 | 8.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47698668 | 1352 | 223.3234 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 6358160 | 6000 | 144 | 6 | 7.8 | 7.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47700012 | 1344 | 224 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 6364203 | 6043 | 145.032 | 6.043 | 7.4 | 7.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47701372 | 1360 | 225.0538 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 | 1.35
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 136 | 6370243 | 6040 | 144.96 | 6.04 | 6.9 | 6.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47702724 | 1352 | 223.8411 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 6376182 | 5939 | 142.536 | 5.939 | 6.5 | 6.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47704044 | 1320 | 222.2596 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 135 | 6381958 | 5776 | 138.624 | 5.776 | 6.2 | 6.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47705412 | 1368 | 236.8421 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 6388068 | 6110 | 146.64 | 6.11 | 5.9 | 5.9 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47706820 | 1408 | 230.4419 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 135 | 6393788 | 5720 | 137.28 | 5.72 | 5.7 | 5.7 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47708144 | 1324 | 231.4685 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 6399575 | 5787 | 138.888 | 5.787 | 5.5 | 5.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47709468 | 1324 | 228.7887 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 6405447 | 5872 | 140.928 | 5.872 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47710816 | 1348 | 229.564 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 143 | 6411276 | 5829 | 139.896 | 5.829 | 5 | 5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47712148 | 1332 | 228.5126 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 6417146 | 5870 | 140.88 | 5.87 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47713492 | 1344 | 228.9608 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 131 | 6422651 | 5505 | 132.12 | 5.505 | 3.9 | 3.9 | 2B+1S | 0 | 1078 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47714596 | 1104 | 200.545 | 0% | 100% | 100% | 100% | 0% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 133 | 6428352 | 5701 | 136.824 | 5.701 | 3.2 | 3.2 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47715940 | 1344 | 235.7481 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 122 | 134 | 6434082 | 5730 | 137.52 | 5.73 | 2.7 | 2.7 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47717316 | 1376 | 240.1396 | 0% | 100% | 100% | 100% | 100% | 0% | 10937368 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 129 | 6439494 | 5412 | 129.888 | 5.412 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47718596 | 1280 | 236.5115 | 0% | 0% | 100% | 100% | 100% | 30% | 10937429 | 61 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 121 | 6444156 | 4662 | 111.888 | 4.662 | 3 | 3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47719716 | 1120 | 240.2402 | 0% | 0% | 100% | 100% | 100% | 30% | 10937856 | 427 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131924 | 131.924 | 131.924 | [12 empty] | 30968 | 30968 | 234.7412 | [6 empty] | 2083 | 2083 | 1.2883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2- STARTED @ 5:16 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31016 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6444156 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47719716 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10937856 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 145 | 116 | 6449066 | 4910 | 117.84 | 4.91 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47720928 | 1212 | 246.8432 | 0% | 0% | 100% | 100% | 100% | 70% | 10938555 | 699 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 113 | 6453734 | 4668 | 112.032 | 4.668 | 4.8 | 4.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47722072 | 1144 | 245.0728 | 0% | 0% | 100% | 100% | 100% | 70% | 10939304 | 749 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 114 | 6458566 | 4832 | 115.968 | 4.832 | 5.7 | 5.7 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47723236 | 1164 | 240.894 | 0% | 0% | 100% | 100% | 100% | 70% | 10940060 | 756 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 116 | 6461704 | 3138 | 75.312 | 3.138 | 8.7 | 8.7 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47724372 | 1136 | 362.014 | 0% | 0% | 100% | 100% | 100% | 70% | 10940281 | 221 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 121 | 6466706 | 5002 | 120.048 | 5.002 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47725612 | 1240 | 247.9008 | 0% | 0% | 100% | 100% | 100% | 70% | 10940381 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 139 | 6472638 | 5932 | 142.368 | 5.932 | 9.4 | 9.4 | 3B+1S | 995 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47726964 | 1352 | 227.9164 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 | 1.35 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 6478541 | 5903 | 141.672 | 5.903 | 9 | 9 | 3B+1S | 1048 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47728316 | 1352 | 229.0361 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 6484698 | 6157 | 147.768 | 6.157 | 8.3 | 8.3 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47729708 | 1392 | 226.0841 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 145 | 6490803 | 6105 | 146.52 | 6.105 | 7.7 | 7.7 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47731068 | 1360 | 222.7682 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 6496992 | 6189 | 148.536 | 6.189 | 7.1 | 7.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47732444 | 1376 | 222.3299 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 | 1.38
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 148 | 6503098 | 6106 | 146.544 | 6.106 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47733820 | 1376 | 225.3521 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 6509029 | 5931 | 142.344 | 5.931 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47735156 | 1336 | 225.2571 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 6514885 | 5856 | 140.544 | 5.856 | 5.6 | 5.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47736500 | 1344 | 229.5082 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 6520641 | 5756 | 138.144 | 5.756 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47737836 | 1336 | 232.1056 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 6526369 | 5728 | 137.472 | 5.728 | 5 | 5 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47739156 | 1320 | 230.4469 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 132 | 6531926 | 5557 | 133.368 | 5.557 | 4.9 | 4.9 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47740464 | 1308 | 235.3788 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 6537768 | 5842 | 140.208 | 5.842 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47741796 | 1332 | 228.0041 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 6543596 | 5828 | 139.872 | 5.828 | 4.4 | 4.4 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47743132 | 1336 | 229.2382 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 6549347 | 5751 | 138.024 | 5.751 | 4 | 4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47744452 | 1320 | 229.5253 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 131 | 6554813 | 5466 | 131.184 | 5.466 | 3.3 | 3.3 | 2B+1S | 1078 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47745580 | 1128 | 206.3666 | 100% | 0% | 0% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 138 | 6560550 | 5737 | 137.688 | 5.737 | 2.7 | 2.7 | 3B+1S | 1096 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47746920 | 1340 | 233.5716 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 130 | 6566166 | 5616 | 134.784 | 5.616 | 2.2 | 2.2 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47748272 | 1352 | 240.7407 | 100% | 0% | 100% | 100% | 100% | 0% | 10940381 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 124 | 6571412 | 5246 | 125.904 | 5.246 | 2.3 | 2.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47749512 | 1240 | 236.3706 | 0% | 0% | 100% | 100% | 100% | 30% | 10940519 | 138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 119 | 6576504 | 5092 | 122.208 | 5.092 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47750732 | 1220 | 239.5915 | 0% | 0% | 100% | 100% | 100% | 30% | 10940987 | 468 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132348 | 132.348 | 132.348 | [12 empty] | 31016 | 31016 | 234.3519 | [6 empty] | 3131 | 3131 | 1.2667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1- STARTED @ 5:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUNE 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31152 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6576504 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47750732 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10940987 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 144 | 123 | 6581564 | 5060 | 121.44 | 5.06 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47751980 | 1248 | 246.6403 | 0% | 0% | 100% | 100% | 100% | 70% | 10941604 | 617 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 110 | 6586366 | 4802 | 115.248 | 4.802 | 4.7 | 4.7 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 47753140 | 1160 | 241.566 | 0% | 0% | 100% | 100% | 100% | 70% | 10942455 | 851 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 108 | 6590892 | 4526 | 108.624 | 4.526 | 5.7 | 5.7 | 3B | 0 | 0 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 47754204 | 1064 | 235.0862 | 0% | 0% | 100% | 100% | 100% | 70% | 10943206 | 751 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 140 | 107 | 6594118 | 3226 | 77.424 | 3.226 | 8.6 | 8.6 | 3B | 0 | 0 | 1127 | 1185 | 1128 | N/A | N/A | N/A | N/A | 47755220 | 1016 | 314.9411 | 0% | 0% | 100% | 100% | 100% | 70% | 10943554 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 120 | 6598988 | 4870 | 116.88 | 4.87 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 47756442 | 1222 | 250.924 | 0% | 0% | 100% | 100% | 100% | 70% | 10943730 | 176 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 133 | 6604608 | 5620 | 134.88 | 5.62 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47757724 | 1282 | 228.1139 | 0% | 0% | 100% | 100% | 100% | 0% | 10943730 | 0 | 1.3 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 143 | 6610481 | 5873 | 140.952 | 5.873 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47758996 | 1272 | 216.5844 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 6616668 | 6187 | 148.488 | 6.187 | 8.9 | 8.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47760368 | 1372 | 221.7553 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 148 | 6622883 | 6215 | 149.16 | 6.215 | 8.3 | 8.3 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47761760 | 1392 | 223.9743 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 6628978 | 6095 | 146.28 | 6.095 | 7.6 | 7.6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47763116 | 1356 | 222.4774 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 | 1.34
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 6635228 | 6250 | 150 | 6.25 | 6.9 | 6.9 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47764516 | 1400 | 224 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 148 | 6641352 | 6124 | 146.976 | 6.124 | 6.3 | 6.3 | 3B+1S | 0 | 1088 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47765900 | 1384 | 225.9961 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 6647359 | 6007 | 144.168 | 6.007 | 5.6 | 5.6 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47767276 | 1376 | 229.0661 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 6653305 | 5946 | 142.704 | 5.946 | 5 | 5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47768636 | 1360 | 228.7252 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 140 | 6658823 | 5518 | 132.432 | 5.518 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47769892 | 1256 | 227.6187 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 139 | 6664655 | 5832 | 139.968 | 5.832 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47771224 | 1332 | 228.3951 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 6670540 | 5885 | 141.24 | 5.885 | 3.9 | 3.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47772572 | 1348 | 229.0569 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 139 | 6676408 | 5868 | 140.832 | 5.868 | 3.6 | 3.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47773908 | 1336 | 227.6755 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 131 | 6682254 | 5846 | 140.304 | 5.846 | 3.3 | 3.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47775244 | 1336 | 228.5323 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 138 | 6687994 | 5740 | 137.76 | 5.74 | 3.1 | 3.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47776560 | 1316 | 229.2683 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 138 | 6694322 | 6328 | 151.872 | 6.328 | 2.6 | 2.6 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47778008 | 1448 | 228.8243 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 139 | 6700098 | 5776 | 138.624 | 5.776 | 2.2 | 2.2 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47779380 | 1372 | 237.5346 | 0% | 100% | 100% | 100% | 100% | 0% | 10943730 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 123 | 6705508 | 5410 | 129.84 | 5.41 | 2 | 2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47780670 | 1290 | 238.4473 | 0% | 0% | 100% | 100% | 100% | 30% | 10943865 | 135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 122 | 6710566 | 5058 | 121.392 | 5.058 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47781884 | 1214 | 240.0158 | 0% | 0% | 100% | 100% | 100% | 30% | 10944143 | 278 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134062 | 134.062 | 134.062 | [12 empty] | 31152 | 31152 | 232.3701 | [6 empty] | 3156 | 3156 | 1.2517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30802 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6710566 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47781884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10944143 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 141 | 119 | 6715807 | 5241 | 125.784 | 5.241 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47783148 | 1264 | 241.1753 | 0% | 0% | 100% | 100% | 100% | 70% | 10944666 | 523 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 115 | 6720534 | 4727 | 113.448 | 4.727 | 3.6 | 3.6 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47784300 | 1152 | 243.7064 | 0% | 0% | 100% | 100% | 100% | 70% | 10945363 | 697 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 118 | 6726154 | 5620 | 134.88 | 5.62 | 4.9 | 4.9 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 47785596 | 1296 | 230.605 | 0% | 0% | 100% | 100% | 100% | 70% | 10946064 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 134 | 117 | 6728872 | 2718 | 65.232 | 2.718 | 7.1 | 7.1 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47786628 | 1032 | 379.6909 | 0% | 0% | 100% | 100% | 100% | 70% | 10946386 | 322 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 119 | 6733122 | 4250 | 102 | 4.25 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 1057 | N/A | N/A | N/A | N/A | 47787836 | 1208 | 284.2353 | 0% | 0% | 100% | 100% | 100% | 70% | 10946586 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 133 | 6738439 | 5317 | 127.608 | 5.317 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1097 | N/A | N/A | N/A | N/A | 47788916 | 1080 | 203.1221 | 0% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 | 1.31 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 136 | 6744201 | 5762 | 138.288 | 5.762 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47790144 | 1228 | 213.1204 | 0% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 147 | 6750324 | 6123 | 146.952 | 6.123 | 9 | 9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47791420 | 1276 | 208.3946 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 149 | 6756552 | 6228 | 149.472 | 6.228 | 8.5 | 8.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47792804 | 1384 | 222.2222 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 6762737 | 6185 | 148.44 | 6.185 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47794180 | 1376 | 222.4737 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 | 1.27
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 6768937 | 6200 | 148.8 | 6.2 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47795560 | 1380 | 222.5806 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 6775051 | 6114 | 146.736 | 6.114 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47796936 | 1376 | 225.0572 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 6780960 | 5909 | 141.816 | 5.909 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47798292 | 1356 | 229.4805 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 139 | 6786827 | 5867 | 140.808 | 5.867 | 5.6 | 5.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47799628 | 1336 | 227.7143 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 6792572 | 5745 | 137.88 | 5.745 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47800956 | 1328 | 231.1575 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 6798454 | 5882 | 141.168 | 5.882 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47802284 | 1328 | 225.7735 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 138 | 6804361 | 5907 | 141.768 | 5.907 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47803628 | 1344 | 227.5267 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 139 | 6810128 | 5767 | 138.408 | 5.767 | 4.6 | 4.6 | 3B+1S | 996 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47804940 | 1312 | 227.5013 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 139 | 6815922 | 5794 | 139.056 | 5.794 | 4.4 | 4.4 | 3B+1S | 994 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47806260 | 1320 | 227.8219 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 115 | 132 | 6821369 | 5447 | 130.728 | 5.447 | 3.6 | 3.6 | 2B+1S | 1057 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47807356 | 1096 | 201.2117 | 100% | 0% | 100% | 100% | 0% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 139 | 6827106 | 5737 | 137.688 | 5.737 | 3 | 3 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47808704 | 1348 | 234.966 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 135 | 6832784 | 5678 | 136.272 | 5.678 | 2.6 | 2.6 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47810060 | 1356 | 238.8165 | 100% | 0% | 100% | 100% | 100% | 0% | 10946586 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 120 | 6837982 | 5198 | 124.752 | 5.198 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47811300 | 1240 | 238.5533 | 0% | 0% | 100% | 100% | 100% | 30% | 10946782 | 196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 119 | 6843674 | 5692 | 136.608 | 5.692 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47812686 | 1386 | 243.4996 | 0% | 0% | 100% | 100% | 100% | 30% | 10947177 | 395 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133108 | 133.108 | 133.108 | [12 empty] | 30802 | 30802 | 231.4061 | [6 empty] | 3034 | 3034 | 1.2383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV1- INCREASE OPENING @ 12:00 AM (70%)
XCV1- CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3 - STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUNE 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30578 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6843674 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47812686 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10947177 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 108 | 6847736 | 4062 | 97.488 | 4.062 | 3.8 | 3.8 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 47813688 | 1002 | 246.6765 | 0% | 0% | 100% | 100% | 100% | 70% | 10947854 | 677 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 105 | 6852394 | 4658 | 111.792 | 4.658 | 5 | 5 | 3B | 0 | 0 | 1137 | 1185 | 1136 | N/A | N/A | N/A | N/A | 47814828 | 1140 | 244.7402 | 0% | 0% | 100% | 100% | 100% | 70% | 10948825 | 971 | 1.37 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 146 | 107 | 6856926 | 4532 | 108.768 | 4.532 | 6 | 6 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 47815928 | 1100 | 242.7184 | 0% | 0% | 100% | 100% | 100% | 70% | 10949727 | 902 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 145 | 104 | 6860772 | 3846 | 92.304 | 3.846 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 47817012 | 1084 | 281.8513 | 0% | 0% | 100% | 100% | 100% | 70% | 10949935 | 208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 125 | 6865544 | 4772 | 114.528 | 4.772 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1138 | N/A | N/A | N/A | N/A | 47818260 | 1248 | 261.5256 | 0% | 0% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 148 | 6871694 | 6150 | 147.6 | 6.15 | 9.3 | 9.3 | 3B+1S | 0 | 1070 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47819648 | 1388 | 225.6911 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 | 1.48 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 144 | 6877793 | 6099 | 146.376 | 6.099 | 8.7 | 8.7 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47821004 | 1356 | 222.3315 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 6884019 | 6226 | 149.424 | 6.226 | 8.1 | 8.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47822384 | 1380 | 221.6511 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 148 | 6890253 | 6234 | 149.616 | 6.234 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47823756 | 1372 | 220.0834 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 149 | 6896524 | 6271 | 150.504 | 6.271 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47825140 | 1384 | 220.6985 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 | 1.36
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 150 | 6902823 | 6299 | 151.176 | 6.299 | 6.4 | 6.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47826524 | 1384 | 219.7174 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 6908991 | 6168 | 148.032 | 6.168 | 6 | 6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47827884 | 1360 | 220.4929 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 140 | 6914917 | 5926 | 142.224 | 5.926 | 5.7 | 5.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47829228 | 1344 | 226.7972 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 139 | 138 | 6920773 | 5856 | 140.544 | 5.856 | 5.5 | 5.5 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47830552 | 1324 | 226.0929 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 134 | 6926474 | 5701 | 136.824 | 5.701 | 5.4 | 5.4 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47831868 | 1316 | 230.8367 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 6932073 | 5599 | 134.376 | 5.599 | 5.3 | 5.3 | 3B+1S | 0 | 995 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47833180 | 1312 | 234.3276 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 6937665 | 5592 | 134.208 | 5.592 | 5.2 | 5.2 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47834492 | 1312 | 234.6209 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 6943140 | 5475 | 131.4 | 5.475 | 5.1 | 5.1 | 3B+1S | 0 | 997 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47835796 | 1304 | 238.1735 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 137 | 6949019 | 5879 | 141.096 | 5.879 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47837140 | 1344 | 228.6103 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 133 | 6954385 | 5366 | 128.784 | 5.366 | 4.1 | 4.1 | 2B+1S | 0 | 1099 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47838236 | 1096 | 204.249 | 0% | 100% | 0% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 141 | 6960195 | 5810 | 139.44 | 5.81 | 3.3 | 3.3 | 3B+1S | 0 | 1098 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47839572 | 1336 | 229.9484 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 136 | 133 | 6965607 | 5412 | 129.888 | 5.412 | 3 | 3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47840844 | 1272 | 235.0333 | 0% | 100% | 100% | 100% | 100% | 0% | 10949935 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 125 | 6970875 | 5268 | 126.432 | 5.268 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47842060 | 1216 | 230.8276 | 0% | 0% | 100% | 100% | 100% | 26% | 10950005 | 70 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 128 | 6975938 | 5063 | 121.512 | 5.063 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47843264 | 1204 | 237.8037 | 0% | 0% | 100% | 100% | 100% | 26% | 10950343 | 338 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132264 | 132.264 | 132.264 | [12 empty] | 30578 | 30578 | 231.1891 | [6 empty] | 3166 | 3166 | 1.3383 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
XCV2- INCREASE OPENING @ 12:00 AM (70%)
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2- STARTED @ 5:16 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (26%)

## JUNE 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30152 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 6975938 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47843264 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10950343 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 79 | 55.6338 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.4 | 137 | 106 | 6980348 | 4410 | 105.84 | 4.41 | 4.6 | 4.6 | 3B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 47844184 | 920 | 208.6168 | 0% | 0% | 100% | 0% | 100% | 60% | 10951377 | 1034 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 80 | 56.338 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A.ONG | 11.2 | 137 | 108 | 6984848 | 4500 | 108 | 4.5 | 5.8 | 5.8 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47845076 | 892 | 198.2222 | 0% | 0% | 100% | 100% | 0% | 60% | 10952260 | 883 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 106 | 6989198 | 4350 | 104.4 | 4.35 | 7.3 | 7.3 | 2B | 0 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47845988 | 912 | 209.6552 | 0% | 0% | 100% | 100% | 0% | 60% | 10953053 | 793 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 127 | 110 | 6993616 | 4418 | 106.032 | 4.418 | 8.9 | 8.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47847074 | 1086 | 245.8126 | 0% | 0% | 100% | 100% | 100% | 60% | 10954023 | 970 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 120 | 6998194 | 4578 | 109.872 | 4.578 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 47848196 | 1122 | 245.0852 | 0% | 0% | 100% | 100% | 100% | 60% | 10954318 | 295 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 140 | 7004345 | 6151 | 147.624 | 6.151 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47849540 | 1344 | 218.5011 | 0% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 144 | 7010356 | 6011 | 144.264 | 6.011 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47850820 | 1280 | 212.9429 | 0% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 148 | 7016599 | 6243 | 149.832 | 6.243 | 9.1 | 9.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47852188 | 1368 | 219.1254 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 149 | 7022904 | 6305 | 151.32 | 6.305 | 8.8 | 8.8 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47853560 | 1372 | 217.6051 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 148 | 7029167 | 6263 | 150.312 | 6.263 | 8.3 | 8.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47854952 | 1392 | 222.2577 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 | 1.19
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 7035333 | 6166 | 147.984 | 6.166 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47856316 | 1364 | 221.2131 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 7041437 | 6104 | 146.496 | 6.104 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47857708 | 1392 | 228.0472 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 7047242 | 5805 | 139.32 | 5.805 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47859048 | 1340 | 230.8355 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 145 | 7053044 | 5802 | 139.248 | 5.802 | 6 | 6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47860396 | 1348 | 232.3337 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 142 | 7058735 | 5691 | 136.584 | 5.691 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47861740 | 1344 | 236.1624 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 7064595 | 5860 | 140.64 | 5.86 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47863084 | 1344 | 229.3515 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 7070444 | 5849 | 140.376 | 5.849 | 4.7 | 4.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47864428 | 1344 | 229.7829 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 7076354 | 5910 | 141.84 | 5.91 | 4.2 | 4.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47865788 | 1360 | 230.1184 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 138 | 146 | 7082249 | 5895 | 141.48 | 5.895 | 3.8 | 3.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47867136 | 1348 | 228.6684 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 133 | 7087797 | 5548 | 133.152 | 5.548 | 3.1 | 3.1 | 2B+1S | 1077 | 0 | 1188 | 1185 | 0 | N/A | N/A | N/A | N/A | 47868252 | 1116 | 201.1536 | 100% | 0% | 100% | 100% | 0% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 140 | 7093634 | 5837 | 140.088 | 5.837 | 2.5 | 2.5 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47869600 | 1348 | 230.9406 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 133 | 7099554 | 5920 | 142.08 | 5.92 | 2.1 | 2.1 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47870978 | 1378 | 232.7703 | 100% | 0% | 100% | 100% | 100% | 0% | 10954318 | 0 | 1.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 144 | 125 | 7104752 | 5198 | 124.752 | 5.198 | 2.3 | 2.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47872196 | 1218 | 234.3209 | 0% | 0% | 100% | 100% | 100% | 30% | 10954562 | 244 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 142 | 120 | 7109854 | 5102 | 122.448 | 5.102 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47873416 | 1220 | 239.1219 | 0% | 0% | 100% | 100% | 100% | 30% | 10955587 | 1025 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133916 | 133.916 | 133.916 | [12 empty] | 30152 | 30152 | 225.1561 | [6 empty] | 5244 | 5244 | 1.2983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 66psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:00 AM TO 5:00 aM AS PER SCHEDULE
BP2 - STOPPED @ 12:00 AM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP2 - STARTED @ 1:26 AM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP3 - STOPPED @ 1:27 AM DUE TO MONTHLY PREVENTIVE MAINTENANCE
BP3 - STARTED @ 3:00 AM DUE TO MONTHLY PREVENTIVE MAINTENANCE
XCV1- INCREASE OPENING @ 12:01 AM (60%)
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 14, 2016 from 5am to 6am the PSI is 83psi and the change operation will be waiting the advised of SPM.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.

## JUNE 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | ANDRO MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30448 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7109854 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47873416 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10955587 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 131 | 112 | 7114608 | 4754 | 114.096 | 4.754 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1015 | N/A | N/A | N/A | N/A | 47874556 | 1140 | 239.7981 | 0% | 0% | 100% | 100% | 100% | 70% | 10956128 | 541 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 107 | 7119178 | 4570 | 109.68 | 4.57 | 4.9 | 4.9 | 3B | 0 | 0 | 1178 | 1185 | 1016 | N/A | N/A | N/A | N/A | 47875652 | 1096 | 239.8249 | 0% | 0% | 100% | 100% | 100% | 70% | 10956718 | 590 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 110 | 7123634 | 4456 | 106.944 | 4.456 | 5.6 | 5.6 | 3B | 0 | 0 | 1137 | 1185 | 1016 | N/A | N/A | N/A | N/A | 47876704 | 1052 | 236.0862 | 0% | 0% | 100% | 100% | 100% | 70% | 10957353 | 635 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 112 | 7126484 | 2850 | 68.4 | 2.85 | 8.5 | 8.5 | 3B | 0 | 0 | 1132 | 1185 | 1016 | N/A | N/A | N/A | N/A | 47877704 | 1000 | 350.8772 | 0% | 0% | 100% | 100% | 100% | 70% | 10957575 | 222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 137 | 134 | 7131568 | 5084 | 122.016 | 5.084 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47878924 | 1220 | 239.9685 | 0% | 0% | 100% | 100% | 100% | 70% | 10957625 | 50 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 142 | 7137520 | 5952 | 142.848 | 5.952 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47880276 | 1352 | 227.1505 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 145 | 7143522 | 6002 | 144.048 | 6.002 | 8.7 | 8.7 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47881644 | 1368 | 227.924 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 148 | 7149678 | 6156 | 147.744 | 6.156 | 8 | 8 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47883028 | 1384 | 224.8213 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 147 | 7155769 | 6091 | 146.184 | 6.091 | 7.4 | 7.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47884400 | 1372 | 225.2504 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 149 | 7162012 | 6243 | 149.832 | 6.243 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47885800 | 1400 | 224.2512 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 | 1.28
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 148 | 7168115 | 6103 | 146.472 | 6.103 | 6.2 | 6.2 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47887172 | 1372 | 224.8075 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 7174072 | 5957 | 142.968 | 5.957 | 5.8 | 5.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47888524 | 1352 | 226.9599 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 141 | 7179925 | 5853 | 140.472 | 5.853 | 5.5 | 5.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47889860 | 1336 | 228.259 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 137 | 7185799 | 5874 | 140.976 | 5.874 | 5.2 | 5.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47891204 | 1344 | 228.8049 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 317 | 7191468 | 5669 | 136.056 | 5.669 | 5 | 5 | 3B+1S | 0 | 995 | 1187 | 11885 | 1186 | N/A | N/A | N/A | N/A | 47892477 | 1273 | 224.5546 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 136 | 7196980 | 5512 | 132.288 | 5.512 | 4.8 | 4.8 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47893687 | 1210 | 219.521 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 136 | 7202683 | 5703 | 136.872 | 5.703 | 4.6 | 4.6 | 3B+1S | 0 | 995 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47894980 | 1293 | 226.7228 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 137 | 7208470 | 5787 | 138.888 | 5.787 | 4.4 | 4.4 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47896316 | 1336 | 230.8623 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 132 | 7214158 | 5688 | 136.512 | 5.688 | 4.2 | 4.2 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47897644 | 1328 | 233.474 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 116 | 127 | 7219577 | 5419 | 130.056 | 5.419 | 3.5 | 3.5 | 2B+1S | 0 | 1058 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47898748 | 1104 | 203.7276 | 0% | 100% | 0% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 138 | 7225356 | 5779 | 138.696 | 5.779 | 3 | 3 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47900092 | 1344 | 232.5662 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 130 | 7230796 | 5440 | 130.56 | 5.44 | 2.5 | 2.5 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47901396 | 1304 | 239.7059 | 0% | 100% | 100% | 100% | 100% | 0% | 10957625 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 124 | 7236174 | 5378 | 129.072 | 5.378 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47902672 | 1276 | 237.2629 | 0% | 0% | 100% | 100% | 100% | 30% | 10957772 | 147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 120 | 7241052 | 4878 | 117.072 | 4.878 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47903864 | 1192 | 244.3624 | 0% | 0% | 100% | 100% | 100% | 30% | 10958435 | 663 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131198 | 131.198 | 131.198 | [12 empty] | 30448 | 30448 | 232.0767 | [6 empty] | 2848 | 2848 | 1.18 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 5:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
EXPONENT ARRIVE FOR CHANGE IP OF PLC, HMI, SCADA
BPI- STOPPED @ 2:32 PM DUE TO SHIFT MANUAL OPERATION
BPI- STARTED@ 2:35 PM DUE TO SHIFT MANUAL OPERATION
BP3- STOPPED @ 2:37 PM DUE TO SHIFT MANUAL OPERATION
BP3- STARTED@ 2:39 PM DUE TO SHIFT MANUAL OPERATION
BP2- STOPPED @ 2:41 PM DUE TO SHIFT MANUAL OPERATION
BP2- STARTED@ 2:45 PM DUE TO SHIFT MANUAL OPERATION
SP2- STOPPED @2;47PM DUE TO SHIFT MANUAL OPERATION
SP2- STARTED @2;49PM DUE TO SHIFT MANUAL OPERATION
NORMAL OPERATION @ 2:51 PM DUE TO SHIFT MANUAL OPERATION
BPI- STOPPED @ 3:28 PM DUE TO SHIFT AUTO OPERATION
BPI- STARTED@ 3:30 PM DUE TO SHIFT AUTO OPERATION
BP3- STOPPED @ 3:33 PM DUE TO SHIFT AUTO OPERATION
BP3- STARTED@ 3:35 PM DUE TO SHIFT AUTO OPERATION
BP2- STOPPED @ 3:37 PM DUE TO SHIFT AUTO OPERATION
BP2- STARTED@ 3:39 PM DUE TO SHIFT AUTO OPERATION
SP2- STOPPED @3;42PM DUE TO SHIFT AUTO OPERATION
SP2- STARTED @3;44PM DUE TO SHIFT AUTO OPERATION
NORMAL OPERATION @ 3:47 PM DUE TO SHIFT AUTO OPERATION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JUNE 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-06-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29272 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7241052 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47903864 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10958435 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 134 | 106 | 7245614 | 4562 | 109.488 | 4.562 | 4.4 | 4.4 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 47904932 | 1068 | 234.1078 | 0% | 0% | 100% | 100% | 100% | 70% | 10959585 | 1150 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 100 | 7249857 | 4243 | 101.832 | 4.243 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47905836 | 904 | 213.0568 | 0% | 0% | 100% | 100% | 100% | 70% | 10960839 | 1254 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 104 | 7254016 | 4159 | 99.816 | 4.159 | 6.1 | 6.1 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 47906680 | 844 | 202.9334 | 0% | 0% | 100% | 0% | 100% | 70% | 10961771 | 932 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 133 | 106 | 7258417 | 4401 | 105.624 | 4.401 | 7.6 | 7.6 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47907588 | 908 | 206.3167 | 0% | 0% | 100% | 0% | 100% | 70% | 10962656 | 885 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 120 | 7262566 | 4149 | 99.576 | 4.149 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47908576 | 988 | 238.1297 | 0% | 0% | 100% | 0% | 100% | 70% | 10962711 | 55 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 109 | 133 | 7267465 | 4899 | 117.576 | 4.899 | 9.3 | 9.3 | 2B+1S | 1165 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47909508 | 932 | 190.2429 | 100% | 100% | 100% | 0% | 100% | 0% | 10962711 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 114 | 142 | 7273411 | 5946 | 142.704 | 5.946 | 7.8 | 7.8 | 2B+2S | 1189 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47910748 | 1240 | 208.5436 | 100% | 100% | 100% | 0% | 100% | 0% | 10962711 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 113 | 141 | 7279379 | 5968 | 143.232 | 5.968 | 6.5 | 6.5 | 2B+2S | 1189 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47911984 | 1236 | 207.1046 | 100% | 100% | 100% | 0% | 100% | 0% | 10962711 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 133 | 137 | 7285221 | 5842 | 140.208 | 5.842 | 5.2 | 5.2 | 2B+2S | 1189 | 1006 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 47913228 | 1244 | 212.9408 | 100% | 100% | 100% | 0% | 100% | 0% | 10962711 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 142 | 7291267 | 6046 | 145.104 | 6.046 | 4.7 | 4.7 | 3B+1S | 1049 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47914636 | 1408 | 232.8812 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 | 1.25
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 140 | 7297238 | 5971 | 143.304 | 5.971 | 4.5 | 4.5 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47915996 | 1360 | 227.7675 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 138 | 7303226 | 5988 | 143.712 | 5.988 | 4.3 | 4.3 | 3B+1S | 1008 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47917356 | 1360 | 227.1209 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 137 | 141 | 7308985 | 5759 | 138.216 | 5.759 | 4.1 | 4.1 | 3B+1S | 1008 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47918676 | 1320 | 229.2065 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 138 | 7315106 | 6121 | 146.904 | 6.121 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47920092 | 1416 | 231.3347 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 141 | 135 | 7320649 | 5543 | 133.032 | 5.543 | 3.8 | 3.8 | 3B+1S | 1009 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47921392 | 1300 | 234.53 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 139 | 7326504 | 5855 | 140.52 | 5.855 | 3.7 | 3.7 | 3B+1S | 1014 | 0 | 1188 | 1185 | 1166 | N/A | N/A | N/A | N/A | 47922708 | 1316 | 224.7652 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 138 | 7332389 | 5885 | 141.24 | 5.885 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 47924028 | 1320 | 224.2991 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 141 | 7338252 | 5863 | 140.712 | 5.863 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1177 | N/A | N/A | N/A | N/A | 47925358 | 1330 | 226.8463 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 7343983 | 5731 | 137.544 | 5.731 | 3 | 3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1178 | N/A | N/A | N/A | N/A | 47926684 | 1326 | 231.3732 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 138 | 7349702 | 5719 | 137.256 | 5.719 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1177 | N/A | N/A | N/A | N/A | 47928008 | 1324 | 231.509 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 136 | 7355439 | 5737 | 137.688 | 5.737 | 2.3 | 2.3 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47929364 | 1356 | 236.3605 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 131 | 7361258 | 5819 | 139.656 | 5.819 | 1.9 | 1.9 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47930744 | 1380 | 237.1542 | 100% | 0% | 100% | 100% | 100% | 0% | 10962711 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 123 | 7366620 | 5362 | 128.688 | 5.362 | 2 | 2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47932022 | 1278 | 238.3439 | 0% | 0% | 100% | 100% | 100% | 30% | 10962820 | 109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 119 | 7371288 | 4668 | 112.032 | 4.668 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47933136 | 1114 | 238.6461 | 0% | 0% | 100% | 100% | 100% | 30% | 10963198 | 378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130236 | 130.236 | 130.236 | [12 empty] | 29272 | 29272 | 224.7612 | [6 empty] | 4763 | 4763 | 1.1817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
BP2- STOPPED @ 1:40 AM DUE TO SHIFT AUTO OPERATION
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:16 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 5:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP2, STRARTED @ 6:00 AM DUE TO PROVIDE THE 83 TARGET DISCHARGE PRESSURE (BP2 NOT RUNNING)
SP2 - STOPPED @ 9:00 AM DUE TO HIGH DSCHARGE PRESSURE
BP2 - STARTED @ 9:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI
Additional 3 psi to target discharge pressure from 12:01 PM to 5am (JUNE 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)