## JULY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31432 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7371288 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47933136 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10963198 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 149 | 121 | 7376318 | 5030 | 120.72 | 5.03 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47934380 | 1244 | 247.3161 | 0% | 0% | 100% | 100% | 100% | 70% | 10964159 | 961 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 149 | 114 | 7381144 | 4826 | 115.824 | 4.826 | 4.7 | 4.7 | 3B | 0 | 0 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 47935572 | 1192 | 246.9954 | 0% | 0% | 100% | 100% | 100% | 70% | 10965019 | 860 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 108 | 7385715 | 4571 | 109.704 | 4.571 | 6 | 6 | 3B | 0 | 0 | 1065 | 1185 | 1076 | N/A | N/A | N/A | N/A | 47936644 | 1072 | 234.522 | 0% | 0% | 100% | 100% | 100% | 70% | 10966002 | 983 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 160 | 100 | 7389734 | 4019 | 96.456 | 4.019 | 7.2 | 7.2 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47937704 | 1060 | 263.7472 | 0% | 0% | 100% | 100% | 100% | 70% | 10966520 | 518 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 156 | 112 | 7394208 | 4474 | 107.376 | 4.474 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47938984 | 1280 | 286.0975 | 0% | 0% | 100% | 100% | 100% | 70% | 10966620 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 144 | 7399939 | 5731 | 137.544 | 5.731 | 9.2 | 9.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47940368 | 1384 | 241.4936 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 141 | 7405724 | 5785 | 138.84 | 5.785 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47941766 | 1398 | 241.6595 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 145 | 7411948 | 6224 | 149.376 | 6.224 | 7.9 | 7.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47943192 | 1426 | 229.1131 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 7417964 | 6016 | 144.384 | 6.016 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47944580 | 1388 | 230.7181 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 7424182 | 6218 | 149.232 | 6.218 | 6.5 | 6.5 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47945974 | 1394 | 224.1878 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 | 0.84
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 7430358 | 6176 | 148.224 | 6.176 | 5.9 | 5.9 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47947364 | 1390 | 225.0648 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 7436216 | 5858 | 140.592 | 5.858 | 5.3 | 5.3 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47948740 | 1376 | 234.8925 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 132 | 7442060 | 5844 | 140.256 | 5.844 | 4.8 | 4.8 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47950100 | 1360 | 232.7173 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 133 | 7447946 | 5886 | 141.264 | 5.886 | 4.4 | 4.4 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47951464 | 1364 | 231.7363 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 | 135 | 7453763 | 5817 | 139.608 | 5.817 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47952804 | 1340 | 230.3593 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 | 136 | 7459670 | 5907 | 141.768 | 5.907 | 4 | 4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47954148 | 1344 | 227.5267 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 141 | 140 | 7465567 | 5897 | 141.528 | 5.897 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47955492 | 1344 | 227.9125 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 141 | 141 | 7471420 | 5853 | 140.472 | 5.853 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47956836 | 1344 | 229.6258 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 126 | 138 | 7477213 | 5793 | 139.032 | 5.793 | 3.1 | 3.1 | 3B+1S | 0 | 1087 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 47958128 | 1292 | 223.0278 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 135 | 7483103 | 5890 | 141.36 | 5.89 | 2.5 | 2.5 | 3B+1S | 0 | 1066 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 47959428 | 1300 | 220.7131 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 137 | 136 | 7488950 | 5847 | 140.328 | 5.847 | 2.1 | 2.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47960764 | 1336 | 228.4932 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 136 | 7494654 | 5704 | 136.896 | 5.704 | 1.8 | 1.8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47962092 | 1328 | 232.8191 | 0% | 100% | 100% | 100% | 100% | 0% | 10966620 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 141 | 126 | 7499985 | 5331 | 127.944 | 5.331 | 2 | 2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47963340 | 1248 | 234.1024 | 0% | 0% | 100% | 100% | 100% | 70% | 10966934 | 314 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 142 | 121 | 7505181 | 5196 | 124.704 | 5.196 | 2.5 | 2.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 47964568 | 1228 | 236.3356 | 0% | 0% | 100% | 100% | 100% | 70% | 10967584 | 650 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133893 | 133.893 | 133.893 | [12 empty] | 31432 | 31432 | 234.7546 | [6 empty] | 4386 | 4386 | 1.05 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 5:26 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## JULY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31364 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7505181 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47964568 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10967584 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 136 | 110 | 7509967 | 4786 | 114.864 | 4.786 | 3.9 | 3.9 | 3B | 0 | 0 | 1147 | 1185 | 1096 | N/A | N/A | N/A | N/A | 47965700 | 1132 | 236.5232 | 0% | 0% | 100% | 100% | 100% | 75% | 10968133 | 549 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 109 | 7514588 | 4621 | 110.904 | 4.621 | 5.2 | 5.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 47966788 | 1088 | 235.4469 | 0% | 0% | 100% | 100% | 100% | 75% | 10968738 | 605 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 109 | 7519100 | 4512 | 108.288 | 4.512 | 6.9 | 6.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 47967820 | 1032 | 228.7234 | 0% | 0% | 100% | 100% | 100% | 75% | 10969421 | 683 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 116 | 7523462 | 4362 | 104.688 | 4.362 | 8.6 | 8.6 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 47969052 | 1232 | 282.4392 | 0% | 0% | 100% | 100% | 100% | 75% | 10970079 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 139 | 117 | 7527981 | 4519 | 108.456 | 4.519 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47970350 | 1298 | 287.2317 | 0% | 0% | 100% | 100% | 100% | 75% | 10970165 | 86 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 137 | 7533196 | 5215 | 125.16 | 5.215 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47971620 | 1270 | 243.5283 | 0% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 | 0.82 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 146 | 7539135 | 5939 | 142.536 | 5.939 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 47972972 | 1352 | 227.6478 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 147 | 7545402 | 6267 | 150.408 | 6.267 | 8.7 | 8.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47974364 | 1392 | 222.1158 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 152 | 7551368 | 5966 | 143.184 | 5.966 | 8 | 8 | 3B+1S | 1108 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47975708 | 1344 | 225.2766 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 151 | 7557722 | 6354 | 152.496 | 6.354 | 7.1 | 7.1 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47977138 | 1430 | 225.0551 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 | 1.24
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 7563812 | 6090 | 146.16 | 6.09 | 6.3 | 6.3 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47978540 | 1402 | 230.2135 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 150 | 7570306 | 6494 | 155.856 | 6.494 | 5.4 | 5.4 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47980009 | 1469 | 226.2088 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 145 | 7576112 | 5806 | 139.344 | 5.806 | 4.6 | 4.6 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47981372 | 1363 | 234.7571 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 137 | 7581859 | 5747 | 137.928 | 5.747 | 3.8 | 3.8 | 3B+1S | 1023 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47982711 | 1339 | 232.9911 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 7587654 | 5795 | 139.08 | 5.795 | 3.5 | 3.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47984032 | 1321 | 227.9551 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 7593233 | 5579 | 133.896 | 5.579 | 3.3 | 3.3 | 3B+1S | 1011 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47985352 | 1320 | 236.6015 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 144 | 7599114 | 5881 | 141.144 | 5.881 | 2.9 | 2.9 | 3B+1S | 1033 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47986708 | 1356 | 230.573 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 138 | 140 | 7604952 | 5838 | 140.112 | 5.838 | 2.6 | 2.6 | 3B+1S | 1011 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47988044 | 1336 | 228.8455 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 134 | 7610769 | 5817 | 139.608 | 5.817 | 2.4 | 2.4 | 3B+1S | 1011 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47989380 | 1336 | 229.6717 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 135 | 7616510 | 5741 | 137.784 | 5.741 | 2.2 | 2.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47990720 | 1340 | 233.4088 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 136 | 137 | 7622307 | 5797 | 139.128 | 5.797 | 2 | 2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47992052 | 1332 | 229.774 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 132 | 7628310 | 6003 | 144.072 | 6.003 | 1.8 | 1.8 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47993460 | 1408 | 234.5494 | 100% | 0% | 100% | 100% | 100% | 0% | 10970165 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 132 | 7633639 | 5329 | 127.896 | 5.329 | 1.9 | 1.9 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47994704 | 1244 | 233.4397 | 0% | 0% | 100% | 100% | 100% | 70% | 10970317 | 152 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 118 | 7638785 | 5146 | 123.504 | 5.146 | 2.4 | 2.4 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47995932 | 1228 | 238.6319 | 0% | 0% | 100% | 100% | 100% | 70% | 10970779 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133604 | 133.604 | 133.604 | [12 empty] | 31364 | 31364 | 234.7535 | [6 empty] | 3195 | 3195 | 1.13 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (70%)

## JULY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30596 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7638785 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 47995932 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10970779 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 143 | 115 | 7643699 | 4914 | 117.936 | 4.914 | 3.7 | 3.7 | 3B | 0 | 0 | 1156 | 1185 | 1116 | N/A | N/A | N/A | N/A | 47997096 | 1164 | 236.8742 | 0% | 0% | 100% | 100% | 100% | 75% | 10971464 | 685 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 | 110 | 7648445 | 4746 | 113.904 | 4.746 | 5.6 | 5.6 | 3B | 0 | 0 | 1116 | 1185 | 1096 | N/A | N/A | N/A | N/A | 47998200 | 1104 | 232.6169 | 0% | 0% | 100% | 100% | 100% | 75% | 10972177 | 713 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 107 | 7653025 | 4580 | 109.92 | 4.58 | 7.8 | 7.8 | 3B | 0 | 0 | 1097 | 1185 | 1076 | N/A | N/A | N/A | N/A | 47999244 | 1044 | 227.9476 | 0% | 0% | 100% | 100% | 100% | 75% | 10972906 | 729 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 149 | 116 | 7656997 | 3972 | 95.328 | 3.972 | 8.9 | 8.9 | 3B | 0 | 0 | 1127 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48000410 | 1166 | 293.5549 | 0% | 0% | 100% | 100% | 100% | 75% | 10973672 | 766 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 119 | 7661184 | 4187 | 100.488 | 4.187 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48001572 | 1162 | 277.5257 | 0% | 0% | 100% | 100% | 100% | 75% | 10973796 | 124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 130 | 7666394 | 5210 | 125.04 | 5.21 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1055 | N/A | N/A | N/A | N/A | 48002652 | 1080 | 207.2937 | 0% | 0% | 100% | 100% | 100% | 0% | 10973796 | 0 | 0.72 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 147 | 141 | 7672107 | 5713 | 137.112 | 5.713 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48003860 | 1208 | 211.4476 | 0% | 0% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 143 | 7678188 | 6081 | 145.944 | 6.081 | 9.4 | 9.4 | 3B+1S | 0 | 996 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48005196 | 1336 | 219.7007 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 147 | 7684330 | 6142 | 147.408 | 6.142 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48006564 | 1368 | 222.7288 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 7690583 | 6253 | 150.072 | 6.253 | 8.5 | 8.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48007964 | 1400 | 223.8925 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 | 1.23
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 7696786 | 6203 | 148.872 | 6.203 | 7.7 | 7.7 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48009336 | 1372 | 221.1833 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 7702852 | 6066 | 145.584 | 6.066 | 7.1 | 7.1 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48010744 | 1408 | 232.1134 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 7708869 | 6017 | 144.408 | 6.017 | 6.4 | 6.4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48012124 | 1380 | 229.3502 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 142 | 7714852 | 5983 | 143.592 | 5.983 | 5.7 | 5.7 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48013508 | 1384 | 231.3221 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 140 | 7720665 | 5813 | 139.512 | 5.813 | 5.2 | 5.2 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48014816 | 1308 | 225.0129 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 143 | 7726460 | 5795 | 139.08 | 5.795 | 4.6 | 4.6 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48016128 | 1312 | 226.4021 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 142 | 7732274 | 5814 | 139.536 | 5.814 | 4 | 4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48017500 | 1372 | 235.9821 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 139 | 7738129 | 5855 | 140.52 | 5.855 | 3.5 | 3.5 | 3B+1S | 0 | 1055 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48018844 | 1344 | 229.5474 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 7743899 | 5770 | 138.48 | 5.77 | 3 | 3 | 3B+1S | 0 | 1055 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48020156 | 1312 | 227.383 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 122 | 138 | 7749747 | 5848 | 140.352 | 5.848 | 2.4 | 2.4 | 3B+1S | 0 | 1086 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 48021440 | 1284 | 219.5622 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 139 | 7755383 | 5636 | 135.264 | 5.636 | 2 | 2 | 3B+1S | 0 | 1054 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48022756 | 1316 | 233.4989 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 136 | 131 | 7760933 | 5550 | 133.2 | 5.55 | 1.8 | 1.8 | 3B+1S | 0 | 1054 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48024068 | 1312 | 236.3964 | 0% | 100% | 100% | 100% | 100% | 0% | 10973796 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 123 | 7766155 | 5222 | 125.328 | 5.222 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48025312 | 1244 | 238.2229 | 0% | 0% | 100% | 100% | 100% | 70% | 10974430 | 634 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 146 | 120 | 7771202 | 5047 | 121.128 | 5.047 | 3.3 | 3.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48026528 | 1216 | 240.9352 | 0% | 0% | 100% | 100% | 100% | 70% | 10974940 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132417 | 132.417 | 132.417 | [12 empty] | 30596 | 30596 | 231.0579 | [6 empty] | 4161 | 4161 | 1.0817 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (70%)

## JULY 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30560 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7771202 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48026528 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10974940 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 146 | 108 | 7775892 | 4690 | 112.56 | 4.69 | 3.7 | 3.7 | 3B | 0 | 0 | 1076 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48027628 | 1100 | 234.5416 | 0% | 0% | 100% | 100% | 100% | 75% | 10975720 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 142 | 109 | 7780367 | 4475 | 107.4 | 4.475 | 5.6 | 5.6 | 3B | 0 | 0 | 1076 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48028636 | 1008 | 225.2514 | 0% | 0% | 100% | 100% | 100% | 75% | 10976865 | 1145 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 106 | 7784877 | 4510 | 108.24 | 4.51 | 7.5 | 7.5 | 3B | 0 | 0 | 1046 | 1185 | 1097 | N/A | N/A | N/A | N/A | 48029652 | 1016 | 225.2772 | 0% | 0% | 100% | 100% | 100% | 75% | 10978036 | 1171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 117 | 7789297 | 4420 | 106.08 | 4.42 | 8.9 | 8.9 | 3B | 0 | 0 | 1106 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48030756 | 1104 | 249.7738 | 0% | 0% | 100% | 100% | 100% | 75% | 10979198 | 1162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 124 | 7793911 | 4614 | 110.736 | 4.614 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 48031912 | 1156 | 250.5418 | 0% | 0% | 100% | 100% | 100% | 75% | 10979306 | 108 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 138 | 7799724 | 5813 | 139.512 | 5.813 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48033188 | 1276 | 219.508 | 0% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 | 0.83 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 148 | 7805756 | 6032 | 144.768 | 6.032 | 9.2 | 9.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48034552 | 1364 | 226.1273 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 144 | 7811750 | 5994 | 143.856 | 5.994 | 8.6 | 8.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48035900 | 1348 | 224.8916 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 144 | 7817506 | 5756 | 138.144 | 5.756 | 8.2 | 8.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48037196 | 1296 | 225.1564 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 7823772 | 6266 | 150.384 | 6.266 | 7.6 | 7.6 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48038588 | 1392 | 222.1513 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 | 1.31
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 152 | 7829974 | 6202 | 148.848 | 6.202 | 7 | 7 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48039972 | 1384 | 223.1538 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 7836206 | 6232 | 149.568 | 6.232 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48041372 | 1400 | 224.647 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 145 | 7842218 | 6012 | 144.288 | 6.012 | 6 | 6 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48042740 | 1368 | 227.5449 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 136 | 139 | 7847953 | 5735 | 137.64 | 5.735 | 5.6 | 5.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48044060 | 1320 | 230.1656 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 7853772 | 5819 | 139.656 | 5.819 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48045400 | 1340 | 230.2801 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 142 | 7859429 | 5657 | 135.768 | 5.657 | 5 | 5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48046692 | 1292 | 228.3896 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 141 | 7865340 | 5911 | 141.864 | 5.911 | 4.7 | 4.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48048036 | 1344 | 227.3727 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 7871337 | 5997 | 143.928 | 5.997 | 4.3 | 4.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48049400 | 1364 | 227.4471 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 142 | 7877190 | 5853 | 140.472 | 5.853 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48050740 | 1340 | 228.9424 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 141 | 7882926 | 5736 | 137.664 | 5.736 | 3.5 | 3.5 | 3B+1S | 1025 | 0 | 1165 | 1185 | 1165 | N/A | N/A | N/A | N/A | 48052036 | 1296 | 225.9414 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 143 | 7888737 | 5811 | 139.464 | 5.811 | 3 | 3 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48053396 | 1360 | 234.0389 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 130 | 7893983 | 5246 | 125.904 | 5.246 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48054640 | 1244 | 237.1331 | 100% | 0% | 100% | 100% | 100% | 0% | 10979306 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 123 | 7899254 | 5271 | 126.504 | 5.271 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48055867 | 1227 | 232.7832 | 0% | 0% | 100% | 100% | 100% | 31% | 10979410 | 104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 124 | 7904174 | 4920 | 118.08 | 4.92 | 3.1 | 3.1 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48057088 | 1221 | 248.1707 | 0% | 0% | 100% | 100% | 100% | 31% | 10979787 | 377 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132972 | 132.972 | 132.972 | [12 empty] | 30560 | 30560 | 229.8228 | [6 empty] | 4847 | 4847 | 1.1333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (31%)

## JULY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30404 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 7904174 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48057088 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10979787 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 139 | 120 | 7908563 | 4389 | 105.336 | 4.389 | 5.3 | 5.3 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48058059 | 971 | 221.2349 | 0% | 0% | 100% | 100% | 100% | 60% | 10980586 | 799 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 108 | 7912978 | 4415 | 105.96 | 4.415 | 6.8 | 6.8 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48059057 | 998 | 226.0476 | 0% | 0% | 100% | 100% | 100% | 60% | 10981366 | 780 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 105 | 7917408 | 4430 | 106.32 | 4.43 | 7.5 | 7.5 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48060076 | 1019 | 230.0226 | 0% | 0% | 100% | 100% | 100% | 60% | 10982166 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 131 | 118 | 7921858 | 4450 | 106.8 | 4.45 | 8.9 | 8.9 | 3B | 0 | 0 | 1105 | 1185 | 1116 | N/A | N/A | N/A | N/A | 48061260 | 1184 | 266.0674 | 0% | 0% | 100% | 100% | 100% | 60% | 10982866 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 120 | 7926511 | 4653 | 111.672 | 4.653 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48062372 | 1112 | 238.9856 | 0% | 0% | 100% | 100% | 100% | 60% | 10983065 | 199 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 141 | 7932416 | 5905 | 141.72 | 5.905 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48063692 | 1320 | 223.5394 | 0% | 0% | 100% | 100% | 100% | 0% | 10983065 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 150 | 7938466 | 6050 | 145.2 | 6.05 | 8.9 | 8.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48065064 | 1372 | 226.7769 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 147 | 7944522 | 6056 | 145.344 | 6.056 | 8.2 | 8.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48066424 | 1360 | 224.5707 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 150 | 7950684 | 6162 | 147.888 | 6.162 | 7.6 | 7.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48067812 | 1388 | 225.2515 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 7956838 | 6154 | 147.696 | 6.154 | 7.1 | 7.1 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48069192 | 1380 | 224.2444 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 7962776 | 5938 | 142.512 | 5.938 | 6.6 | 6.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48070532 | 1340 | 225.6652 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 137 | 7968954 | 6178 | 148.272 | 6.178 | 6.1 | 6.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48071940 | 1408 | 227.9055 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 135 | 7974816 | 5862 | 140.688 | 5.862 | 5.7 | 5.7 | 3B+1S | 0 | 1037 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48073276 | 1336 | 227.9086 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 137 | 140 | 7980530 | 5714 | 137.136 | 5.714 | 5.4 | 5.4 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48074612 | 1336 | 233.8117 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 7986229 | 5699 | 136.776 | 5.699 | 5.2 | 5.2 | 3B+1S | 0 | 1014 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48075916 | 1304 | 228.8121 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 7992081 | 5852 | 140.448 | 5.852 | 4.9 | 4.9 | 3B+1S | 0 | 1065 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48077208 | 1292 | 220.7792 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 7997941 | 5860 | 140.64 | 5.86 | 4.3 | 4.3 | 3B+1S | 0 | 1045 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48078496 | 1288 | 219.7952 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 8003856 | 5915 | 141.96 | 5.915 | 3.8 | 3.8 | 3B+1S | 0 | 1024 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48079820 | 1324 | 223.8377 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 8009577 | 5721 | 137.304 | 5.721 | 3.5 | 3.5 | 3B+1S | 0 | 1023 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48081116 | 1296 | 226.5338 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 137 | 8015286 | 5709 | 137.016 | 5.709 | 3 | 3 | 3B+1S | 0 | 1056 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 48082372 | 1256 | 220.0035 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 142 | 8021037 | 5751 | 138.024 | 5.751 | 2.6 | 2.6 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48083724 | 1352 | 235.0895 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 141 | 128 | 8026523 | 5486 | 131.664 | 5.486 | 2.3 | 2.3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48085028 | 1304 | 237.696 | 0% | 100% | 100% | 100% | 100% | 0% | 10983065 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 124 | 8031785 | 5262 | 126.288 | 5.262 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48086268 | 1240 | 235.6518 | 0% | 0% | 100% | 100% | 100% | 50% | 10983448 | 383 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 148 | 119 | 8036864 | 5079 | 121.896 | 5.079 | 3.1 | 3.1 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48087492 | 1224 | 240.9923 | 0% | 0% | 100% | 100% | 100% | 50% | 10983893 | 445 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132690 | 132.69 | 132.69 | [12 empty] | 30404 | 30404 | 229.1356 | [6 empty] | 4106 | 4106 | 1.25 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8036864 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48087492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10983893 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 140 | 109 | 8041610 | 4746 | 113.904 | 4.746 | 4.5 | 4.5 | 3B | 0 | 0 | 1147 | 1185 | 1086 | N/A | N/A | N/A | N/A | 48088604 | 1112 | 234.3026 | 0% | 0% | 100% | 100% | 100% | 70% | 10984571 | 678 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 104 | 8046108 | 4498 | 107.952 | 4.498 | 5.8 | 5.8 | 3B | 0 | 0 | 1056 | 1185 | 1086 | N/A | N/A | N/A | N/A | 48089628 | 1024 | 227.6567 | 0% | 0% | 100% | 100% | 100% | 70% | 10985398 | 827 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 105 | 8050541 | 4433 | 106.392 | 4.433 | 7.3 | 7.3 | 3B | 0 | 0 | 1055 | 1185 | 1086 | N/A | N/A | N/A | N/A | 48090620 | 992 | 223.7762 | 0% | 0% | 100% | 100% | 100% | 70% | 10986328 | 930 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 142 | 115 | 8054828 | 4287 | 102.888 | 4.287 | 8.6 | 8.6 | 3B | 0 | 0 | 1056 | 1185 | 1125 | N/A | N/A | N/A | N/A | 48091686 | 1066 | 248.6587 | 0% | 0% | 100% | 100% | 100% | 70% | 10987198 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 119 | 8059323 | 4495 | 107.88 | 4.495 | 9.5 | 9.5 | 3B | 0 | 0 | 1026 | 1185 | 1026 | N/A | N/A | N/A | N/A | 48092820 | 1134 | 252.2803 | 0% | 0% | 100% | 100% | 100% | 70% | 10987618 | 420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 138 | 8064466 | 5143 | 123.432 | 5.143 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1166 | N/A | N/A | N/A | N/A | 48093852 | 1032 | 200.6611 | 0% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 142 | 8070482 | 6016 | 144.384 | 6.016 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48095148 | 1296 | 215.4255 | 0% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 146 | 8076604 | 6122 | 146.928 | 6.122 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48096500 | 1352 | 220.8429 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 8082818 | 6214 | 149.136 | 6.214 | 8.7 | 8.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48097876 | 1376 | 221.4355 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 149 | 8089166 | 6348 | 152.352 | 6.348 | 8.1 | 8.1 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48099280 | 1404 | 221.172 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 | 1.05
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 150 | 8095394 | 6228 | 149.472 | 6.228 | 7.4 | 7.4 | 3B+1S | 1078 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48100684 | 1404 | 225.4335 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 8101228 | 5834 | 140.016 | 5.834 | 6.6 | 6.6 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48102012 | 1328 | 227.6311 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 8107306 | 6078 | 145.872 | 6.078 | 5.9 | 5.9 | 3B+1S | 1078 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48103404 | 1392 | 229.0227 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 145 | 8113321 | 6015 | 144.36 | 6.015 | 5.2 | 5.2 | 3B+1S | 1076 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48104812 | 1408 | 234.0815 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 140 | 8119248 | 5927 | 142.248 | 5.927 | 4.6 | 4.6 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48106188 | 1376 | 232.1579 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 8125047 | 5799 | 139.176 | 5.799 | 4.1 | 4.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48107532 | 1344 | 231.7641 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 143 | 8131024 | 5977 | 143.448 | 5.977 | 3.5 | 3.5 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48108908 | 1376 | 230.2158 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 8136949 | 5925 | 142.2 | 5.925 | 2.9 | 2.9 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48110276 | 1368 | 230.8861 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 141 | 8142887 | 5938 | 142.512 | 5.938 | 2.5 | 2.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48111636 | 1360 | 229.0333 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 139 | 8148657 | 5770 | 138.48 | 5.77 | 2.1 | 2.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48112972 | 1336 | 231.5425 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 141 | 8154457 | 5800 | 139.2 | 5.8 | 1.6 | 1.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48114332 | 1360 | 234.4828 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 132 | 8160146 | 5689 | 136.536 | 5.689 | 1.4 | 1.4 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48115700 | 1368 | 240.4641 | 100% | 0% | 100% | 100% | 100% | 0% | 10987618 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 123 | 8165352 | 5206 | 124.944 | 5.206 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48116916 | 1216 | 233.5766 | 0% | 0% | 100% | 100% | 100% | 50% | 10988077 | 459 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 122 | 8170456 | 5104 | 122.496 | 5.104 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48118132 | 1216 | 238.2445 | 0% | 0% | 100% | 100% | 100% | 50% | 10988496 | 419 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133592 | 133.592 | 133.592 | [12 empty] | 30640 | 30640 | 229.3551 | [6 empty] | 4603 | 4603 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30592 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8170456 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48118132 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10988496 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 144 | 113 | 8175260 | 4804 | 115.296 | 4.804 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48119272 | 1140 | 237.3022 | 0% | 0% | 100% | 100% | 100% | 70% | 10989175 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 141 | 108 | 8179847 | 4587 | 110.088 | 4.587 | 5.5 | 5.5 | 3B | 0 | 0 | 1146 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48120364 | 1092 | 238.0641 | 0% | 0% | 100% | 100% | 100% | 70% | 10990081 | 906 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 110 | 8184424 | 4577 | 109.848 | 4.577 | 7.4 | 7.4 | 3B | 0 | 0 | 1147 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48121424 | 1060 | 231.5927 | 0% | 0% | 100% | 100% | 100% | 70% | 10991036 | 955 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 132 | 119 | 8188647 | 4223 | 101.352 | 4.223 | 8.7 | 8.7 | 3B | 0 | 0 | 1147 | 1185 | 1067 | N/A | N/A | N/A | N/A | 48122496 | 1072 | 253.848 | 0% | 0% | 100% | 100% | 100% | 70% | 10991896 | 860 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 133 | 123 | 8192997 | 4350 | 104.4 | 4.35 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1136 | N/A | N/A | N/A | N/A | 48123632 | 1136 | 261.1494 | 0% | 0% | 100% | 100% | 100% | 70% | 10992287 | 391 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 136 | 8197998 | 5001 | 120.024 | 5.001 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48124908 | 1276 | 255.149 | 0% | 0% | 100% | 100% | 100% | 0% | 10992287 | 0 | 1.21 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 146 | 8203957 | 5959 | 143.016 | 5.959 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48126260 | 1352 | 226.8837 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 8210045 | 6088 | 146.112 | 6.088 | 8.8 | 8.8 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48127628 | 1368 | 224.7043 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 146 | 8216136 | 6091 | 146.184 | 6.091 | 8.3 | 8.3 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48128988 | 1360 | 223.2802 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 145 | 8222236 | 6100 | 146.4 | 6.1 | 7.8 | 7.8 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48130356 | 1368 | 224.2623 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 | 1.09
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 140 | 8228301 | 6065 | 145.56 | 6.065 | 7.4 | 7.4 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48131716 | 1360 | 224.2374 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 8234282 | 5981 | 143.544 | 5.981 | 7 | 7 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48133060 | 1344 | 224.7116 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 138 | 8240061 | 5779 | 138.696 | 5.779 | 6.7 | 6.7 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48134420 | 1360 | 235.3348 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 8246370 | 6309 | 151.416 | 6.309 | 6.4 | 6.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48135836 | 1416 | 224.4413 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 | 1.33 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 138 | 8251995 | 5625 | 135 | 5.625 | 6.1 | 6.1 | 3B+1S | 0 | 1015 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 48137132 | 1296 | 230.4 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 8257773 | 5778 | 138.672 | 5.778 | 5.8 | 5.8 | 3B+1S | 0 | 1015 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 48138420 | 1288 | 222.9145 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 139 | 8263682 | 5909 | 141.816 | 5.909 | 5.5 | 5.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48139756 | 1336 | 226.0958 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 8269502 | 5820 | 139.68 | 5.82 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48141100 | 1344 | 230.9278 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 8275295 | 5793 | 139.032 | 5.793 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48142448 | 1348 | 232.6946 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 114 | 134 | 8280815 | 5520 | 132.48 | 5.52 | 4 | 4 | 2B+1S | 0 | 1139 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 48143572 | 1124 | 203.6232 | 0% | 100% | 100% | 100% | 0% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 137 | 8286665 | 5850 | 140.4 | 5.85 | 3.4 | 3.4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48144932 | 1360 | 232.4786 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 136 | 8292286 | 5621 | 134.904 | 5.621 | 3.1 | 3.1 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48146268 | 1336 | 237.6801 | 0% | 100% | 100% | 100% | 100% | 0% | 10992287 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 129 | 8297581 | 5295 | 127.08 | 5.295 | 3.4 | 3.4 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48147516 | 1248 | 235.6941 | 0% | 0% | 100% | 100% | 100% | 50% | 10992543 | 256 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 118 | 8302582 | 5001 | 120.024 | 5.001 | 3.9 | 3.9 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48148724 | 1208 | 241.5517 | 0% | 0% | 100% | 100% | 100% | 50% | 10992914 | 371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132126 | 132.126 | 132.126 | [12 empty] | 30592 | 30592 | 231.5366 | [6 empty] | 4418 | 4418 | 1.215 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:00 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29864 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8302582 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48148724 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10992914 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 137 | 110 | 8307347 | 4765 | 114.36 | 4.765 | 5.2 | 5.2 | 3B | 0 | 0 | 1047 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48149852 | 1128 | 236.7261 | 0% | 0% | 100% | 100% | 100% | 70% | 10993860 | 946 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 101 | 8311622 | 4275 | 102.6 | 4.275 | 6.8 | 6.8 | 3B | 0 | 0 | 1045 | 1185 | 1086 | N/A | N/A | N/A | N/A | 48150852 | 1000 | 233.9181 | 0% | 0% | 100% | 100% | 100% | 70% | 10994787 | 927 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 102 | 8315863 | 4241 | 101.784 | 4.241 | 8.2 | 7.4 | 3B | 0 | 0 | 1045 | 1185 | 1055 | N/A | N/A | N/A | N/A | 48151828 | 976 | 230.1344 | 0% | 0% | 100% | 100% | 100% | 70% | 10995781 | 994 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 142 | 115 | 8320115 | 4252 | 102.048 | 4.252 | 9.4 | 8.7 | 3B | 0 | 0 | 1056 | 1185 | 1076 | N/A | N/A | N/A | N/A | 48152872 | 1044 | 245.5315 | 0% | 0% | 100% | 100% | 100% | 70% | 10996620 | 839 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 120 | 8324616 | 4501 | 108.024 | 4.501 | 9.5 | 9.5 | 3B | 0 | 0 | 1095 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48153932 | 1060 | 235.5032 | 0% | 0% | 100% | 100% | 100% | 70% | 10996665 | 45 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 131 | 8329826 | 5210 | 125.04 | 5.21 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48155068 | 1136 | 218.0422 | 0% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 | 1.26 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 140 | 8335584 | 5758 | 138.192 | 5.758 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48156320 | 1252 | 217.4366 | 0% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 139 | 8342016 | 6432 | 154.368 | 6.432 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48157764 | 1444 | 224.5025 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 144 | 8347802 | 5786 | 138.864 | 5.786 | 9 | 9 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48159060 | 1296 | 223.9889 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 142 | 148 | 8353814 | 6012 | 144.288 | 6.012 | 8.6 | 8.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48160388 | 1328 | 220.8916 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 | 1.16
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 153 | 8359808 | 5994 | 143.856 | 5.994 | 8.2 | 8.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48161732 | 1344 | 224.2242 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 8365934 | 6126 | 147.024 | 6.126 | 7.7 | 7.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48163116 | 1384 | 225.9223 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 137 | 8371826 | 5892 | 141.408 | 5.892 | 7.2 | 7.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48164468 | 1352 | 229.4637 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 8377648 | 5822 | 139.728 | 5.822 | 6.8 | 6.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48165816 | 1348 | 231.5356 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 8383373 | 5725 | 137.4 | 5.725 | 6.5 | 6.5 | 3B+1S | 1025 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 48167120 | 1304 | 227.7729 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 145 | 8389189 | 5816 | 139.584 | 5.816 | 6.1 | 6.1 | 3B+1S | 1025 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 48168428 | 1308 | 224.8968 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 8394971 | 5782 | 138.768 | 5.782 | 5.7 | 5.7 | 3B+1S | 1027 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48169732 | 1304 | 225.5275 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 8400815 | 5844 | 140.256 | 5.844 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48171044 | 1312 | 224.5038 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 8406607 | 5792 | 139.008 | 5.792 | 4.9 | 4.9 | 3B+1S | 1026 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48172360 | 1316 | 227.2099 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 113 | 140 | 8412111 | 5504 | 132.096 | 5.504 | 4 | 4 | 2B+1S | 1149 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48173492 | 1132 | 205.6686 | 100% | 0% | 0% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 137 | 8417832 | 5721 | 137.304 | 5.721 | 3.5 | 3.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48174816 | 1324 | 231.4281 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 149 | 132 | 8423377 | 5545 | 133.08 | 5.545 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48176132 | 1316 | 237.3309 | 100% | 0% | 100% | 100% | 100% | 0% | 10996665 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 125 | 8428642 | 5265 | 126.36 | 5.265 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48177372 | 1240 | 235.5176 | 0% | 0% | 100% | 100% | 100% | 50% | 10996989 | 324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 114 | 8433704 | 5062 | 121.488 | 5.062 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48178588 | 1216 | 240.2213 | 0% | 0% | 100% | 100% | 100% | 50% | 10997437 | 448 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131122 | 131.122 | 131.122 | [12 empty] | 29864 | 29864 | 227.7574 | [6 empty] | 4523 | 4523 | 1.2083 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:08 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:00 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP1- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP1- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30488 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8433704 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48178588 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 10997437 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 131 | 110 | 8438456 | 4752 | 114.048 | 4.752 | 5.5 | 5.5 | 3B | 0 | 0 | 1146 | 1185 | 1035 | N/A | N/A | N/A | N/A | 48179692 | 1104 | 232.3232 | 0% | 0% | 100% | 100% | 100% | 70% | 10998131 | 694 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 109 | 8443044 | 4588 | 110.112 | 4.588 | 7.2 | 7.2 | 3B | 0 | 0 | 1146 | 1185 | 1036 | N/A | N/A | N/A | N/A | 48180756 | 1064 | 231.9093 | 0% | 0% | 100% | 100% | 100% | 70% | 10998851 | 720 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 111 | 8447528 | 4484 | 107.616 | 4.484 | 8.6 | 8.6 | 3B | 0 | 0 | 1146 | 1185 | 1035 | N/A | N/A | N/A | N/A | 48181788 | 1032 | 230.1517 | 0% | 0% | 100% | 100% | 100% | 70% | 10999536 | 685 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 111 | 8451765 | 4237 | 101.688 | 4.237 | 9.5 | 9.5 | 3B | 0 | 0 | 1156 | 1185 | 1057 | N/A | N/A | N/A | N/A | 48182869 | 1081 | 255.1333 | 0% | 0% | 100% | 100% | 100% | 70% | 11000212 | 676 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 119 | 8456118 | 4353 | 104.472 | 4.353 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1057 | N/A | N/A | N/A | N/A | 48184020 | 1151 | 264.4153 | 0% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 128 | 8461492 | 5374 | 128.976 | 5.374 | 9.5 | 9.5 | 3B | 0 | 0 | 1087 | 1185 | 1057 | N/A | N/A | N/A | N/A | 48185124 | 1104 | 205.4336 | 0% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 137 | 8467018 | 5526 | 132.624 | 5.526 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 48186224 | 1100 | 199.059 | 0% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 140 | 8472654 | 5636 | 135.264 | 5.636 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48187428 | 1204 | 213.6267 | 0% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 148 | 8478738 | 6084 | 146.016 | 6.084 | 9.3 | 9.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48188780 | 1352 | 222.2222 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 152 | 8484968 | 6230 | 149.52 | 6.23 | 8.8 | 8.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48190164 | 1384 | 222.1509 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 | 1.09
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 147 | 8491186 | 6218 | 149.232 | 6.218 | 8 | 8 | 3B+1S | 1128 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48191568 | 1404 | 225.7961 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 149 | 8497578 | 6392 | 153.408 | 6.392 | 7.1 | 7.1 | 3B+1S | 1128 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48193016 | 1448 | 226.5332 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 143 | 8503614 | 6036 | 144.864 | 6.036 | 6.2 | 6.2 | 3B+1S | 1127 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48194420 | 1404 | 232.6044 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 138 | 8509188 | 5574 | 133.776 | 5.574 | 5.4 | 5.4 | 3B+1S | 1127 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48195736 | 1316 | 236.0962 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 142 | 8515004 | 5816 | 139.584 | 5.816 | 5 | 5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48197054 | 1318 | 226.6162 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 8520923 | 5919 | 142.056 | 5.919 | 4.5 | 4.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48198416 | 1362 | 230.1064 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 8526908 | 5985 | 143.64 | 5.985 | 4 | 4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48199764 | 1348 | 225.2297 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 140 | 8532840 | 5932 | 142.368 | 5.932 | 3.6 | 3.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48201120 | 1356 | 228.5907 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 140 | 8538676 | 5836 | 140.064 | 5.836 | 3 | 3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48202468 | 1348 | 230.9801 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 138 | 8544430 | 5754 | 138.096 | 5.754 | 3 | 3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48203796 | 1328 | 230.796 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 138 | 8550328 | 5898 | 141.552 | 5.898 | 2.5 | 2.5 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48205176 | 1380 | 233.9776 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 134 | 8556302 | 5974 | 143.376 | 5.974 | 2.3 | 2.3 | 3B+1S | 1086 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48206586 | 1410 | 236.0228 | 100% | 0% | 100% | 100% | 100% | 0% | 11000212 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 123 | 8561683 | 5381 | 129.144 | 5.381 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48207856 | 1270 | 236.0156 | 0% | 0% | 100% | 100% | 100% | 50% | 11000610 | 398 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 121 | 8566800 | 5117 | 122.808 | 5.117 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48209076 | 1220 | 238.4209 | 0% | 0% | 100% | 100% | 100% | 50% | 11000965 | 355 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133096 | 133.096 | 133.096 | [12 empty] | 30488 | 30488 | 229.0677 | [6 empty] | 3528 | 3528 | 1.16 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30556 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8566800 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48209076 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11000965 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 109 | 8571588 | 4788 | 114.912 | 4.788 | 4.1 | 4.1 | 3B | 0 | 0 | 1065 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48210220 | 1144 | 238.9307 | 0% | 0% | 100% | 100% | 100% | 70% | 11001673 | 708 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 109 | 8576152 | 4564 | 109.536 | 4.564 | 5.8 | 5.8 | 3B | 0 | 0 | 1026 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48211320 | 1100 | 241.0167 | 0% | 0% | 100% | 100% | 100% | 70% | 11002466 | 793 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 110 | 8580647 | 4495 | 107.88 | 4.495 | 7.6 | 7.6 | 3B | 0 | 0 | 1027 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48212364 | 1044 | 232.2581 | 0% | 0% | 100% | 100% | 100% | 70% | 11003305 | 839 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 112 | 8584838 | 4191 | 100.584 | 4.191 | 8.8 | 8.8 | 3B | 0 | 0 | 1046 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48213467 | 1103 | 263.183 | 0% | 0% | 100% | 100% | 100% | 70% | 11004112 | 807 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 115 | 8588922 | 4084 | 98.016 | 4.084 | 9.5 | 9.5 | 3B | 0 | 0 | 1044 | 1185 | 1147 | N/A | N/A | N/A | N/A | 48214604 | 1137 | 278.4035 | 0% | 0% | 100% | 100% | 100% | 70% | 11004441 | 329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 127 | 8594368 | 5446 | 130.704 | 5.446 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1036 | N/A | N/A | N/A | N/A | 48215668 | 1064 | 195.3728 | 0% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 138 | 8599532 | 5164 | 123.936 | 5.164 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 48216688 | 1020 | 197.5213 | 0% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 147 | 142 | 8605414 | 5882 | 141.168 | 5.882 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48217924 | 1236 | 210.1326 | 0% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 147 | 8611692 | 6278 | 150.672 | 6.278 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48219316 | 1392 | 221.7267 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 8617886 | 6194 | 148.656 | 6.194 | 8.6 | 8.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48220708 | 1392 | 224.7336 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 | 1.13
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 149 | 8624152 | 6266 | 150.384 | 6.266 | 7.6 | 7.6 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48222148 | 1440 | 229.8117 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 144 | 8630216 | 6064 | 145.536 | 6.064 | 6.7 | 6.7 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48223560 | 1412 | 232.8496 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 143 | 8636396 | 6180 | 148.32 | 6.18 | 5.8 | 5.8 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48224992 | 1432 | 231.7152 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 142 | 8642380 | 5984 | 143.616 | 5.984 | 4.9 | 4.9 | 3B+1S | 1147 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48226404 | 1412 | 235.9626 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 | 1.36 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 8648344 | 5964 | 143.136 | 5.964 | 4.2 | 4.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48227766 | 1362 | 228.3702 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 8654309 | 5965 | 143.16 | 5.965 | 3.6 | 3.6 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48229140 | 1374 | 230.3437 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 8660229 | 5920 | 142.08 | 5.92 | 3.1 | 3.1 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48230508 | 1368 | 231.0811 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 139 | 8666090 | 5861 | 140.664 | 5.861 | 2.7 | 2.7 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48231860 | 1352 | 230.6774 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 138 | 8671882 | 5792 | 139.008 | 5.792 | 2.5 | 2.5 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48233192 | 1332 | 229.9724 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 135 | 8677565 | 5683 | 136.392 | 5.683 | 2.3 | 2.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48234524 | 1332 | 234.3832 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 138 | 8683301 | 5736 | 137.664 | 5.736 | 2 | 2 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48235860 | 1336 | 232.9149 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 128 | 8688837 | 5536 | 132.864 | 5.536 | 1.7 | 1.7 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48237188 | 1328 | 239.8844 | 100% | 0% | 100% | 100% | 100% | 0% | 11004441 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 125 | 8693986 | 5149 | 123.576 | 5.149 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48238420 | 1232 | 239.2698 | 0% | 0% | 100% | 100% | 100% | 50% | 11004755 | 314 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 118 | 8699013 | 5027 | 120.648 | 5.027 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48239632 | 1212 | 241.0981 | 0% | 0% | 100% | 100% | 100% | 50% | 11005104 | 349 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132213 | 132.213 | 132.213 | [12 empty] | 30556 | 30556 | 231.1119 | [6 empty] | 4139 | 4139 | 1.1833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30860 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8699013 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48239632 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11005104 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 139 | 111 | 8703744 | 4731 | 113.544 | 4.731 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48240764 | 1132 | 239.2729 | 0% | 0% | 100% | 100% | 100% | 70% | 11006024 | 920 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 108 | 8708308 | 4564 | 109.536 | 4.564 | 5.6 | 5.6 | 3B | 0 | 0 | 1147 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48241844 | 1080 | 236.6345 | 0% | 0% | 100% | 100% | 100% | 70% | 11006996 | 972 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 110 | 8712830 | 4522 | 108.528 | 4.522 | 7.3 | 7.3 | 3B | 0 | 0 | 1146 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48242896 | 1052 | 232.6404 | 0% | 0% | 100% | 100% | 100% | 70% | 11007997 | 1001 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 116 | 8716873 | 4043 | 97.032 | 4.043 | 8.9 | 8.9 | 3B | 0 | 0 | 1146 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48243935 | 1039 | 256.9874 | 0% | 0% | 100% | 100% | 100% | 70% | 11008892 | 895 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 119 | 8721197 | 4324 | 103.776 | 4.324 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1076 | N/A | N/A | N/A | N/A | 48245144 | 1209 | 279.6022 | 0% | 0% | 100% | 100% | 100% | 70% | 11009030 | 138 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 143 | 8726956 | 5759 | 138.216 | 5.759 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48246372 | 1228 | 213.2315 | 0% | 0% | 100% | 100% | 100% | 0% | 11009030 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 140 | 8732764 | 5808 | 139.392 | 5.808 | 9.3 | 9.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48247676 | 1304 | 224.5179 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 8738812 | 6048 | 145.152 | 6.048 | 8.9 | 8.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48249036 | 1360 | 224.8677 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 8744888 | 6076 | 145.824 | 6.076 | 8.3 | 8.3 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48250400 | 1364 | 224.4898 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 8751282 | 6394 | 153.456 | 6.394 | 7.5 | 7.5 | 3B+1S | 0 | 1118 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48251832 | 1432 | 223.96 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 | 0.84
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 145 | 8757504 | 6222 | 149.328 | 6.222 | 6.6 | 6.6 | 3B+1S | 0 | 1118 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48253240 | 1408 | 226.2938 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 147 | 8763784 | 6280 | 150.72 | 6.28 | 5.7 | 5.7 | 3B+1S | 0 | 1118 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48254700 | 1460 | 232.4841 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 142 | 8769638 | 5854 | 140.496 | 5.854 | 5 | 5 | 3B+1S | 0 | 1118 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48256052 | 1352 | 230.9532 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 8775649 | 6011 | 144.264 | 6.011 | 4.4 | 4.4 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48257448 | 1396 | 232.2409 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 8781293 | 5644 | 135.456 | 5.644 | 4 | 4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48258772 | 1324 | 234.5854 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 8787009 | 5716 | 137.184 | 5.716 | 3.8 | 3.8 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48260100 | 1328 | 232.3303 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 8793028 | 6019 | 144.456 | 6.019 | 3.5 | 3.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48261504 | 1404 | 233.2613 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 | 141 | 8798674 | 5646 | 135.504 | 5.646 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48262780 | 1276 | 226.0007 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 138 | 8804516 | 5842 | 140.208 | 5.842 | 3.1 | 3.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48264120 | 1340 | 229.3735 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 134 | 8810206 | 5690 | 136.56 | 5.69 | 2.9 | 2.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48265452 | 1332 | 234.0949 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 140 | 8816006 | 5800 | 139.2 | 5.8 | 2.5 | 2.5 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48266804 | 1352 | 233.1034 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 131 | 8821210 | 5204 | 124.896 | 5.204 | 2.2 | 2.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48268032 | 1228 | 235.9723 | 0% | 100% | 100% | 100% | 100% | 0% | 11009030 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 122 | 8826339 | 5129 | 123.096 | 5.129 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48269244 | 1212 | 236.3034 | 0% | 0% | 100% | 100% | 100% | 25% | 11009255 | 225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 127 | 120 | 8831516 | 5177 | 124.248 | 5.177 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48270492 | 1248 | 241.0663 | 0% | 0% | 100% | 100% | 100% | 25% | 11009501 | 246 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132503 | 132.503 | 132.503 | [12 empty] | 30860 | 30860 | 232.9004 | [6 empty] | 4397 | 4397 | 1.1317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (25%)

## JULY 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31036 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8831516 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48270492 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11009501 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 134 | 110 | 8835756 | 4240 | 101.76 | 4.24 | 4.8 | 4.8 | 3B | 0 | 0 | 1137 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48271509 | 1017 | 239.8585 | 0% | 0% | 100% | 100% | 100% | 70% | 11010387 | 886 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 103 | 8839966 | 4210 | 101.04 | 4.21 | 6.9 | 6.9 | 3B | 0 | 0 | 1137 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48272533 | 1024 | 243.2304 | 0% | 0% | 100% | 100% | 100% | 70% | 11011237 | 850 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 105 | 8844314 | 4348 | 104.352 | 4.348 | 8 | 8 | 3B | 0 | 0 | 1137 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48273616 | 1083 | 249.08 | 0% | 0% | 100% | 100% | 100% | 70% | 11012107 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 131 | 108 | 8848594 | 4280 | 102.72 | 4.28 | 9.3 | 9.3 | 3B | 0 | 0 | 1116 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48274718 | 1102 | 257.4766 | 0% | 0% | 100% | 100% | 100% | 70% | 11013037 | 930 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 114 | 8852992 | 4398 | 105.552 | 4.398 | 9.5 | 9.5 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 48275876 | 1158 | 263.3015 | 0% | 0% | 100% | 100% | 100% | 70% | 11013128 | 91 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 146 | 104 | 8859148 | 6156 | 147.744 | 6.156 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48277216 | 1340 | 217.6738 | 0% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 142 | 8865016 | 5868 | 140.832 | 5.868 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48278532 | 1316 | 224.2672 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 148 | 8871166 | 6150 | 147.6 | 6.15 | 8.8 | 8.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48279908 | 1376 | 223.7398 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 149 | 8877198 | 6032 | 144.768 | 6.032 | 8.1 | 8.1 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48281268 | 1360 | 225.4642 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 8883676 | 6478 | 155.472 | 6.478 | 7.5 | 7.5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48282716 | 1448 | 223.5258 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 | 1.08
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 146 | 8889664 | 5988 | 143.712 | 5.988 | 6.8 | 6.8 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48284072 | 1356 | 226.4529 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 139 | 8895856 | 6192 | 148.608 | 6.192 | 6 | 6 | 3B+1S | 1117 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48285510 | 1438 | 232.2351 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 140 | 8901532 | 5676 | 136.224 | 5.676 | 5.3 | 5.3 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48286852 | 1342 | 236.4341 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 137 | 8907459 | 5927 | 142.248 | 5.927 | 4.6 | 4.6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48288250 | 1398 | 235.8697 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 8913150 | 5691 | 136.584 | 5.691 | 4.2 | 4.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48289600 | 1350 | 237.2167 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 8918933 | 5783 | 138.792 | 5.783 | 3.8 | 3.8 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48290940 | 1340 | 231.7136 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 137 | 8924837 | 5904 | 141.696 | 5.904 | 3.4 | 3.4 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48292300 | 1360 | 230.3523 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 142 | 8930696 | 5859 | 140.616 | 5.859 | 3.1 | 3.1 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48293644 | 1344 | 229.3907 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 8936547 | 5851 | 140.424 | 5.851 | 2.7 | 2.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48295004 | 1360 | 232.4389 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 139 | 8942396 | 5849 | 140.376 | 5.849 | 2.3 | 2.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48296356 | 1352 | 231.1506 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 137 | 8948180 | 5784 | 138.816 | 5.784 | 1.7 | 1.7 | 3B+1S | 1096 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48297720 | 1364 | 235.823 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 127 | 8953774 | 5594 | 134.256 | 5.594 | 1.4 | 1.4 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48299080 | 1360 | 243.1176 | 100% | 0% | 100% | 100% | 100% | 0% | 11013128 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 120 | 8958972 | 5198 | 124.752 | 5.198 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48300316 | 1236 | 237.7838 | 0% | 0% | 100% | 100% | 100% | 50% | 11013502 | 374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 115 | 8963970 | 4998 | 119.952 | 4.998 | 2.2 | 2.2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48301528 | 1212 | 242.497 | 0% | 0% | 100% | 100% | 100% | 50% | 11013997 | 495 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132454 | 132.454 | 132.454 | [12 empty] | 31036 | 31036 | 234.3153 | [6 empty] | 4496 | 4496 | 1.16 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31028 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 8963970 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48301528 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11013997 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 136 | 107 | 8968615 | 4645 | 111.48 | 4.645 | 3.9 | 3.9 | 3B | 0 | 0 | 1044 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48302668 | 1140 | 245.4252 | 0% | 0% | 100% | 100% | 100% | 70% | 11014690 | 693 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 105 | 8973175 | 4560 | 109.44 | 4.56 | 5.3 | 5.3 | 3B | 0 | 0 | 1044 | 1185 | 1145 | N/A | N/A | N/A | N/A | 48303772 | 1104 | 242.1053 | 0% | 0% | 100% | 100% | 100% | 70% | 11015588 | 898 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 105 | 8977597 | 4422 | 106.128 | 4.422 | 6.9 | 6.9 | 3B | 0 | 0 | 1044 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48304824 | 1052 | 237.9014 | 0% | 0% | 100% | 100% | 100% | 70% | 11016480 | 892 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 118 | 8981499 | 3902 | 93.648 | 3.902 | 8.6 | 8.6 | 3B | 0 | 0 | 1044 | 1185 | 1176 | N/A | N/A | N/A | N/A | 48305916 | 1092 | 279.8565 | 0% | 0% | 100% | 100% | 100% | 70% | 11017350 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 119 | 8985503 | 4004 | 96.096 | 4.004 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48307124 | 1208 | 301.6983 | 0% | 0% | 100% | 100% | 100% | 70% | 11017505 | 155 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 136 | 8990931 | 5428 | 130.272 | 5.428 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48308316 | 1192 | 219.6021 | 0% | 0% | 100% | 100% | 100% | 0% | 11017505 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 143 | 8996876 | 5945 | 142.68 | 5.945 | 9.1 | 9.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48309660 | 1344 | 226.0723 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 9002992 | 6116 | 146.784 | 6.116 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48311052 | 1392 | 227.5997 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 151 | 9009058 | 6066 | 145.584 | 6.066 | 7.8 | 7.8 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48312428 | 1376 | 226.8381 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 9015222 | 6164 | 147.936 | 6.164 | 7 | 7 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48313836 | 1408 | 228.4231 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 | 1.04
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 144 | 9021336 | 6114 | 146.736 | 6.114 | 6.2 | 6.2 | 3B+1S | 0 | 1097 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48315244 | 1408 | 230.2911 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 141 | 9027148 | 5812 | 139.488 | 5.812 | 5.5 | 5.5 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48316588 | 1344 | 231.2457 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 140 | 9033116 | 5968 | 143.232 | 5.968 | 4.8 | 4.8 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48317996 | 1408 | 235.9249 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 142 | 9039138 | 6022 | 144.528 | 6.022 | 4.1 | 4.1 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48319392 | 1396 | 231.8167 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 9044867 | 5729 | 137.496 | 5.729 | 3.6 | 3.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48320724 | 1332 | 232.5013 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 9050676 | 5809 | 139.416 | 5.809 | 3.2 | 3.2 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48322076 | 1352 | 232.7423 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 9056492 | 5816 | 139.584 | 5.816 | 2.8 | 2.8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48323428 | 1352 | 232.4622 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 137 | 9062292 | 5800 | 139.2 | 5.8 | 2.5 | 2.5 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48324764 | 1336 | 230.3448 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 137 | 9067988 | 5696 | 136.704 | 5.696 | 2.2 | 2.2 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48326092 | 1328 | 233.1461 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 136 | 9073684 | 5696 | 136.704 | 5.696 | 1.9 | 1.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48327428 | 1336 | 234.5506 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 139 | 9079380 | 5696 | 136.704 | 5.696 | 1.6 | 1.6 | 3B+1S | 0 | 1086 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48328764 | 1336 | 234.5506 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 134 | 9085072 | 5692 | 136.608 | 5.692 | 1.3 | 1.3 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48330116 | 1352 | 237.5264 | 0% | 100% | 100% | 100% | 100% | 0% | 11017505 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 137 | 120 | 9090233 | 5161 | 123.864 | 5.161 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48331340 | 1224 | 237.1633 | 0% | 0% | 100% | 100% | 100% | 50% | 11017796 | 291 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 116 | 9095207 | 4974 | 119.376 | 4.974 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48332556 | 1216 | 244.4713 | 0% | 0% | 100% | 100% | 100% | 50% | 11018126 | 330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131237 | 131.237 | 131.237 | [12 empty] | 31028 | 31028 | 236.4272 | [6 empty] | 4129 | 4129 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:16 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30528 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9095207 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48332556 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11018126 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 140 | 107 | 9099918 | 4711 | 113.064 | 4.711 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48333708 | 1152 | 244.5341 | 0% | 0% | 100% | 100% | 100% | 70% | 11018998 | 872 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 110 | 9104454 | 4536 | 108.864 | 4.536 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48334796 | 1088 | 239.8589 | 0% | 0% | 100% | 100% | 100% | 70% | 11019924 | 926 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 109 | 9108701 | 4247 | 101.928 | 4.247 | 6.9 | 6.9 | 3B | 0 | 0 | 1147 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48335828 | 1032 | 242.9951 | 0% | 0% | 100% | 100% | 100% | 70% | 11020874 | 950 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 115 | 9112728 | 4027 | 96.648 | 4.027 | 8.6 | 8.6 | 3B | 0 | 0 | 1167 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48336890 | 1062 | 263.7199 | 0% | 0% | 100% | 100% | 100% | 70% | 11021702 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 120 | 9116888 | 4160 | 99.84 | 4.16 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1084 | N/A | N/A | N/A | N/A | 48338056 | 1166 | 280.2885 | 0% | 0% | 100% | 100% | 100% | 70% | 11022072 | 370 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 137 | 9122462 | 5574 | 133.776 | 5.574 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48339312 | 1256 | 225.3319 | 0% | 0% | 100% | 100% | 100% | 0% | 11022072 | 0 | 1.24 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 9128119 | 5657 | 135.768 | 5.657 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48340588 | 1276 | 225.5613 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 9134179 | 6060 | 145.44 | 6.06 | 8.6 | 8.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48341956 | 1368 | 225.7426 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 9140122 | 5943 | 142.632 | 5.943 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48343296 | 1340 | 225.4753 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 143 | 9146209 | 6087 | 146.088 | 6.087 | 7.6 | 7.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48344654 | 1358 | 223.0984 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 9152178 | 5969 | 143.256 | 5.969 | 7 | 7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48346032 | 1378 | 230.8594 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 9158068 | 5890 | 141.36 | 5.89 | 6.5 | 6.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48347392 | 1360 | 230.8998 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 9163891 | 5823 | 139.752 | 5.823 | 6 | 6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48348740 | 1348 | 231.4958 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 138 | 9170025 | 6134 | 147.216 | 6.134 | 5.6 | 5.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48350172 | 1432 | 233.4529 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 9175637 | 5612 | 134.688 | 5.612 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48351492 | 1320 | 235.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 9181421 | 5784 | 138.816 | 5.784 | 5.1 | 5.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48352832 | 1340 | 231.6736 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 9187126 | 5705 | 136.92 | 5.705 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48354148 | 1316 | 230.6748 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 136 | 9192844 | 5718 | 137.232 | 5.718 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48355484 | 1336 | 233.6481 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 139 | 9198545 | 5701 | 136.824 | 5.701 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48356812 | 1328 | 232.9416 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 134 | 9204045 | 5500 | 132 | 5.5 | 3.2 | 3.2 | 2B+1S | 0 | 1170 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 48357948 | 1136 | 206.5455 | 0% | 100% | 100% | 100% | 0% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 137 | 9209747 | 5702 | 136.848 | 5.702 | 2.6 | 2.6 | 3B+1S | 0 | 1076 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48359292 | 1344 | 235.7068 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 129 | 9215314 | 5567 | 133.608 | 5.567 | 2.3 | 2.3 | 3B+1S | 0 | 1075 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48360628 | 1336 | 239.9856 | 0% | 100% | 100% | 100% | 100% | 0% | 11022072 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 124 | 9220496 | 5182 | 124.368 | 5.182 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48361868 | 1240 | 239.2898 | 0% | 0% | 100% | 100% | 100% | 50% | 11022268 | 196 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 117 | 9225506 | 5010 | 120.24 | 5.01 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48363084 | 1216 | 242.7146 | 0% | 0% | 100% | 100% | 100% | 50% | 11022505 | 237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130299 | 130.299 | 130.299 | [12 empty] | 30528 | 30528 | 234.2919 | [6 empty] | 4379 | 4379 | 1.2033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP3- STOPPED @ 7:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
BP3- STARTED @ 8:00 PM DUE TO HIGH DISCHARGE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30876 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9225506 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48363084 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11022505 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 106 | 9230139 | 4633 | 111.192 | 4.633 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48364212 | 1128 | 243.4708 | 0% | 0% | 100% | 100% | 100% | 70% | 11023397 | 892 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 105 | 9234579 | 4440 | 106.56 | 4.44 | 5.5 | 5.5 | 3B | 0 | 0 | 1147 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48365276 | 1064 | 239.6396 | 0% | 0% | 100% | 100% | 100% | 70% | 11024318 | 921 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 104 | 9239025 | 4446 | 106.704 | 4.446 | 6.9 | 6.9 | 3B | 0 | 0 | 1107 | 1185 | 1047 | N/A | N/A | N/A | N/A | 48366316 | 1040 | 233.9181 | 0% | 0% | 100% | 100% | 100% | 70% | 11025257 | 939 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 | 112 | 9243128 | 4103 | 98.472 | 4.103 | 8.6 | 8.6 | 3B | 0 | 0 | 1147 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48367396 | 1080 | 263.222 | 0% | 0% | 100% | 100% | 100% | 70% | 11026111 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 122 | 9247352 | 4224 | 101.376 | 4.224 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1106 | N/A | N/A | N/A | N/A | 48368544 | 1148 | 271.7803 | 0% | 0% | 100% | 100% | 100% | 70% | 11026240 | 129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 141 | 9252694 | 5342 | 128.208 | 5.342 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48369776 | 1232 | 230.6252 | 0% | 0% | 100% | 100% | 100% | 0% | 11026240 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 144 | 9258656 | 5962 | 143.088 | 5.962 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48371120 | 1344 | 225.4277 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 9264587 | 5931 | 142.344 | 5.931 | 8.7 | 8.7 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48372464 | 1344 | 226.606 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 9270696 | 6109 | 146.616 | 6.109 | 8.1 | 8.1 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48373798 | 1334 | 218.3663 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 9276736 | 6040 | 144.96 | 6.04 | 7.6 | 7.6 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48375210 | 1412 | 233.7748 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 | 1.1
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 140 | 9283008 | 6272 | 150.528 | 6.272 | 6.8 | 6.8 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48376634 | 1424 | 227.0408 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 9288846 | 5838 | 140.112 | 5.838 | 6.2 | 6.2 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48377796 | 1162 | 199.0408 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 9294904 | 6058 | 145.392 | 6.058 | 5.6 | 5.6 | 3B+1S | 0 | 1066 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48379212 | 1416 | 233.7405 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 136 | 9300588 | 5684 | 136.416 | 5.684 | 5 | 5 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48380748 | 1536 | 270.2322 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 138 | 9306224 | 5636 | 135.264 | 5.636 | 4.6 | 4.6 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48382076 | 1328 | 235.6281 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 141 | 9312036 | 5812 | 139.488 | 5.812 | 4 | 4 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48383436 | 1360 | 233.9986 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 140 | 9317845 | 5809 | 139.416 | 5.809 | 3.4 | 3.4 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48384800 | 1364 | 234.8081 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 138 | 9323663 | 5818 | 139.632 | 5.818 | 2.9 | 2.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48386148 | 1348 | 231.6947 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 139 | 9329427 | 5764 | 138.336 | 5.764 | 2.6 | 2.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48387492 | 1344 | 233.1714 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 137 | 9335152 | 5725 | 137.4 | 5.725 | 2.3 | 2.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48388828 | 1336 | 233.3624 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 139 | 9340897 | 5745 | 137.88 | 5.745 | 2 | 2 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48390164 | 1336 | 232.55 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 133 | 132 | 9346595 | 5698 | 136.752 | 5.698 | 1.7 | 1.7 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48391500 | 1336 | 234.4682 | 0% | 100% | 100% | 100% | 100% | 0% | 11026240 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 121 | 9351825 | 5230 | 125.52 | 5.23 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48392740 | 1240 | 237.0937 | 0% | 0% | 100% | 100% | 100% | 50% | 11026482 | 242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 144 | 121 | 9356846 | 5021 | 120.504 | 5.021 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48393960 | 1220 | 242.9795 | 0% | 0% | 100% | 100% | 100% | 50% | 11026709 | 227 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131340 | 131.34 | 131.34 | [12 empty] | 30876 | 30876 | 235.0845 | [6 empty] | 4204 | 4204 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30968 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9356846 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48393960 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11026709 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 139 | 109 | 9361654 | 4808 | 115.392 | 4.808 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48395140 | 1180 | 245.4243 | 0% | 0% | 100% | 100% | 100% | 70% | 11027364 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 108 | 9366194 | 4540 | 108.96 | 4.54 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48396244 | 1104 | 243.1718 | 0% | 0% | 100% | 100% | 100% | 70% | 11028146 | 782 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 108 | 9370629 | 4435 | 106.44 | 4.435 | 6.8 | 6.8 | 3B | 0 | 0 | 1136 | 1185 | 1055 | N/A | N/A | N/A | N/A | 48397288 | 1044 | 235.4002 | 0% | 0% | 100% | 100% | 100% | 70% | 11028936 | 790 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 112 | 9374832 | 4203 | 100.872 | 4.203 | 8.6 | 8.6 | 3B | 0 | 0 | 1146 | 1185 | 1055 | N/A | N/A | N/A | N/A | 48398352 | 1064 | 253.1525 | 0% | 0% | 100% | 100% | 100% | 70% | 11029678 | 742 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 116 | 9379095 | 4263 | 102.312 | 4.263 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48399450 | 1098 | 257.5651 | 0% | 0% | 100% | 100% | 100% | 70% | 11030052 | 374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 137 | 9383776 | 4681 | 112.344 | 4.681 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1097 | N/A | N/A | N/A | N/A | 48400692 | 1242 | 265.3279 | 0% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 139 | 9389518 | 5742 | 137.808 | 5.742 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48401916 | 1224 | 213.1661 | 0% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 9395462 | 5944 | 142.656 | 5.944 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48403244 | 1328 | 223.4186 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 146 | 9401625 | 6163 | 147.912 | 6.163 | 8.4 | 8.4 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48404644 | 1400 | 227.1621 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 127 | 143 | 9407966 | 6341 | 152.184 | 6.341 | 7.5 | 7.5 | 3B+1S | 1148 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48406112 | 1468 | 231.5092 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 | 1.29
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 144 | 9413834 | 5868 | 140.832 | 5.868 | 6.5 | 6.5 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48407492 | 1380 | 235.1738 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 142 | 9419918 | 6084 | 146.016 | 6.084 | 5.6 | 5.6 | 3B+1S | 1149 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48408916 | 1424 | 234.0565 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 125 | 144 | 9426284 | 6366 | 152.784 | 6.366 | 4.7 | 4.7 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48410360 | 1444 | 226.83 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 130 | 9431734 | 5450 | 130.8 | 5.45 | 3.9 | 3.9 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48411661 | 1301 | 238.7156 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 9437228 | 5494 | 131.856 | 5.494 | 3.6 | 3.6 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48412944 | 1283 | 233.5275 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 9442927 | 5699 | 136.776 | 5.699 | 3.2 | 3.2 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48414332 | 1388 | 243.5515 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 9448690 | 5763 | 138.312 | 5.763 | 2.9 | 2.9 | 3B+1S | 1028 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48415672 | 1340 | 232.5178 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 9454461 | 5771 | 138.504 | 5.771 | 2.6 | 2.6 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48417014 | 1342 | 232.542 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 135 | 9460222 | 5761 | 138.264 | 5.761 | 2.4 | 2.4 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48418336 | 1322 | 229.474 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 140 | 9465961 | 5739 | 137.736 | 5.739 | 2.2 | 2.2 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48419668 | 1332 | 232.0962 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 138 | 9471736 | 5775 | 138.6 | 5.775 | 1.8 | 1.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48421020 | 1352 | 234.1126 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 135 | 9477544 | 5808 | 139.392 | 5.808 | 1.5 | 1.5 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48422412 | 1392 | 239.6694 | 100% | 0% | 100% | 100% | 100% | 0% | 11030052 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 125 | 9483136 | 5592 | 134.208 | 5.592 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48423692 | 1280 | 228.8984 | 0% | 0% | 100% | 100% | 100% | 50% | 11030277 | 225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 124 | 9488345 | 5209 | 125.016 | 5.209 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48424928 | 1236 | 237.2816 | 0% | 0% | 100% | 100% | 100% | 50% | 11030607 | 330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131499 | 131.499 | 131.499 | [12 empty] | 30968 | 30968 | 235.4999 | [6 empty] | 3898 | 3898 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30908 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9488345 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48424928 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11030607 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 140 | 113 | 9493219 | 4874 | 116.976 | 4.874 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1095 | N/A | N/A | N/A | N/A | 48426072 | 1144 | 234.7148 | 0% | 0% | 100% | 100% | 100% | 70% | 11031328 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 110 | 9497966 | 4747 | 113.928 | 4.747 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 1185 | 1036 | N/A | N/A | N/A | N/A | 48427188 | 1116 | 235.0959 | 0% | 0% | 100% | 100% | 100% | 70% | 11032097 | 769 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 108 | 9502546 | 4580 | 109.92 | 4.58 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 1036 | N/A | N/A | N/A | N/A | 48428284 | 1096 | 239.3013 | 0% | 0% | 100% | 100% | 100% | 70% | 11032923 | 826 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 | 112 | 9506747 | 4201 | 100.824 | 4.201 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48429395 | 1111 | 264.4608 | 0% | 0% | 100% | 100% | 100% | 70% | 11033695 | 772 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 115 | 9511086 | 4339 | 104.136 | 4.339 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48430612 | 1217 | 280.4794 | 0% | 0% | 100% | 100% | 100% | 70% | 11033924 | 229 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 128 | 9515736 | 4650 | 111.6 | 4.65 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1049 | N/A | N/A | N/A | N/A | 48431764 | 1152 | 247.7419 | 0% | 0% | 100% | 100% | 100% | 0% | 11033924 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 135 | 9520986 | 5250 | 126 | 5.25 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1126 | N/A | N/A | N/A | N/A | 48432888 | 1124 | 214.0952 | 0% | 0% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 9527092 | 6106 | 146.544 | 6.106 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48434260 | 1372 | 224.697 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 150 | 9533216 | 6124 | 146.976 | 6.124 | 8.5 | 8.5 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48435650 | 1390 | 226.9758 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 9539224 | 6008 | 144.192 | 6.008 | 7.7 | 7.7 | 3B+1S | 0 | 1076 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48437040 | 1390 | 231.3582 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 | 1.05
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 9545348 | 6124 | 146.976 | 6.124 | 7 | 7 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48438444 | 1404 | 229.2619 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 142 | 9551316 | 5968 | 143.232 | 5.968 | 6.3 | 6.3 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48439828 | 1384 | 231.9035 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 148 | 9557290 | 5974 | 143.376 | 5.974 | 5.5 | 5.5 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48441212 | 1384 | 231.6706 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 143 | 9563336 | 6046 | 145.104 | 6.046 | 5 | 5 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48442616 | 1404 | 232.2196 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 9569129 | 5793 | 139.032 | 5.793 | 4.5 | 4.5 | 3B+1S | 0 | 1043 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48443964 | 1348 | 232.6946 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 142 | 9575017 | 5888 | 141.312 | 5.888 | 3.9 | 3.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48445332 | 1368 | 232.337 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 9580952 | 5935 | 142.44 | 5.935 | 3.4 | 3.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48446684 | 1352 | 227.8012 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 9586673 | 5721 | 137.304 | 5.721 | 3 | 3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48448016 | 1332 | 232.8264 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 140 | 9592525 | 5852 | 140.448 | 5.852 | 2.7 | 2.7 | 3B+1S | 0 | 1022 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48449364 | 1348 | 230.3486 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 137 | 9598245 | 5720 | 137.28 | 5.72 | 2.4 | 2.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48450692 | 1328 | 232.1678 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 138 | 9604028 | 5783 | 138.792 | 5.783 | 2 | 2 | 3B+1S | 0 | 1066 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48452048 | 1356 | 234.4804 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 137 | 9609669 | 5641 | 135.384 | 5.641 | 1.7 | 1.7 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48453388 | 1340 | 237.5465 | 0% | 100% | 100% | 100% | 100% | 0% | 11033924 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 121 | 9614882 | 5213 | 125.112 | 5.213 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48454616 | 1228 | 235.5649 | 0% | 0% | 100% | 100% | 100% | 50% | 11034175 | 251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 118 | 9619958 | 5076 | 121.824 | 5.076 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48455836 | 1220 | 240.3467 | 0% | 0% | 100% | 100% | 100% | 50% | 11034474 | 299 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131613 | 131.613 | 131.613 | [12 empty] | 30908 | 30908 | 234.84 | [6 empty] | 3867 | 3867 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (50%)

## JULY 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30912 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9619958 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48455836 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11034474 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 140 | 112 | 9624720 | 4762 | 114.288 | 4.762 | 4 | 4 | 3B | 0 | 0 | 1067 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48456980 | 1144 | 240.2352 | 0% | 0% | 100% | 100% | 100% | 70% | 11035234 | 760 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 | 108 | 9629375 | 4655 | 111.72 | 4.655 | 5.7 | 5.7 | 3B | 0 | 0 | 1045 | 1185 | 1147 | N/A | N/A | N/A | N/A | 48458080 | 1100 | 236.305 | 0% | 0% | 100% | 100% | 100% | 70% | 11036049 | 815 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 109 | 9633864 | 4489 | 107.736 | 4.489 | 7.2 | 7.2 | 3B | 0 | 0 | 1045 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48459128 | 1048 | 233.4596 | 0% | 0% | 100% | 100% | 100% | 70% | 11036817 | 768 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 123 | 9637913 | 4049 | 97.176 | 4.049 | 8.7 | 8.7 | 3B | 0 | 0 | 1045 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48460246 | 1118 | 276.1176 | 0% | 0% | 100% | 100% | 100% | 70% | 11037556 | 739 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 126 | 9642197 | 4284 | 102.816 | 4.284 | 9.5 | 9.5 | 3B | 0 | 0 | 1085 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48461444 | 1198 | 279.6452 | 0% | 0% | 100% | 100% | 100% | 70% | 11037837 | 281 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 144 | 143 | 9647734 | 5537 | 132.888 | 5.537 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48462664 | 1220 | 220.3359 | 0% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 147 | 9653522 | 5788 | 138.912 | 5.788 | 9.2 | 9.2 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48463968 | 1304 | 225.2937 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 9659644 | 6122 | 146.928 | 6.122 | 8.8 | 8.8 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48465344 | 1376 | 224.7631 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 149 | 9665976 | 6332 | 151.968 | 6.332 | 8.1 | 8.1 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48466770 | 1426 | 225.2053 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 146 | 9671928 | 5952 | 142.848 | 5.952 | 7.4 | 7.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48468132 | 1362 | 228.8306 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 | 1.07
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 9677885 | 5957 | 142.968 | 5.957 | 6.7 | 6.7 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48469500 | 1368 | 229.6458 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 9683841 | 5956 | 142.944 | 5.956 | 6 | 6 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48470868 | 1368 | 229.6844 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 9689713 | 5872 | 140.928 | 5.872 | 5.4 | 5.4 | 3B+1S | 1066 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48472236 | 1368 | 232.97 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 136 | 9695577 | 5864 | 140.736 | 5.864 | 5 | 5 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48473612 | 1376 | 234.6521 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 9701307 | 5730 | 137.52 | 5.73 | 4.6 | 4.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48474948 | 1336 | 233.1588 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 9707076 | 5769 | 138.456 | 5.769 | 4.2 | 4.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48476284 | 1336 | 231.5826 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 9712876 | 5800 | 139.2 | 5.8 | 3.7 | 3.7 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48477628 | 1344 | 231.7241 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 137 | 9718705 | 5829 | 139.896 | 5.829 | 3.3 | 3.3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48478976 | 1348 | 231.2575 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 9724489 | 5784 | 138.816 | 5.784 | 2.9 | 2.9 | 3B+1S | 1036 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48480320 | 1344 | 232.3651 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 139 | 9730261 | 5772 | 138.528 | 5.772 | 2.6 | 2.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48481660 | 1340 | 232.1552 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 141 | 9736050 | 5789 | 138.936 | 5.789 | 2.1 | 2.1 | 3B+1S | 1076 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48483028 | 1368 | 236.3102 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 132 | 9741329 | 5279 | 126.696 | 5.279 | 1.6 | 1.6 | 3B+1S | 1076 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48484280 | 1252 | 237.1661 | 100% | 0% | 100% | 100% | 100% | 0% | 11037837 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 126 | 9746610 | 5281 | 126.744 | 5.281 | 1.6 | 1.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48485520 | 1240 | 234.804 | 0% | 0% | 100% | 100% | 100% | 20% | 11038007 | 170 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 121 | 9751733 | 5123 | 122.952 | 5.123 | 1.9 | 1.9 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48486748 | 1228 | 239.7033 | 0% | 0% | 100% | 100% | 100% | 20% | 11038226 | 219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131775 | 131.775 | 131.775 | [12 empty] | 30912 | 30912 | 234.5817 | [6 empty] | 3752 | 3752 | 1.18 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO EXCESS CAPACITY
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## JULY 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31052 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9751733 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48486748 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11038226 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 109 | 9755975 | 4242 | 101.808 | 4.242 | 3.8 | 3.8 | 3B | 0 | 0 | 1057 | 1185 | 1127 | N/A | N/A | N/A | N/A | 48487771 | 1023 | 241.1598 | 0% | 0% | 100% | 100% | 100% | 70% | 11039096 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 110 | 9760205 | 4230 | 101.52 | 4.23 | 5.3 | 5.3 | 3B | 0 | 0 | 1057 | 1185 | 1127 | N/A | N/A | N/A | N/A | 48488781 | 1010 | 238.7707 | 0% | 0% | 100% | 100% | 100% | 70% | 11039916 | 820 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 9764565 | 4360 | 104.64 | 4.36 | 7.7 | 7.7 | 3B | 0 | 0 | 1057 | 1185 | 1127 | N/A | N/A | N/A | N/A | 48489892 | 1111 | 254.8165 | 0% | 0% | 100% | 100% | 100% | 70% | 11040716 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 117 | 9768996 | 4431 | 106.344 | 4.431 | 8.9 | 8.9 | 3B | 0 | 0 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48491028 | 1136 | 256.3755 | 0% | 0% | 100% | 100% | 100% | 70% | 11041506 | 790 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 119 | 9773445 | 4449 | 106.776 | 4.449 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48492244 | 1216 | 273.3198 | 0% | 0% | 100% | 100% | 100% | 70% | 11041740 | 234 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 136 | 9779546 | 6101 | 146.424 | 6.101 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48493546 | 1302 | 213.4076 | 0% | 0% | 100% | 100% | 100% | 0% | 11041740 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 145 | 9785317 | 5771 | 138.504 | 5.771 | 9.2 | 9.2 | 3B+1S | 0 | 1087 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48494824 | 1278 | 221.4521 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 9791494 | 6177 | 148.248 | 6.177 | 8.4 | 8.4 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48496260 | 1436 | 232.4753 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 143 | 9797512 | 6018 | 144.432 | 6.018 | 7.6 | 7.6 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48497696 | 1436 | 238.6175 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 140 | 9803633 | 6121 | 146.904 | 6.121 | 6.8 | 6.8 | 3B+1S | 0 | 1086 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48499100 | 1404 | 229.3743 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 | 0.91
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 143 | 9809811 | 6178 | 148.272 | 6.178 | 6 | 6 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48500522 | 1422 | 230.1716 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 9816015 | 6204 | 148.896 | 6.204 | 5.2 | 5.2 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48501966 | 1444 | 232.7531 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 140 | 9821528 | 5513 | 132.312 | 5.513 | 4.7 | 4.7 | 3B+1S | 0 | 1086 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48503264 | 1298 | 235.4435 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 9827346 | 5818 | 139.632 | 5.818 | 4.1 | 4.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48504636 | 1372 | 235.8199 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 141 | 9833124 | 5778 | 138.672 | 5.778 | 3.7 | 3.7 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48505972 | 1336 | 231.2219 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 9839029 | 5905 | 141.72 | 5.905 | 3.3 | 3.3 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48507332 | 1360 | 230.3133 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 9844867 | 5838 | 140.112 | 5.838 | 2.9 | 2.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48508676 | 1344 | 230.2158 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 140 | 9850767 | 5900 | 141.6 | 5.9 | 2.5 | 2.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48510036 | 1360 | 230.5085 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 141 | 9856613 | 5846 | 140.304 | 5.846 | 2.2 | 2.2 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48511380 | 1344 | 229.9008 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 138 | 9862451 | 5838 | 140.112 | 5.838 | 1.7 | 1.7 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48512744 | 1364 | 233.6417 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 137 | 9868150 | 5699 | 136.776 | 5.699 | 1.3 | 1.3 | 3B+1S | 0 | 1075 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48514076 | 1332 | 233.7252 | 0% | 100% | 100% | 100% | 100% | 0% | 11041740 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 132 | 9873676 | 5526 | 132.624 | 5.526 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48515332 | 1256 | 227.2892 | 0% | 0% | 100% | 100% | 100% | 0% | 11041740 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 | 121 | 9878975 | 5299 | 127.176 | 5.299 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48516580 | 1248 | 235.5161 | 0% | 0% | 100% | 100% | 100% | 50% | 11041874 | 134 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 119 | 9884066 | 5091 | 122.184 | 5.091 | 2.2 | 2.2 | 3b | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48517800 | 1220 | 239.6386 | 0% | 0% | 100% | 100% | 100% | 50% | 11042093 | 219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132333 | 132.333 | 132.333 | [12 empty] | 31052 | 31052 | 234.6505 | [6 empty] | 3867 | 3867 | 1.105 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (40%)

## JULY 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31080 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 9884066 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48517800 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11042093 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 141 | 109 | 9888780 | 4714 | 113.136 | 4.714 | 3.9 | 3.9 | 3B | 0 | 0 | 1066 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48518940 | 1140 | 241.8328 | 0% | 0% | 100% | 100% | 100% | 70% | 11042799 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 109 | 9893388 | 4608 | 110.592 | 4.608 | 5.4 | 5.4 | 3B | 0 | 0 | 1066 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48520052 | 1112 | 241.3194 | 0% | 0% | 100% | 100% | 100% | 70% | 11043581 | 782 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 9897912 | 4524 | 108.576 | 4.524 | 6.9 | 6.9 | 3B | 0 | 0 | 1066 | 1185 | 1147 | N/A | N/A | N/A | N/A | 48521112 | 1060 | 234.3059 | 0% | 0% | 100% | 100% | 100% | 70% | 11044477 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 114 | 9902359 | 4447 | 106.728 | 4.447 | 8.6 | 8.6 | 3B | 0 | 0 | 1087 | 1185 | 1156 | N/A | N/A | N/A | N/A | 48522204 | 1092 | 245.5588 | 0% | 0% | 100% | 100% | 100% | 70% | 11045245 | 768 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 122 | 9906876 | 4517 | 108.408 | 4.517 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48523348 | 1144 | 253.2654 | 0% | 0% | 100% | 100% | 100% | 70% | 11045533 | 288 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 136 | 9911510 | 4634 | 111.216 | 4.634 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48524668 | 1320 | 284.8511 | 0% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 145 | 9917328 | 5818 | 139.632 | 5.818 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48525980 | 1312 | 225.507 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 149 | 9923432 | 6104 | 146.496 | 6.104 | 8.5 | 8.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48527358 | 1378 | 225.7536 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 146 | 9929474 | 6042 | 145.008 | 6.042 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48528728 | 1370 | 226.7461 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 140 | 9935635 | 6161 | 147.864 | 6.161 | 7.3 | 7.3 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48530104 | 1376 | 223.3404 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 | 0.83
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 9941786 | 6151 | 147.624 | 6.151 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48531478 | 1374 | 223.3783 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 139 | 9948121 | 6335 | 152.04 | 6.335 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48532948 | 1470 | 232.0442 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 9953583 | 5462 | 131.088 | 5.462 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48534212 | 1264 | 231.4171 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 9959498 | 5915 | 141.96 | 5.915 | 5.2 | 5.2 | 3B+1S | 1024 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48535604 | 1392 | 235.3339 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 9965113 | 5615 | 134.76 | 5.615 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48536924 | 1320 | 235.0846 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 9970916 | 5803 | 139.272 | 5.803 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48538256 | 1332 | 229.5364 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 9976718 | 5802 | 139.248 | 5.802 | 4.3 | 4.3 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48539589 | 1333 | 229.7484 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 137 | 9982756 | 6038 | 144.912 | 6.038 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48540972 | 1383 | 229.0494 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 9988470 | 5714 | 137.136 | 5.714 | 3.4 | 3.4 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48542296 | 1324 | 231.7116 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 140 | 9994293 | 5823 | 139.752 | 5.823 | 3 | 3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48543644 | 1348 | 231.4958 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 142 | 10000146 | 5853 | 140.472 | 5.853 | 2.4 | 2.4 | 3B+1S | 1128 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48545028 | 1384 | 236.4599 | 100% | 0% | 100% | 100% | 100% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 122 | 136 | 10006063 | 5917 | 142.008 | 5.917 | 1.7 | 1.7 | 3B | 1127 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48546404 | 1376 | 232.5503 | 0% | 0% | 0% | 0% | 0% | 0% | 11045533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 123 | 10011859 | 5796 | 139.104 | 5.796 | 1.9 | 1.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48547724 | 1320 | 227.7433 | 0% | 0% | 0% | 0% | 0% | 70% | 11045707 | 174 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 120 | 10016214 | 4355 | 104.52 | 4.355 | 2.3 | 2.3 | 3b | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48548880 | 1156 | 265.442 | 0% | 0% | 0% | 0% | 0% | 70% | 11046273 | 566 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132148 | 132.148 | 132.148 | [12 empty] | 31080 | 31080 | 235.1908 | [6 empty] | 4180 | 4180 | 1.076 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## JULY 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30736 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10016214 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48548880 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11046273 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 108 | 10021132 | 4918 | 118.032 | 4.918 | 3.6 | 3.6 | 3B | 0 | 0 | 1035 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48550180 | 1300 | 264.3351 | 0% | 0% | 100% | 100% | 100% | 70% | 11047113 | 840 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 110 | 10025576 | 4444 | 106.656 | 4.444 | 4.5 | 4.5 | 3B | 0 | 0 | 1035 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48551152 | 972 | 218.7219 | 0% | 0% | 100% | 100% | 100% | 70% | 11048103 | 990 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 103 | 10029676 | 4100 | 98.4 | 4.1 | 6 | 6 | 3B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 48551916 | 764 | 186.3415 | 0% | 0% | 100% | 100% | 100% | 70% | 11048824 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 115 | 10033786 | 4110 | 98.64 | 4.11 | 7.9 | 7.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48552976 | 1060 | 257.9075 | 0% | 0% | 100% | 100% | 100% | 70% | 11049588 | 764 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | A.MIRAFLOR/P. LABIAN
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 137 | 130 | 10038599 | 4813 | 115.512 | 4.813 | 9 | 9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48554108 | 1132 | 235.1963 | 0% | 100% | 100% | 100% | 100% | 70% | 11049888 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 130 | 138 | 10043986 | 5387 | 129.288 | 5.387 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48555484 | 1376 | 255.4297 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 144 | 10049446 | 5460 | 131.04 | 5.46 | 8 | 8 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48556840 | 1356 | 248.3516 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 10055286 | 5840 | 140.16 | 5.84 | 7.4 | 7.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48558212 | 1372 | 234.9315 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 142 | 10061319 | 6033 | 144.792 | 6.033 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48559544 | 1332 | 220.7857 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 143 | 10067360 | 6041 | 144.984 | 6.041 | 6.2 | 6.2 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48560956 | 1412 | 233.7361 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 | 1.02
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 141 | 10073360 | 6000 | 144 | 6 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48562324 | 1368 | 228 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 142 | 10079282 | 5922 | 142.128 | 5.922 | 5.2 | 5.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48563644 | 1320 | 222.8977 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 139 | 10085137 | 5855 | 140.52 | 5.855 | 4.7 | 4.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48565028 | 1384 | 236.3792 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 137 | 10091168 | 6031 | 144.744 | 6.031 | 4.4 | 4.4 | 3B+1S | 0 | 1020 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48566436 | 1408 | 233.4605 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 136 | 10096822 | 5654 | 135.696 | 5.654 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48567748 | 1312 | 232.0481 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 10102638 | 5816 | 139.584 | 5.816 | 3.9 | 3.9 | 3B+1S | 0 | 1014 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48569076 | 1328 | 228.3356 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 140 | 10108408 | 5770 | 138.48 | 5.77 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48570412 | 1336 | 231.5425 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 139 | 10114271 | 5863 | 140.712 | 5.863 | 3.3 | 3.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48571752 | 1340 | 228.5519 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 141 | 10120136 | 5865 | 140.76 | 5.865 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48573094 | 1342 | 228.815 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 142 | 10125911 | 5775 | 138.6 | 5.775 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48574444 | 1350 | 233.7662 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 141 | 10131866 | 5955 | 142.92 | 5.955 | 2.2 | 2.2 | 3B+1S | 0 | 1127 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48575836 | 1392 | 233.7531 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 138 | 135 | 10137429 | 5563 | 133.512 | 5.563 | 1.9 | 1.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48577152 | 1316 | 236.563 | 0% | 100% | 100% | 100% | 100% | 0% | 11049888 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 147 | 122 | 10142760 | 5331 | 127.944 | 5.331 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48578408 | 1256 | 235.6031 | 0% | 0% | 100% | 100% | 100% | 30% | 11050118 | 230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 145 | 118 | 10147787 | 5027 | 120.648 | 5.027 | 3.1 | 3.1 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48579616 | 1208 | 240.3024 | 0% | 0% | 100% | 100% | 100% | 30% | 11050403 | 285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131573 | 131.573 | 131.573 | [12 empty] | 30736 | 30736 | 233.6042 | [6 empty] | 4130 | 4130 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.0M)
BP2 - STOPPED @ 2:15 AM DUE TO CONDUCT FROM MANUAL TO REMOTE AUTOMATIC OPERATIONAL
BP2 - STARTED @ 3:29 AM DUE TO REMOVE MANUAL TO REMOTE AUTOMATIC OPERATIONAL
SP2 - STARTED @ 4: 35 AM DUE TO TEST FROM MANUAL TO REMOTE AUTOMATIC OPERATIONAL
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JULY 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | P.LABIAN/A.MIRAFLOR
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30540 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10147787 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48579616 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11050403 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 127 | 104 | 10152410 | 4623 | 110.952 | 4.623 | 4.2 | 4.2 | 3B | 0 | 0 | 1127 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48580720 | 1104 | 238.806 | 0% | 0% | 100% | 100% | 100% | 50% | 11051137 | 734 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 122 | 108 | 10156833 | 4423 | 106.152 | 4.423 | 5.7 | 5.7 | 3B | 0 | 0 | 1127 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48581764 | 1044 | 236.0389 | 0% | 0% | 100% | 100% | 100% | 50% | 11051889 | 752 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 124 | 108 | 10161026 | 4193 | 100.632 | 4.193 | 7.1 | 7.1 | 3B | 0 | 0 | 1126 | 1185 | 1057 | N/A | N/A | N/A | N/A | 48582784 | 1020 | 243.2626 | 0% | 0% | 100% | 100% | 100% | 50% | 11052636 | 747 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 112 | 10165272 | 4246 | 101.904 | 4.246 | 8.7 | 8.7 | 3B | 0 | 0 | 1157 | 1185 | 1076 | N/A | N/A | N/A | N/A | 48583818 | 1034 | 243.5233 | 0% | 0% | 100% | 100% | 100% | 50% | 11053361 | 725 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 135 | 118 | 10169789 | 4517 | 108.408 | 4.517 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1096 | N/A | N/A | N/A | N/A | 48584942 | 1124 | 248.8377 | 0% | 0% | 100% | 100% | 100% | 50% | 11053487 | 126 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 138 | 10175128 | 5339 | 128.136 | 5.339 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48586316 | 1374 | 257.3516 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 10181055 | 5927 | 142.248 | 5.927 | 8.8 | 8.8 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48587704 | 1388 | 234.1826 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 10187080 | 6025 | 144.6 | 6.025 | 8.2 | 8.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48589076 | 1372 | 227.7178 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 141 | 10193144 | 6064 | 145.536 | 6.064 | 7.6 | 7.6 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48590456 | 1380 | 227.5726 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 10199284 | 6140 | 147.36 | 6.14 | 7 | 7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48591848 | 1392 | 226.7101 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 144 | 10205394 | 6110 | 146.64 | 6.11 | 6.3 | 6.3 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48593236 | 1388 | 227.1686 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 10211342 | 5948 | 142.752 | 5.948 | 5.7 | 5.7 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48594608 | 1372 | 230.6658 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 140 | 10217214 | 5872 | 140.928 | 5.872 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48595968 | 1360 | 231.6076 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 10222981 | 5767 | 138.408 | 5.767 | 5 | 5 | 3B+1S | 1005 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48597300 | 1332 | 230.9693 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 10228945 | 5964 | 143.136 | 5.964 | 4.8 | 4.8 | 3B+1S | 1004 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48598576 | 1276 | 213.9504 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 10234256 | 5311 | 127.464 | 5.311 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48599844 | 1268 | 238.7498 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 139 | 10240031 | 5775 | 138.6 | 5.775 | 4 | 4 | 3B+1S | 1066 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48601140 | 1296 | 224.4156 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 137 | 10245806 | 5775 | 138.6 | 5.775 | 3.4 | 3.4 | 3B+1S | 1066 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48602436 | 1296 | 224.4156 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 136 | 10251529 | 5723 | 137.352 | 5.723 | 2.9 | 2.9 | 3B+1S | 1066 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48603756 | 1320 | 230.6483 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 138 | 10257295 | 5766 | 138.384 | 5.766 | 2.4 | 2.4 | 3B+1S | 1046 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48605060 | 1304 | 226.1533 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 137 | 10262949 | 5654 | 135.696 | 5.654 | 2.1 | 2.1 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48606388 | 1328 | 234.878 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 139 | 131 | 10268490 | 5541 | 132.984 | 5.541 | 1.8 | 1.8 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48607684 | 1296 | 233.8928 | 100% | 0% | 100% | 100% | 100% | 0% | 11053487 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 147 | 122 | 10273687 | 5197 | 124.728 | 5.197 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48608940 | 1256 | 241.6779 | 0% | 0% | 100% | 100% | 100% | 30% | 11053793 | 306 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 147 | 118 | 10278771 | 5084 | 122.016 | 5.084 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48610156 | 1216 | 239.1817 | 0% | 0% | 100% | 100% | 100% | 30% | 11054247 | 454 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130984 | 130.984 | 130.984 | [12 empty] | 30540 | 30540 | 233.1582 | [6 empty] | 3844 | 3844 | 1.1667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 5:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JULY 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30572 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10278771 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48610156 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11054247 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 125 | 110 | 10283390 | 4619 | 110.856 | 4.619 | 4.5 | 4.5 | 3B | 0 | 0 | 1045 | 1185 | 1137 | N/A | N/A | N/A | N/A | 48611252 | 1096 | 237.2808 | 0% | 0% | 100% | 100% | 100% | 50% | 11054992 | 745 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 108 | 10287846 | 4456 | 106.944 | 4.456 | 6.1 | 6.1 | 3B | 0 | 0 | 1045 | 1185 | 1137 | N/A | N/A | N/A | N/A | 48612292 | 1040 | 233.3932 | 0% | 0% | 100% | 100% | 100% | 50% | 11055752 | 760 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 123 | 109 | 10292259 | 4413 | 105.912 | 4.413 | 7.6 | 7.6 | 3B | 0 | 0 | 1045 | 1185 | 1137 | N/A | N/A | N/A | N/A | 48613328 | 1036 | 234.7609 | 0% | 0% | 100% | 100% | 100% | 50% | 11056474 | 722 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 115 | 10296290 | 4031 | 96.744 | 4.031 | 8.9 | 8.9 | 3B | 0 | 0 | 1045 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48614433 | 1105 | 274.1255 | 0% | 0% | 100% | 100% | 100% | 50% | 11057164 | 690 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 119 | 10300470 | 4180 | 100.32 | 4.18 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48615632 | 1199 | 286.8421 | 0% | 0% | 100% | 100% | 100% | 50% | 11057323 | 159 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 129 | 10305677 | 5207 | 124.968 | 5.207 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48616772 | 1140 | 218.936 | 0% | 0% | 100% | 100% | 100% | 0% | 11057323 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 137 | 10311400 | 5723 | 137.352 | 5.723 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48617988 | 1216 | 212.476 | 0% | 0% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 10317450 | 6050 | 145.2 | 6.05 | 9.2 | 9.2 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48619332 | 1344 | 222.1488 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 10323586 | 6136 | 147.264 | 6.136 | 8.6 | 8.6 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48620716 | 1384 | 225.5541 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 10329707 | 6121 | 146.904 | 6.121 | 7.9 | 7.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48622104 | 1388 | 226.7603 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 145 | 10335747 | 6040 | 144.96 | 6.04 | 7.1 | 7.1 | 3B+1S | 0 | 1099 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48623484 | 1380 | 228.4768 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 147 | 10341816 | 6069 | 145.656 | 6.069 | 6.3 | 6.3 | 3B+1S | 0 | 1097 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48624884 | 1400 | 230.6805 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 146 | 10347793 | 5977 | 143.448 | 5.977 | 5.5 | 5.5 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48626276 | 1392 | 232.8928 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 10353341 | 5548 | 133.152 | 5.548 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48627554 | 1278 | 230.3533 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 10359168 | 5827 | 139.848 | 5.827 | 4.4 | 4.4 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48628916 | 1362 | 233.7395 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 10364863 | 5695 | 136.68 | 5.695 | 4 | 4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48630252 | 1336 | 234.5917 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 10370442 | 5579 | 133.896 | 5.579 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48631564 | 1312 | 235.1676 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 135 | 10376188 | 5746 | 137.904 | 5.746 | 3.4 | 3.4 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48632896 | 1332 | 231.8134 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 10381913 | 5725 | 137.4 | 5.725 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48634228 | 1332 | 232.6638 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 136 | 10387628 | 5715 | 137.16 | 5.715 | 3 | 3 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48635560 | 1332 | 233.0709 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 137 | 10393328 | 5700 | 136.8 | 5.7 | 2.6 | 2.6 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48636900 | 1340 | 235.0877 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 130 | 10399059 | 5731 | 137.544 | 5.731 | 2.2 | 2.2 | 3B+1S | 0 | 1055 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48638230 | 1330 | 232.0712 | 0% | 100% | 100% | 100% | 100% | 0% | 11057323 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 120 | 10404536 | 5477 | 131.448 | 5.477 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48639546 | 1316 | 240.2775 | 0% | 0% | 100% | 100% | 100% | 30% | 11057582 | 259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 119 | 10409461 | 4925 | 118.2 | 4.925 | 3 | 3 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48640728 | 1182 | 240 | 0% | 0% | 100% | 100% | 100% | 30% | 11057875 | 293 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130690 | 130.69 | 130.69 | [12 empty] | 30572 | 30572 | 233.9276 | [6 empty] | 3628 | 3628 | 1.185 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:17 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JULY 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30664 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10409461 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48640728 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11057875 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 110 | 10414250 | 4789 | 114.936 | 4.789 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48641878 | 1150 | 240.1336 | 0% | 0% | 100% | 100% | 100% | 50% | 11058582 | 707 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 110 | 10418935 | 4685 | 112.44 | 4.685 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48642980 | 1102 | 235.2188 | 0% | 0% | 100% | 100% | 100% | 50% | 11059362 | 780 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 111 | 10423302 | 4367 | 104.808 | 4.367 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 1185 | 1026 | N/A | N/A | N/A | N/A | 48644060 | 1080 | 247.3094 | 0% | 0% | 100% | 100% | 100% | 50% | 11060096 | 734 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 114 | 10427412 | 4110 | 98.64 | 4.11 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1055 | N/A | N/A | N/A | N/A | 48645204 | 1144 | 278.3455 | 0% | 0% | 100% | 100% | 100% | 50% | 11060408 | 312 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 118 | 10431654 | 4242 | 101.808 | 4.242 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48646404 | 1200 | 282.8854 | 0% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 133 | 129 | 10436482 | 4828 | 115.872 | 4.828 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1056 | N/A | N/A | N/A | N/A | 48647452 | 1048 | 217.0671 | 0% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 138 | 10441886 | 5404 | 129.696 | 5.404 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48648556 | 1104 | 204.2931 | 0% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 141 | 145 | 10447984 | 6098 | 146.352 | 6.098 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48649908 | 1352 | 221.712 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 10454088 | 6104 | 146.496 | 6.104 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48651284 | 1376 | 225.426 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 10460203 | 6115 | 146.76 | 6.115 | 8 | 8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48652660 | 1376 | 225.0204 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 | 1.11
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 10466291 | 6088 | 146.112 | 6.088 | 7.4 | 7.4 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48654044 | 1384 | 227.3325 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 10472465 | 6174 | 148.176 | 6.174 | 6.5 | 6.5 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48655466 | 1422 | 230.3207 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 140 | 10478307 | 5842 | 140.208 | 5.842 | 5.9 | 5.9 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48656828 | 1362 | 233.1393 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 138 | 10484182 | 5875 | 141 | 5.875 | 5.3 | 5.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48658204 | 1376 | 234.2128 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 141 | 10490020 | 5838 | 140.112 | 5.838 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48659560 | 1356 | 232.2713 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 10495950 | 5930 | 142.32 | 5.93 | 4.4 | 4.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48660920 | 1360 | 229.3423 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 10501833 | 5883 | 141.192 | 5.883 | 3.9 | 3.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48662276 | 1356 | 230.4946 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 142 | 10507692 | 5859 | 140.616 | 5.859 | 3.5 | 3.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48663620 | 1344 | 229.3907 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 10513414 | 5722 | 137.328 | 5.722 | 3.1 | 3.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48664948 | 1328 | 232.0867 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 10519158 | 5744 | 137.856 | 5.744 | 2.9 | 2.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48666292 | 1344 | 233.9833 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 138 | 10524827 | 5669 | 136.056 | 5.669 | 2.5 | 2.5 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48667632 | 1340 | 236.3733 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 132 | 10530400 | 5573 | 133.752 | 5.573 | 2.1 | 2.1 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48668964 | 1332 | 239.0095 | 100% | 0% | 100% | 100% | 100% | 0% | 11060408 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 123 | 10535583 | 5183 | 124.392 | 5.183 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48670180 | 1216 | 234.6132 | 0% | 0% | 100% | 100% | 100% | 30% | 11060657 | 249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 119 | 10540516 | 4933 | 118.392 | 4.933 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48671392 | 1212 | 245.6923 | 0% | 0% | 100% | 100% | 100% | 30% | 11060994 | 337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131055 | 131.055 | 131.055 | [12 empty] | 30664 | 30664 | 233.9781 | [6 empty] | 3119 | 3119 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JULY 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30692 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10540516 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48671392 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11060994 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 137 | 111 | 10545150 | 4634 | 111.216 | 4.634 | 4.3 | 4.3 | 3B | 0 | 0 | 1056 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48672504 | 1112 | 239.9655 | 0% | 0% | 100% | 100% | 100% | 50% | 11061696 | 702 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 10549631 | 4481 | 107.544 | 4.481 | 5.8 | 5.8 | 3B | 0 | 0 | 1056 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48673564 | 1060 | 236.5543 | 0% | 0% | 100% | 100% | 100% | 50% | 11062477 | 781 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 108 | 10553923 | 4292 | 103.008 | 4.292 | 7.6 | 7.6 | 3B | 0 | 0 | 1056 | 1185 | 1095 | N/A | N/A | N/A | N/A | 48674548 | 984 | 229.2637 | 0% | 0% | 100% | 100% | 100% | 50% | 11063263 | 786 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 115 | 10558023 | 4100 | 98.4 | 4.1 | 9.1 | 9.1 | 3B | 0 | 0 | 1055 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48675644 | 1096 | 267.3171 | 0% | 0% | 100% | 100% | 100% | 50% | 11064032 | 769 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 120 | 10562336 | 4313 | 103.512 | 4.313 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48676868 | 1224 | 283.7932 | 0% | 0% | 100% | 100% | 100% | 50% | 11064070 | 38 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 140 | 10567832 | 5496 | 131.904 | 5.496 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48678100 | 1232 | 224.163 | 0% | 0% | 100% | 100% | 100% | 0% | 11064070 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 135 | 10573465 | 5633 | 135.192 | 5.633 | 9.3 | 9.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48679380 | 1280 | 227.2324 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 143 | 10579466 | 6001 | 144.024 | 6.001 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48680740 | 1360 | 226.6289 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 142 | 10585681 | 6215 | 149.16 | 6.215 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48682144 | 1404 | 225.9051 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 140 | 10591673 | 5992 | 143.808 | 5.992 | 7.3 | 7.3 | 3B+1S | 0 | 1048 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48683500 | 1356 | 226.3017 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 | 1.33
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 10597717 | 6044 | 145.056 | 6.044 | 6.7 | 6.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48684892 | 1392 | 230.3111 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 10603504 | 5787 | 138.888 | 5.787 | 6.1 | 6.1 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48686244 | 1352 | 233.6271 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 137 | 10609248 | 5744 | 137.856 | 5.744 | 5.7 | 5.7 | 3B+1S | 0 | 1026 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48687592 | 1348 | 234.6797 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 138 | 10615273 | 6025 | 144.6 | 6.025 | 5.4 | 5.4 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48688956 | 1364 | 226.39 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 10620993 | 5720 | 137.28 | 5.72 | 5.2 | 5.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48690276 | 1320 | 230.7692 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 139 | 10626802 | 5809 | 139.416 | 5.809 | 4.9 | 4.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48691620 | 1344 | 231.3651 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 10632702 | 5900 | 141.6 | 5.9 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48692964 | 1344 | 227.7966 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 138 | 10638416 | 5714 | 137.136 | 5.714 | 4.5 | 4.5 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48694292 | 1328 | 232.4116 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 139 | 10644276 | 5860 | 140.64 | 5.86 | 4.1 | 4.1 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48695644 | 1352 | 230.7167 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 137 | 10650023 | 5747 | 137.928 | 5.747 | 3.6 | 3.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48696980 | 1336 | 232.4691 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 141 | 10655874 | 5851 | 140.424 | 5.851 | 3 | 3 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48698356 | 1376 | 235.1735 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 130 | 10661161 | 5287 | 126.888 | 5.287 | 2.6 | 2.6 | 3B+1S | 0 | 11015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48699628 | 1272 | 240.5901 | 0% | 100% | 100% | 100% | 100% | 0% | 11064070 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 125 | 10666300 | 5139 | 123.336 | 5.139 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48700828 | 1200 | 233.5085 | 0% | 0% | 100% | 100% | 100% | 20% | 11064192 | 122 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 129 | 117 | 10671488 | 5188 | 124.512 | 5.188 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48702084 | 1256 | 242.0971 | 0% | 0% | 100% | 100% | 100% | 20% | 11064324 | 132 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130972 | 130.972 | 130.972 | [12 empty] | 30692 | 30692 | 234.3402 | [6 empty] | 3330 | 3330 | 1.16 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (20%)

## JULY 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 31096 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10671488 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48702084 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11064324 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 137 | 110 | 10675689 | 4201 | 100.824 | 4.201 | 4.3 | 4.3 | 3B | 0 | 0 | 1037 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48703174 | 1090 | 259.462 | 0% | 0% | 100% | 100% | 100% | 63% | 11064831 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 109 | 10679874 | 4185 | 100.44 | 4.185 | 6.8 | 6.8 | 3B | 0 | 0 | 1037 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48704274 | 1100 | 262.8435 | 0% | 0% | 100% | 100% | 100% | 63% | 11065232 | 401 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 107 | 10684094 | 4220 | 101.28 | 4.22 | 8 | 8 | 3B | 0 | 0 | 1037 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48705404 | 1130 | 267.7725 | 0% | 0% | 100% | 100% | 100% | 63% | 11065782 | 550 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 117 | 10688444 | 4350 | 104.4 | 4.35 | 9.2 | 9.2 | 3B | 0 | 0 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48706549 | 1145 | 263.2184 | 0% | 0% | 100% | 100% | 100% | 63% | 11066382 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 120 | 10692844 | 4400 | 105.6 | 4.4 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48707784 | 1235 | 280.6818 | 0% | 0% | 100% | 100% | 100% | 63% | 11066753 | 371 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 138 | 10698802 | 5958 | 142.992 | 5.958 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48709116 | 1332 | 223.565 | 0% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 147 | 10704776 | 5974 | 143.376 | 5.974 | 9.2 | 9.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48710460 | 1344 | 224.9749 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 10710761 | 5985 | 143.64 | 5.985 | 8.6 | 8.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48711820 | 1360 | 227.2348 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 10716773 | 6012 | 144.288 | 6.012 | 7.9 | 7.9 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48713188 | 1368 | 227.5449 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 10722847 | 6074 | 145.776 | 6.074 | 7.3 | 7.3 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48714564 | 1376 | 226.5393 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 | 1.17
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 138 | 10728805 | 5958 | 142.992 | 5.958 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48715932 | 1368 | 229.6073 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 10734674 | 5869 | 140.856 | 5.869 | 6.1 | 6.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48717288 | 1356 | 231.0445 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 10740538 | 5864 | 140.736 | 5.864 | 5.6 | 5.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48718652 | 1364 | 232.6057 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 10746293 | 5755 | 138.12 | 5.755 | 5.2 | 5.2 | 3B+1S | 933 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48720008 | 1356 | 235.6212 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 139 | 10752024 | 5731 | 137.544 | 5.731 | 5 | 5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48721324 | 1316 | 229.6283 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 10757784 | 5760 | 138.24 | 5.76 | 4.8 | 4.8 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48722660 | 1336 | 231.9444 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 10763678 | 5894 | 141.456 | 5.894 | 4.3 | 4.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48724024 | 1364 | 231.4218 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 10769545 | 5867 | 140.808 | 5.867 | 3.7 | 3.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48725372 | 1348 | 229.7597 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 139 | 10775298 | 5753 | 138.072 | 5.753 | 3.4 | 3.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48726716 | 1344 | 233.6172 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 137 | 10781063 | 5765 | 138.36 | 5.765 | 2.9 | 2.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48728068 | 1352 | 234.5186 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 142 | 10786776 | 5713 | 137.112 | 5.713 | 2.5 | 2.5 | 3B+1S | 1086 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48729416 | 1348 | 235.9531 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 128 | 10792390 | 5614 | 134.736 | 5.614 | 2.1 | 2.1 | 3B+1S | 1045 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48730752 | 1336 | 237.9765 | 100% | 0% | 100% | 100% | 100% | 0% | 11066753 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 122 | 10797563 | 5173 | 124.152 | 5.173 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48731972 | 1220 | 235.8399 | 0% | 0% | 100% | 100% | 100% | 30% | 11066959 | 206 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 117 | 10802505 | 4942 | 118.608 | 4.942 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48733180 | 1208 | 244.4355 | 0% | 0% | 100% | 100% | 100% | 30% | 11067453 | 494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131017 | 131.017 | 131.017 | [12 empty] | 31096 | 31096 | 237.3432 | [6 empty] | 3129 | 3129 | 1.12 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (63%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JULY 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30868 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10802505 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48733180 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11067453 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 110 | 10807128 | 4623 | 110.952 | 4.623 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1065 | N/A | N/A | N/A | N/A | 48734300 | 1120 | 242.2669 | 0% | 0% | 100% | 100% | 100% | 60% | 11068046 | 593 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 108 | 10811581 | 4453 | 106.872 | 4.453 | 5.7 | 5.7 | 3B | 0 | 0 | 1136 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48735352 | 1052 | 236.2452 | 0% | 0% | 100% | 100% | 100% | 60% | 11068679 | 633 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 108 | 10815982 | 4401 | 105.624 | 4.401 | 7.4 | 7.4 | 3B | 0 | 0 | 1136 | 1185 | 1065 | N/A | N/A | N/A | N/A | 48736396 | 1044 | 237.2188 | 0% | 0% | 100% | 100% | 100% | 60% | 11069317 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 111 | 10820420 | 4438 | 106.512 | 4.438 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 1065 | N/A | N/A | N/A | N/A | 48737480 | 1084 | 244.2542 | 0% | 0% | 100% | 100% | 100% | 63% | 11069898 | 581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 120 | 10824879 | 4459 | 107.016 | 4.459 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1107 | N/A | N/A | N/A | N/A | 48738628 | 1148 | 257.4568 | 0% | 0% | 100% | 100% | 100% | 63% | 11070039 | 141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 136 | 10829314 | 4435 | 106.44 | 4.435 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48739930 | 1302 | 293.5738 | 0% | 0% | 100% | 100% | 100% | 0% | 11070039 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 143 | 10835247 | 5933 | 142.392 | 5.933 | 9 | 9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48741276 | 1346 | 226.8667 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 10841401 | 6154 | 147.696 | 6.154 | 8.3 | 8.3 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48742672 | 1396 | 226.8443 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 150 | 10847345 | 5944 | 142.656 | 5.944 | 7.6 | 7.6 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48744044 | 1372 | 230.821 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 10853446 | 6101 | 146.424 | 6.101 | 6.9 | 6.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48745436 | 1392 | 228.1593 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 | 0.8
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 142 | 10859362 | 5916 | 141.984 | 5.916 | 6.3 | 6.3 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48746808 | 1372 | 231.9135 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 10865313 | 5951 | 142.824 | 5.951 | 5.6 | 5.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48748188 | 1380 | 231.8938 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 140 | 10871108 | 5795 | 139.08 | 5.795 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48749528 | 1340 | 231.2338 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 10876762 | 5654 | 135.696 | 5.654 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48750868 | 1340 | 237.0004 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 10882479 | 5717 | 137.208 | 5.717 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48752196 | 1328 | 232.2897 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 10888232 | 5753 | 138.072 | 5.753 | 4.1 | 4.1 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48753532 | 1336 | 232.2267 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 10894053 | 5821 | 139.704 | 5.821 | 3.5 | 3.5 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48754892 | 1360 | 233.6368 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 137 | 10899874 | 5821 | 139.704 | 5.821 | 3.2 | 3.2 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48756228 | 1336 | 229.5138 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 10905689 | 5815 | 139.56 | 5.815 | 2.8 | 2.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48757588 | 1360 | 233.8779 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 139 | 10911343 | 5654 | 135.696 | 5.654 | 2.5 | 2.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48758900 | 1312 | 232.0481 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 141 | 10917153 | 5810 | 139.44 | 5.81 | 2.1 | 2.1 | 3B+1S | 0 | 1076 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48760252 | 1352 | 232.7022 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 135 | 10922772 | 5619 | 134.856 | 5.619 | 1.8 | 1.8 | 3B+1S | 0 | 1045 | 1185 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48761588 | 1336 | 237.7647 | 0% | 100% | 100% | 100% | 100% | 0% | 11070039 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 126 | 10928064 | 5292 | 127.008 | 5.292 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48762832 | 1244 | 235.0718 | 0% | 0% | 100% | 100% | 100% | 30% | 11070247 | 208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 124 | 10933125 | 5061 | 121.464 | 5.061 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48764048 | 1216 | 240.2687 | 0% | 0% | 100% | 100% | 100% | 30% | 11070471 | 224 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130620 | 130.62 | 130.62 | [12 empty] | 30868 | 30868 | 236.3191 | [6 empty] | 3018 | 3018 | 1.0567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:19 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JULY 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30836 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 10933125 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48764048 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11070471 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 112 | 10937979 | 4854 | 116.496 | 4.854 | 3.9 | 3.9 | 3B | 0 | 0 | 1054 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48765188 | 1140 | 234.8578 | 0% | 0% | 100% | 100% | 100% | 60% | 11071094 | 623 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 10942536 | 4557 | 109.368 | 4.557 | 5.4 | 5.4 | 3B | 0 | 0 | 1054 | 1185 | 1136 | N/A | N/A | N/A | N/A | 48766272 | 1084 | 237.8758 | 0% | 0% | 100% | 100% | 100% | 60% | 11071781 | 687 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 10946856 | 4320 | 103.68 | 4.32 | 7 | 7 | 3B | 0 | 0 | 1056 | 1185 | 1137 | N/A | N/A | N/A | N/A | 48767324 | 1052 | 243.5185 | 0% | 0% | 100% | 100% | 100% | 60% | 11072486 | 705 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 115 | 10951062 | 4206 | 100.944 | 4.206 | 8.6 | 8.6 | 3B | 0 | 0 | 1077 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48768428 | 1104 | 262.4822 | 0% | 0% | 100% | 100% | 100% | 60% | 11073130 | 644 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 124 | 10955536 | 4474 | 107.376 | 4.474 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48769554 | 1126 | 251.6764 | 0% | 0% | 100% | 100% | 100% | 60% | 11073356 | 226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 136 | 10960208 | 4672 | 112.128 | 4.672 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48770884 | 1330 | 284.6747 | 0% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 139 | 10966225 | 6017 | 144.408 | 6.017 | 9 | 9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48772240 | 1356 | 225.3615 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 10972266 | 6041 | 144.984 | 6.041 | 8.5 | 8.5 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48773604 | 1364 | 225.7904 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 142 | 10978244 | 5978 | 143.472 | 5.978 | 7.9 | 7.9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48774972 | 1368 | 228.8391 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 10984241 | 5997 | 143.928 | 5.997 | 7.3 | 7.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48776340 | 1368 | 228.1141 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 | 1.14
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 140 | 10990150 | 5909 | 141.816 | 5.909 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48777711 | 1371 | 232.019 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 137 | 10996009 | 5859 | 140.616 | 5.859 | 6.2 | 6.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48779052 | 1341 | 228.8786 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 135 | 11001784 | 5775 | 138.6 | 5.775 | 5.7 | 5.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48780396 | 1344 | 232.7273 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 138 | 11007839 | 6055 | 145.32 | 6.055 | 5.3 | 5.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48781820 | 1424 | 235.1775 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 11013459 | 5620 | 134.88 | 5.62 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48783140 | 1320 | 234.8754 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 11018897 | 5438 | 130.512 | 5.438 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48784444 | 1304 | 239.794 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 11024617 | 5720 | 137.28 | 5.72 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48785776 | 1332 | 232.8671 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 142 | 11030403 | 5786 | 138.864 | 5.786 | 3.9 | 3.9 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48787124 | 1348 | 232.9761 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 135 | 11036116 | 5713 | 137.112 | 5.713 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48788468 | 1344 | 235.2529 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 137 | 11041775 | 5659 | 135.816 | 5.659 | 3.2 | 3.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48789800 | 1332 | 235.3773 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 139 | 11047429 | 5654 | 135.696 | 5.654 | 2.7 | 2.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48791140 | 1340 | 237.0004 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 135 | 11052973 | 5544 | 133.056 | 5.544 | 2.3 | 2.3 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48792460 | 1320 | 238.0952 | 100% | 0% | 100% | 100% | 100% | 0% | 11073356 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 120 | 11058180 | 5207 | 124.968 | 5.207 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48793692 | 1232 | 236.6046 | 0% | 0% | 100% | 100% | 100% | 30% | 11073545 | 189 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 124 | 115 | 11062991 | 4811 | 115.464 | 4.811 | 2.9 | 2.9 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48794884 | 1192 | 247.7655 | 0% | 0% | 100% | 100% | 100% | 30% | 11073788 | 243 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129866 | 129.866 | 129.866 | [12 empty] | 30836 | 30836 | 237.4448 | [6 empty] | 3317 | 3317 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JULY 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | ANDRO MIRAFLOR
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30620 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11062991 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48794884 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11073788 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 129 | 109 | 11067417 | 4426 | 106.224 | 4.426 | 3.8 | 3.8 | 3B | 0 | 0 | 1186 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48795984 | 1100 | 248.5314 | 0% | 0% | 100% | 100% | 100% | 60% | 11074378 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 127 | 108 | 11071757 | 4340 | 104.16 | 4.34 | 5.2 | 5.2 | 3B | 0 | 0 | 1116 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48797020 | 1036 | 238.7097 | 0% | 0% | 100% | 100% | 100% | 60% | 11075012 | 634 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 108 | 11076093 | 4336 | 104.064 | 4.336 | 6.8 | 6.8 | 3B | 0 | 0 | 1116 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48798036 | 1016 | 234.3173 | 0% | 0% | 100% | 100% | 100% | 60% | 11075644 | 632 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 119 | 11080386 | 4293 | 103.032 | 4.293 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48799078 | 1042 | 242.7207 | 0% | 0% | 100% | 100% | 100% | 60% | 11076119 | 475 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 123 | 11084785 | 4399 | 105.576 | 4.399 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1136 | N/A | N/A | N/A | N/A | 48800240 | 1162 | 264.1509 | 0% | 0% | 100% | 100% | 100% | 60% | 11076382 | 263 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 131 | 11089468 | 4683 | 112.392 | 4.683 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48801544 | 1304 | 278.454 | 0% | 0% | 100% | 100% | 100% | 0% | 11076382 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 140 | 11095313 | 5845 | 140.28 | 5.845 | 9.2 | 9.2 | 3B+1S | 0 | 986 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48802868 | 1324 | 226.5184 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 137 | 11101451 | 6138 | 147.312 | 6.138 | 8.7 | 8.7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48804252 | 1384 | 225.4806 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 139 | 11107567 | 6116 | 146.784 | 6.116 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48805642 | 1390 | 227.2727 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 11113515 | 5948 | 142.752 | 5.948 | 7.6 | 7.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48807012 | 1370 | 230.3295 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 | 1.16
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 11119272 | 5757 | 138.168 | 5.757 | 7 | 7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48808332 | 1320 | 229.2861 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 11125134 | 5862 | 140.688 | 5.862 | 6.4 | 6.4 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48809676 | 1344 | 229.2733 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 11130986 | 5852 | 140.448 | 5.852 | 5.9 | 5.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48811016 | 1340 | 228.9815 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 11136666 | 5680 | 136.32 | 5.68 | 5.5 | 5.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48812380 | 1364 | 240.1408 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 11142264 | 5598 | 134.352 | 5.598 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48813692 | 1312 | 234.3694 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 11148052 | 5788 | 138.912 | 5.788 | 5 | 5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48815036 | 1344 | 232.2046 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 11153893 | 5841 | 140.184 | 5.841 | 4.6 | 4.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48816392 | 1356 | 232.152 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 137 | 11159677 | 5784 | 138.816 | 5.784 | 4.1 | 4.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48817732 | 1340 | 231.6736 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 11165319 | 5642 | 135.408 | 5.642 | 3.8 | 3.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48819056 | 1324 | 234.6686 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 134 | 11170927 | 5608 | 134.592 | 5.608 | 3.5 | 3.5 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48820376 | 1320 | 235.378 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 137 | 11176636 | 5709 | 137.016 | 5.709 | 3 | 3 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48821752 | 1376 | 241.0229 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 125 | 11182109 | 5473 | 131.352 | 5.473 | 2.6 | 2.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48823060 | 1308 | 238.9914 | 0% | 100% | 100% | 100% | 100% | 0% | 11076382 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 121 | 11187418 | 5309 | 127.416 | 5.309 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48824324 | 1264 | 238.0863 | 0% | 0% | 100% | 100% | 100% | 30% | 11076633 | 251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 119 | 11192286 | 4868 | 116.832 | 4.868 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48825504 | 1180 | 242.3993 | 0% | 0% | 100% | 100% | 100% | 30% | 11076922 | 289 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129295 | 129.295 | 129.295 | [12 empty] | 30620 | 30620 | 236.8228 | [6 empty] | 3134 | 3134 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:33 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## JULY 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30540 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11192286 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48825504 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11076922 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 136 | 110 | 11196847 | 4561 | 109.464 | 4.561 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48826608 | 1104 | 242.0522 | 0% | 0% | 100% | 100% | 100% | 60% | 11077632 | 710 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 108 | 11201302 | 4455 | 106.92 | 4.455 | 5.9 | 5.9 | 3B | 0 | 0 | 1137 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48827656 | 1048 | 235.2413 | 0% | 0% | 100% | 100% | 100% | 60% | 11078386 | 754 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 109 | 11205688 | 4386 | 105.264 | 4.386 | 7.6 | 7.6 | 3B | 0 | 0 | 1136 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48828684 | 1028 | 234.3821 | 0% | 0% | 100% | 100% | 100% | 60% | 11079120 | 734 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 115 | 11209751 | 4063 | 97.512 | 4.063 | 9.1 | 9.1 | 3B | 0 | 0 | 1146 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48829756 | 1072 | 263.8444 | 0% | 0% | 100% | 100% | 100% | 60% | 11079840 | 720 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 121 | 11214108 | 4357 | 104.568 | 4.357 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48830932 | 1176 | 269.9105 | 0% | 0% | 100% | 100% | 100% | 60% | 11079887 | 47 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 135 | 11219444 | 5336 | 128.064 | 5.336 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1166 | N/A | N/A | N/A | N/A | 48832068 | 1136 | 212.8936 | 0% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 136 | 11224925 | 5481 | 131.544 | 5.481 | 9.5 | 9.5 | 3B | 0 | 0 | 1156 | 1185 | 1167 | N/A | N/A | N/A | N/A | 48833236 | 1168 | 213.0998 | 0% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 140 | 11230961 | 6036 | 144.864 | 6.036 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48834596 | 1360 | 225.3148 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 142 | 11236937 | 5976 | 143.424 | 5.976 | 8.8 | 8.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48835944 | 1348 | 225.5689 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 149 | 11243103 | 6166 | 147.984 | 6.166 | 8 | 8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48837360 | 1416 | 229.6464 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 | 1.26
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 126 | 141 | 11249262 | 6159 | 147.816 | 6.159 | 7 | 7 | 3B+1S | 1149 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48838802 | 1442 | 234.1289 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 138 | 11255076 | 5814 | 139.536 | 5.814 | 6.1 | 6.1 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48840164 | 1362 | 234.2621 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 145 | 11260908 | 5832 | 139.968 | 5.832 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48841520 | 1356 | 232.5103 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 132 | 11266619 | 5711 | 137.064 | 5.711 | 4.9 | 4.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48842872 | 1352 | 236.7361 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 11272118 | 5499 | 131.976 | 5.499 | 4.4 | 4.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48844184 | 1312 | 238.5888 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 11277979 | 5861 | 140.664 | 5.861 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48845524 | 1340 | 228.6299 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 11283728 | 5749 | 137.976 | 5.749 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48846852 | 1328 | 230.9967 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 11289524 | 5796 | 139.104 | 5.796 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48848188 | 1336 | 230.5038 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 134 | 11295216 | 5692 | 136.608 | 5.692 | 2.9 | 2.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48849504 | 1316 | 231.2017 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 11300957 | 5741 | 137.784 | 5.741 | 2.7 | 2.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48850840 | 1336 | 232.7121 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 138 | 11306661 | 5704 | 136.896 | 5.704 | 2.3 | 2.3 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48852188 | 1348 | 236.3254 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 130 | 11312528 | 5867 | 140.808 | 5.867 | 2 | 2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48853600 | 1412 | 240.6681 | 100% | 0% | 100% | 100% | 100% | 0% | 11079887 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 121 | 11317706 | 5178 | 124.272 | 5.178 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48854832 | 1232 | 237.9297 | 0% | 0% | 100% | 100% | 100% | 30% | 11080063 | 176 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 119 | 11322716 | 5010 | 120.24 | 5.01 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48856044 | 1212 | 241.9162 | 0% | 0% | 100% | 100% | 100% | 30% | 11080275 | 212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130430 | 130.43 | 130.43 | [12 empty] | 30540 | 30540 | 234.1486 | [6 empty] | 3353 | 3353 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:08 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JULY 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-07-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30408 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11322716 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48856044 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11080275 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 108 | 11327357 | 4641 | 111.384 | 4.641 | 3.8 | 3.8 | 3B | 0 | 0 | 1045 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48857156 | 1112 | 239.6035 | 0% | 0% | 100% | 100% | 100% | 60% | 11080795 | 520 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 107 | 11331880 | 4523 | 108.552 | 4.523 | 5.4 | 5.4 | 3B | 0 | 0 | 1046 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48858260 | 1104 | 244.0858 | 0% | 0% | 100% | 100% | 100% | 60% | 11081369 | 574 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 105 | 11336182 | 4302 | 103.248 | 4.302 | 7 | 7 | 3B | 0 | 0 | 1045 | 1185 | 1136 | N/A | N/A | N/A | N/A | 48859288 | 1028 | 238.9586 | 0% | 0% | 100% | 100% | 100% | 60% | 11082014 | 645 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 112 | 11340375 | 4193 | 100.632 | 4.193 | 8.4 | 8.4 | 3B | 0 | 0 | 1045 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48860408 | 1120 | 267.1119 | 0% | 0% | 100% | 100% | 100% | 60% | 11082559 | 545 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 115 | 11344676 | 4301 | 103.224 | 4.301 | 9.5 | 9.5 | 3B | 0 | 0 | 1045 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48861588 | 1180 | 274.3548 | 0% | 0% | 100% | 100% | 100% | 60% | 11082779 | 220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 131 | 11348988 | 4312 | 103.488 | 4.312 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48862768 | 1180 | 273.6549 | 0% | 0% | 100% | 100% | 100% | 0% | 11082779 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 134 | 11354333 | 5345 | 128.28 | 5.345 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48863892 | 1124 | 210.29 | 0% | 0% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 140 | 11360094 | 5761 | 138.264 | 5.761 | 9.5 | 9.5 | 3B+1S | 0 | 975 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48865164 | 1272 | 220.795 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 11366021 | 5927 | 142.248 | 5.927 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48866504 | 1340 | 226.084 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 11372265 | 6244 | 149.856 | 6.244 | 8.4 | 8.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48867908 | 1404 | 224.8559 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 | 1.22
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 139 | 11378267 | 6002 | 144.048 | 6.002 | 7.6 | 7.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48869272 | 1364 | 227.2576 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 11384276 | 6009 | 144.216 | 6.009 | 7 | 7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48870648 | 1376 | 228.9898 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 11390232 | 5956 | 142.944 | 5.956 | 6.3 | 6.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48872024 | 1376 | 231.0275 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 138 | 11396030 | 5798 | 139.152 | 5.798 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48873380 | 1356 | 233.8737 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 139 | 11401911 | 5881 | 141.144 | 5.881 | 5.4 | 5.4 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48874740 | 1360 | 231.2532 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 11407763 | 5852 | 140.448 | 5.852 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48876076 | 1336 | 228.298 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 11413306 | 5543 | 133.032 | 5.543 | 4.6 | 4.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48877388 | 1312 | 236.6949 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 136 | 11419004 | 5698 | 136.752 | 5.698 | 4.2 | 4.2 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48878692 | 1304 | 228.8522 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 11424834 | 5830 | 139.92 | 5.83 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48880040 | 1348 | 231.2178 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 132 | 11430456 | 5622 | 134.928 | 5.622 | 3.8 | 3.8 | 3B+1S | 0 | 1006 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48881372 | 1332 | 236.9264 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 137 | 11436158 | 5702 | 136.848 | 5.702 | 3.4 | 3.4 | 3B+1S | 0 | 1076 | 1185 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48882732 | 1360 | 238.5128 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 130 | 11441575 | 5417 | 130.008 | 5.417 | 3 | 3 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48884024 | 1292 | 238.5084 | 0% | 100% | 100% | 100% | 100% | 0% | 11082779 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 119 | 11446726 | 5151 | 123.624 | 5.151 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48885252 | 1228 | 238.4003 | 0% | 0% | 100% | 100% | 100% | 30% | 11082986 | 207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 112 | 11451612 | 4886 | 117.264 | 4.886 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48886452 | 1200 | 245.5997 | 0% | 0% | 100% | 100% | 100% | 30% | 11083369 | 383 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128896 | 128.896 | 128.896 | [12 empty] | 30408 | 30408 | 235.9111 | [6 empty] | 3094 | 3094 | 1.0783 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (JULY 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 5am the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)