## AUG 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30468 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11451612 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48886452 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11083369 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 131 | 108 | 11456240 | 4628 | 111.072 | 4.628 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48887596 | 1144 | 247.191 | 0% | 0% | 100% | 100% | 100% | 50% | 11084065 | 696 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 105 | 11460601 | 4361 | 104.664 | 4.361 | 6.7 | 6.7 | 3B | 0 | 0 | 1106 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48888616 | 1020 | 233.8913 | 0% | 0% | 100% | 100% | 100% | 50% | 11084796 | 731 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 126 | 105 | 11464980 | 4379 | 105.096 | 4.379 | 7.9 | 7.9 | 3B | 0 | 0 | 1106 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48889628 | 1012 | 231.103 | 0% | 0% | 100% | 100% | 100% | 50% | 11085558 | 762 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 114 | 11469190 | 4210 | 101.04 | 4.21 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48890740 | 1112 | 264.133 | 0% | 0% | 100% | 100% | 100% | 50% | 11086179 | 621 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 135 | 125 | 11473540 | 4350 | 104.4 | 4.35 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48891868 | 1128 | 259.3103 | 0% | 0% | 100% | 100% | 100% | 50% | 11086279 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 128 | 11479021 | 5481 | 131.544 | 5.481 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48893068 | 1200 | 218.9381 | 0% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 | 1.19 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 141 | 11484856 | 5835 | 140.04 | 5.835 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48894380 | 1312 | 224.85 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 143 | 11490888 | 6032 | 144.768 | 6.032 | 9 | 9 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48895736 | 1356 | 224.8011 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 145 | 11496899 | 6011 | 144.264 | 6.011 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48897084 | 1348 | 224.2555 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 144 | 11502960 | 6061 | 145.464 | 6.061 | 8.1 | 8.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48898444 | 1360 | 224.3854 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 | 1.23
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 141 | 11508928 | 5968 | 143.232 | 5.968 | 7.6 | 7.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48899796 | 1352 | 226.5416 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 141 | 11514859 | 5931 | 142.344 | 5.931 | 6.9 | 6.9 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48901172 | 1376 | 232.0013 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 137 | 11520670 | 5811 | 139.464 | 5.811 | 6.3 | 6.3 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48902540 | 1368 | 235.4156 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 124 | 133 | 11526422 | 5752 | 138.048 | 5.752 | 5.6 | 5.6 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48903908 | 1368 | 237.8303 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 138 | 11532064 | 5642 | 135.408 | 5.642 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48905232 | 1324 | 234.6686 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 139 | 11537786 | 5722 | 137.328 | 5.722 | 4.7 | 4.7 | 3B+1S | 1045 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48906576 | 1344 | 234.8829 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 11543645 | 5859 | 140.616 | 5.859 | 4.2 | 4.2 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48907940 | 1364 | 232.8042 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 141 | 11549428 | 5783 | 138.792 | 5.783 | 3.7 | 3.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48909276 | 1336 | 231.022 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 139 | 11555276 | 5848 | 140.352 | 5.848 | 3.3 | 3.3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48910636 | 1360 | 232.5581 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 136 | 11561074 | 5798 | 139.152 | 5.798 | 3 | 3 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48911996 | 1360 | 234.5636 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 132 | 11566336 | 5262 | 126.288 | 5.262 | 2.9 | 2.9 | 3B+1S | 1003 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48913244 | 1248 | 237.1722 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 133 | 124 | 11571464 | 5128 | 123.072 | 5.128 | 2.8 | 2.8 | 3B+1S | 1003 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48914488 | 1244 | 242.5897 | 100% | 0% | 100% | 100% | 100% | 0% | 11086279 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 122 | 11576628 | 5164 | 123.936 | 5.164 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48915716 | 1228 | 237.8002 | 0% | 0% | 100% | 100% | 100% | 18% | 11086300 | 21 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 120 | 11581560 | 4932 | 118.368 | 4.932 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48916920 | 1204 | 244.12 | 0% | 0% | 100% | 100% | 100% | 18% | 11086793 | 493 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129948 | 129.948 | 129.948 | [12 empty] | 30468 | 30468 | 234.463 | [6 empty] | 3424 | 3424 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:05 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (18%)

## AUG 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30724 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11581560 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48916920 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11086793 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 109 | 11585774 | 4214 | 101.136 | 4.214 | 4.9 | 4.9 | 3B | 0 | 0 | 1096 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48917910 | 990 | 234.9312 | 0% | 0% | 100% | 100% | 100% | 70% | 11087426 | 633 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 107 | 11590004 | 4230 | 101.52 | 4.23 | 6.7 | 6.7 | 3B | 0 | 0 | 1096 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48918915 | 1005 | 237.5887 | 0% | 0% | 100% | 100% | 100% | 70% | 11088081 | 655 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 127 | 105 | 11594254 | 4250 | 102 | 4.25 | 7.7 | 7.7 | 3B | 0 | 0 | 1096 | 1185 | 1066 | N/A | N/A | N/A | N/A | 48919980 | 1065 | 250.5882 | 0% | 0% | 100% | 100% | 100% | 70% | 11088701 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 115 | 11598594 | 4340 | 104.16 | 4.34 | 8.8 | 8.8 | 3B | 0 | 0 | 1126 | 1185 | 1107 | N/A | N/A | N/A | N/A | 48921076 | 1096 | 252.5346 | 0% | 0% | 100% | 100% | 100% | 70% | 11089311 | 610 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 120 | 11603082 | 4488 | 107.712 | 4.488 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48922272 | 1196 | 266.4884 | 0% | 0% | 100% | 100% | 100% | 70% | 11089527 | 216 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 135 | 11608887 | 5805 | 139.32 | 5.805 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48923588 | 1316 | 226.7011 | 0% | 0% | 100% | 100% | 100% | 0% | 11089527 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 143 | 11614797 | 5910 | 141.84 | 5.91 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48924932 | 1344 | 227.4112 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 11620817 | 6020 | 144.48 | 6.02 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48926300 | 1368 | 227.2425 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 11626856 | 6039 | 144.936 | 6.039 | 7.8 | 7.8 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48927676 | 1376 | 227.8523 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 11632944 | 6088 | 146.112 | 6.088 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48929060 | 1384 | 227.3325 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 | 1.37
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 11639007 | 6063 | 145.512 | 6.063 | 6.5 | 6.5 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48930444 | 1384 | 228.2698 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 11644901 | 5894 | 141.456 | 5.894 | 5.9 | 5.9 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48931804 | 1360 | 230.7431 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 11650731 | 5830 | 139.92 | 5.83 | 5.4 | 5.4 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48933164 | 1360 | 233.2762 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 11656306 | 5575 | 133.8 | 5.575 | 5 | 5 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48934464 | 1300 | 233.1839 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 141 | 11662118 | 5812 | 139.488 | 5.812 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48935824 | 1360 | 233.9986 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 11667750 | 5632 | 135.168 | 5.632 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48937132 | 1308 | 232.2443 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 11673537 | 5787 | 138.888 | 5.787 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48938468 | 1336 | 230.8623 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 138 | 11679402 | 5865 | 140.76 | 5.865 | 4.1 | 4.1 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48939812 | 1344 | 229.156 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 11685272 | 5870 | 140.88 | 5.87 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48941162 | 1350 | 229.983 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 135 | 11690764 | 5492 | 131.808 | 5.492 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48942440 | 1278 | 232.7021 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 139 | 11696624 | 5860 | 140.64 | 5.86 | 3.2 | 3.2 | 3B+1S | 0 | 1096 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48943812 | 1372 | 234.1297 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 136 | 11702441 | 5817 | 139.608 | 5.817 | 2.7 | 2.7 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48945204 | 1392 | 239.2986 | 0% | 100% | 100% | 100% | 100% | 0% | 11089527 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 127 | 11707474 | 5033 | 120.792 | 5.033 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48946436 | 1232 | 244.7844 | 0% | 0% | 100% | 100% | 100% | 35% | 11089589 | 62 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 118 | 11712568 | 5094 | 122.256 | 5.094 | 3.6 | 3.6 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 48947644 | 1208 | 237.1417 | 0% | 0% | 100% | 100% | 100% | 35% | 11090342 | 753 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131008 | 131.008 | 131.008 | [12 empty] | 30724 | 30724 | 234.52 | [6 empty] | 3549 | 3549 | 1.14 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## AUG 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30488 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11712568 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48947644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11090342 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 106 | 11716963 | 4395 | 105.48 | 4.395 | 5.3 | 5.3 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48948620 | 976 | 222.0705 | 0% | 0% | 100% | 100% | 100% | 70% | 11091347 | 1005 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 104 | 11721250 | 4287 | 102.888 | 4.287 | 6.9 | 6.9 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48949572 | 952 | 222.0667 | 0% | 0% | 100% | 100% | 100% | 70% | 11092267 | 920 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 126 | 103 | 11725584 | 4334 | 104.016 | 4.334 | 8.1 | 8.1 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48950532 | 960 | 221.5044 | 0% | 0% | 100% | 100% | 100% | 70% | 11093120 | 853 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 114 | 11729934 | 4350 | 104.4 | 4.35 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 48951694 | 1162 | 267.1264 | 0% | 0% | 100% | 100% | 100% | 70% | 11093538 | 418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 122 | 11734276 | 4342 | 104.208 | 4.342 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48952852 | 1158 | 266.6974 | 0% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 144 | 139 | 11739797 | 5521 | 132.504 | 5.521 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48954092 | 1240 | 224.597 | 0% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 146 | 11745867 | 6070 | 145.68 | 6.07 | 9.3 | 9.3 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48955452 | 1360 | 224.0527 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 145 | 11751971 | 6104 | 146.496 | 6.104 | 8.7 | 8.7 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48956832 | 1380 | 226.0813 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 144 | 11758113 | 6142 | 147.408 | 6.142 | 8 | 8 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48958228 | 1396 | 227.2875 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 11764155 | 6042 | 145.008 | 6.042 | 7.3 | 7.3 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48959614 | 1386 | 229.3942 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 | 1.3
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 142 | 11770074 | 5919 | 142.056 | 5.919 | 6.5 | 6.5 | 3B+1S | 1068 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48960964 | 1350 | 228.0791 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 11775973 | 5899 | 141.576 | 5.899 | 5.9 | 5.9 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48962340 | 1376 | 233.2599 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 11781795 | 5822 | 139.728 | 5.822 | 5.3 | 5.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48963689 | 1349 | 231.7073 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 11787346 | 5551 | 133.224 | 5.551 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48964980 | 1291 | 232.5707 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 132 | 11793098 | 5752 | 138.048 | 5.752 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48966340 | 1360 | 236.4395 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 11798828 | 5730 | 137.52 | 5.73 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 48967692 | 1352 | 235.9511 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 11804614 | 5786 | 138.864 | 5.786 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48969004 | 1312 | 226.7542 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 142 | 11810378 | 5764 | 138.336 | 5.764 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48970332 | 1328 | 230.3956 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 138 | 11816118 | 5740 | 137.76 | 5.74 | 3.2 | 3.2 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48971668 | 1336 | 232.7526 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 136 | 11821610 | 5492 | 131.808 | 5.492 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48972948 | 1280 | 233.0663 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 138 | 11827466 | 5856 | 140.544 | 5.856 | 2.4 | 2.4 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48974332 | 1384 | 236.3388 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 137 | 11833280 | 5814 | 139.536 | 5.814 | 2.2 | 2.2 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48975720 | 1388 | 238.7341 | 100% | 0% | 100% | 100% | 100% | 0% | 11093538 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 134 | 11838558 | 5278 | 126.672 | 5.278 | 2.4 | 2.4 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48976968 | 1248 | 236.4532 | 0% | 0% | 100% | 100% | 100% | 50% | 11093896 | 358 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 125 | 11843425 | 4867 | 116.808 | 4.867 | 3.1 | 3.1 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 48978132 | 1164 | 239.1617 | 0% | 0% | 100% | 100% | 100% | 50% | 11094203 | 307 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130857 | 130.857 | 130.857 | [12 empty] | 30488 | 30488 | 232.9872 | [6 empty] | 3861 | 3861 | 1.0683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## AUG 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30512 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11843425 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 48978132 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11094203 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 103 | 11847703 | 4278 | 102.672 | 4.278 | 5 | 5 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 48979100 | 968 | 226.274 | 0% | 0% | 100% | 100% | 100% | 75% | 11094865 | 662 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 100 | 11851903 | 4200 | 100.8 | 4.2 | 6.7 | 6.7 | 3B | 0 | 0 | 1045 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48979976 | 876 | 208.5714 | 0% | 0% | 100% | 100% | 100% | 75% | 11095765 | 900 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 126 | 101 | 11856104 | 4201 | 100.824 | 4.201 | 7.8 | 7.8 | 3B | 0 | 0 | 1045 | 1185 | 1046 | N/A | N/A | N/A | N/A | 48981004 | 1028 | 244.7036 | 0% | 0% | 100% | 100% | 100% | 75% | 11096371 | 606 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 132 | 115 | 11859477 | 3373 | 80.952 | 3.373 | 8.6 | 8.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 48982048 | 1044 | 309.5168 | 0% | 0% | 100% | 100% | 100% | 75% | 11097129 | 758 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 137 | 125 | 11864250 | 4773 | 114.552 | 4.773 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48983292 | 1244 | 260.6327 | 0% | 0% | 100% | 100% | 100% | 75% | 11097491 | 362 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 136 | 11869513 | 5263 | 126.312 | 5.263 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48984472 | 1180 | 224.2067 | 0% | 0% | 100% | 100% | 100% | 0% | 11097491 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 140 | 11875455 | 5942 | 142.608 | 5.942 | 9.3 | 9.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48985820 | 1348 | 226.8596 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 11881479 | 6024 | 144.576 | 6.024 | 8.8 | 8.8 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48987144 | 1324 | 219.7875 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 144 | 11887500 | 6021 | 144.504 | 6.021 | 8.1 | 8.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48988556 | 1412 | 234.5125 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 143 | 11893523 | 6023 | 144.552 | 6.023 | 7.5 | 7.5 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48989932 | 1376 | 228.4576 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 | 1.21
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 139 | 11899510 | 5987 | 143.688 | 5.987 | 6.8 | 6.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48991314 | 1382 | 230.8335 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 11905418 | 5908 | 141.792 | 5.908 | 6.1 | 6.1 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48992644 | 1330 | 225.1185 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 135 | 11911229 | 5811 | 139.464 | 5.811 | 5.6 | 5.6 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48994024 | 1380 | 237.4806 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 129 | 11917348 | 6119 | 146.856 | 6.119 | 5.1 | 5.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48995444 | 1420 | 232.0641 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 11922862 | 5514 | 132.336 | 5.514 | 4.8 | 4.8 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48996752 | 1308 | 237.2144 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 135 | 11928636 | 5774 | 138.576 | 5.774 | 4.4 | 4.4 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48998092 | 1340 | 232.0748 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 138 | 11934514 | 5878 | 141.072 | 5.878 | 3.9 | 3.9 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 48999444 | 1352 | 230.0102 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 11940404 | 5890 | 141.36 | 5.89 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49000800 | 1356 | 230.2207 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 11946222 | 5818 | 139.632 | 5.818 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49002148 | 1348 | 231.6947 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 11951964 | 5742 | 137.808 | 5.742 | 2.7 | 2.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49003480 | 1332 | 231.9749 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 137 | 11957646 | 5682 | 136.368 | 5.682 | 2.2 | 2.2 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49004808 | 1328 | 233.7205 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 134 | 11963573 | 5927 | 142.248 | 5.927 | 1.8 | 1.8 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49006204 | 1396 | 235.5323 | 0% | 100% | 100% | 100% | 100% | 0% | 11097491 | 0 | 1.36 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 130 | 11968775 | 5202 | 124.848 | 5.202 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49007428 | 1224 | 235.2941 | 0% | 0% | 100% | 100% | 100% | 35% | 11097834 | 343 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 148 | 120 | 11973867 | 5092 | 122.208 | 5.092 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49008644 | 1216 | 238.806 | 0% | 0% | 100% | 100% | 100% | 35% | 11098274 | 440 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130442 | 130.442 | 130.442 | [12 empty] | 30512 | 30512 | 233.9124 | [6 empty] | 4071 | 4071 | 1.1717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (35%)

## AUG 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30500 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 11973867 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49008644 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11098274 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 137 | 102 | 11978253 | 4386 | 105.264 | 4.386 | 5.2 | 5.2 | 3B | 0 | 0 | 1045 | 1185 | 1046 | N/A | N/A | N/A | N/A | 49009620 | 976 | 222.5262 | 0% | 0% | 100% | 100% | 100% | 70% | 11098784 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 100 | 11982517 | 4264 | 102.336 | 4.264 | 6.9 | 6.9 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49010576 | 956 | 224.2026 | 0% | 0% | 100% | 100% | 100% | 70% | 11099330 | 546 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 103 | 11986777 | 4260 | 102.24 | 4.26 | 7.6 | 7.6 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49011528 | 952 | 223.4742 | 0% | 0% | 100% | 100% | 100% | 70% | 11099835 | 505 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 120 | 11990798 | 4021 | 96.504 | 4.021 | 8.5 | 8.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49012656 | 1128 | 280.5272 | 0% | 0% | 100% | 100% | 100% | 70% | 11100565 | 730 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 123 | 11995362 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49013900 | 1244 | 272.5679 | 0% | 0% | 100% | 100% | 100% | 70% | 11101402 | 837 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 136 | 12000851 | 5489 | 131.736 | 5.489 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49015120 | 1220 | 222.2627 | 0% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 12006932 | 6081 | 145.944 | 6.081 | 9 | 9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49016480 | 1360 | 223.6474 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 12012976 | 6044 | 145.056 | 6.044 | 8.4 | 8.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49017844 | 1364 | 225.6784 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 147 | 12019052 | 6076 | 145.824 | 6.076 | 7.7 | 7.7 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49019220 | 1376 | 226.4648 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 12025152 | 6100 | 146.4 | 6.1 | 7 | 7 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49020604 | 1384 | 226.8852 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 | 1.3
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 142 | 12031168 | 6016 | 144.384 | 6.016 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49021972 | 1368 | 227.3936 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 139 | 12037135 | 5967 | 143.208 | 5.967 | 5.7 | 5.7 | 3B+1S | 1065 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49023348 | 1376 | 230.6016 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 12042935 | 5800 | 139.2 | 5.8 | 5.3 | 5.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49024692 | 1344 | 231.7241 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 12048522 | 5587 | 134.088 | 5.587 | 4.8 | 4.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49026004 | 1312 | 234.8309 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 135 | 12054466 | 5944 | 142.656 | 5.944 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49027364 | 1360 | 228.8022 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 12060284 | 5818 | 139.632 | 5.818 | 4 | 4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49028712 | 1348 | 231.6947 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 12066046 | 5762 | 138.288 | 5.762 | 3.6 | 3.6 | 3B+1S | 1024 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49030044 | 1332 | 231.1697 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 137 | 12071894 | 5848 | 140.352 | 5.848 | 3.3 | 3.3 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49031396 | 1352 | 231.1902 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 12077386 | 5492 | 131.808 | 5.492 | 3 | 3 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49032668 | 1272 | 231.6096 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 12083204 | 5818 | 139.632 | 5.818 | 2.6 | 2.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49034026 | 1358 | 233.4135 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 134 | 12089056 | 5852 | 140.448 | 5.852 | 2.3 | 2.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49035388 | 1362 | 232.7409 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 133 | 12094587 | 5531 | 132.744 | 5.531 | 2 | 2 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49036704 | 1316 | 237.9317 | 100% | 0% | 100% | 100% | 100% | 0% | 11101402 | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 125 | 12099840 | 5253 | 126.072 | 5.253 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49037936 | 1232 | 234.5326 | 0% | 0% | 100% | 100% | 100% | 50% | 11101574 | 172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 121 | 12104893 | 5053 | 121.272 | 5.053 | 3.6 | 3.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49039144 | 1208 | 239.0659 | 0% | 0% | 100% | 100% | 100% | 50% | 11102113 | 539 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131026 | 131.026 | 131.026 | [12 empty] | 30500 | 30500 | 232.7782 | [6 empty] | 3839 | 3839 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:40AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (50%)

## AUG 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30400 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12104893 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49039144 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11102113 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 133 | 102 | 12109302 | 4409 | 105.816 | 4.409 | 4.9 | 4.9 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49040116 | 972 | 220.4582 | 0% | 0% | 100% | 100% | 100% | 75% | 11102662 | 549 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 101 | 12113598 | 4296 | 103.104 | 4.296 | 6.7 | 6.7 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49041068 | 952 | 221.6015 | 0% | 0% | 100% | 100% | 100% | 75% | 11103406 | 744 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 103 | 12117954 | 4356 | 104.544 | 4.356 | 7.5 | 7.5 | 3B | 0 | 0 | 1045 | 1185 | 1046 | N/A | N/A | N/A | N/A | 49042020 | 952 | 218.5491 | 0% | 0% | 100% | 100% | 100% | 75% | 11104161 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 110 | 12121582 | 3628 | 87.072 | 3.628 | 8.6 | 8.6 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49043122 | 1102 | 303.7486 | 0% | 0% | 100% | 100% | 100% | 75% | 11104732 | 571 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 115 | 12126110 | 4528 | 108.672 | 4.528 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49044284 | 1162 | 256.6254 | 0% | 0% | 100% | 100% | 100% | 75% | 11105132 | 400 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 139 | 12131448 | 5338 | 128.112 | 5.338 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49045420 | 1136 | 212.8138 | 0% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 131 | 12137302 | 5854 | 140.496 | 5.854 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49046684 | 1264 | 215.9207 | 0% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 12143322 | 6020 | 144.48 | 6.02 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49048032 | 1348 | 223.9203 | 0% | 100% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 12149425 | 6103 | 146.472 | 6.103 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49049408 | 1376 | 225.4629 | 0% | 100% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 12155534 | 6109 | 146.616 | 6.109 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49050788 | 1380 | 225.8962 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 | 1.27
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 143 | 12161549 | 6015 | 144.36 | 6.015 | 7.1 | 7.1 | 3B+1S | 1048 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49052160 | 1372 | 228.0964 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 145 | 12167572 | 6023 | 144.552 | 6.023 | 6.2 | 6.2 | 3B+1S | 1096 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49053564 | 1404 | 233.1064 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 147 | 12173686 | 6114 | 146.736 | 6.114 | 5.4 | 5.4 | 3B+1S | 1097 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49054964 | 1400 | 228.9827 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 12179272 | 5586 | 134.064 | 5.586 | 4.7 | 4.7 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49056250 | 1286 | 230.2184 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 129 | 12184993 | 5721 | 137.304 | 5.721 | 4.2 | 4.2 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49057596 | 1346 | 235.2736 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 142 | 12190922 | 5929 | 142.296 | 5.929 | 3.5 | 3.5 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49058956 | 1360 | 229.381 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 12196835 | 5913 | 141.912 | 5.913 | 3 | 3 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49060324 | 1368 | 231.3546 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 139 | 12202730 | 5895 | 141.48 | 5.895 | 2.1 | 2.1 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49061668 | 1344 | 227.9898 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 138 | 12208550 | 5820 | 139.68 | 5.82 | 2.5 | 2.5 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49063004 | 1336 | 229.5533 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 138 | 12214283 | 5733 | 137.592 | 5.733 | 2.2 | 2.2 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49064324 | 1320 | 230.2459 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 137 | 12220031 | 5748 | 137.952 | 5.748 | 1.9 | 1.9 | 3B+1S | 1065 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49065664 | 1340 | 233.1246 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 131 | 12226020 | 5989 | 143.736 | 5.989 | 1.8 | 1.8 | 3B+1S | 1043 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49067108 | 1444 | 241.1087 | 100% | 0% | 100% | 100% | 100% | 0% | 11105132 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 126 | 12231243 | 5223 | 125.352 | 5.223 | 2.5 | 2.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49068328 | 1220 | 233.5822 | 0% | 0% | 100% | 100% | 100% | 40% | 11105450 | 318 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 3 | 2.1127 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 124 | 12236354 | 5111 | 122.664 | 5.111 | 3.2 | 3.2 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49069544 | 1216 | 237.9182 | 0% | 0% | 100% | 100% | 100% | 40% | 11105760 | 310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131461 | 131.461 | 131.461 | [12 empty] | 30400 | 30400 | 231.2473 | [6 empty] | 3647 | 3647 | 1.1217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
CHANGE OPERATION SP2 TO SP1 DUE TO PREVENTIVE MAINTENANCE
SP2- STOPPED @ 9: 28 AM
SP1- STARTED @ 9:30 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (45%)

## AUG 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29884 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12236354 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49069544 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11105760 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 136 | 107 | 12240831 | 4477 | 107.448 | 4.477 | 5.2 | 5.2 | 3B | 0 | 0 | 1044 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49070520 | 976 | 218.0031 | 0% | 0% | 100% | 100% | 100% | 70% | 11106343 | 583 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 3 | 2.1127 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 104 | 12245207 | 4376 | 105.024 | 4.376 | 6.9 | 6.9 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49071476 | 956 | 218.4644 | 0% | 0% | 100% | 100% | 100% | 70% | 11106905 | 562 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 | 105 | 12249300 | 4093 | 98.232 | 4.093 | 8.6 | 8.6 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49072372 | 896 | 218.9103 | 0% | 0% | 100% | 100% | 100% | 70% | 11107953 | 1048 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 116 | 12252896 | 3596 | 86.304 | 3.596 | 9.5 | 9.5 | 3B | 0 | 0 | 1105 | 1185 | 1105 | N/A | N/A | N/A | N/A | 49073374 | 1002 | 278.6429 | 0% | 0% | 100% | 100% | 100% | 70% | 11108960 | 1007 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 117 | 12257400 | 4504 | 108.096 | 4.504 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49074632 | 1258 | 279.3073 | 0% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 124 | 12262447 | 5047 | 121.128 | 5.047 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49075692 | 1060 | 210.0258 | 0% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 136 | 12267945 | 5498 | 131.952 | 5.498 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49076792 | 1100 | 200.0728 | 0% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 145 | 12273826 | 5881 | 141.144 | 5.881 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49078052 | 1260 | 214.2493 | 0% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 12279940 | 6114 | 146.736 | 6.114 | 9.2 | 9.2 | 3B+1S | 1017 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49079412 | 1360 | 222.4403 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 147 | 12286111 | 6171 | 148.104 | 6.171 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1186 | 185 | 1186 | N/A | N/A | N/A | N/A | 49080788 | 1376 | 222.9784 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 | 1.25
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 12292280 | 6169 | 148.056 | 6.169 | 8 | 8 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49082172 | 1384 | 224.3475 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 12298300 | 6020 | 144.48 | 6.02 | 7.3 | 7.3 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49083540 | 1368 | 227.2425 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 12304237 | 5937 | 142.488 | 5.937 | 6.6 | 6.6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49084908 | 1368 | 230.4194 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 134 | 12310143 | 5906 | 141.744 | 5.906 | 6 | 6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49086268 | 1360 | 230.2743 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 141 | 12315966 | 5823 | 139.752 | 5.823 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49087612 | 1344 | 230.8089 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 144 | 12321794 | 5828 | 139.872 | 5.828 | 5 | 5 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49088964 | 1352 | 231.9835 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 12327707 | 5913 | 141.912 | 5.913 | 4.5 | 4.5 | 3B+1S | 1045 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49090316 | 1352 | 228.6487 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 140 | 12333529 | 5822 | 139.728 | 5.822 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49091660 | 1344 | 230.8485 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 135 | 12339363 | 5834 | 140.016 | 5.834 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49092992 | 1332 | 228.3168 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 133 | 12345153 | 5790 | 138.96 | 5.79 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49094332 | 1340 | 231.4335 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 134 | 12350925 | 5772 | 138.528 | 5.772 | 3.1 | 3.1 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49095656 | 1324 | 229.3832 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 130 | 12356497 | 5572 | 133.728 | 5.572 | 3 | 3 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49096980 | 1324 | 237.6167 | 100% | 0% | 100% | 100% | 100% | 0% | 11108960 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 127 | 12361753 | 5256 | 126.144 | 5.256 | 3.3 | 3.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49098212 | 1232 | 234.3988 | 0% | 0% | 100% | 100% | 100% | 40% | 11109228 | 268 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 124 | 120 | 12366901 | 5148 | 123.552 | 5.148 | 3.8 | 3.8 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49099428 | 1216 | 236.2082 | 0% | 0% | 100% | 100% | 100% | 40% | 11109594 | 366 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130547 | 130.547 | 130.547 | [12 empty] | 29884 | 29884 | 228.9137 | [6 empty] | 3834 | 3834 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## AUG 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29628 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12366901 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49099428 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11109594 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 124 | 105 | 12371262 | 4361 | 104.664 | 4.361 | 5.1 | 5.1 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49100389 | 961 | 220.3623 | 0% | 0% | 100% | 100% | 100% | 75% | 11110156 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 103 | 12375527 | 4265 | 102.36 | 4.265 | 6.9 | 6.9 | 3B | 0 | 0 | 1044 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49101356 | 967 | 226.7292 | 0% | 0% | 100% | 100% | 100% | 75% | 11110722 | 566 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 122 | 104 | 12379827 | 4300 | 103.2 | 4.3 | 7.5 | 7.5 | 3B | 0 | 0 | 1045 | 1185 | 1045 | N/A | N/A | N/A | N/A | 49102308 | 952 | 221.3953 | 0% | 0% | 100% | 100% | 100% | 75% | 11111257 | 535 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 117 | 12383754 | 3927 | 94.248 | 3.927 | 8.6 | 8.6 | 3B | 0 | 0 | 1095 | 1185 | 1095 | N/A | N/A | N/A | N/A | 49103352 | 1044 | 265.8518 | 0% | 0% | 100% | 100% | 100% | 75% | 11111735 | 478 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 137 | 131 | 12388227 | 4473 | 107.352 | 4.473 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49104508 | 1156 | 258.4395 | 0% | 0% | 100% | 100% | 100% | 75% | 11112015 | 280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 134 | 12393776 | 5549 | 133.176 | 5.549 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49105764 | 1256 | 226.3471 | 0% | 0% | 100% | 100% | 100% | 0% | 11112015 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 142 | 12399569 | 5793 | 139.032 | 5.793 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49107028 | 1264 | 218.1944 | 0% | 0% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 144 | 12405365 | 5796 | 139.104 | 5.796 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49108295 | 1267 | 218.599 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 141 | 12411466 | 6101 | 146.424 | 6.101 | 8.7 | 8.7 | 3B+1S | 0 | 995 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49109700 | 1405 | 230.2901 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 12417522 | 6056 | 145.344 | 6.056 | 8.3 | 8.3 | 3B+1S | 0 | 1018 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49111080 | 1380 | 227.8732 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 | 1.19
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 12423520 | 5998 | 143.952 | 5.998 | 7.9 | 7.9 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49112436 | 1356 | 226.0754 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 142 | 12429444 | 5924 | 142.176 | 5.924 | 7.4 | 7.4 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49113788 | 1352 | 228.2242 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 140 | 12435299 | 5855 | 140.52 | 5.855 | 7 | 7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49115132 | 1344 | 229.5474 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 142 | 12441020 | 5721 | 137.304 | 5.721 | 6.7 | 6.7 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49116460 | 1328 | 232.1273 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 12446570 | 5550 | 133.2 | 5.55 | 6.6 | 6.6 | 3B+1S | 0 | 995 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49117768 | 1308 | 235.6757 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 12452250 | 5680 | 136.32 | 5.68 | 6.4 | 6.4 | 3B+1S | 0 | 994 | 1187 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49119056 | 1288 | 226.7606 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 12457935 | 5685 | 136.44 | 5.685 | 6.1 | 6.1 | 3B+1S | 0 | 995 | 1186 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49120340 | 1284 | 225.8575 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 12463624 | 5689 | 136.536 | 5.689 | 5.9 | 5.9 | 3B+1S | 0 | 995 | 1186 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49121628 | 1288 | 226.4018 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 139 | 12469300 | 5676 | 136.224 | 5.676 | 5.6 | 5.6 | 3B+1S | 0 | 997 | 1185 | 1185 | 1145 | N/A | N/A | N/A | N/A | 49122916 | 1288 | 226.9204 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 132 | 12474930 | 5630 | 135.12 | 5.63 | 5.2 | 5.2 | 3B+1S | 0 | 995 | 1186 | 1185 | 1145 | N/A | N/A | N/A | N/A | 49124200 | 1284 | 228.0639 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 134 | 12480627 | 5697 | 136.728 | 5.697 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49125528 | 1328 | 233.1051 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 133 | 133 | 12485890 | 5263 | 126.312 | 5.263 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49126760 | 1232 | 234.087 | 0% | 100% | 100% | 100% | 100% | 0% | 11112015 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 121 | 12491231 | 5341 | 128.184 | 5.341 | 4.6 | 4.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49127996 | 1236 | 231.4173 | 0% | 0% | 100% | 100% | 100% | 19% | 11112016 | 1 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 124 | 120 | 12495994 | 4763 | 114.312 | 4.763 | 4.7 | 4.7 | 3B | 0 | 0 | 1095 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49129056 | 1060 | 222.5488 | 0% | 0% | 100% | 100% | 100% | 19% | 11112165 | 149 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129093 | 129.093 | 129.093 | [12 empty] | 29628 | 29628 | 229.509 | [6 empty] | 2571 | 2571 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (19%)

## AUG 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30100 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12495994 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49129056 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11112165 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 139 | 106 | 12500241 | 4247 | 101.928 | 4.247 | 5.3 | 5.3 | 3B | 0 | 0 | 1055 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49129993 | 937 | 220.6263 | 0% | 0% | 100% | 100% | 100% | 75% | 11112682 | 517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 103 | 12504441 | 4200 | 100.8 | 4.2 | 7 | 7 | 3B | 0 | 0 | 1055 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49130948 | 955 | 227.381 | 0% | 0% | 100% | 100% | 100% | 75% | 11113197 | 515 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 105 | 12508721 | 4280 | 102.72 | 4.28 | 8.1 | 8.1 | 3B | 0 | 0 | 1055 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49131988 | 1040 | 242.9907 | 0% | 0% | 100% | 100% | 100% | 75% | 11113727 | 530 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 110 | 12513191 | 4470 | 107.28 | 4.47 | 9.2 | 9.2 | 3B | 0 | 0 | 1115 | 1185 | 1075 | N/A | N/A | N/A | N/A | 49133070 | 1082 | 242.0582 | 0% | 0% | 100% | 100% | 100% | 75% | 11114238 | 511 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 111 | 12517831 | 4640 | 111.36 | 4.64 | 9.5 | 9.5 | 3B | 0 | 0 | 1115 | 1185 | 1075 | N/A | N/A | N/A | N/A | 49134172 | 1102 | 237.5 | 0% | 0% | 100% | 100% | 100% | 75% | 11114347 | 109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 129 | 12523671 | 5840 | 140.16 | 5.84 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49135484 | 1312 | 224.6575 | 0% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 12529695 | 6024 | 144.576 | 6.024 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49136844 | 1360 | 225.7636 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 12535606 | 5911 | 141.864 | 5.911 | 8.8 | 8.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49138192 | 1348 | 228.0494 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 144 | 12541526 | 5920 | 142.08 | 5.92 | 8.4 | 8.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49139536 | 1344 | 227.027 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 142 | 12547512 | 5986 | 143.664 | 5.986 | 8.1 | 8.1 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49140884 | 1348 | 225.1921 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 | 1.27
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 140 | 12553340 | 5828 | 139.872 | 5.828 | 7.7 | 7.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49142220 | 1336 | 229.2382 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 136 | 12559109 | 5769 | 138.456 | 5.769 | 7.4 | 7.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49143556 | 1336 | 231.5826 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 12564832 | 5723 | 137.352 | 5.723 | 7 | 7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49144880 | 1324 | 231.3472 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 134 | 12570504 | 5672 | 136.128 | 5.672 | 6.7 | 6.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49146204 | 1324 | 233.4274 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 138 | 136 | 12575856 | 5352 | 128.448 | 5.352 | 6.5 | 6.5 | 3B+1S | 985 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49147460 | 1256 | 234.6786 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 12581864 | 6008 | 144.192 | 6.008 | 6.3 | 6.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49148836 | 1376 | 229.028 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 12587562 | 5698 | 136.752 | 5.698 | 6.1 | 6.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49150152 | 1316 | 230.9582 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 12593286 | 5724 | 137.376 | 5.724 | 5.8 | 5.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49151476 | 1324 | 231.3068 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 137 | 12599198 | 5912 | 141.888 | 5.912 | 5.3 | 5.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49152844 | 1368 | 231.3938 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 12604955 | 5757 | 138.168 | 5.757 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49154180 | 1336 | 232.0653 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 132 | 12610798 | 5843 | 140.232 | 5.843 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49155556 | 1376 | 235.4955 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 132 | 12616202 | 5404 | 129.696 | 5.404 | 4.5 | 4.5 | 3B+1S | 994 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49156852 | 1296 | 239.8224 | 100% | 0% | 100% | 100% | 100% | 0% | 11114347 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 124 | 129 | 12621312 | 5110 | 122.64 | 5.11 | 4.6 | 4.6 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49158052 | 1200 | 234.8337 | 0% | 0% | 100% | 100% | 100% | 35% | 11114510 | 163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 123 | 120 | 12626122 | 4810 | 115.44 | 4.81 | 5 | 5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49159156 | 1104 | 229.5218 | 0% | 0% | 100% | 100% | 100% | 35% | 11114884 | 374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130128 | 130.128 | 130.128 | [12 empty] | 30100 | 30100 | 231.3107 | [6 empty] | 2719 | 2719 | 1.1417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (35%)

## AUG 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 29792 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12626122 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49159156 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11114884 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 122 | 103 | 12630303 | 4181 | 100.344 | 4.181 | 6 | 6 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49160110 | 954 | 228.1751 | 0% | 0% | 100% | 100% | 100% | 70% | 11115487 | 603 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 123 | 102 | 12634529 | 4226 | 101.424 | 4.226 | 7.5 | 7.5 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49161060 | 950 | 224.7989 | 0% | 0% | 100% | 100% | 100% | 70% | 11116170 | 683 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 118 | 100 | 12638570 | 4041 | 96.984 | 4.041 | 8.7 | 8.7 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49162020 | 960 | 237.565 | 0% | 0% | 100% | 100% | 100% | 70% | 11116768 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 | 114 | 12642775 | 4205 | 100.92 | 4.205 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49163021 | 1001 | 238.0499 | 0% | 0% | 100% | 100% | 100% | 70% | 11117015 | 247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 117 | 12647321 | 4546 | 109.104 | 4.546 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49164116 | 1095 | 240.8711 | 0% | 0% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 122 | 12652371 | 5050 | 121.2 | 5.05 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49165196 | 1080 | 213.8614 | 0% | 0% | 100% | 100% | 100% | 0% | 11117015 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 136 | 12658014 | 5643 | 135.432 | 5.643 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49166388 | 1192 | 211.2352 | 0% | 0% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 12663918 | 5904 | 141.696 | 5.904 | 9.2 | 9.2 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49167724 | 1336 | 226.2873 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 145 | 12669841 | 5923 | 142.152 | 5.923 | 8.8 | 8.8 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49169076 | 1352 | 228.2627 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 12675869 | 6028 | 144.672 | 6.028 | 8.4 | 8.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49170428 | 1352 | 224.2867 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 | 1.23
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 140 | 12681831 | 5962 | 143.088 | 5.962 | 7.9 | 7.9 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49171788 | 1360 | 228.1114 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 142 | 12687750 | 5919 | 142.056 | 5.919 | 7.4 | 7.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49173132 | 1344 | 227.0654 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 142 | 12693586 | 5836 | 140.064 | 5.836 | 7 | 7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49174476 | 1344 | 230.2947 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 135 | 12699608 | 6022 | 144.528 | 6.022 | 6.6 | 6.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49175856 | 1380 | 229.1597 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 143 | 140 | 12705277 | 5669 | 136.056 | 5.669 | 6.5 | 6.5 | 3B+1S | 0 | 975 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49177164 | 1308 | 230.7285 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 12711116 | 5839 | 140.136 | 5.839 | 6.3 | 6.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49178500 | 1336 | 228.8063 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 145 | 12716858 | 5742 | 137.808 | 5.742 | 5.8 | 5.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49179820 | 1320 | 229.8851 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 142 | 12722944 | 6086 | 146.064 | 6.086 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49181218 | 1398 | 229.7075 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 141 | 12728758 | 5814 | 139.536 | 5.814 | 4.8 | 4.8 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49182568 | 1350 | 232.1981 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 12734700 | 5942 | 142.608 | 5.942 | 4.2 | 4.2 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49183930 | 1362 | 229.2158 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 140 | 12740246 | 5546 | 133.104 | 5.546 | 3.6 | 3.6 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49185248 | 1318 | 237.6488 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 132 | 12745846 | 5600 | 134.4 | 5.6 | 3.2 | 3.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49186588 | 1340 | 239.2857 | 0% | 100% | 100% | 100% | 100% | 0% | 11117015 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 120 | 12750950 | 5104 | 122.496 | 5.104 | 3.4 | 3.4 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 49187788 | 1200 | 235.1097 | 0% | 0% | 100% | 100% | 100% | 30% | 11117177 | 162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 122 | 117 | 12755827 | 4877 | 117.048 | 4.877 | 4 | 4 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 49188948 | 1160 | 237.8511 | 0% | 0% | 100% | 100% | 100% | 30% | 11117574 | 397 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129705 | 129.705 | 129.705 | [12 empty] | 29792 | 29792 | 229.6905 | [6 empty] | 2690 | 2690 | 1.17 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (30%)

## AUG 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 30088 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12755827 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49188948 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11117574 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 125 | 101 | 12760046 | 4219 | 101.256 | 4.219 | 5.1 | 5.1 | 3B | 0 | 0 | 1026 | 1185 | 1026 | N/A | N/A | N/A | N/A | 49189880 | 932 | 220.9054 | 0% | 0% | 100% | 100% | 100% | 75% | 11117825 | 251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 103 | 12764274 | 4228 | 101.472 | 4.228 | 6.8 | 6.8 | 3B | 0 | 0 | 1025 | 1185 | 1025 | N/A | N/A | N/A | N/A | 49190820 | 940 | 222.3273 | 0% | 0% | 100% | 100% | 100% | 75% | 11118614 | 789 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 120 | 100 | 12768370 | 4096 | 98.304 | 4.096 | 7.5 | 7.5 | 3B | 0 | 0 | 1026 | 1185 | 1026 | N/A | N/A | N/A | N/A | 49191752 | 932 | 227.5391 | 0% | 0% | 100% | 100% | 100% | 75% | 11119212 | 598 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 111 | 12771782 | 3412 | 81.888 | 3.412 | 8.8 | 8.8 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49192772 | 1020 | 298.9449 | 0% | 0% | 100% | 100% | 100% | 75% | 11119872 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 121 | 12776244 | 4462 | 107.088 | 4.462 | 9.5 | 9.5 | 3B | 0 | 0 | 1125 | 1185 | 1125 | N/A | N/A | N/A | N/A | 49193884 | 1112 | 249.2156 | 0% | 0% | 100% | 100% | 100% | 75% | 11120250 | 378 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 136 | 12781316 | 5072 | 121.728 | 5.072 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49194964 | 1080 | 212.9338 | 0% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 139 | 12787300 | 5984 | 143.616 | 5.984 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49196316 | 1352 | 225.9358 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 144 | 12793320 | 6020 | 144.48 | 6.02 | 8.8 | 8.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49197676 | 1360 | 225.9136 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 12799385 | 6065 | 145.56 | 6.065 | 8.3 | 8.3 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49199040 | 1364 | 224.8969 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 143 | 12805451 | 6066 | 145.584 | 6.066 | 7.7 | 7.7 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49200404 | 1364 | 224.8599 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 | 1.21
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 148 | 12811492 | 6041 | 144.984 | 6.041 | 7.2 | 7.2 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49201788 | 1384 | 229.1011 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 145 | 12817356 | 5864 | 140.736 | 5.864 | 6.5 | 6.5 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49203152 | 1364 | 232.6057 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 12823194 | 5838 | 140.112 | 5.838 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49204514 | 1362 | 233.2991 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 136 | 12829246 | 6052 | 145.248 | 6.052 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49205916 | 1402 | 231.659 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 144 | 12834999 | 5753 | 138.072 | 5.753 | 5 | 5 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49207280 | 1364 | 237.0937 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 12840804 | 5805 | 139.32 | 5.805 | 4.7 | 4.7 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49208636 | 1356 | 233.5917 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 142 | 12846528 | 5724 | 137.376 | 5.724 | 4.3 | 4.3 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49209956 | 1320 | 230.608 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 12852214 | 5686 | 136.464 | 5.686 | 3.8 | 3.8 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49211272 | 1316 | 231.4457 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 12858074 | 5860 | 140.64 | 5.86 | 3.4 | 3.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49212620 | 1348 | 230.0341 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 168 | 12863866 | 5792 | 139.008 | 5.792 | 3 | 3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49213964 | 1344 | 232.0442 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 141 | 12869662 | 5796 | 139.104 | 5.796 | 2.6 | 2.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49215324 | 1360 | 234.6446 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 138 | 131 | 12875206 | 5544 | 133.056 | 5.544 | 2.4 | 2.4 | 3B+1S | 1045 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49216656 | 1332 | 240.2597 | 100% | 0% | 100% | 100% | 100% | 0% | 11120250 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 126 | 12880415 | 5209 | 125.016 | 5.209 | 2.9 | 2.9 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49217892 | 1236 | 237.2816 | 0% | 0% | 100% | 100% | 100% | 30% | 11120416 | 166 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 100 | 12884954 | 4539 | 108.936 | 4.539 | 3.7 | 3.7 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49219036 | 1144 | 252.0379 | 0% | 0% | 100% | 100% | 100% | 30% | 11120693 | 277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129127 | 129.127 | 129.127 | [12 empty] | 30088 | 30088 | 233.0109 | [6 empty] | 3119 | 3119 | 1.1483 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (30%)

## AUG 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27752 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 12884954 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49219036 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11120693 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 125 | 98 | 12888585 | 3631 | 87.144 | 3.631 | 5 | 5 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49219964 | 928 | 255.577 | 0% | 0% | 100% | 100% | 100% | 70% | 11121755 | 1062 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 101 | 12892495 | 3910 | 93.84 | 3.91 | 6.7 | 6.7 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49220936 | 972 | 248.5934 | 0% | 0% | 100% | 100% | 100% | 70% | 11122774 | 1019 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 126 | 100 | 12896463 | 3968 | 95.232 | 3.968 | 8.3 | 8.3 | 3B | 0 | 0 | 1037 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49221852 | 916 | 230.8468 | 0% | 0% | 100% | 100% | 100% | 70% | 11123918 | 1144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 104 | 12900733 | 4270 | 102.48 | 4.27 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49222904 | 1052 | 246.37 | 0% | 0% | 100% | 100% | 100% | 70% | 11124966 | 1048 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 120 | 12905420 | 4687 | 112.488 | 4.687 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49223976 | 1072 | 228.7177 | 0% | 0% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 133 | 12910935 | 5515 | 132.36 | 5.515 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49225224 | 1248 | 226.2919 | 0% | 0% | 100% | 100% | 100% | 0% | 11124966 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 12916840 | 5905 | 141.72 | 5.905 | 9.1 | 9.1 | 3B+1S | 0 | 996 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49226568 | 1344 | 227.6037 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 147 | 12922816 | 5976 | 143.424 | 5.976 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49227928 | 1360 | 227.577 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 12928904 | 6088 | 146.112 | 6.088 | 7.8 | 7.8 | 3B+1S | 0 | 1068 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49229308 | 1380 | 226.6754 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 12934950 | 6046 | 145.104 | 6.046 | 7.2 | 7.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49230692 | 1384 | 228.9117 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 | 1.21
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 143 | 12941009 | 6059 | 145.416 | 6.059 | 6.6 | 6.6 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49232068 | 1376 | 227.1002 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 12946960 | 5951 | 142.824 | 5.951 | 6.1 | 6.1 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49233420 | 1352 | 227.1887 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 12952756 | 5796 | 139.104 | 5.796 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49234776 | 1356 | 233.9545 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 12958428 | 5672 | 136.128 | 5.672 | 5.1 | 5.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49236100 | 1324 | 233.4274 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 12964116 | 5688 | 136.512 | 5.688 | 4.8 | 4.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49237420 | 1320 | 232.0675 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 143 | 12970034 | 5918 | 142.032 | 5.918 | 4.5 | 4.5 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49238780 | 1360 | 229.8074 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 12976066 | 6032 | 144.768 | 6.032 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49240164 | 1384 | 229.443 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 137 | 12981734 | 5668 | 136.032 | 5.668 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49241460 | 1296 | 228.6521 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 135 | 12987466 | 5732 | 137.568 | 5.732 | 3.7 | 3.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49242792 | 1332 | 232.3796 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 | 132 | 12992992 | 5526 | 132.624 | 5.526 | 3.6 | 3.6 | 3B+1S | 0 | 984 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49244096 | 1304 | 235.9754 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 129 | 12998608 | 5616 | 134.784 | 5.616 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49245428 | 1332 | 237.1795 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 130 | 13004408 | 5800 | 139.2 | 5.8 | 3.4 | 3.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49246788 | 1360 | 234.4828 | 0% | 100% | 100% | 100% | 100% | 0% | 11124966 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 122 | 13008526 | 4118 | 98.832 | 4.118 | 3.6 | 3.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49246788 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 30% | 11125069 | 103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 126 | 119 | 13013647 | 5121 | 122.904 | 5.121 | 3.9 | 3.9 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49246788 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 30% | 11125299 | 230 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128693 | 128.693 | 128.693 | [12 empty] | 27752 | 27752 | 215.645 | [6 empty] | 4606 | 4606 | 1.1333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective JUNE 6, 2016 from 8pm to 12mn the PSI is 83psi and the change operation will be waiting the advised of SPM.
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (30%)
POWER INTERRUPTION AT 10:00PM
ALL PUMP STOPPED DUE TO INTERRUPTION @ 10:00PM / GENSET I OPERATED
BP2 POWER RESUME @ 10:02PM
BP3 POWER RESUME @ 10:04PM
BP1 POWER RESUME @ 10:06PM

## AUG 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26124 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13013647 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49246788 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11125299 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 110 | 13018322 | 4675 | 112.2 | 4.675 | 4.5 | 4.5 | 3B | 0 | 0 | 1016 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49246788 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 60% | 11125830 | 531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 106 | 13022750 | 4428 | 106.272 | 4.428 | 5.5 | 5.5 | 3B | 0 | 0 | 1035 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49247532 | 744 | 168.0217 | 0% | 0% | 100% | 100% | 100% | 60% | 11126792 | 962 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 119 | 107 | 13027249 | 4499 | 107.976 | 4.499 | 6.5 | 6.5 | 3B | 0 | 0 | 1035 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49248564 | 1032 | 229.3843 | 0% | 0% | 100% | 100% | 100% | 60% | 11127721 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 108 | 13031942 | 4693 | 112.632 | 4.693 | 7 | 7 | 3B | 0 | 0 | 1106 | 1185 | 1136 | N/A | N/A | N/A | N/A | 49249644 | 1080 | 230.13 | 0% | 0% | 100% | 100% | 100% | 60% | 11128255 | 534 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 142 | 105 | 13036033 | 4091 | 98.184 | 4.091 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49250852 | 1208 | 295.2823 | 0% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 122 | 13041086 | 5053 | 121.272 | 5.053 | 9.5 | 9.5 | 3B | 0 | 0 | 1036 | 1185 | 1046 | N/A | N/A | N/A | N/A | 49251904 | 1052 | 208.1932 | 0% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 13046559 | 5473 | 131.352 | 5.473 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49253024 | 1120 | 204.641 | 0% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 137 | 13052398 | 5839 | 140.136 | 5.839 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49254276 | 1252 | 214.4203 | 0% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 13058408 | 6010 | 144.24 | 6.01 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49255600 | 1324 | 220.2995 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 13064453 | 6045 | 145.08 | 6.045 | 8.9 | 8.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49256956 | 1356 | 224.3176 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 | 1.2
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 143 | 13070557 | 6104 | 146.496 | 6.104 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49258316 | 1360 | 222.8047 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 13076622 | 6065 | 145.56 | 6.065 | 7.7 | 7.7 | 3B+1S | 1066 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49259684 | 1368 | 225.5565 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 13082615 | 5993 | 143.832 | 5.993 | 7 | 7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49261060 | 1376 | 229.6012 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 145 | 13088546 | 5931 | 142.344 | 5.931 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49262428 | 1368 | 230.6525 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 13093954 | 5408 | 129.792 | 5.408 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49263680 | 1252 | 231.5089 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 138 | 13099677 | 5723 | 137.352 | 5.723 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49265004 | 1324 | 231.3472 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 13105458 | 5781 | 138.744 | 5.781 | 5.2 | 5.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49266340 | 1336 | 231.1019 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 139 | 13111222 | 5764 | 138.336 | 5.764 | 4.7 | 4.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49267676 | 1336 | 231.7835 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 140 | 13116961 | 5739 | 137.736 | 5.739 | 4.3 | 4.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49269020 | 1344 | 234.1871 | 100% | 0% | 100% | 100% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 62 | 43.662 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 18 | A ONG | 16.6 | 96 | 102 | 13122080 | 5119 | 122.856 | 5.119 | 3.6 | 3.6 | 2B+1S | 1007 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 49269980 | 960 | 187.5366 | 100% | 0% | 100% | 0% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 62 | 43.662 | Automatic - Pressure Setting | 40.1408 | 41.5493 | 45.7746 | 18 | A ONG | 16.1 | 99 | 101 | 13126755 | 4675 | 112.2 | 4.675 | 2.9 | 2.9 | 2B+1S | 997 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 49270756 | 776 | 165.9893 | 100% | 0% | 100% | 0% | 100% | 0% | 11128255 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 61 | 42.9577 | Automatic - Pressure Setting | 39.4366 | 40.8451 | 45.0704 | 14 | A ONG | 12.6 | 124 | 101 | 13131548 | 4793 | 115.032 | 4.793 | 2.7 | 2.7 | 2B+1S | 977 | 0 | 1057 | 0 | 1056 | N/A | N/A | N/A | N/A | 49271584 | 828 | 172.7519 | 100% | 0% | 100% | 0% | 100% | 0% | 11128255 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 60 | 42.2535 | Automatic - Pressure Setting | 37.3239 | 38.7324 | 42.9577 | 14 | A ONG | 11.9 | 130 | 100 | 13135571 | 4023 | 96.552 | 4.023 | 3.9 | 3.9 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 49272244 | 660 | 164.0567 | 0% | 0% | 100% | 0% | 100% | 40% | 11129087 | 832 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 63 | 44.3662 | Automatic - Pressure Setting | 39.4366 | 40.8451 | 45.0704 | 14 | A ONG | 11.5 | 136 | 100 | 13139767 | 4196 | 100.704 | 4.196 | 4.7 | 4.7 | 2B | 0 | 0 | 1057 | 0 | 1057 | N/A | N/A | N/A | N/A | 49272912 | 668 | 159.1992 | 0% | 0% | 100% | 0% | 100% | 40% | 11130063 | 976 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126120 | 126.12 | 126.12 | [12 empty] | 26124 | 26124 | 207.1361 | [6 empty] | 4764 | 4764 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective June 28.2016,target pressure for 12MN-3AM will be changed to 75 psi only. This was requested by PQE BA due to good pressure survey taken last night.
XCV1- INCREASE OPENING @ 12:01 AM (60%)
ALL PUMP STOPPED DUE TO RESUME POWER TRANSFER TO MERALCO @ 1:10AM / GENSET I OPERATED
BP2 POWER RESUME @ 1:12AM
BP3 POWER RESUME @ 1:14AM
BP1 POWER RESUME @ 1:16AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
Change operation as per advise of sir Alvin Cruz effective AUGUST 13, 2016 from 7pm to 12mn TARGET MLD IS 100, (change operation will be waiting the advised of SPM.)
BP2- STOPPED @ 7:01 PM DUE TO CHANGE OPERATION @ 7PM TARGET MLD IS 100
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)

## AUG 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22660 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13139767 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49272912 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11130063 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 45 | 31.6901 | Automatic - Pressure Setting | 26.7606 | 28.169 | 32.3944 | 14 | A.ONG | 11.4 | 96 | 70 | 13142960 | 3193 | 76.632 | 3.193 | 6.1 | 6.1 | 1B | 0 | 0 | 1007 | 0 | 0 | N/A | N/A | N/A | N/A | 49273316 | 404 | 126.5268 | 0% | 0% | 100% | 0% | 0% | 45% | 11131362 | 1299 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 12 | 8.4507 | 45 | 31.6901 | Automatic - Pressure Setting | 26.7606 | 28.169 | 32.3944 | 14 | A.ONG | 11.2 | 100 | 70 | 13146154 | 3194 | 76.656 | 3.194 | 7.8 | 7.8 | 1B | 0 | 0 | 1007 | 0 | 0 | N/A | N/A | N/A | N/A | 49273640 | 324 | 101.4402 | 0% | 0% | 100% | 0% | 0% | 45% | 11132631 | 1269 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 14 | 9.8592 | 46 | 32.3944 | Automatic - Pressure Setting | 27.4648 | 28.8732 | 33.0986 | 14 | A.ONG | 11.2 | 100 | 70 | 13148721 | 2567 | 61.608 | 2.567 | 8.3 | 8.3 | 1B | 0 | 0 | 1007 | 0 | 0 | N/A | N/A | N/A | N/A | 49273966 | 326 | 126.9965 | 0% | 0% | 100% | 0% | 0% | 45% | 11134022 | 1391 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 18 | 12.6761 | 47 | 33.0986 | Automatic - Pressure Setting | 28.169 | 29.5775 | 33.8028 | 14 | A.ONG | 12.8 | 69 | 70 | 13151924 | 3203 | 76.872 | 3.203 | 9.5 | 9.5 | 1B | 0 | 0 | 1007 | 0 | 0 | N/A | N/A | N/A | N/A | 49274324 | 358 | 111.7702 | 0% | 0% | 100% | 0% | 0% | 45% | 11134864 | 842 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 117 | 13156148 | 4224 | 101.376 | 4.224 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1095 | N/A | N/A | N/A | N/A | 49275156 | 832 | 196.9697 | 0% | 0% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 124 | 121 | 13161254 | 5106 | 122.544 | 5.106 | 9.5 | 9.5 | 3B | 0 | 0 | 1095 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49276220 | 1064 | 208.3823 | 0% | 0% | 100% | 100% | 100% | 0% | 11134864 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 136 | 13166696 | 5442 | 130.608 | 5.442 | 9.5 | 9.5 | 3B | 0 | 0 | 1156 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49277368 | 1148 | 210.9519 | 0% | 0% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 140 | 13172752 | 6056 | 145.344 | 6.056 | 9.3 | 9.3 | 3B+1S | 0 | 1037 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49278668 | 1300 | 214.6631 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 67 | 47.1831 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 48.6031 | 19 | A ONG | 18.4 | 112 | 153 | 13179605 | 6853 | 164.472 | 6.853 | 8.4 | 8.4 | 3B+1S | 0 | 1118 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49280048 | 1380 | 201.3717 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 67 | 47.1831 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 48.6031 | 19 | A ONG | 17.7 | 110 | 155 | 13185723 | 6118 | 146.832 | 6.118 | 7 | 7 | 3B+1S | 0 | 1078 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49281368 | 1320 | 215.7568 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 | 1.23
58:00 | 11:00 | 4 | 2.8169 | 67 | 47.1831 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 48.6031 | 19 | A ONG | 17.7 | 108 | 150 | 13191919 | 6196 | 148.704 | 6.196 | 6.3 | 6.3 | 3B+1S | 0 | 1058 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49282728 | 1360 | 219.4964 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 74 | 52.1127 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | 111 | 156 | 13197892 | 5973 | 143.352 | 5.973 | 5.5 | 5.5 | 3B+1S | 0 | 1038 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49284036 | 1308 | 218.9854 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 19 | A ONG | 17.5 | 97 | 112 | 13203370 | 5478 | 131.472 | 5.478 | 4.9 | 4.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 996 | N/A | N/A | N/A | N/A | 49285288 | 1252 | 228.5506 | 0% | 100% | 100% | 100% | 100% | 0% | 11134864 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 17.3 | 99 | 96 | 13208672 | 5302 | 127.248 | 5.302 | 4.1 | 4.1 | 2B+1S | 0 | 1006 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 49286416 | 1128 | 212.7499 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.9 | 99 | 92 | 13213266 | 4594 | 110.256 | 4.594 | 3.4 | 3.4 | 2B+1S | 0 | 1006 | 1186 | 1185 | 0 | N/A | N/A | N/A | N/A | 49287332 | 916 | 199.3905 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A ONG | 16.7 | 98 | 94 | 13217706 | 4440 | 106.56 | 4.44 | 2.9 | 2.9 | 2B+1S | 0 | 986 | 1156 | 1185 | 0 | N/A | N/A | N/A | N/A | 49288264 | 932 | 209.9099 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.49 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 3 | 2.1127 | 69 | 48.5915 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 18 | A ONG | 16.7 | 101 | 92 | 13222788 | 5082 | 121.968 | 5.082 | 2.5 | 2.5 | 2B+1S | 0 | 986 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 49289284 | 1020 | 200.7084 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 3 | 2.1127 | 70 | 49.2958 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A ONG | 16.7 | 101 | 91 | 13226972 | 4184 | 100.416 | 4.184 | 2.2 | 2.2 | 2B+1S | 0 | 985 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 49290156 | 872 | 208.413 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 3 | 2.1127 | 71 | 50 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.6 | 102 | 90 | 13231536 | 4564 | 109.536 | 4.564 | 1.9 | 1.9 | 2B+1S | 0 | 985 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 49291100 | 944 | 206.8361 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.41 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 3 | 2.1127 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 103 | 92 | 13235848 | 4312 | 103.488 | 4.312 | 1.8 | 1.8 | 2B+1S | 0 | 985 | 1156 | 1185 | 0 | N/A | N/A | N/A | N/A | 49292004 | 904 | 209.6475 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 3 | 2.1127 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 106 | 94 | 13240256 | 4408 | 105.792 | 4.408 | 1.7 | 1.7 | 2B+1S | 0 | 974 | 1156 | 1185 | 0 | N/A | N/A | N/A | N/A | 49292924 | 920 | 208.7114 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 3 | 2.1127 | 70 | 49.2958 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 12.6 | 122 | 93 | 13245273 | 5017 | 120.408 | 5.017 | 1.5 | 1.5 | 2B+1S | 0 | 975 | 1157 | 1185 | 0 | N/A | N/A | N/A | N/A | 49293900 | 976 | 194.5386 | 0% | 100% | 100% | 100% | 0% | 0% | 11134864 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 126 | 92 | 13249999 | 4726 | 113.424 | 4.726 | 1.9 | 1.9 | 2B | 0 | 0 | 1097 | 1185 | 0 | N/A | N/A | N/A | N/A | 49294744 | 844 | 178.5865 | 0% | 0% | 100% | 100% | 0% | 25% | 11135404 | 540 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 72 | 50.7042 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 116 | 92 | 13254528 | 4529 | 108.696 | 4.529 | 2.5 | 2.5 | 2B | 0 | 0 | 1096 | 1185 | 0 | N/A | N/A | N/A | N/A | 49295572 | 828 | 182.8218 | 0% | 0% | 100% | 100% | 0% | 25% | 11136199 | 795 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 114761 | 114.761 | 114.761 | [12 empty] | 22660 | 22660 | 197.4538 | [6 empty] | 6136 | 6136 | 1.2414 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise of sir Alvin Cruz effective AUGUST 13, 2016 from 12mn to 4am TARGET MLD IS 70, (change operation will be waiting the advised of SPM.)
BP3- STOPPED @ 12:01 AM DUE TO CHANGE OPERATION @ 12AM-4AM TARGET MLD IS 70
XCV2- INCREASE OPENING @ 12:02 AM (45%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
BP2- STARTED @ 4:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP3- STARTED @ 4:02 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 83 PSI DUE TO LSP STARTED @ 9:00 AM
Change operation as per advise of sir Alvin Cruz effective AUGUST 14, 2016 from 1PM to 12AM TARGET MLD IS 90, (change operation will be waiting the advised of SPM.)
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 81 PSI DUE TO LSP STARTED @ 1:00 PM TO 12AM TARGET MLD IS 90
BP3- STOPPED @ 1:00 PM DUE TO CHANGE OPERATION @ 1PM-12AM TARGET MLD IS 90
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 78 PSI DUE TO LSP STARTED @ 1:00 PM TO 12AM TARGET MLD IS 90
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 76 PSI DUE TO LSP STARTED @ 1:00 PM TO 12AM TARGET MLD IS 90
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 83 PSI DUE TO LSP STARTED @ 1:00 PM TO 12AM TARGET MLD IS 90
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (25%)

## AUG 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22904 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13254528 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49295572 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11136199 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 43 | 30.2817 | Automatic - Pressure Setting | 25.3521 | 26.7606 | 30.9859 | 14 | A.ONG | 11.4 | 139 | 52 | 13257124 | 2596 | 62.304 | 2.596 | 5.6 | 5.6 | 1B | 0 | 0 | 996 | 0 | 0 | N/A | N/A | N/A | N/A | 49295916 | 344 | 132.5116 | 0% | 0% | 100% | 0% | 0% | 50% | 11138195 | 1996 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 44 | 30.9859 | Automatic - Pressure Setting | 26.0563 | 27.4648 | 31.6901 | 14 | A.ONG | 11.2 | 137 | 53 | 13259844 | 2720 | 65.28 | 2.72 | 8.4 | 8.4 | 1B | 0 | 0 | 997 | 0 | 0 | N/A | N/A | N/A | N/A | 49296240 | 324 | 119.1176 | 0% | 0% | 100% | 0% | 0% | 50% | 11141000 | 2805 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 14 | 9.8592 | 46 | 32.3944 | Automatic - Pressure Setting | 27.4648 | 28.8732 | 33.0986 | 14 | A.ONG | 11.2 | 74 | 54 | 13262823 | 2979 | 71.496 | 2.979 | 9.5 | 9.5 | 1B | 0 | 0 | 997 | 0 | 0 | N/A | N/A | N/A | N/A | 49296556 | 316 | 106.0759 | 0% | 0% | 100% | 0% | 0% | 50% | 11143034 | 2034 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 21 | 14.7887 | 47 | 33.0986 | Automatic - Pressure Setting | 28.169 | 29.5775 | 33.8028 | 14 | A.ONG | 12.8 | 67 | 54 | 13265902 | 3079 | 73.896 | 3.079 | 9.5 | 9.5 | 1B | 0 | 0 | 997 | 0 | 0 | N/A | N/A | N/A | N/A | 49296916 | 360 | 116.9211 | 0% | 0% | 100% | 0% | 0% | 0% | 11143034 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 117 | 13270331 | 4429 | 106.296 | 4.429 | 9.5 | 9.5 | 3B | 0 | 0 | 1176 | 1185 | 1176 | N/A | N/A | N/A | N/A | 49297792 | 876 | 197.7873 | 0% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 121 | 13275665 | 5334 | 128.016 | 5.334 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49298996 | 1204 | 225.7218 | 0% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 74 | 52.1127 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 16.7 | 117 | 157 | 13281820 | 6155 | 147.72 | 6.155 | 9 | 9 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49300340 | 1344 | 218.3591 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.22 | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 71 | 50 | Automatic - Pressure Setting | 48.5915 | 50 | 51.42 | 19 | A ONG | 17.3 | 116 | 160 | 13288725 | 6905 | 165.72 | 6.905 | 8.2 | 8.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49301668 | 1328 | 192.3244 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.15 | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 70 | 49.2958 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 50.7158 | 19 | A ONG | 18.4 | 115 | 155 | 13295156 | 6431 | 154.344 | 6.431 | 7.3 | 7.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49302988 | 1320 | 205.2558 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.23 | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 3 | 2.1127 | 70 | 49.2958 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 50.7158 | 19 | A ONG | 17.7 | 115 | 133 | 13301482 | 6326 | 151.824 | 6.326 | 6.5 | 6.5 | 3B+1S | 1014 | 0 | 1185 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49304292 | 1304 | 206.1334 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.26
58:00 | 11:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 17.7 | 115 | 150 | 13307594 | 6112 | 146.688 | 6.112 | 5.8 | 5.8 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49305580 | 1288 | 210.733 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.17 | Normal operation schedule
59:00 | 12:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 49.3073 | 19 | A ONG | 17.3 | 119 | 160 | 13313617 | 6023 | 144.552 | 6.023 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49306892 | 1312 | 217.8316 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.2 | Normal operation schedule | UNITS
60:00 | 13:00 | 3 | 2.1127 | 68 | 47.8873 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 19 | A ONG | 17.5 | 120 | 162 | 13319753 | 6136 | 147.264 | 6.136 | 4.5 | 4.5 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49308196 | 1304 | 212.5163 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 3 | 2.1127 | 62 | 43.662 | Automatic - Pressure Setting | 42.2535 | 43.662 | 47.8873 | 18 | A ONG | 17.3 | 110 | 102 | 13326064 | 6311 | 151.464 | 6.311 | 3.8 | 3.8 | 3B+1S | 987 | 0 | 1035 | 1185 | 1055 | N/A | N/A | N/A | N/A | 49309332 | 1136 | 180.0032 | 100% | 0% | 100% | 100% | 100% | 0% | 11143034 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 3 | 2.1127 | 65 | 45.7746 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A ONG | 16.9 | 116 | 98 | 13332412 | 6348 | 152.352 | 6.348 | 3.1 | 3.1 | 2B+1S | 977 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49310264 | 932 | 146.8179 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 3 | 2.1127 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.7 | 122 | 94 | 13338882 | 6470 | 155.28 | 6.47 | 2.6 | 2.6 | 2B+1S | 966 | 0 | 0 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49311264 | 1000 | 154.5595 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.7 | 123 | 96 | 13345172 | 6290 | 150.96 | 6.29 | 2.3 | 2.3 | 2B+1S | 966 | 0 | 0 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49312144 | 880 | 139.9046 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.43 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 70 | 49.2958 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A ONG | 16.7 | 132 | 92 | 13350822 | 5650 | 135.6 | 5.65 | 2.1 | 2.1 | 2B+1S | 965 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49313100 | 956 | 169.2035 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 8 | 5.6338 | 70 | 49.2958 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A ONG | 16.6 | 134 | 95 | 13356262 | 5440 | 130.56 | 5.44 | 2 | 2 | 2B+1S | 965 | 0 | 0 | 1185 | 1106 | N/A | N/A | N/A | N/A | 49314004 | 904 | 166.1765 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 10 | 7.0423 | 70 | 49.2958 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A ONG | 16.6 | 136 | 92 | 13361884 | 5622 | 134.928 | 5.622 | 1.9 | 1.9 | 2B+1S | 964 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49314948 | 944 | 167.9118 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 13 | 9.1549 | 72 | 50.7042 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.1 | 135 | 94 | 13367768 | 5884 | 141.216 | 5.884 | 1.8 | 1.8 | 2B+1S | 984 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49315940 | 992 | 168.5928 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 16 | 11.2676 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 12.6 | 135 | 93 | 13372779 | 5011 | 120.264 | 5.011 | 1.8 | 1.8 | 2B+1S | 994 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49316752 | 812 | 162.0435 | 100% | 0% | 0% | 100% | 100% | 0% | 11143034 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 17 | 11.9718 | 71 | 50 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 177 | 94 | 13377725 | 4946 | 118.704 | 4.946 | 3.5 | 3.5 | 2B | 0 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49317612 | 860 | 173.8779 | 0% | 0% | 0% | 100% | 100% | 40% | 11145002 | 1968 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 17 | 11.9718 | 72 | 50.7042 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 176 | 94 | 13382824 | 5099 | 122.376 | 5.099 | 5.8 | 5.8 | 2B | 0 | 0 | 0 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49318476 | 864 | 169.445 | 0% | 0% | 0% | 100% | 100% | 40% | 11147095 | 2093 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 128296 | 128.296 | 128.296 | [12 empty] | 22904 | 22904 | 178.5247 | [6 empty] | 10896 | 10896 | 1.1883 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise of sir Alvin Cruz effective AUGUST 14, 2016 from 12mn to 4am TARGET MLD IS 50, (change operation will be waiting the advised of SPM.)
BP2- STOPPED @ 12:01 AM DUE TO CHANGE OPERATION @ 12AM-4AM TARGET MLD IS 50
XCV2- INCREASE OPENING @ 12:02 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
BP2- STARTED @ 4:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
BP3- STARTED @ 4:02 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 83 PSI DUE TO LSP
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Change operation as per advise of sir Alvin Cruz effective AUGUST 14, 2016 from 1PM to 12AM TARGET MLD IS 90, (change operation will be waiting the advised of SPM.)
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 81 PSI DUE TO LSP STARTED @ 1:00 PM TO 12AM TARGET MLD IS 90
POWER FLUCTUATION AT 1:32PM
ALL PUMP STOPPED DUE TO POWER FLUCTUATION @ 1:32PM
BP2 POWER RESUME @ 1:34PM
BP3 POWER RESUME @ 1:36PM
BP1 POWER RESUME @ 1:38PM
SP1 POWER RESUME @ 1:40PM
BP1- STOPPED @ 2:00 PM DUE TO CHANGE OPERATION @ 1PM-12AM TARGET MLD IS 90
Change operation as per advise of sir Alvin Cruz effective AUGUST 15, 2016 from 5PM to 12AM TARGET MLD IS 90 / from 12AM to 4AM TARGET MLD IS 50 , (change operation will be waiting the advised of SPM.)
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 78 PSI DUE TO LSP STARTED @ 5:00 PM TO 12AM TARGET MLD IS 90
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 76 PSI DUE TO LSP STARTED @ 5:00 PM TO 12AM TARGET MLD IS 90
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
UNABLED TO MEET TARGET DISCHARGE PRESSURE OF 83 PSI DUE TO LSP STARTED @ 5:00 PM TO 12AM TARGET MLD IS 90
SP1 - STOPPED @ 10:00 PM DUE TO CHANGE OF OPERATION
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2-OPENED @ 10:01 PM (40%)

## AUG 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 21764 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13382824 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49318476 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11147095 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 16 | 11.2676 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 147 | 71 | 13385793 | 2969 | 71.256 | 2.969 | 8.8 | 8.8 | 1B | 0 | 0 | 0 | 0 | 1188 | N/A | N/A | N/A | N/A | 49318888 | 412 | 138.7673 | 0% | 0% | 0% | 0% | 100% | 60% | 11150216 | 3121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 110 | 13390333 | 4540 | 108.96 | 4.54 | 9.5 | 9.5 | 2B | 0 | 0 | 1135 | 0 | 1125 | N/A | N/A | N/A | N/A | 49319585 | 697 | 153.5242 | 0% | 0% | 100% | 0% | 100% | 60% | 11150546 | 330 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 107 | 13395143 | 4810 | 115.44 | 4.81 | 9.5 | 9.5 | 2B | 0 | 0 | 1135 | 0 | 1125 | N/A | N/A | N/A | N/A | 49320345 | 760 | 158.0042 | 0% | 0% | 100% | 0% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 | 117 | 13400268 | 5125 | 123 | 5.125 | 9.5 | 9.5 | 3B | 0 | 0 | 1135 | 1185 | 1125 | N/A | N/A | N/A | N/A | 49321624 | 1279 | 249.561 | 0% | 0% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 125 | 13405212 | 4944 | 118.656 | 4.944 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49322752 | 1128 | 228.1553 | 0% | 0% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 132 | 13410725 | 5513 | 132.312 | 5.513 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49324012 | 1260 | 228.5507 | 0% | 0% | 100% | 100% | 100% | 0% | 11150546 | 0 | 1.8 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 13416768 | 6043 | 145.032 | 6.043 | 9.1 | 9.1 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49325368 | 1356 | 224.3919 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 139 | 13423257 | 6489 | 155.736 | 6.489 | 8.4 | 8.4 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49326848 | 1480 | 228.0783 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 146 | 13429505 | 6248 | 149.952 | 6.248 | 7.7 | 7.7 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49328228 | 1380 | 220.8707 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 13435597 | 6092 | 146.208 | 6.092 | 7 | 7 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49329612 | 1384 | 227.1832 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 | 1.23
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 141 | 13441739 | 6142 | 147.408 | 6.142 | 6.3 | 6.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49330996 | 1384 | 225.3338 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 139 | 13447737 | 5998 | 143.952 | 5.998 | 5.7 | 5.7 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49332364 | 1368 | 228.076 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 13453664 | 5927 | 142.248 | 5.927 | 5.1 | 5.1 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49333732 | 1368 | 230.8082 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 13459738 | 6074 | 145.776 | 6.074 | 4.6 | 4.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49335128 | 1396 | 229.8321 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 13465378 | 5640 | 135.36 | 5.64 | 4.2 | 4.2 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49336428 | 1300 | 230.4965 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 13471416 | 6038 | 144.912 | 6.038 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49337804 | 1376 | 227.89 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 13476986 | 5570 | 133.68 | 5.57 | 3.4 | 3.4 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49339108 | 1304 | 234.1113 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 122 | 121 | 13481918 | 4932 | 118.368 | 4.932 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1185 | N/A | N/A | N/A | N/A | 49340240 | 1132 | 229.5215 | 0% | 100% | 100% | 100% | 100% | 0% | 11150546 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 0 | 0 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 0 | 0 | 13481918 | 0 | 0 | 0 | 3.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 0 | 0 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 0 | 0 | 13481918 | 0 | 0 | 0 | 3.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 0 | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 0 | 0 | 13481918 | 0 | 0 | 0 | 3.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11150546 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 0 | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 0 | 0 | 13481918 | 0 | 0 | 0 | 3.2 | 3.2 |  | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11150546 | 0 | 0 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 0 | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 0 | 0 | 13481918 | 0 | 0 | 0 | 4.8 | 4.8 |  | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11151100 | 554 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 0 | 0 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 0 | 0 | 13481918 | 0 | 0 | 0 | 5 | 5 |  | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 0% | 11152124 | 1024 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL |  |  |  |  | 13481918 | 99094 | 99.094 | 99.094 | [12 empty] | 21764 | 21764 | 219.6298 | [6 empty] | 5029 | 5029 | 1.0933 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
Change operation as per advise of sir Alvin Cruz effective AUGUST 14, 2016 from 12mn to 4am TARGET MLD IS 50, (change operation will be waiting the advised of SPM.)
BP2- STOPPED @ 12:01 AM DUE TO CHANGE OPERATION @ 12AM-4AM TARGET MLD IS 50
XCV2- INCREASE OPENING @ 12:02 AM (60%)
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
BP1- STARTED @ 1:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
XCV2- CLOSED @ 1:13 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
BP2- STARTED @ 4:02 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
ALL PUMP STOOPED AT 6PM DUE TO CONDUIT FOR PLC TO UPGRADING THE ATS FOR SYNCHRONIZING THE COTROL PANEL AND REPAIR THE LEAK AT 900MM AND REPLACEMENT THE GASKET / INSTALLATION OF NEW NUTS / BOLTS
MERALCO SHUT DOWN AT 7:50PM DUE TO CONDUIT FOR PLC TO ATS
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1-OPENED @ 10:01 PM (40%)

## AUG 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13481918 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49340240 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11152124 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 0 | 0 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 0 | 0 | 13481918 | 0 | 0 | 0 | 5.3 | 5.3 | 3B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 60% | 11152884 | 760 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 0 | 0 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 0 | 0 | 13481918 | 0 | 0 | 0 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 49340240 | 0 | #DIV/0! | 0% | 0% | 0% | 0% | 0% | 60% | 11153400 | 516 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 12 | 8.4507 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 130 | 13490647 | 8729 | 209.496 | 8.729 | 7.6 | 7.6 | 3B | 0 | 0 | 116 | 1185 | 1126 | N/A | N/A | N/A | N/A | 49341009 | 769 | 88.0971 | 0% | 0% | 100% | 100% | 100% | 60% | 11154400 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 113 | 129 | 13495884 | 5237 | 125.688 | 5.237 | 8.5 | 8.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 49341941 | 932 | 177.9645 | 0% | 0% | 100% | 100% | 100% | 60% | 11155210 | 810 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 135 | 129 | 13500033 | 4149 | 99.576 | 4.149 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49342992 | 1051 | 253.3141 | 0% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 133 | 13505566 | 5533 | 132.792 | 5.533 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49344149 | 1157 | 209.109 | 0% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 138 | 13511466 | 5900 | 141.6 | 5.9 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49345297 | 1148 | 194.5763 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 13517456 | 5990 | 143.76 | 5.99 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49346498 | 1201 | 200.5008 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 146 | 13523433 | 5977 | 143.448 | 5.977 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49347695 | 1197 | 200.2677 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 13529615 | 6182 | 148.368 | 6.182 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49348912 | 1217 | 196.8619 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 | 1.23
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 139 | 13535547 | 5932 | 142.368 | 5.932 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49350103 | 1191 | 200.7755 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 13541522 | 5975 | 143.4 | 5.975 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49351300 | 1197 | 200.3347 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 133 | 13547572 | 6050 | 145.2 | 6.05 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49352555 | 1255 | 207.438 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 136 | 13553478 | 5906 | 141.744 | 5.906 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49353729 | 1174 | 198.7809 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 130 | 13558882 | 5404 | 129.696 | 5.404 | 4.7 | 4.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49354832 | 1103 | 204.1081 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 134 | 13564444 | 5562 | 133.488 | 5.562 | 4.4 | 4.4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49356030 | 1198 | 215.3901 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 13569852 | 5408 | 129.792 | 5.408 | 4 | 4 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49357114 | 1084 | 200.4438 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 13575806 | 5954 | 142.896 | 5.954 | 3.6 | 3.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49358317 | 1203 | 202.049 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 130 | 13581134 | 5328 | 127.872 | 5.328 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49359444 | 1127 | 211.524 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 131 | 13586758 | 5624 | 134.976 | 5.624 | 3 | 3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49360620 | 1176 | 209.1038 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 138 | 129 | 13592386 | 5628 | 135.072 | 5.628 | 2.9 | 2.9 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49361792 | 1172 | 208.2445 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 131 | 13598195 | 5809 | 139.416 | 5.809 | 2.7 | 2.7 | 3B+1S | 995 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49362885 | 1093 | 188.1563 | 100% | 0% | 100% | 100% | 100% | 0% | 11155210 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 149 | 127 | 13603415 | 5220 | 125.28 | 5.22 | 3.7 | 3.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49363874 | 989 | 189.4636 | 0% | 0% | 100% | 100% | 100% | 30% | 11155458 | 248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 148 | 125 | 13608579 | 5164 | 123.936 | 5.164 | 5 | 5 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 49364840 | 966 | 187.0643 | 0% | 0% | 100% | 100% | 100% | 30% | 11156405 | 947 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126661 | 126.661 | 126.661 | [12 empty] | 24600 | 24600 | 194.2192 | [6 empty] | 4281 | 4281 | 1.1767 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:02 AM (60%)
BACK TO NORMAL OPERATION @ 2:00AM
BP1-STARETED @ 2:00AM
BP3 STARTED @ 2:03AM
BP2-STARTED @ 2:0AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (30%)

## AUG 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26132 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13608579 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49364840 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11156405 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 10 | 7.0423 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 145 | 111 | 13613374 | 4795 | 115.08 | 4.795 | 6.3 | 6.3 | 3B | 0 | 0 | 976 | 1185 | 976 | N/A | N/A | N/A | N/A | 49365656 | 816 | 170.1773 | 0% | 0% | 100% | 100% | 100% | 40% | 11157643 | 1238 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 13 | 9.1549 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 146 | 112 | 13618072 | 4698 | 112.752 | 4.698 | 7.9 | 7.9 | 3B | 0 | 0 | 976 | 1185 | 976 | N/A | N/A | N/A | N/A | 49366440 | 784 | 166.8795 | 0% | 0% | 100% | 100% | 100% | 40% | 11158998 | 1355 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 15 | 10.5634 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 147 | 106 | 13622738 | 4666 | 111.984 | 4.666 | 9.5 | 9.5 | 3B | 0 | 0 | 976 | 1185 | 976 | N/A | N/A | N/A | N/A | 49367219 | 779 | 166.9524 | 0% | 0% | 100% | 100% | 100% | 40% | 11160328 | 1330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 16 | 11.2676 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 112 | 110 | 13627647 | 4909 | 117.816 | 4.909 | 9.5 | 9.5 | 3B | 0 | 0 | 1015 | 1185 | 1015 | N/A | N/A | N/A | N/A | 49368102 | 883 | 179.8737 | 0% | 0% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 133 | 120 | 13632581 | 4934 | 118.416 | 4.934 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 49369065 | 963 | 195.1763 | 0% | 0% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 128 | 13638035 | 5454 | 130.896 | 5.454 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49370061 | 996 | 182.6183 | 0% | 0% | 100% | 100% | 100% | 0% | 11160328 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 13643750 | 5715 | 137.16 | 5.715 | 9.1 | 9.1 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49371245 | 1184 | 207.1741 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 143 | 13649883 | 6133 | 147.192 | 6.133 | 8.6 | 8.6 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49372448 | 1203 | 196.152 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 139 | 13655916 | 6033 | 144.792 | 6.033 | 8.1 | 8.1 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49373639 | 1191 | 197.4142 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 13662018 | 6102 | 146.448 | 6.102 | 7.5 | 7.5 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49374842 | 1203 | 197.1485 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 | 1.18
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 141 | 13668199 | 6181 | 148.344 | 6.181 | 7 | 7 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49376044 | 1202 | 194.4669 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 137 | 13674127 | 5928 | 142.272 | 5.928 | 6.4 | 6.4 | 3B+1S | 0 | 1056 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49377237 | 1193 | 201.2483 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 135 | 13680122 | 5995 | 143.88 | 5.995 | 5.7 | 5.7 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49378428 | 1191 | 198.6656 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 133 | 13686506 | 6384 | 153.216 | 6.384 | 5.3 | 5.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49379690 | 1262 | 197.6817 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 136 | 13692108 | 5602 | 134.448 | 5.602 | 4.8 | 4.8 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49380840 | 1150 | 205.2838 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 13697820 | 5712 | 137.088 | 5.712 | 4.5 | 4.5 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49382018 | 1178 | 206.2325 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 13703552 | 5732 | 137.568 | 5.732 | 3.9 | 3.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49383192 | 1174 | 204.8151 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 137 | 13709356 | 5804 | 139.296 | 5.804 | 3.5 | 3.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49384358 | 1166 | 200.8959 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 13715296 | 5940 | 142.56 | 5.94 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49385584 | 1226 | 206.3973 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 132 | 13720938 | 5642 | 135.408 | 5.642 | 2.9 | 2.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49386734 | 1150 | 203.8284 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 142 | 139 | 13726466 | 5528 | 132.672 | 5.528 | 2.8 | 2.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49387902 | 1168 | 211.288 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 130 | 13731916 | 5450 | 130.8 | 5.45 | 2.7 | 2.7 | 3B+1S | 0 | 994 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49388987 | 1085 | 199.0826 | 0% | 100% | 100% | 100% | 100% | 0% | 11160328 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 149 | 124 | 13737218 | 5302 | 127.248 | 5.302 | 3.6 | 3.6 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49389986 | 999 | 188.4195 | 0% | 0% | 100% | 100% | 100% | 30% | 11161148 | 820 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 143 | 120 | 13742383 | 5165 | 123.96 | 5.165 | 4.6 | 4.6 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49390972 | 986 | 190.9003 | 0% | 0% | 100% | 100% | 100% | 30% | 11162003 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133804 | 133.804 | 133.804 | [12 empty] | 26132 | 26132 | 195.3006 | [6 empty] | 5598 | 5598 | 1.075 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV1- INCREASE OPENING @ 12:01 AM (40%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## AUG 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26421 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13742383 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49390972 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11162003 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 8 | 5.6338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 142 | 110 | 13747064 | 4681 | 112.344 | 4.681 | 5.7 | 5.7 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49391831 | 859 | 183.5078 | 0% | 0% | 100% | 100% | 100% | 50% | 11163499 | 1496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 9 | 6.338 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 141 | 111 | 13751713 | 4649 | 111.576 | 4.649 | 7.9 | 7.9 | 3B | 0 | 0 | 1036 | 1185 | 1036 | N/A | N/A | N/A | N/A | 49392698 | 867 | 186.4917 | 0% | 0% | 100% | 100% | 100% | 50% | 11165008 | 1509 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 11 | 7.7465 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 108 | 13756403 | 4690 | 112.56 | 4.69 | 9.5 | 9.5 | 3B | 0 | 0 | 1015 | 1185 | 1016 | N/A | N/A | N/A | N/A | 49393502 | 804 | 171.4286 | 0% | 0% | 100% | 100% | 100% | 50% | 11166760 | 1752 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 117 | 13761472 | 5069 | 121.656 | 5.069 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1047 | N/A | N/A | N/A | N/A | 49394359 | 857 | 169.0669 | 0% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 13 | 9.1549 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 126 | 13766805 | 5333 | 127.992 | 5.333 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1177 | N/A | N/A | N/A | N/A | 49395274 | 915 | 171.5732 | 0% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 131 | 13772116 | 5311 | 127.464 | 5.311 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49396338 | 1064 | 200.3389 | 0% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 13778022 | 5906 | 141.744 | 5.906 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49397519 | 1181 | 199.9661 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 13784019 | 5997 | 143.928 | 5.997 | 8.7 | 8.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49398714 | 1195 | 199.2663 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 140 | 13790052 | 6033 | 144.792 | 6.033 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49399904 | 1190 | 197.2485 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 140 | 13796102 | 6050 | 145.2 | 6.05 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49401105 | 1201 | 198.5124 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 | 1.22
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 13802259 | 6157 | 147.768 | 6.157 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49402305 | 1200 | 194.9001 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 138 | 13808447 | 6188 | 148.512 | 6.188 | 6.5 | 6.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49403502 | 1197 | 193.4389 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 136 | 13814246 | 5799 | 139.176 | 5.799 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49404681 | 1179 | 203.3109 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 133 | 13820414 | 6168 | 148.032 | 6.168 | 5.4 | 5.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49405902 | 1221 | 197.9572 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 126 | 13825772 | 5358 | 128.592 | 5.358 | 5 | 5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49407006 | 1104 | 206.047 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 13831840 | 6068 | 145.632 | 6.068 | 4.7 | 4.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49408221 | 1215 | 200.2307 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 13837438 | 5598 | 134.352 | 5.598 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49409366 | 1145 | 204.5373 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 13843356 | 5918 | 142.032 | 5.918 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49410584 | 1218 | 205.8128 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 13849012 | 5656 | 135.744 | 5.656 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49411712 | 1128 | 199.4342 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 140 | 13854866 | 5854 | 140.496 | 5.854 | 3.1 | 3.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49412912 | 1200 | 204.988 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 131 | 13860486 | 5620 | 134.88 | 5.62 | 2.7 | 2.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49414050 | 1138 | 202.4911 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 132 | 13866135 | 5649 | 135.576 | 5.649 | 2.4 | 2.4 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49415228 | 1178 | 208.5325 | 100% | 0% | 100% | 100% | 100% | 0% | 11166760 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 123 | 13871439 | 5304 | 127.296 | 5.304 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49416317 | 1089 | 205.3167 | 0% | 0% | 100% | 100% | 100% | 35% | 11166845 | 85 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 122 | 13876579 | 5140 | 123.36 | 5.14 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49417393 | 1076 | 209.3385 | 0% | 0% | 100% | 100% | 100% | 35% | 11167108 | 263 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134196 | 134.196 | 134.196 | [12 empty] | 26421 | 26421 | 196.8837 | [6 empty] | 5105 | 5105 | 1.1633 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (50%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## AUG 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
10pm - 6am
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26929 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 13876579 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49417393 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11167108 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 109 | 13881228 | 4649 | 111.576 | 4.649 | 5.6 | 5.6 | 3B | 0 | 0 | 1095 | 1185 | 1095 | N/A | N/A | N/A | N/A | 49418316 | 923 | 198.5373 | 0% | 0% | 100% | 100% | 100% | 60% | 11167950 | 842 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 108 | 13885853 | 4625 | 111 | 4.625 | 6.8 | 6.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49419231 | 915 | 197.8378 | 0% | 0% | 100% | 100% | 100% | 60% | 11168851 | 901 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 111 | 13890191 | 4338 | 104.112 | 4.338 | 8 | 8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49420093 | 862 | 198.7091 | 0% | 0% | 100% | 100% | 100% | 60% | 11169710 | 859 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 121 | 13893560 | 3369 | 80.856 | 3.369 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49421126 | 1033 | 306.6192 | 0% | 0% | 100% | 100% | 100% | 60% | 11170125 | 415 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 122 | 13898216 | 4656 | 111.744 | 4.656 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49422205 | 1079 | 231.744 | 0% | 0% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 132 | 13903613 | 5397 | 129.528 | 5.397 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 49423237 | 1032 | 191.2173 | 0% | 0% | 100% | 100% | 100% | 0% | 11170125 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 145 | 144 | 13909337 | 5724 | 137.376 | 5.724 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49424367 | 1130 | 197.4144 | 0% | 0% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 13915465 | 6128 | 147.072 | 6.128 | 9.1 | 9.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49425576 | 1209 | 197.2911 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 13921535 | 6070 | 145.68 | 6.07 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49426779 | 1203 | 198.1878 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 13927711 | 6176 | 148.224 | 6.176 | 7.7 | 7.7 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49427992 | 1213 | 196.4054 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 147 | 13933869 | 6158 | 147.792 | 6.158 | 7 | 7 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49429220 | 1228 | 199.4154 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 13939889 | 6020 | 144.48 | 6.02 | 6.3 | 6.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49430426 | 1206 | 200.3322 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 13945988 | 6099 | 146.376 | 6.099 | 5.6 | 5.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49431634 | 1208 | 198.0653 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 141 | 13951899 | 5911 | 141.864 | 5.911 | 5.1 | 5.1 | 3B+1S | 0 | 1096 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49432827 | 1193 | 201.8271 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 142 | 13957332 | 5433 | 130.392 | 5.433 | 4.7 | 4.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49433896 | 1069 | 196.7605 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 13963030 | 5698 | 136.752 | 5.698 | 4.2 | 4.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49435074 | 1178 | 206.7392 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 13968754 | 5724 | 137.376 | 5.724 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49436257 | 1183 | 206.6737 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 13974427 | 5673 | 136.152 | 5.673 | 3.4 | 3.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49437421 | 1164 | 205.1824 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 13980055 | 5628 | 135.072 | 5.628 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49438586 | 1165 | 207.0007 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 133 | 13985580 | 5525 | 132.6 | 5.525 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49439741 | 1155 | 209.0498 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 134 | 13991337 | 5757 | 138.168 | 5.757 | 2.5 | 2.5 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49440924 | 1183 | 205.489 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 129 | 13997374 | 6037 | 144.888 | 6.037 | 2.3 | 2.3 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49442181 | 1257 | 208.216 | 0% | 100% | 100% | 100% | 100% | 0% | 11170125 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 123 | 14002604 | 5230 | 125.52 | 5.23 | 2.5 | 2.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49443261 | 1080 | 206.501 | 0% | 0% | 100% | 100% | 100% | 45% | 11170150 | 25 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 118 | 14007721 | 5117 | 122.808 | 5.117 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49444322 | 1061 | 207.3481 | 0% | 0% | 100% | 100% | 100% | 45% | 11170372 | 222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131142 | 131.142 | 131.142 | [12 empty] | 26929 | 26929 | 205.3423 | [6 empty] | 3264 | 3264 | 1.165 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (45%)

## AUG 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26435 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14007721 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49444322 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11170372 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 133 | 106 | 14012542 | 4821 | 115.704 | 4.821 | 4.9 | 4.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49445312 | 990 | 205.3516 | 0% | 0% | 100% | 100% | 100% | 60% | 11171160 | 788 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 108 | 14016998 | 4456 | 106.944 | 4.456 | 6.8 | 6.8 | 3B | 0 | 0 | 1075 | 1185 | 1075 | N/A | N/A | N/A | N/A | 49446144 | 832 | 186.7145 | 0% | 0% | 100% | 100% | 100% | 60% | 11172076 | 916 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 | 110 | 14021353 | 4355 | 104.52 | 4.355 | 8 | 8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49447009 | 865 | 198.6223 | 0% | 0% | 100% | 100% | 100% | 60% | 11172760 | 684 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 119 | 14024763 | 3410 | 81.84 | 3.41 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49448025 | 1016 | 297.9472 | 0% | 0% | 100% | 100% | 100% | 60% | 11173160 | 400 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 121 | 14029276 | 4513 | 108.312 | 4.513 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49449060 | 1035 | 229.3375 | 0% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 130 | 14034542 | 5266 | 126.384 | 5.266 | 9.5 | 9.5 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49449917 | 857 | 162.7421 | 0% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 | 1.05 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 138 | 14040124 | 5582 | 133.968 | 5.582 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49450875 | 958 | 171.6231 | 0% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 138 | 14046105 | 5981 | 143.544 | 5.981 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49451954 | 1079 | 180.4046 | 0% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 141 | 146 | 14052231 | 6126 | 147.024 | 6.126 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49453140 | 1186 | 193.601 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 14058360 | 6129 | 147.096 | 6.129 | 8.7 | 8.7 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49454336 | 1196 | 195.1379 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 | 1.32
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 14064555 | 6195 | 148.68 | 6.195 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49455551 | 1215 | 196.1259 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 14070649 | 6094 | 146.256 | 6.094 | 7.5 | 7.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49456750 | 1199 | 196.7509 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 137 | 14076715 | 6066 | 145.584 | 6.066 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49457959 | 1209 | 199.3076 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 138 | 14082950 | 6235 | 149.64 | 6.235 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49459162 | 1203 | 192.9431 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 140 | 14088982 | 6032 | 144.768 | 6.032 | 5.7 | 5.7 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49460384 | 1222 | 202.5862 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 144 | 14094694 | 5712 | 137.088 | 5.712 | 5.2 | 5.2 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49461518 | 1134 | 198.5294 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 14100766 | 6072 | 145.728 | 6.072 | 4.6 | 4.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49462727 | 1209 | 199.1107 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 14107028 | 6262 | 150.288 | 6.262 | 4 | 4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49463938 | 1211 | 193.3887 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 | 1.32 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 141 | 14113022 | 5994 | 143.856 | 5.994 | 3.5 | 3.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49465118 | 1180 | 196.8635 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 132 | 14118558 | 5536 | 132.864 | 5.536 | 3.1 | 3.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49466244 | 1126 | 203.396 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 136 | 14124366 | 5808 | 139.392 | 5.808 | 2.7 | 2.7 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49467434 | 1190 | 204.8898 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 14129941 | 5575 | 133.8 | 5.575 | 2.5 | 2.5 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49468623 | 1189 | 213.2735 | 100% | 0% | 100% | 100% | 100% | 0% | 11173160 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 123 | 14135358 | 5417 | 130.008 | 5.417 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49469694 | 1071 | 197.7109 | 0% | 0% | 100% | 100% | 100% | 45% | 11173289 | 129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 120 | 14140391 | 5033 | 120.792 | 5.033 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49470757 | 1063 | 211.206 | 0% | 0% | 100% | 100% | 100% | 45% | 11173500 | 211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132670 | 132.67 | 132.67 | [12 empty] | 26435 | 26435 | 199.2538 | [6 empty] | 3128 | 3128 | 1.185 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (45%)

## AUG 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26789 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14140391 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49470757 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11173500 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 116 | 14145175 | 4784 | 114.816 | 4.784 | 4.9 | 4.9 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49471693 | 936 | 195.6522 | 0% | 0% | 100% | 100% | 100% | 60% | 11173901 | 401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 106 | 14149804 | 4629 | 111.096 | 4.629 | 6.5 | 6.5 | 3B | 0 | 0 | 1075 | 1185 | 1075 | N/A | N/A | N/A | N/A | 49472586 | 893 | 192.9142 | 0% | 0% | 100% | 100% | 100% | 60% | 11174697 | 796 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 110 | 14154136 | 4332 | 103.968 | 4.332 | 7.8 | 7.8 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49473447 | 861 | 198.7535 | 0% | 0% | 100% | 100% | 100% | 60% | 11175335 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 115 | 14157639 | 3503 | 84.072 | 3.503 | 8.8 | 8.8 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49474387 | 940 | 268.3414 | 0% | 0% | 100% | 100% | 100% | 60% | 11176165 | 830 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 123 | 14162393 | 4754 | 114.096 | 4.754 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 49475426 | 1039 | 218.5528 | 0% | 0% | 100% | 100% | 100% | 60% | 11176765 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 144 | 136 | 14167971 | 5578 | 133.872 | 5.578 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49476519 | 1093 | 195.9484 | 0% | 0% | 100% | 100% | 100% | 0% | 11176765 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 14173896 | 5925 | 142.2 | 5.925 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49477719 | 1200 | 202.5316 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 14179995 | 6099 | 146.376 | 6.099 | 8.5 | 8.5 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49478922 | 1203 | 197.2455 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 14186198 | 6203 | 148.872 | 6.203 | 8 | 8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49480114 | 1192 | 192.1651 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 146 | 14192399 | 6201 | 148.824 | 6.201 | 7.4 | 7.4 | 3B+1S | 0 | 1037 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49481330 | 1216 | 196.0974 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 | 1.27
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 140 | 14198613 | 6214 | 149.136 | 6.214 | 6.8 | 6.8 | 3B+1S | 0 | 1067 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49482532 | 1202 | 193.4342 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 142 | 14204598 | 5985 | 143.64 | 5.985 | 6.1 | 6.1 | 3B+1S | 0 | 1065 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49483733 | 1201 | 200.6683 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 14210634 | 6036 | 144.864 | 6.036 | 5.5 | 5.5 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49484933 | 1200 | 198.8072 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 135 | 14216743 | 6109 | 146.616 | 6.109 | 5 | 5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49486119 | 1186 | 194.1398 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 134 | 14222603 | 5860 | 140.64 | 5.86 | 4.5 | 4.5 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49487287 | 1168 | 199.3174 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 138 | 14228487 | 5884 | 141.216 | 5.884 | 4 | 4 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49488469 | 1182 | 200.8838 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 14234388 | 5901 | 141.624 | 5.901 | 3.6 | 3.6 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49489638 | 1169 | 198.102 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 141 | 14239925 | 5537 | 132.888 | 5.537 | 3.3 | 3.3 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49490711 | 1073 | 193.7872 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 129 | 14245746 | 5821 | 139.704 | 5.821 | 3 | 3 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49491871 | 1160 | 199.2785 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 128 | 14251312 | 5566 | 133.584 | 5.566 | 2.8 | 2.8 | 3B+1S | 0 | 1005 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49493035 | 1164 | 209.1268 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 136 | 14257168 | 5856 | 140.544 | 5.856 | 2.3 | 2.3 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49494220 | 1185 | 202.3566 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 14262855 | 5687 | 136.488 | 5.687 | 1.9 | 1.9 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49495394 | 1174 | 206.4357 | 0% | 100% | 100% | 100% | 100% | 0% | 11176765 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 124 | 14268138 | 5283 | 126.792 | 5.283 | 1.9 | 1.9 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49496481 | 1087 | 205.7543 | 0% | 0% | 100% | 100% | 100% | 20% | 11176815 | 50 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 116 | 14273297 | 5159 | 123.816 | 5.159 | 2.3 | 2.3 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49497546 | 1065 | 206.4354 | 0% | 0% | 100% | 100% | 100% | 20% | 11177217 | 402 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132906 | 132.906 | 132.906 | [12 empty] | 26789 | 26789 | 201.5635 | [6 empty] | 3717 | 3717 | 1.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV1 -OPENED @ 10:01 PM (20%)

## AUG 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27056 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14273297 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49497546 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11177217 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 115 | 14277489 | 4192 | 100.608 | 4.192 | 4.1 | 4.1 | 3B | 0 | 0 | 1115 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49498426 | 880 | 209.9237 | 0% | 0% | 100% | 100% | 100% | 65% | 11177842 | 625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 140 | 108 | 14281702 | 4213 | 101.112 | 4.213 | 6.3 | 6.3 | 3B | 0 | 0 | 1115 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49499336 | 910 | 215.9981 | 0% | 0% | 100% | 100% | 100% | 65% | 11178457 | 615 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 112 | 14285927 | 4225 | 101.4 | 4.225 | 8.8 | 8.8 | 3B | 0 | 0 | 1115 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49500273 | 937 | 221.7751 | 0% | 0% | 100% | 100% | 100% | 65% | 11179087 | 630 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 135 | 118 | 14290469 | 4542 | 109.008 | 4.542 | 9.3 | 9.3 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49501411 | 1138 | 250.5504 | 0% | 0% | 100% | 100% | 100% | 65% | 11179697 | 610 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 121 | 14295049 | 4580 | 109.92 | 4.58 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49502479 | 1068 | 233.1878 | 0% | 0% | 100% | 100% | 100% | 65% | 11179939 | 242 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 130 | 14300973 | 5924 | 142.176 | 5.924 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49503633 | 1154 | 194.8008 | 0% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 145 | 14307007 | 6034 | 144.816 | 6.034 | 9.3 | 9.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49504830 | 1197 | 198.3759 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 14313045 | 6038 | 144.912 | 6.038 | 8.8 | 8.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49506023 | 1193 | 197.582 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 14319076 | 6031 | 144.744 | 6.031 | 8.2 | 8.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49507224 | 1201 | 199.1378 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 14325096 | 6020 | 144.48 | 6.02 | 7.7 | 7.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49508415 | 1191 | 197.8405 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 | 1.18
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 140 | 14331125 | 6029 | 144.696 | 6.029 | 7.2 | 7.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49509605 | 1190 | 197.3793 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 14336993 | 5868 | 140.832 | 5.868 | 6.7 | 6.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49510786 | 1181 | 201.2611 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 138 | 14342857 | 5864 | 140.736 | 5.864 | 6.2 | 6.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49511971 | 1185 | 202.0805 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 132 | 14349022 | 6165 | 147.96 | 6.165 | 5.8 | 5.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49513176 | 1205 | 195.4582 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 142 | 14354626 | 5604 | 134.496 | 5.604 | 5.5 | 5.5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49514288 | 1112 | 198.4297 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 139 | 140 | 14360364 | 5738 | 137.712 | 5.738 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49515440 | 1152 | 200.7668 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 136 | 14366402 | 6038 | 144.912 | 6.038 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49516650 | 1210 | 200.3975 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 14372036 | 5634 | 135.216 | 5.634 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49517808 | 1158 | 205.5378 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 | 1.39 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 14377494 | 5458 | 130.992 | 5.458 | 4.5 | 4.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49518938 | 1130 | 207.0355 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 133 | 14383220 | 5726 | 137.424 | 5.726 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49520126 | 1188 | 207.4747 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 134 | 14388978 | 5758 | 138.192 | 5.758 | 3.6 | 3.6 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49521300 | 1174 | 203.8902 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 131 | 14394546 | 5568 | 133.632 | 5.568 | 3.2 | 3.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49522461 | 1161 | 208.5129 | 100% | 0% | 100% | 100% | 100% | 0% | 11179939 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 123 | 14399827 | 5281 | 126.744 | 5.281 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49523548 | 1087 | 205.8322 | 0% | 0% | 100% | 100% | 100% | 35% | 11179981 | 42 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 120 | 14404879 | 5052 | 121.248 | 5.052 | 3.9 | 3.9 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49524602 | 1054 | 208.6302 | 0% | 0% | 100% | 100% | 100% | 35% | 11180382 | 401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131582 | 131.582 | 131.582 | [12 empty] | 27056 | 27056 | 205.6208 | [6 empty] | 3165 | 3165 | 1.1917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV1- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## AUG 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26827 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14404879 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49524602 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11180382 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 131 | 109 | 14409336 | 4457 | 106.968 | 4.457 | 4.9 | 4.9 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49525405 | 803 | 180.166 | 0% | 0% | 100% | 100% | 100% | 65% | 11181167 | 785 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 108 | 14413765 | 4429 | 106.296 | 4.429 | 5.8 | 5.8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49526288 | 883 | 199.3678 | 0% | 0% | 100% | 100% | 100% | 65% | 11181720 | 553 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 103 | 14418151 | 4386 | 105.264 | 4.386 | 7.1 | 7.1 | 3B | 0 | 0 | 1056 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49527157 | 869 | 198.1304 | 0% | 0% | 100% | 100% | 100% | 65% | 11182229 | 509 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 114 | 14422637 | 4486 | 107.664 | 4.486 | 8.6 | 8.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 49528126 | 969 | 216.0053 | 0% | 0% | 100% | 100% | 100% | 65% | 11182791 | 562 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 127 | 14427143 | 4506 | 108.144 | 4.506 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 49529256 | 1130 | 250.7767 | 0% | 0% | 100% | 100% | 100% | 65% | 11183165 | 374 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 130 | 14432731 | 5588 | 134.112 | 5.588 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49530369 | 1113 | 199.1768 | 0% | 0% | 100% | 100% | 100% | 0% | 11183165 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 14438760 | 6029 | 144.696 | 6.029 | 9.1 | 9.1 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49531561 | 1192 | 197.7111 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 143 | 14444853 | 6093 | 146.232 | 6.093 | 8.5 | 8.5 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49532770 | 1209 | 198.4244 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 144 | 14450894 | 6041 | 144.984 | 6.041 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49533969 | 1199 | 198.4771 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 143 | 14457015 | 6121 | 146.904 | 6.121 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49535179 | 1210 | 197.6801 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 | 1.16
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 14463013 | 5998 | 143.952 | 5.998 | 6.6 | 6.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49536380 | 1201 | 200.2334 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 136 | 14468886 | 5873 | 140.952 | 5.873 | 6 | 6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49537572 | 1192 | 202.9627 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 134 | 14474857 | 5971 | 143.304 | 5.971 | 5.4 | 5.4 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49538771 | 1199 | 200.8039 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 14480788 | 5931 | 142.344 | 5.931 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49539944 | 1173 | 197.7744 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 134 | 14486384 | 5596 | 134.304 | 5.596 | 4.8 | 4.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49541088 | 1144 | 204.4317 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 14492272 | 5888 | 141.312 | 5.888 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49542254 | 1166 | 198.0299 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 138 | 14498344 | 6072 | 145.728 | 6.072 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49543458 | 1204 | 198.2872 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 139 | 14503982 | 5638 | 135.312 | 5.638 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49544604 | 1146 | 203.2636 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 135 | 14509680 | 5698 | 136.752 | 5.698 | 3.8 | 3.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49545760 | 1156 | 202.8782 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 133 | 14515366 | 5686 | 136.464 | 5.686 | 3.5 | 3.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49546922 | 1162 | 204.3616 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 136 | 14521244 | 5878 | 141.072 | 5.878 | 3.1 | 3.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49548120 | 1198 | 203.8108 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 133 | 14526860 | 5616 | 134.784 | 5.616 | 2.9 | 2.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49549285 | 1165 | 207.443 | 0% | 100% | 100% | 100% | 100% | 0% | 11183165 | 0 | 1.31 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 124 | 14532254 | 5394 | 129.456 | 5.394 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49550363 | 1078 | 199.8517 | 0% | 0% | 100% | 100% | 100% | 35% | 11183311 | 146 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 14537297 | 5043 | 121.032 | 5.043 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49551429 | 1066 | 211.3821 | 0% | 0% | 100% | 100% | 100% | 35% | 11183468 | 157 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132418 | 132.418 | 132.418 | [12 empty] | 26827 | 26827 | 202.5933 | [6 empty] | 3086 | 3086 | 1.1917 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## AUG 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26785 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14537297 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49551429 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11183468 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 137 | 105 | 14541740 | 4443 | 106.632 | 4.443 | 4.8 | 4.8 | 3B | 0 | 0 | 1075 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49552318 | 889 | 200.09 | 0% | 0% | 100% | 100% | 100% | 65% | 11184246 | 778 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 | 105 | 14546065 | 4325 | 103.8 | 4.325 | 5.6 | 5.6 | 3B | 0 | 0 | 1076 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49553217 | 899 | 207.8613 | 0% | 0% | 100% | 100% | 100% | 65% | 11184975 | 729 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 | 108 | 14550325 | 4260 | 102.24 | 4.26 | 6.9 | 6.9 | 3B | 0 | 0 | 1056 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49554073 | 856 | 200.939 | 0% | 0% | 100% | 100% | 100% | 65% | 11185775 | 800 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 114 | 14554672 | 4347 | 104.328 | 4.347 | 8.7 | 8.7 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49555036 | 963 | 221.5321 | 0% | 0% | 100% | 100% | 100% | 65% | 11186552 | 777 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 123 | 14559551 | 4879 | 117.096 | 4.879 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49555993 | 957 | 196.1468 | 0% | 0% | 100% | 100% | 100% | 65% | 11187132 | 580 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 132 | 14564677 | 5126 | 123.024 | 5.126 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49556994 | 1001 | 195.279 | 0% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 14570897 | 6220 | 149.28 | 6.22 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49558191 | 1197 | 192.4437 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 14577016 | 6119 | 146.856 | 6.119 | 8.7 | 8.7 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49559395 | 1204 | 196.7642 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 142 | 14583160 | 6144 | 147.456 | 6.144 | 8 | 8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49560608 | 1213 | 197.4284 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 149 | 14589366 | 6206 | 148.944 | 6.206 | 7.3 | 7.3 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49561812 | 1204 | 194.0058 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 14595584 | 6218 | 149.232 | 6.218 | 6.8 | 6.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49563029 | 1217 | 195.7221 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 148 | 14601811 | 6227 | 149.448 | 6.227 | 6.2 | 6.2 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49564217 | 1188 | 190.7821 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 133 | 14608025 | 6214 | 149.136 | 6.214 | 5.7 | 5.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49565457 | 1240 | 199.5494 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 132 | 14614254 | 6229 | 149.496 | 6.229 | 5.3 | 5.3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49566728 | 1271 | 204.0456 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 14620020 | 5766 | 138.384 | 5.766 | 5 | 5 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49567920 | 1192 | 206.7291 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 139 | 14625402 | 5382 | 129.168 | 5.382 | 4.7 | 4.7 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49569000 | 1080 | 200.6689 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 14631348 | 5946 | 142.704 | 5.946 | 4.4 | 4.4 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49570186 | 1186 | 199.4618 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 133 | 14637042 | 5694 | 136.656 | 5.694 | 3.9 | 3.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49571322 | 1136 | 199.5083 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 138 | 14642942 | 5900 | 141.6 | 5.9 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49572518 | 1196 | 202.7119 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 136 | 14648904 | 5962 | 143.088 | 5.962 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49573736 | 1218 | 204.2939 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 136 | 137 | 14655132 | 6228 | 149.472 | 6.228 | 2.8 | 2.8 | 3B+1S | 1055 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49575012 | 1276 | 204.8812 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 132 | 14660261 | 5129 | 123.096 | 5.129 | 2.7 | 2.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49576077 | 1065 | 207.6428 | 100% | 0% | 100% | 100% | 100% | 0% | 11187132 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 122 | 14665340 | 5079 | 121.896 | 5.079 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49577142 | 1065 | 209.6869 | 0% | 0% | 100% | 100% | 100% | 30% | 11187350 | 218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 120 | 14670514 | 5174 | 124.176 | 5.174 | 3.8 | 3.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49578214 | 1072 | 207.1898 | 0% | 0% | 100% | 100% | 100% | 30% | 11187555 | 205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133217 | 133.217 | 133.217 | [12 empty] | 26785 | 26785 | 201.0629 | [6 empty] | 4087 | 4087 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## AUG 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26715 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14670514 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49578214 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11187555 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 136 | 108 | 14675183 | 4669 | 112.056 | 4.669 | 4.6 | 4.6 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49579118 | 904 | 193.6175 | 0% | 0% | 100% | 100% | 100% | 60% | 11188091 | 536 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 106 | 14679715 | 4532 | 108.768 | 4.532 | 5.9 | 5.9 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49580004 | 886 | 195.4987 | 0% | 0% | 100% | 100% | 100% | 60% | 11189050 | 959 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 108 | 14684208 | 4493 | 107.832 | 4.493 | 7.5 | 7.5 | 3B | 0 | 0 | 1056 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49580855 | 851 | 189.4057 | 0% | 0% | 100% | 100% | 100% | 60% | 11189875 | 825 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 124 | 14687835 | 3627 | 87.048 | 3.627 | 8.8 | 8.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49581812 | 957 | 263.8544 | 0% | 0% | 100% | 100% | 100% | 60% | 11190575 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 126 | 14692599 | 4764 | 114.336 | 4.764 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49582863 | 1051 | 220.6129 | 0% | 0% | 100% | 100% | 100% | 60% | 11191100 | 525 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 129 | 14698108 | 5509 | 132.216 | 5.509 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49583952 | 1089 | 197.6765 | 0% | 0% | 100% | 100% | 100% | 0% | 11191100 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 144 | 14703936 | 5828 | 139.872 | 5.828 | 9.2 | 9.2 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49585127 | 1175 | 201.6129 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 14709986 | 6050 | 145.2 | 6.05 | 8.7 | 8.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49586329 | 1202 | 198.6777 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 142 | 14715993 | 6007 | 144.168 | 6.007 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49587519 | 1190 | 198.1022 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 142 | 14722019 | 6026 | 144.624 | 6.026 | 7.6 | 7.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49588704 | 1185 | 196.6479 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 | 1.19
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 14728147 | 6128 | 147.072 | 6.128 | 7.1 | 7.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49589896 | 1192 | 194.517 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 139 | 14734151 | 6004 | 144.096 | 6.004 | 6.7 | 6.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49591093 | 1197 | 199.3671 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 14740253 | 6102 | 146.448 | 6.102 | 6.2 | 6.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49592269 | 1176 | 192.7237 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 144 | 14746195 | 5942 | 142.608 | 5.942 | 5.8 | 5.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49593448 | 1179 | 198.418 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 14752006 | 5811 | 139.464 | 5.811 | 5.5 | 5.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49594594 | 1146 | 197.2122 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 14758244 | 6238 | 149.712 | 6.238 | 5.1 | 5.1 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49595800 | 1206 | 193.3312 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 14764462 | 6218 | 149.232 | 6.218 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49597028 | 1228 | 197.4912 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 142 | 14770004 | 5542 | 133.008 | 5.542 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49598176 | 1148 | 207.1454 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 136 | 14775644 | 5640 | 135.36 | 5.64 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49599304 | 1128 | 200 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 132 | 14781476 | 5832 | 139.968 | 5.832 | 3.9 | 3.9 | 3B+1S | 0 | 994 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49600494 | 1190 | 204.0466 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 133 | 14787102 | 5626 | 135.024 | 5.626 | 3.6 | 3.6 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49601634 | 1140 | 202.6306 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 130 | 14792721 | 5619 | 134.856 | 5.619 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49602824 | 1190 | 211.7815 | 0% | 100% | 100% | 100% | 100% | 0% | 11191100 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 121 | 14797988 | 5267 | 126.408 | 5.267 | 3.8 | 3.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49603891 | 1067 | 202.5821 | 0% | 0% | 100% | 100% | 100% | 40% | 11191307 | 207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 14803084 | 5096 | 122.304 | 5.096 | 4.5 | 4.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49604929 | 1038 | 203.6892 | 0% | 0% | 100% | 100% | 100% | 40% | 11191525 | 218 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132570 | 132.57 | 132.57 | [12 empty] | 26715 | 26715 | 201.5162 | [6 empty] | 3970 | 3970 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## AUG 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26597 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14803084 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49604929 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11191525 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 133 | 111 | 14807750 | 4666 | 111.984 | 4.666 | 5.3 | 5.3 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49605830 | 901 | 193.099 | 0% | 0% | 100% | 100% | 100% | 65% | 11192025 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 | 106 | 14812408 | 4658 | 111.792 | 4.658 | 6.9 | 6.9 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49606720 | 890 | 191.0691 | 0% | 0% | 100% | 100% | 100% | 65% | 11192836 | 811 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 133 | 105 | 14816925 | 4517 | 108.408 | 4.517 | 8.6 | 8.6 | 3B | 0 | 0 | 1056 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49607588 | 868 | 192.1629 | 0% | 0% | 100% | 100% | 100% | 65% | 11193621 | 785 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 120 | 14821042 | 4117 | 98.808 | 4.117 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49608487 | 899 | 218.3629 | 0% | 0% | 100% | 100% | 100% | 65% | 11194623 | 1002 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 116 | 14825560 | 4518 | 108.432 | 4.518 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49609477 | 990 | 219.1235 | 0% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 130 | 14831097 | 5537 | 132.888 | 5.537 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49610536 | 1059 | 191.2588 | 0% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 144 | 14836682 | 5585 | 134.04 | 5.585 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49611604 | 1068 | 191.2265 | 0% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 14842710 | 6028 | 144.672 | 6.028 | 9.2 | 9.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49612792 | 1188 | 197.0803 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 14848742 | 6032 | 144.768 | 6.032 | 8.7 | 8.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49613979 | 1187 | 196.7838 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 146 | 14854925 | 6183 | 148.392 | 6.183 | 8.2 | 8.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49615186 | 1207 | 195.2127 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 | 1.2
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 14861223 | 6298 | 151.152 | 6.298 | 7.7 | 7.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49616372 | 1186 | 188.3138 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 14867559 | 6336 | 152.064 | 6.336 | 7.1 | 7.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49617598 | 1226 | 193.4975 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 14873606 | 6047 | 145.128 | 6.047 | 6.6 | 6.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49618788 | 1190 | 196.7918 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 138 | 14879630 | 6024 | 144.576 | 6.024 | 6.1 | 6.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49619972 | 1184 | 196.5471 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 14885326 | 5696 | 136.704 | 5.696 | 5.7 | 5.7 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49621142 | 1170 | 205.4073 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 14891370 | 6044 | 145.056 | 6.044 | 5.2 | 5.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49622326 | 1184 | 195.8968 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 138 | 14897399 | 6029 | 144.696 | 6.029 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49623520 | 1194 | 198.0428 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 141 | 14903337 | 5938 | 142.512 | 5.938 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49624693 | 1173 | 197.5413 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 14909322 | 5985 | 143.64 | 5.985 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49625875 | 1182 | 197.4937 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 140 | 14915119 | 5797 | 139.128 | 5.797 | 3.6 | 3.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49627042 | 1167 | 201.311 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 139 | 14920960 | 5841 | 140.184 | 5.841 | 3.3 | 3.3 | 3B+1S | 1024 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49628212 | 1170 | 200.3082 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 132 | 14926733 | 5773 | 138.552 | 5.773 | 3.2 | 3.2 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49629372 | 1160 | 200.9354 | 100% | 0% | 100% | 100% | 100% | 0% | 11194623 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 128 | 14932181 | 5448 | 130.752 | 5.448 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49630458 | 1086 | 199.3392 | 0% | 0% | 100% | 100% | 100% | 40% | 11194786 | 163 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 121 | 14937411 | 5230 | 125.52 | 5.23 | 4.1 | 4.1 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49631526 | 1068 | 204.2065 | 0% | 0% | 100% | 100% | 100% | 40% | 11194950 | 164 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134327 | 134.327 | 134.327 | [12 empty] | 26597 | 26597 | 198.0019 | [6 empty] | 3425 | 3425 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (40%)

## AUG 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26418 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 14937411 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49631526 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11194950 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 109 | 14942099 | 4688 | 112.512 | 4.688 | 4.8 | 4.8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49632427 | 901 | 192.1928 | 0% | 0% | 100% | 100% | 100% | 65% | 11195303 | 353 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 136 | 108 | 14946783 | 4684 | 112.416 | 4.684 | 5.9 | 5.9 | 3B | 0 | 0 | 1075 | 1185 | 1075 | N/A | N/A | N/A | N/A | 49633323 | 896 | 191.2895 | 0% | 0% | 100% | 100% | 100% | 65% | 11196161 | 858 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 110 | 14951397 | 4614 | 110.736 | 4.614 | 6.8 | 6.8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49634171 | 848 | 183.7885 | 0% | 0% | 100% | 100% | 100% | 65% | 11197026 | 865 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 115 | 14955720 | 4323 | 103.752 | 4.323 | 8.7 | 8.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49635185 | 1014 | 234.5593 | 0% | 0% | 100% | 100% | 100% | 65% | 11197570 | 544 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 127 | 14960243 | 4523 | 108.552 | 4.523 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49636200 | 1015 | 224.4086 | 0% | 0% | 100% | 100% | 100% | 65% | 11197870 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 133 | 128 | 14965805 | 5562 | 133.488 | 5.562 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49637180 | 980 | 176.1956 | 0% | 0% | 100% | 100% | 100% | 0% | 11197870 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 135 | 14971333 | 5528 | 132.672 | 5.528 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49638189 | 1009 | 182.5253 | 0% | 0% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 145 | 141 | 14977155 | 5822 | 139.728 | 5.822 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49639272 | 1083 | 186.0186 | 0% | 0% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 146 | 14983105 | 5950 | 142.8 | 5.95 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49640421 | 1149 | 193.1092 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 144 | 14989279 | 6174 | 148.176 | 6.174 | 8.7 | 8.7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49641631 | 1210 | 195.9832 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 | 1.23
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 14995447 | 6168 | 148.032 | 6.168 | 8.2 | 8.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49642820 | 1189 | 192.7691 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 15001584 | 6137 | 147.288 | 6.137 | 7.7 | 7.7 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49644027 | 1207 | 196.6759 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 15007909 | 6325 | 151.8 | 6.325 | 7.1 | 7.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49645226 | 1199 | 189.5652 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 139 | 15013912 | 6003 | 144.072 | 6.003 | 6.6 | 6.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49646378 | 1152 | 191.904 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 15020066 | 6154 | 147.696 | 6.154 | 6.1 | 6.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49647552 | 1174 | 190.7702 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 15025922 | 5856 | 140.544 | 5.856 | 5.8 | 5.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49648716 | 1164 | 198.7705 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 15032164 | 6242 | 149.808 | 6.242 | 5.3 | 5.3 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49649980 | 1264 | 202.4992 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 142 | 15037798 | 5634 | 135.216 | 5.634 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49651114 | 1134 | 201.278 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 136 | 15043614 | 5816 | 139.584 | 5.816 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49652280 | 1166 | 200.4814 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 138 | 129 | 15049422 | 5808 | 139.392 | 5.808 | 4.6 | 4.6 | 3B+1S | 0 | 974 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49653466 | 1186 | 204.2011 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 137 | 15055166 | 5744 | 137.856 | 5.744 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49654616 | 1150 | 200.2089 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 133 | 132 | 15060824 | 5658 | 135.792 | 5.658 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49655792 | 1176 | 207.8473 | 0% | 100% | 100% | 100% | 100% | 0% | 11197870 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 126 | 15066234 | 5410 | 129.84 | 5.41 | 4.3 | 4.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49656896 | 1104 | 204.0665 | 0% | 0% | 100% | 100% | 100% | 30% | 11197938 | 68 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 122 | 15071404 | 5170 | 124.08 | 5.17 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49657944 | 1048 | 202.7079 | 0% | 0% | 100% | 100% | 100% | 30% | 11198129 | 191 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133993 | 133.993 | 133.993 | [12 empty] | 26418 | 26418 | 197.1596 | [6 empty] | 3179 | 3179 | 1.175 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## AUG 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26559 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15071404 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49657944 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11198129 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 109 | 15076392 | 4988 | 119.712 | 4.988 | 5 | 5 | 3B | 0 | 0 | 1096 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49658926 | 982 | 196.8725 | 0% | 0% | 100% | 100% | 100% | 60% | 11198558 | 429 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 121 | 110 | 15080882 | 4490 | 107.76 | 4.49 | 5.8 | 5.8 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49659802 | 876 | 195.1002 | 0% | 0% | 100% | 100% | 100% | 60% | 11199156 | 598 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 123 | 107 | 15085340 | 4458 | 106.992 | 4.458 | 6.3 | 6.3 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49660666 | 864 | 193.8089 | 0% | 0% | 100% | 100% | 100% | 60% | 11199586 | 430 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 150 | 91 | 15089374 | 4034 | 96.816 | 4.034 | 8.2 | 8.2 | 3B | 0 | 0 | 1087 | 1185 | 1087 | N/A | N/A | N/A | N/A | 49661532 | 866 | 214.6753 | 0% | 0% | 100% | 100% | 100% | 60% | 11199758 | 172 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 117 | 15093844 | 4470 | 107.28 | 4.47 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49662620 | 1088 | 243.4004 | 0% | 0% | 100% | 100% | 100% | 60% | 11199918 | 160 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 131 | 15099070 | 5226 | 125.424 | 5.226 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 49663630 | 1010 | 193.2644 | 0% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 139 | 15104888 | 5818 | 139.632 | 5.818 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49664644 | 1014 | 174.2867 | 0% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 146 | 138 | 15110824 | 5936 | 142.464 | 5.936 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49665744 | 1100 | 185.31 | 0% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 146 | 15116937 | 6113 | 146.712 | 6.113 | 9.1 | 9.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49666935 | 1191 | 194.8307 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 147 | 15123488 | 6551 | 157.224 | 6.551 | 8.7 | 8.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49668145 | 1210 | 184.7046 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 | 1.05
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 15129929 | 6441 | 154.584 | 6.441 | 8.1 | 8.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49669356 | 1211 | 188.0143 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 146 | 15136347 | 6418 | 154.032 | 6.418 | 7.5 | 7.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49670569 | 1213 | 188.9997 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 142 | 15142603 | 6256 | 150.144 | 6.256 | 6.9 | 6.9 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49671755 | 1186 | 189.578 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 15148972 | 6369 | 152.856 | 6.369 | 6.4 | 6.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49672960 | 1205 | 189.1977 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 140 | 15155134 | 6162 | 147.888 | 6.162 | 5.9 | 5.9 | 3B+1S | 1036 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49674156 | 1196 | 194.0928 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 145 | 15161182 | 6048 | 145.152 | 6.048 | 5.4 | 5.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49675332 | 1176 | 194.4444 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 144 | 15167448 | 6266 | 150.384 | 6.266 | 5 | 5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49676536 | 1204 | 192.1481 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 139 | 15173504 | 6056 | 145.344 | 6.056 | 4.5 | 4.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49677708 | 1172 | 193.5271 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 15179822 | 6318 | 151.632 | 6.318 | 4 | 4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49678888 | 1180 | 186.768 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 138 | 15185922 | 6100 | 146.4 | 6.1 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49680068 | 1180 | 193.4426 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 139 | 15191918 | 5996 | 143.904 | 5.996 | 3.2 | 3.2 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49681242 | 1174 | 195.7972 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 137 | 134 | 15197328 | 5410 | 129.84 | 5.41 | 3 | 3 | 3B+1S | 1013 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49682400 | 1158 | 214.0481 | 100% | 0% | 100% | 100% | 100% | 0% | 11199918 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 126 | 15202795 | 5467 | 131.208 | 5.467 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49683432 | 1032 | 188.769 | 0% | 0% | 100% | 100% | 100% | 20% | 11199959 | 41 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 121 | 15207966 | 5171 | 124.104 | 5.171 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49684503 | 1071 | 207.1166 | 0% | 0% | 100% | 100% | 100% | 20% | 11200421 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136562 | 136.562 | 136.562 | [12 empty] | 26559 | 26559 | 194.4831 | [6 empty] | 2292 | 2292 | 1.055 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 8:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## AUG 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27010 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15207966 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49684503 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11200421 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 141 | 112 | 15212300 | 4334 | 104.016 | 4.334 | 6.1 | 6.1 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49685349 | 846 | 195.2007 | 0% | 0% | 100% | 100% | 100% | 70% | 11201088 | 667 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 105 | 15216710 | 4410 | 105.84 | 4.41 | 7.3 | 7.3 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49686215 | 866 | 196.3719 | 0% | 0% | 100% | 100% | 100% | 70% | 11201688 | 600 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 107 | 15221198 | 4488 | 107.712 | 4.488 | 8.5 | 8.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 49687174 | 959 | 213.6809 | 0% | 0% | 100% | 100% | 100% | 70% | 11202338 | 650 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 135 | 112 | 15225898 | 4700 | 112.8 | 4.7 | 9.3 | 9.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49688175 | 1001 | 212.9787 | 0% | 0% | 100% | 100% | 100% | 70% | 11202998 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 126 | 15230688 | 4790 | 114.96 | 4.79 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49689201 | 1026 | 214.1962 | 0% | 0% | 100% | 100% | 100% | 70% | 11203190 | 192 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 136 | 15236407 | 5719 | 137.256 | 5.719 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49690304 | 1103 | 192.8659 | 0% | 0% | 100% | 100% | 100% | 0% | 11203190 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 140 | 15242626 | 6219 | 149.256 | 6.219 | 9 | 9 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49691600 | 1296 | 208.3936 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 15248919 | 6293 | 151.032 | 6.293 | 8.6 | 8.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49692766 | 1166 | 185.2852 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 142 | 15254927 | 6008 | 144.192 | 6.008 | 8.2 | 8.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49693942 | 1176 | 195.739 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 15261020 | 6093 | 146.232 | 6.093 | 7.8 | 7.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49695137 | 1195 | 196.1267 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 | 1.17
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 146 | 15267317 | 6297 | 151.128 | 6.297 | 7.4 | 7.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49696321 | 1184 | 188.026 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 15273586 | 6269 | 150.456 | 6.269 | 6.8 | 6.8 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49697526 | 1205 | 192.2157 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 134 | 15279932 | 6346 | 152.304 | 6.346 | 6.3 | 6.3 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49698724 | 1198 | 188.7803 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 141 | 15286084 | 6152 | 147.648 | 6.152 | 5.7 | 5.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49699914 | 1190 | 193.433 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 15291976 | 5892 | 141.408 | 5.892 | 5.3 | 5.3 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49701080 | 1166 | 197.8955 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 15298202 | 6226 | 149.424 | 6.226 | 4.9 | 4.9 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49702254 | 1174 | 188.5641 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 15304344 | 6142 | 147.408 | 6.142 | 4.5 | 4.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49703446 | 1192 | 194.0736 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 15310418 | 6074 | 145.776 | 6.074 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49704634 | 1188 | 195.5878 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 | 1.38 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 142 | 15316506 | 6088 | 146.112 | 6.088 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49705798 | 1164 | 191.1958 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 140 | 15322744 | 6238 | 149.712 | 6.238 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49706980 | 1182 | 189.4838 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 142 | 15328660 | 5916 | 141.984 | 5.916 | 2.9 | 2.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49708156 | 1176 | 198.783 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 147 | 138 | 15334602 | 5942 | 142.608 | 5.942 | 2.8 | 2.8 | 3B+1S | 0 | 1030 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49709343 | 1187 | 199.7644 | 0% | 100% | 100% | 100% | 100% | 0% | 11203190 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 126 | 15339926 | 5324 | 127.776 | 5.324 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49710426 | 1083 | 203.4185 | 0% | 0% | 100% | 100% | 100% | 45% | 11203314 | 124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 127 | 15345223 | 5297 | 127.128 | 5.297 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49711513 | 1087 | 205.2105 | 0% | 0% | 100% | 100% | 100% | 45% | 11203487 | 173 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 137257 | 137.257 | 137.257 | [12 empty] | 27010 | 27010 | 196.7841 | [6 empty] | 3066 | 3066 | 1.1833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (45%)

## AUG 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | ANDRO MIRAFLOR
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-08-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26967 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15345223 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49711513 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11203487 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 132 | 114 | 15349698 | 4475 | 107.4 | 4.475 | 4.8 | 4.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49712344 | 831 | 185.6983 | 0% | 0% | 100% | 100% | 100% | 65% | 11203927 | 440 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 105 | 15354075 | 4377 | 105.048 | 4.377 | 5.7 | 5.7 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49713223 | 879 | 200.8225 | 0% | 0% | 100% | 100% | 100% | 65% | 11204514 | 587 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 108 | 15358354 | 4279 | 102.696 | 4.279 | 6.9 | 6.9 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49714000 | 777 | 181.5845 | 0% | 0% | 100% | 100% | 100% | 65% | 11205169 | 655 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 132 | 114 | 15363124 | 4770 | 114.48 | 4.77 | 8.8 | 8.8 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 49715115 | 1115 | 233.7526 | 0% | 0% | 100% | 100% | 100% | 65% | 11205871 | 702 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 117 | 15367899 | 4775 | 114.6 | 4.775 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49716239 | 1124 | 235.3927 | 0% | 0% | 100% | 100% | 100% | 65% | 11206237 | 366 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 125 | 15373490 | 5591 | 134.184 | 5.591 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49717353 | 1114 | 199.2488 | 0% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 142 | 15379491 | 6001 | 144.024 | 6.001 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49718543 | 1190 | 198.3003 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 144 | 15385575 | 6084 | 146.016 | 6.084 | 8.4 | 8.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49719742 | 1199 | 197.0743 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 144 | 15391832 | 6257 | 150.168 | 6.257 | 7.9 | 7.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49720943 | 1201 | 191.945 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 146 | 15398225 | 6393 | 153.432 | 6.393 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49722152 | 1209 | 189.1131 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 | 1.19
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 15404599 | 6374 | 152.976 | 6.374 | 6.7 | 6.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49723359 | 1207 | 189.363 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 15410744 | 6145 | 147.48 | 6.145 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49724556 | 1197 | 194.7925 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 140 | 15416654 | 5910 | 141.84 | 5.91 | 5.6 | 5.6 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49725746 | 1190 | 201.3536 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 131 | 15422786 | 6132 | 147.168 | 6.132 | 5.2 | 5.2 | 3B+1S | 1045 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49726950 | 1204 | 196.347 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 140 | 15428352 | 5566 | 133.584 | 5.566 | 4.8 | 4.8 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49728070 | 1120 | 201.2217 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 141 | 15434356 | 6004 | 144.096 | 6.004 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49729252 | 1182 | 196.8688 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 137 | 15440222 | 5866 | 140.784 | 5.866 | 4.1 | 4.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49730434 | 1182 | 201.5002 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 15446306 | 6084 | 146.016 | 6.084 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49731618 | 1184 | 194.6088 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 139 | 15452422 | 6116 | 146.784 | 6.116 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49732796 | 1178 | 192.6095 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 137 | 15458662 | 6240 | 149.76 | 6.24 | 3.1 | 3.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49734032 | 1236 | 198.0769 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 135 | 15464302 | 5640 | 135.36 | 5.64 | 2.8 | 2.8 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49735136 | 1104 | 195.7447 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 133 | 15470266 | 5964 | 143.136 | 5.964 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49736322 | 1186 | 198.8598 | 100% | 0% | 100% | 100% | 100% | 0% | 11206237 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 127 | 15475631 | 5365 | 128.76 | 5.365 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49737403 | 1081 | 201.4911 | 0% | 0% | 100% | 100% | 100% | 45% | 11206296 | 59 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 124 | 15480824 | 5193 | 124.632 | 5.193 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49738480 | 1077 | 207.3946 | 0% | 0% | 100% | 100% | 100% | 45% | 11206521 | 225 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135601 | 135.601 | 135.601 | [12 empty] | 26967 | 26967 | 198.8702 | [6 empty] | 3034 | 3034 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:00 AM TO 3:00 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (AUG 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 5:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (45%)